## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1201-42_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1201-42_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1201-42_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1201-42_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1201-42_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1201-42_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1201-42_0_4_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_1201-42_0_4_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_1201-42_0_4_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_1201-42_0_4_node_38 | 0.4 | n |  | TRUE
10 | bus_LV_1201-42_0_4_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_1201-42_0_4_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_1201-42_0_4_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_1201-42_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1201-42_0_4_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_1201-42_0_4_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_1201-42_0_4_node_24 | 0.4 | n |  | TRUE
17 | bus_LV_1201-42_0_4_node_26 | 0.4 | n |  | TRUE
18 | bus_LV_1201-42_0_4_node_36 | 0.4 | n |  | TRUE
19 | bus_LV_1201-42_0_4_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_1201-42_0_4_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_1201-42_0_4_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_1201-42_0_4_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_1201-42_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1201-42_0_4_node_32 | 0.4 | n |  | TRUE
25 | bus_LV_1201-42_0_4_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_1201-42_0_4_node_37 | 0.4 | n |  | TRUE
27 | bus_LV_1201-42_0_4_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_1201-42_0_4_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_1201-42_0_4_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_1201-42_0_4_node_33 | 0.4 | n |  | TRUE
31 | bus_MV_14_0_node_139 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1201-42_0_4_load_0 | 0 | 0.015056 | 0.0037734 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1201-42_0_4_load_5 | 5 | 0.015672 | 0.0039278 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1201-42_0_4_load_16 | 6 | 0.019463 | 0.0048779 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1201-42_0_4_load_13 | 7 | 0.009029 | 0.0022629 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1201-42_0_4_load_38 | 9 | 0.02458 | 0.0061603 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1201-42_0_4_load_14 | 11 | 0.0099398 | 0.0024911 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1201-42_0_4_load_8 | 13 | 0.029785 | 0.0074649 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1201-42_0_4_load_15 | 14 | 0.01164 | 0.0029173 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1201-42_0_4_load_23 | 15 | 0.012393 | 0.003106 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1201-42_0_4_load_26 | 17 | 0.0092871 | 0.0023276 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1201-42_0_4_load_36 | 18 | 0.032468 | 0.0081373 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1201-42_0_4_load_17 | 19 | 0.026114 | 0.0065447 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1201-42_0_4_load_21 | 21 | 0.021851 | 0.0054763 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1201-42_0_4_load_32 | 24 | 0.0033254 | 0.00083343 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1201-42_0_4_load_37 | 26 | 0.011502 | 0.0028828 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1201-42_0_4_load_31 | 27 | 0.030537 | 0.0076533 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1201-42_0_4_load_29 | 29 | 0.04651 | 0.011656 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1201-42_0_4_load_33 | 30 | 0.0077979 | 0.0019543 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1201-42_0_4_line_0 |  | 0 | 1 | 0.012686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1201-42_0_4_line_1 |  | 0 | 2 | 0.021083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1201-42_0_4_line_2 |  | 1 | 3 | 0.013632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1201-42_0_4_line_3 |  | 1 | 4 | 0.010425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1201-42_0_4_line_4 |  | 2 | 5 | 0.019559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1201-42_0_4_line_5 |  | 3 | 6 | 0.019188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1201-42_0_4_line_6 |  | 3 | 7 | 0.0082393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1201-42_0_4_line_7 |  | 4 | 8 | 0.009141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1201-42_0_4_line_8 |  | 4 | 9 | 0.014846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1201-42_0_4_line_9 |  | 6 | 10 | 0.0078779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1201-42_0_4_line_10 |  | 7 | 11 | 0.018284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1201-42_0_4_line_11 |  | 8 | 12 | 0.008439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1201-42_0_4_line_12 |  | 8 | 13 | 0.020496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1201-42_0_4_line_13 |  | 10 | 18 | 0.023116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1201-42_0_4_line_14 |  | 11 | 14 | 0.0088472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1201-42_0_4_line_15 |  | 12 | 15 | 0.015033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1201-42_0_4_line_16 |  | 15 | 16 | 0.014108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1201-42_0_4_line_17 |  | 16 | 17 | 0.03739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1201-42_0_4_line_18 |  | 18 | 28 | 0.00078833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1201-42_0_4_line_19 |  | 19 | 20 | 0.041666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1201-42_0_4_line_20 |  | 20 | 21 | 0.017591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1201-42_0_4_line_21 |  | 20 | 22 | 0.017975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1201-42_0_4_line_22 |  | 21 | 25 | 0.012772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1201-42_0_4_line_23 |  | 22 | 26 | 0.0070126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1201-42_0_4_line_24 |  | 22 | 23 | 0.031662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1201-42_0_4_line_25 |  | 23 | 24 | 0.0090934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1201-42_0_4_line_26 |  | 24 | 27 | 0.041869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1201-42_0_4_line_27 |  | 25 | 28 | 0.019914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_1201-42_0_4_line_28 |  | 25 | 29 | 0.019221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1201-42_0_4_line_29 |  | 27 | 30 | 0.030069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1201-42_0_4_trafo_35 | 0.63 MVA 20/0.4 kV | 31 | 10 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2691799.2955 | 1193028.6988 | 2691806.2444 | 1193039.3127
1 | 2691819.1936 | 1193055.9216 | 2691809.0234 | 1193043.5576 | 2691806.2444 | 1193039.3127
2 | 2691799.2955 | 1193028.6988 | 2691788.1884 | 1193036.6446
3 | 2691799.2955 | 1193028.6988 | 2691808.1475 | 1193023.1532
4 | 2691819.1936 | 1193055.9216 | 2691831.6109 | 1193071.0333
5 | 2691788.1884 | 1193036.6446 | 2691775.4897 | 1193024.1196 | 2691774.4307 | 1193023.2793
6 | 2691788.1884 | 1193036.6446 | 2691782.2319 | 1193042.3373
7 | 2691808.1475 | 1193023.1532 | 2691816.0923 | 1193018.5944
8 | 2691808.1475 | 1193023.1532 | 2691800.0381 | 1193010.7177
9 | 2691768.2594 | 1193018.3828 | 2691774.4307 | 1193023.2793
10 | 2691782.2319 | 1193042.3373 | 2691775.9257 | 1193048.3641 | 2691769.0179 | 1193054.9748
11 | 2691823.563 | 1193014.6287 | 2691819.7893 | 1193016.6277 | 2691816.0923 | 1193018.5944
12 | 2691816.0923 | 1193018.5944 | 2691828.5781 | 1193034.849
13 | 2691768.2594 | 1193018.3828 | 2691751.2043 | 1193002.7786
14 | 2691762.626 | 1193061.0917 | 2691769.0179 | 1193054.9748
15 | 2691823.563 | 1193014.6287 | 2691815.0462 | 1193002.2408
16 | 2691807.0537 | 1192990.6155 | 2691815.0462 | 1193002.2408
17 | 2691807.0537 | 1192990.6155 | 2691817.4818 | 1192983.7044 | 2691805.0281 | 1192962.1662
18 | 2691750.6227 | 1193002.2464 | 2691751.2043 | 1193002.7786
19 | 2691741.0312 | 1192968.0441 | 2691744.9786 | 1192963.6685 | 2691753.8583 | 1192953.8316 | 2691737.5711 | 1192938.2783
20 | 2691741.0312 | 1192968.0441 | 2691754.4604 | 1192979.4069
21 | 2691728.972 | 1192981.4011 | 2691741.0312 | 1192968.0441
22 | 2691764.2102 | 1192987.6565 | 2691754.4604 | 1192979.4069
23 | 2691728.972 | 1192981.4011 | 2691734.0238 | 1192986.265
24 | 2691705.5066 | 1192960.0723 | 2691728.972 | 1192981.4011
25 | 2691705.5066 | 1192960.0723 | 2691699.2921 | 1192966.7108
26 | 2691699.2921 | 1192966.7108 | 2691687.3244 | 1192979.495 | 2691701.1738 | 1192999.5312 | 2691701.1738 | 1192999.5312
27 | 2691764.2102 | 1192987.6565 | 2691750.6227 | 1193002.2464
28 | 2691764.2102 | 1192987.6565 | 2691772.7869 | 1192970.455
29 | 2691711.6345 | 1193025.7086 | 2691708.0787 | 1193019.0384 | 2691699.06 | 1193002.156 | 2691701.1738 | 1192999.5312

## bus_geodata
| x | y | coords
0 | 2691806.2444 | 1193039.3127
1 | 2691799.2955 | 1193028.6988
2 | 2691819.1936 | 1193055.9216
3 | 2691788.1884 | 1193036.6446
4 | 2691808.1475 | 1193023.1532
5 | 2691831.6109 | 1193071.0333
6 | 2691774.4307 | 1193023.2793
7 | 2691782.2319 | 1193042.3373
8 | 2691816.0923 | 1193018.5944
9 | 2691800.0381 | 1193010.7177
10 | 2691768.2594 | 1193018.3828
11 | 2691769.0179 | 1193054.9748
12 | 2691823.563 | 1193014.6287
13 | 2691828.5781 | 1193034.849
14 | 2691762.626 | 1193061.0917
15 | 2691815.0462 | 1193002.2408
16 | 2691807.0537 | 1192990.6156
17 | 2691805.0281 | 1192962.1662
18 | 2691751.2043 | 1193002.7786
19 | 2691737.5711 | 1192938.2783
20 | 2691741.0312 | 1192968.0441
21 | 2691754.4604 | 1192979.4069
22 | 2691728.972 | 1192981.4011
23 | 2691705.5066 | 1192960.0723
24 | 2691699.2921 | 1192966.7108
25 | 2691764.2102 | 1192987.6565
26 | 2691734.0238 | 1192986.265
27 | 2691701.1738 | 1192999.5312
28 | 2691750.6227 | 1193002.2464
29 | 2691772.7869 | 1192970.455
30 | 2691711.6345 | 1193025.7086
31 | 2691750.6227 | 1193002.2464

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99535 | -0.089298 | 0.015056 | 0.0037734
1 | 0.99571 | -0.082442 | 0 | 0
2 | 0.99505 | -0.095113 | 0 | 0
3 | 0.99703 | -0.056886 | 0 | 0
4 | 0.99498 | -0.09639 | 0 | 0
5 | 0.99477 | -0.10051 | 0.015672 | 0.0039278
6 | 0.99944 | -0.010775 | 0.019463 | 0.0048779
7 | 0.9968 | -0.061309 | 0.009029 | 0.0022629
8 | 0.99455 | -0.10468 | 0 | 0
9 | 0.99465 | -0.10282 | 0.02458 | 0.0061603
10 | 1 | 0 | -0.34018 | -0.085451
11 | 0.99645 | -0.068233 | 0.0099398 | 0.0024911
12 | 0.99439 | -0.1079 | 0 | 0
13 | 0.994 | -0.11544 | 0.029785 | 0.0074649
14 | 0.99635 | -0.070041 | 0.01164 | 0.0029173
15 | 0.99409 | -0.11365 | 0.012393 | 0.003106
16 | 0.99397 | -0.11596 | 0 | 0
17 | 0.99365 | -0.12209 | 0.0092871 | 0.0023276
18 | 0.9981 | -0.036354 | 0.032468 | 0.0081373
19 | 0.99326 | -0.12958 | 0.026114 | 0.0065447
20 | 0.99425 | -0.11038 | 0 | 0
21 | 0.99553 | -0.085818 | 0.021851 | 0.0054763
22 | 0.99338 | -0.12724 | 0 | 0
23 | 0.99217 | -0.15057 | 0 | 0
24 | 0.99182 | -0.15728 | 0.0033254 | 0.00083343
25 | 0.99671 | -0.06313 | 0 | 0
26 | 0.9933 | -0.12867 | 0.011502 | 0.0028828
27 | 0.99035 | -0.18576 | 0.030537 | 0.0076533
28 | 0.99805 | -0.037372 | 0 | 0
29 | 0.99589 | -0.078827 | 0.04651 | 0.011656
30 | 0.99014 | -0.18993 | 0.0077979 | 0.0019543
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.030737 | -0.0077061 | 0.030747 | 0.0077124 | 1.0045e-05 | 6.264e-06 | 0.045951 | 0.045951 | 0.045951 | 0.99535 | -0.089298 | 0.99571 | -0.082442 | 12.624
1 | 0.015681 | 0.0039327 | -0.015676 | -0.0039302 | 4.345e-06 | 2.5069e-06 | 0.023443 | 0.023443 | 0.023443 | 0.99535 | -0.089298 | 0.99505 | -0.095113 | 6.4404
2 | -0.1069 | -0.026838 | 0.10703 | 0.026921 | 0.00013049 | 8.3337e-05 | 0.15977 | 0.15977 | 0.15977 | 0.99571 | -0.082442 | 0.99703 | -0.056886 | 43.8928
3 | 0.076152 | 0.019125 | -0.076102 | -0.019093 | 5.0645e-05 | 3.2277e-05 | 0.11382 | 0.11382 | 0.11382 | 0.99571 | -0.082442 | 0.99498 | -0.09639 | 31.2688
4 | 0.015676 | 0.0039302 | -0.015672 | -0.0039278 | 4.031e-06 | 2.3258e-06 | 0.023443 | 0.023443 | 0.023443 | 0.99505 | -0.095113 | 0.99477 | -0.10051 | 6.4404
5 | -0.13765 | -0.034601 | 0.13796 | 0.034796 | 0.0003038 | 0.00019418 | 0.20548 | 0.20548 | 0.20548 | 0.99703 | -0.056886 | 0.99944 | -0.010775 | 56.4493
6 | 0.030623 | 0.0076802 | -0.030617 | -0.0076762 | 6.4545e-06 | 4.0234e-06 | 0.045706 | 0.045706 | 0.045706 | 0.99703 | -0.056886 | 0.9968 | -0.061309 | 12.5565
7 | 0.051514 | 0.012928 | -0.051494 | -0.012915 | 2.0348e-05 | 1.2904e-05 | 0.077046 | 0.077046 | 0.077046 | 0.99498 | -0.09639 | 0.99455 | -0.10468 | 21.1666
8 | 0.024588 | 0.006165 | -0.02458 | -0.0061603 | 7.528e-06 | 4.6252e-06 | 0.036772 | 0.036772 | 0.036772 | 0.99498 | -0.09639 | 0.99465 | -0.10282 | 10.1023
9 | -0.15742 | -0.039673 | 0.1575 | 0.039725 | 8.1194e-05 | 5.1757e-05 | 0.23445 | 0.23445 | 0.23445 | 0.99944 | -0.010775 | 1 | 0 | 32.2051
10 | 0.021588 | 0.0054133 | -0.021581 | -0.005409 | 7.1213e-06 | 4.3194e-06 | 0.032227 | 0.032227 | 0.032227 | 0.9968 | -0.061309 | 0.99645 | -0.068233 | 8.8537
11 | 0.021693 | 0.0054409 | -0.02169 | -0.0054389 | 3.334e-06 | 2.0243e-06 | 0.032458 | 0.032458 | 0.032458 | 0.99455 | -0.10468 | 0.99439 | -0.1079 | 8.9171
12 | 0.0298 | 0.0074744 | -0.029785 | -0.0074649 | 1.5281e-05 | 9.5141e-06 | 0.044588 | 0.044588 | 0.044588 | 0.99455 | -0.10468 | 0.994 | -0.11544 | 12.2496
13 | 0.18103 | 0.045726 | -0.18071 | -0.045525 | 0.0003148 | 0.00020087 | 0.2695 | 0.2695 | 0.2695 | 1 | 0 | 0.9981 | -0.036354 | 37.0192
14 | 0.011641 | 0.0029178 | -0.01164 | -0.0029173 | 1.0026e-06 | 5.2645e-07 | 0.017384 | 0.017384 | 0.017384 | 0.99645 | -0.068233 | 0.99635 | -0.070041 | 4.7758
15 | 0.02169 | 0.0054389 | -0.021684 | -0.0054353 | 5.9392e-06 | 3.6061e-06 | 0.032458 | 0.032458 | 0.032458 | 0.99439 | -0.1079 | 0.99409 | -0.11365 | 8.9171
16 | 0.0092908 | 0.0023293 | -0.0092898 | -0.0023288 | 1.0232e-06 | 4.7199e-07 | 0.013907 | 0.013907 | 0.013907 | 0.99409 | -0.11365 | 0.99397 | -0.11596 | 3.8207
17 | 0.0092898 | 0.0023288 | -0.0092871 | -0.0023276 | 2.7119e-06 | 1.2512e-06 | 0.013907 | 0.013908 | 0.013908 | 0.99397 | -0.11596 | 0.99365 | -0.12209 | 3.8208
18 | 0.14825 | 0.037388 | -0.14824 | -0.037383 | 7.2255e-06 | 4.6037e-06 | 0.22109 | 0.22109 | 0.22109 | 0.9981 | -0.036354 | 0.99805 | -0.037372 | 30.3701
19 | -0.026114 | -0.0065447 | 0.026138 | 0.0065595 | 2.3913e-05 | 1.4764e-05 | 0.039121 | 0.039121 | 0.039121 | 0.99326 | -0.12958 | 0.99425 | -0.11038 | 10.7476
20 | -0.079457 | -0.019982 | 0.079551 | 0.020042 | 9.3325e-05 | 5.95e-05 | 0.11894 | 0.11894 | 0.11894 | 0.99425 | -0.11038 | 0.99553 | -0.085818 | 32.6763
21 | 0.05332 | 0.013423 | -0.053277 | -0.013395 | 4.2947e-05 | 2.7253e-05 | 0.079821 | 0.079821 | 0.079821 | 0.99425 | -0.11038 | 0.99338 | -0.12724 | 21.9288
22 | -0.1014 | -0.025518 | 0.10151 | 0.025588 | 0.00011007 | 7.0281e-05 | 0.1516 | 0.1516 | 0.1516 | 0.99553 | -0.085818 | 0.99671 | -0.06313 | 41.6488
23 | 0.011503 | 0.0028832 | -0.011502 | -0.0028828 | 7.808e-07 | 4.0893e-07 | 0.017231 | 0.017231 | 0.017231 | 0.99338 | -0.12724 | 0.9933 | -0.12867 | 4.7338
24 | 0.041774 | 0.010512 | -0.041727 | -0.010483 | 4.6513e-05 | 2.9359e-05 | 0.06259 | 0.06259 | 0.06259 | 0.99338 | -0.12724 | 0.99217 | -0.15057 | 17.195
25 | 0.041727 | 0.010483 | -0.041714 | -0.010474 | 1.3359e-05 | 8.4322e-06 | 0.06259 | 0.06259 | 0.06259 | 0.99217 | -0.15057 | 0.99182 | -0.15728 | 17.195
26 | 0.038388 | 0.009641 | -0.038336 | -0.0096082 | 5.2093e-05 | 3.28e-05 | 0.057601 | 0.057601 | 0.057601 | 0.99182 | -0.15728 | 0.99035 | -0.18576 | 15.8244
27 | -0.14806 | -0.037267 | 0.14824 | 0.037383 | 0.00018252 | 0.00011629 | 0.22109 | 0.22109 | 0.22109 | 0.99671 | -0.06313 | 0.99805 | -0.037372 | 30.3701
28 | 0.046545 | 0.011679 | -0.04651 | -0.011656 | 3.4809e-05 | 2.2027e-05 | 0.069493 | 0.069493 | 0.069493 | 0.99671 | -0.06313 | 0.99589 | -0.078827 | 19.0915
29 | 0.0077995 | 0.0019549 | -0.0077979 | -0.0019543 | 1.5486e-06 | 6.0426e-07 | 0.011719 | 0.011719 | 0.011719 | 0.99035 | -0.18576 | 0.99014 | -0.18993 | 3.2195

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.34018 | 0.085451

## res_load
| p_mw | q_mvar
0 | 0.015056 | 0.0037734
1 | 0.015672 | 0.0039278
2 | 0.019463 | 0.0048779
3 | 0.009029 | 0.0022629
4 | 0.02458 | 0.0061603
5 | 0.0099398 | 0.0024911
6 | 0.029785 | 0.0074649
7 | 0.01164 | 0.0029173
8 | 0.012393 | 0.003106
9 | 0.0092871 | 0.0023276
10 | 0.032468 | 0.0081373
11 | 0.026114 | 0.0065447
12 | 0.021851 | 0.0054763
13 | 0.0033254 | 0.00083343
14 | 0.011502 | 0.0028828
15 | 0.030537 | 0.0076533
16 | 0.04651 | 0.011656
17 | 0.0077979 | 0.0019543

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1