## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1201-7_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1201-7_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1201-7_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1201-7_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1201-7_0_4_node_32 | 0.4 | n |  | TRUE
5 | bus_LV_1201-7_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1201-7_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1201-7_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1201-7_0_4_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_1201-7_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1201-7_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1201-7_0_4_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_1201-7_0_4_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_1201-7_0_4_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_1201-7_0_4_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_1201-7_0_4_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_1201-7_0_4_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1201-7_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1201-7_0_4_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_1201-7_0_4_node_28 | 0.4 | n |  | TRUE
20 | bus_LV_1201-7_0_4_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1201-7_0_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_1201-7_0_4_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_1201-7_0_4_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1201-7_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1201-7_0_4_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_1201-7_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_1201-7_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_1201-7_0_4_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_1201-7_0_4_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_1201-7_0_4_node_31 | 0.4 | n |  | TRUE
31 | bus_MV_11_0_node_63 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1201-7_0_4_load_0 | 0 | 0.0347 | 0.0086967 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1201-7_0_4_load_1 | 1 | 0.0093163 | 0.0023349 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1201-7_0_4_load_3 | 3 | 0.043032 | 0.010785 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1201-7_0_4_load_32 | 4 | 0.044588 | 0.011175 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1201-7_0_4_load_5 | 5 | 0.0096701 | 0.0024235 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1201-7_0_4_load_6 | 6 | 0.0027844 | 0.00069783 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1201-7_0_4_load_7 | 7 | 0.0028081 | 0.00070378 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1201-7_0_4_load_10 | 8 | 0.0029035 | 0.00072769 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1201-7_0_4_load_8 | 9 | 0.042454 | 0.01064 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1201-7_0_4_load_9 | 10 | 0.0027851 | 0.00069802 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1201-7_0_4_load_11 | 11 | 0.0028057 | 0.00070317 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1201-7_0_4_load_14 | 12 | 0.0029016 | 0.00072721 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1201-7_0_4_load_12 | 13 | 0.058733 | 0.01472 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1201-7_0_4_load_26 | 14 | 0.0065638 | 0.001645 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1201-7_0_4_load_22 | 15 | 0.0042163 | 0.0010567 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1201-7_0_4_load_13 | 16 | 0.0028465 | 0.0007134 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1201-7_0_4_load_27 | 18 | 0.016945 | 0.0042469 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1201-7_0_4_load_20 | 20 | 0.0029472 | 0.00073863 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1201-7_0_4_load_19 | 21 | 0.020202 | 0.0050632 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1201-7_0_4_load_29 | 22 | 0.0015225 | 0.00038158 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1201-7_0_4_load_21 | 23 | 0.00041898 | 0.00010501 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1201-7_0_4_load_24 | 24 | 0.0070798 | 0.0017744 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1201-7_0_4_load_16 | 26 | 0.043018 | 0.010781 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1201-7_0_4_load_30 | 29 | 0.0012419 | 0.00031124 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1201-7_0_4_load_31 | 30 | 0.0011866 | 0.0002974 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1201-7_0_4_line_0 |  | 0 | 1 | 0.030232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1201-7_0_4_line_1 |  | 0 | 2 | 0.029551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1201-7_0_4_line_2 |  | 1 | 3 | 0.0041356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1201-7_0_4_line_3 |  | 2 | 4 | 0.095696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1201-7_0_4_line_4 |  | 3 | 5 | 0.0048384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1201-7_0_4_line_5 |  | 5 | 6 | 0.027016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1201-7_0_4_line_6 |  | 6 | 7 | 0.0082315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1201-7_0_4_line_7 |  | 7 | 8 | 0.0084498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1201-7_0_4_line_8 |  | 8 | 9 | 0.0075015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1201-7_0_4_line_9 |  | 9 | 10 | 0.017517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1201-7_0_4_line_10 |  | 10 | 11 | 0.008459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1201-7_0_4_line_11 |  | 11 | 12 | 0.0080887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1201-7_0_4_line_12 |  | 12 | 13 | 0.027128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1201-7_0_4_line_13 |  | 13 | 16 | 0.042919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1201-7_0_4_line_14 |  | 14 | 15 | 0.080342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1201-7_0_4_line_15 |  | 15 | 20 | 0.039566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1201-7_0_4_line_16 |  | 15 | 16 | 0.098437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1201-7_0_4_line_17 |  | 16 | 17 | 0.0011352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1201-7_0_4_line_18 |  | 17 | 18 | 0.017764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1201-7_0_4_line_19 |  | 17 | 19 | 0.052555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1201-7_0_4_line_20 |  | 18 | 21 | 0.020172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1201-7_0_4_line_21 |  | 19 | 22 | 0.015258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1201-7_0_4_line_22 |  | 20 | 23 | 0.039852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1201-7_0_4_line_23 |  | 21 | 27 | 0.021888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1201-7_0_4_line_24 |  | 22 | 29 | 0.017724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1201-7_0_4_line_25 |  | 23 | 28 | 0.02133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1201-7_0_4_line_26 |  | 24 | 25 | 0.05575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1201-7_0_4_line_27 |  | 25 | 28 | 0.031736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1201-7_0_4_line_28 |  | 26 | 27 | 0.038347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1201-7_0_4_line_29 |  | 29 | 30 | 0.0062437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1201-7_0_4_trafo_8 | 0.63 MVA 20/0.4 kV | 31 | 9 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2691075.2036 | 1191935.3319 | 2691076.8202 | 1191913.4124 | 2691077.4275 | 1191905.1823
1 | 2691072.9727 | 1191964.7979 | 2691073.294 | 1191961.2227 | 2691075.2036 | 1191935.3319
2 | 2691077.7317 | 1191901.0579 | 2691077.4275 | 1191905.1823
3 | 2691072.9727 | 1191964.7979 | 2691168.5086 | 1191970.3336
4 | 2691078.0878 | 1191896.2326 | 2691077.7317 | 1191901.0579
5 | 2691078.0878 | 1191896.2326 | 2691078.7802 | 1191886.8475 | 2691080.6555 | 1191869.3426
6 | 2691080.6555 | 1191869.3426 | 2691080.6555 | 1191869.3426 | 2691082.6241 | 1191861.35
7 | 2691084.6449 | 1191853.1454 | 2691082.6241 | 1191861.35
8 | 2691084.6449 | 1191853.1454 | 2691086.4389 | 1191845.8615
9 | 2691090.6282 | 1191828.8526 | 2691086.4389 | 1191845.8615
10 | 2691090.6282 | 1191828.8526 | 2691092.6512 | 1191820.6391
11 | 2691094.5856 | 1191812.7852 | 2691092.6512 | 1191820.6391
12 | 2691094.5856 | 1191812.7852 | 2691100.5323 | 1191786.3171
13 | 2691100.5323 | 1191786.3171 | 2691103.7792 | 1191771.8656 | 2691104.5825 | 1191744.6493 | 2691104.7322 | 1191743.7831
14 | 2691007.7408 | 1191726.9759 | 2690955.724 | 1191788.2062
15 | 2691007.7408 | 1191726.9759 | 2691017.5293 | 1191688.6394
16 | 2691104.7322 | 1191743.7831 | 2691007.7408 | 1191726.9759
17 | 2691104.9254 | 1191742.6644 | 2691104.7322 | 1191743.7831
18 | 2691104.9254 | 1191742.6644 | 2691122.0996 | 1191747.2047
19 | 2691121.7159 | 1191695.0785 | 2691112.4916 | 1191702.9653 | 2691110.2991 | 1191711.7486 | 2691104.9254 | 1191742.6644
20 | 2691141.6021 | 1191752.3604 | 2691122.0996 | 1191747.2047
21 | 2691121.7159 | 1191695.0785 | 2691125.9524 | 1191680.4206
22 | 2691027.3885 | 1191650.026 | 2691017.5293 | 1191688.6394
23 | 2691162.7636 | 1191757.9548 | 2691141.6021 | 1191752.3604
24 | 2691125.9524 | 1191680.4206 | 2691130.8736 | 1191663.3937
25 | 2691032.6653 | 1191629.3593 | 2691027.3885 | 1191650.026
26 | 2691001.8839 | 1191621.286 | 2690988.813 | 1191675.4821
27 | 2691032.6653 | 1191629.3593 | 2691001.8839 | 1191621.286
28 | 2691162.7636 | 1191757.9548 | 2691157.7696 | 1191778.9477 | 2691156.9793 | 1191782.2711 | 2691167.1941 | 1191784.9395 | 2691169.8985 | 1191785.6448
29 | 2691130.8736 | 1191663.3937 | 2691132.6072 | 1191657.3955

## bus_geodata
| x | y | coords
0 | 2691075.2036 | 1191935.3319
1 | 2691077.4275 | 1191905.1823
2 | 2691072.9727 | 1191964.7979
3 | 2691077.7317 | 1191901.0579
4 | 2691168.5086 | 1191970.3336
5 | 2691078.0878 | 1191896.2326
6 | 2691080.6555 | 1191869.3426
7 | 2691082.6241 | 1191861.35
8 | 2691084.6449 | 1191853.1454
9 | 2691086.4389 | 1191845.8615
10 | 2691090.6282 | 1191828.8526
11 | 2691092.6512 | 1191820.6391
12 | 2691094.5856 | 1191812.7852
13 | 2691100.5323 | 1191786.3171
14 | 2690955.724 | 1191788.2062
15 | 2691007.7408 | 1191726.9759
16 | 2691104.7322 | 1191743.7831
17 | 2691104.9254 | 1191742.6644
18 | 2691122.0996 | 1191747.2047
19 | 2691121.7159 | 1191695.0785
20 | 2691017.5293 | 1191688.6394
21 | 2691141.6021 | 1191752.3604
22 | 2691125.9524 | 1191680.4206
23 | 2691027.3885 | 1191650.026
24 | 2690988.813 | 1191675.4821
25 | 2691001.8839 | 1191621.286
26 | 2691169.8985 | 1191785.6448
27 | 2691162.7636 | 1191757.9548
28 | 2691032.6653 | 1191629.3593
29 | 2691130.8736 | 1191663.3937
30 | 2691132.6072 | 1191657.3955
31 | 2691094.5856 | 1191812.7852

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99352 | -0.12429 | 0.0347 | 0.0086967
1 | 0.99572 | -0.082059 | 0.0093163 | 0.0023349
2 | 0.99231 | -0.14759 | 0 | 0
3 | 0.99605 | -0.075619 | 0.043032 | 0.010785
4 | 0.9884 | -0.22342 | 0.044588 | 0.011175
5 | 0.99663 | -0.064435 | 0.0096701 | 0.0024235
6 | 0.99838 | -0.030999 | 0.0027844 | 0.00069783
7 | 0.99892 | -0.020634 | 0.0028081 | 0.00070378
8 | 0.99949 | -0.0097988 | 0.0029035 | 0.00072769
9 | 1 | 0 | -0.32929 | -0.083042
10 | 0.99859 | -0.02682 | 0.0027851 | 0.00069802
11 | 0.99792 | -0.039592 | 0.0028057 | 0.00070317
12 | 0.99729 | -0.051621 | 0.0029016 | 0.00072721
13 | 0.99522 | -0.091386 | 0.058733 | 0.01472
14 | 0.98856 | -0.22004 | 0.0065638 | 0.001645
15 | 0.98904 | -0.21064 | 0.0042163 | 0.0010567
16 | 0.99096 | -0.17346 | 0.0028465 | 0.0007134
17 | 0.99087 | -0.17516 | 0 | 0
18 | 0.98956 | -0.20047 | 0.016945 | 0.0042469
19 | 0.99068 | -0.17885 | 0 | 0
20 | 0.98866 | -0.21801 | 0.0029472 | 0.00073863
21 | 0.98839 | -0.2232 | 0.020202 | 0.0050632
22 | 0.99062 | -0.17992 | 0.0015225 | 0.00038158
23 | 0.98839 | -0.22334 | 0.00041898 | 0.00010501
24 | 0.98768 | -0.2371 | 0.0070798 | 0.0017744
25 | 0.98804 | -0.23005 | 0 | 0
26 | 0.98601 | -0.26954 | 0.043018 | 0.010781
27 | 0.98752 | -0.24001 | 0 | 0
28 | 0.98825 | -0.22604 | 0 | 0
29 | 0.99058 | -0.18068 | 0.0012419 | 0.00031124
30 | 0.99058 | -0.18081 | 0.0011866 | 0.0002974
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0795 | -0.020005 | 0.079661 | 0.020108 | 0.0001608 | 0.00010252 | 0.1191 | 0.1191 | 0.1191 | 0.99352 | -0.12429 | 0.99572 | -0.082059 | 32.7191
1 | 0.0448 | 0.011309 | -0.04475 | -0.011277 | 4.9933e-05 | 3.1575e-05 | 0.067126 | 0.067126 | 0.067126 | 0.99352 | -0.12429 | 0.99231 | -0.14759 | 18.4413
2 | -0.088977 | -0.022443 | 0.089005 | 0.02246 | 2.7441e-05 | 1.7509e-05 | 0.13302 | 0.13302 | 0.13302 | 0.99572 | -0.082059 | 0.99605 | -0.075619 | 36.5439
3 | 0.04475 | 0.011277 | -0.044588 | -0.011175 | 0.0001617 | 0.00010226 | 0.067126 | 0.067127 | 0.067127 | 0.99231 | -0.14759 | 0.9884 | -0.22342 | 18.4415
4 | -0.13204 | -0.033245 | 0.13211 | 0.03329 | 7.0635e-05 | 4.5143e-05 | 0.19731 | 0.19731 | 0.19731 | 0.99605 | -0.075619 | 0.99663 | -0.064435 | 54.205
5 | -0.14178 | -0.035714 | 0.142 | 0.035859 | 0.00022711 | 0.00014465 | 0.21174 | 0.21174 | 0.21174 | 0.99663 | -0.064435 | 0.99838 | -0.030999 | 29.0857
6 | -0.14479 | -0.036556 | 0.14486 | 0.036602 | 7.1939e-05 | 4.5825e-05 | 0.21589 | 0.21589 | 0.21589 | 0.99838 | -0.030999 | 0.99892 | -0.020634 | 29.6557
7 | -0.14767 | -0.037306 | 0.14775 | 0.037355 | 7.6735e-05 | 4.8889e-05 | 0.22008 | 0.22008 | 0.22008 | 0.99892 | -0.020634 | 0.99949 | -0.0097988 | 30.2303
8 | -0.15065 | -0.038083 | 0.15072 | 0.038128 | 7.0826e-05 | 4.5132e-05 | 0.2244 | 0.2244 | 0.2244 | 0.99949 | -0.0097988 | 1 | 0 | 30.8241
9 | 0.17692 | 0.044914 | -0.17669 | -0.044769 | 0.00022797 | 0.00014544 | 0.26346 | 0.26346 | 0.26346 | 1 | 0 | 0.99859 | -0.02682 | 36.189
10 | 0.1739 | 0.044071 | -0.1738 | -0.044003 | 0.00010665 | 6.8032e-05 | 0.25931 | 0.25931 | 0.25931 | 0.99859 | -0.02682 | 0.99792 | -0.039592 | 35.619
11 | 0.17099 | 0.0433 | -0.17089 | -0.043237 | 9.8713e-05 | 6.2965e-05 | 0.25512 | 0.25512 | 0.25512 | 0.99792 | -0.039592 | 0.99729 | -0.051621 | 35.0443
12 | 0.16799 | 0.042509 | -0.16767 | -0.042305 | 0.00031993 | 0.00020405 | 0.25079 | 0.25079 | 0.25079 | 0.99729 | -0.051621 | 0.99522 | -0.091386 | 34.4496
13 | 0.10894 | 0.027585 | -0.10851 | -0.027312 | 0.0004275 | 0.00027305 | 0.16298 | 0.16298 | 0.16298 | 0.99522 | -0.091386 | 0.99096 | -0.17346 | 44.7743
14 | -0.0065638 | -0.001645 | 0.0065667 | 0.0016459 | 2.9409e-06 | 8.5163e-07 | 0.0098801 | 0.0098797 | 0.0098801 | 0.98856 | -0.22004 | 0.98904 | -0.21064 | 2.7143
15 | 0.010456 | 0.0026221 | -0.010453 | -0.0026203 | 3.6722e-06 | 1.8427e-06 | 0.015732 | 0.015732 | 0.015732 | 0.98904 | -0.21064 | 0.98866 | -0.21801 | 4.322
16 | -0.021239 | -0.0053247 | 0.021277 | 0.0053476 | 3.7693e-05 | 2.2858e-05 | 0.031955 | 0.031955 | 0.031955 | 0.98904 | -0.21064 | 0.99096 | -0.17346 | 8.7789
17 | 0.084386 | 0.021251 | -0.084379 | -0.021247 | 6.8393e-06 | 4.3626e-06 | 0.12675 | 0.12675 | 0.12675 | 0.99096 | -0.17346 | 0.99087 | -0.17516 | 34.8213
18 | 0.080427 | 0.020257 | -0.08033 | -0.020195 | 9.7234e-05 | 6.2002e-05 | 0.12081 | 0.12081 | 0.12081 | 0.99087 | -0.17516 | 0.98956 | -0.20047 | 33.1909
19 | 0.003952 | 0.00098968 | -0.0039513 | -0.00098991 | 6.9414e-07 | -2.3257e-07 | 0.0059346 | 0.0059348 | 0.0059348 | 0.99087 | -0.17516 | 0.99068 | -0.17885 | 1.6305
20 | 0.063384 | 0.015948 | -0.063316 | -0.015905 | 6.8752e-05 | 4.3743e-05 | 0.095334 | 0.095334 | 0.095334 | 0.98956 | -0.20047 | 0.98839 | -0.2232 | 26.1907
21 | 0.0039513 | 0.00098991 | -0.0039511 | -0.00098998 | 2.0153e-07 | -6.7465e-08 | 0.0059348 | 0.0059349 | 0.0059349 | 0.99068 | -0.17885 | 0.99062 | -0.17992 | 1.6305
22 | 0.0075054 | 0.0018817 | -0.0075035 | -0.001881 | 1.9071e-06 | 7.0964e-07 | 0.011296 | 0.011297 | 0.011297 | 0.98866 | -0.21801 | 0.98839 | -0.22334 | 3.1035
23 | 0.043113 | 0.010841 | -0.043079 | -0.01082 | 3.4594e-05 | 2.186e-05 | 0.06492 | 0.06492 | 0.06492 | 0.98839 | -0.2232 | 0.98752 | -0.24001 | 17.8351
24 | 0.0024286 | 0.00060839 | -0.0024285 | -0.00060857 | 8.8448e-08 | -1.7157e-07 | 0.0036479 | 0.003648 | 0.003648 | 0.99062 | -0.17992 | 0.99058 | -0.18068 | 1.0022
25 | 0.0070845 | 0.001776 | -0.0070836 | -0.0017756 | 9.0994e-07 | 3.0903e-07 | 0.010666 | 0.010666 | 0.010666 | 0.98839 | -0.22334 | 0.98825 | -0.22604 | 2.9302
26 | -0.0070798 | -0.0017744 | 0.0070822 | 0.0017752 | 2.3785e-06 | 8.0846e-07 | 0.010666 | 0.010666 | 0.010666 | 0.98768 | -0.2371 | 0.98804 | -0.23005 | 2.9303
27 | -0.0070822 | -0.0017752 | 0.0070836 | 0.0017756 | 1.3539e-06 | 4.5996e-07 | 0.010666 | 0.010666 | 0.010666 | 0.98804 | -0.23005 | 0.98825 | -0.22604 | 2.9302
28 | -0.043018 | -0.010781 | 0.043079 | 0.01082 | 6.0607e-05 | 3.8298e-05 | 0.06492 | 0.06492 | 0.06492 | 0.98601 | -0.26954 | 0.98752 | -0.24001 | 17.8351
29 | 0.0011866 | 0.00029732 | -0.0011866 | -0.0002974 | 7.4394e-09 | -7.5616e-08 | 0.0017825 | 0.0017825 | 0.0017825 | 0.99058 | -0.18068 | 0.99058 | -0.18081 | 0.4897

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37174 | 0.093682

## res_load
| p_mw | q_mvar
0 | 0.0347 | 0.0086967
1 | 0.0093163 | 0.0023349
2 | 0.043032 | 0.010785
3 | 0.044588 | 0.011175
4 | 0.0096701 | 0.0024235
5 | 0.0027844 | 0.00069783
6 | 0.0028081 | 0.00070378
7 | 0.0029035 | 0.00072769
8 | 0.042454 | 0.01064
9 | 0.0027851 | 0.00069802
10 | 0.0028057 | 0.00070317
11 | 0.0029016 | 0.00072721
12 | 0.058733 | 0.01472
13 | 0.0065638 | 0.001645
14 | 0.0042163 | 0.0010567
15 | 0.0028465 | 0.0007134
16 | 0.016945 | 0.0042469
17 | 0.0029472 | 0.00073863
18 | 0.020202 | 0.0050632
19 | 0.0015225 | 0.00038158
20 | 0.00041898 | 0.00010501
21 | 0.0070798 | 0.0017744
22 | 0.043018 | 0.010781
23 | 0.0012419 | 0.00031124
24 | 0.0011866 | 0.0002974

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1