## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1203-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1203-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1203-1_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1203-1_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1203-1_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1203-1_0_3_node_59 | 0.4 | n |  | TRUE
6 | bus_LV_1203-1_0_3_node_83 | 0.4 | n |  | TRUE
7 | bus_LV_1203-1_0_3_node_57 | 0.4 | n |  | TRUE
8 | bus_LV_1203-1_0_3_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_1203-1_0_3_node_67 | 0.4 | n |  | TRUE
10 | bus_LV_1203-1_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1203-1_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1203-1_0_3_node_82 | 0.4 | n |  | TRUE
13 | bus_LV_1203-1_0_3_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_1203-1_0_3_node_71 | 0.4 | n |  | TRUE
15 | bus_LV_1203-1_0_3_node_72 | 0.4 | n |  | TRUE
16 | bus_LV_1203-1_0_3_node_73 | 0.4 | n |  | TRUE
17 | bus_LV_1203-1_0_3_node_74 | 0.4 | n |  | TRUE
18 | bus_LV_1203-1_0_3_node_75 | 0.4 | n |  | TRUE
19 | bus_LV_1203-1_0_3_node_76 | 0.4 | n |  | TRUE
20 | bus_LV_1203-1_0_3_node_107 | 0.4 | n |  | TRUE
21 | bus_LV_1203-1_0_3_node_94 | 0.4 | n |  | TRUE
22 | bus_LV_1203-1_0_3_node_95 | 0.4 | n |  | TRUE
23 | bus_LV_1203-1_0_3_node_102 | 0.4 | n |  | TRUE
24 | bus_LV_1203-1_0_3_node_96 | 0.4 | n |  | TRUE
25 | bus_LV_1203-1_0_3_node_97 | 0.4 | n |  | TRUE
26 | bus_LV_1203-1_0_3_node_36 | 0.4 | n |  | TRUE
27 | bus_LV_1203-1_0_3_node_55 | 0.4 | n |  | TRUE
28 | bus_LV_1203-1_0_3_node_54 | 0.4 | n |  | TRUE
29 | bus_LV_1203-1_0_3_node_81 | 0.4 | n |  | TRUE
30 | bus_LV_1203-1_0_3_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_1203-1_0_3_node_7 | 0.4 | n |  | TRUE
32 | bus_LV_1203-1_0_3_node_8 | 0.4 | n |  | TRUE
33 | bus_LV_1203-1_0_3_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_1203-1_0_3_node_9 | 0.4 | n |  | TRUE
35 | bus_LV_1203-1_0_3_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_1203-1_0_3_node_10 | 0.4 | n |  | TRUE
37 | bus_LV_1203-1_0_3_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_1203-1_0_3_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_1203-1_0_3_node_11 | 0.4 | n |  | TRUE
40 | bus_LV_1203-1_0_3_node_12 | 0.4 | n |  | TRUE
41 | bus_LV_1203-1_0_3_node_13 | 0.4 | n |  | TRUE
42 | bus_LV_1203-1_0_3_node_14 | 0.4 | n |  | TRUE
43 | bus_LV_1203-1_0_3_node_53 | 0.4 | n |  | TRUE
44 | bus_LV_1203-1_0_3_node_51 | 0.4 | n |  | TRUE
45 | bus_LV_1203-1_0_3_node_79 | 0.4 | n |  | TRUE
46 | bus_LV_1203-1_0_3_node_80 | 0.4 | n |  | TRUE
47 | bus_LV_1203-1_0_3_node_78 | 0.4 | n |  | TRUE
48 | bus_LV_1203-1_0_3_node_17 | 0.4 | n |  | TRUE
49 | bus_LV_1203-1_0_3_node_18 | 0.4 | n |  | TRUE
50 | bus_LV_1203-1_0_3_node_103 | 0.4 | n |  | TRUE
51 | bus_LV_1203-1_0_3_node_19 | 0.4 | n |  | TRUE
52 | bus_LV_1203-1_0_3_node_20 | 0.4 | n |  | TRUE
53 | bus_LV_1203-1_0_3_node_21 | 0.4 | n |  | TRUE
54 | bus_LV_1203-1_0_3_node_68 | 0.4 | n |  | TRUE
55 | bus_LV_1203-1_0_3_node_88 | 0.4 | n |  | TRUE
56 | bus_LV_1203-1_0_3_node_69 | 0.4 | n |  | TRUE
57 | bus_LV_1203-1_0_3_node_89 | 0.4 | n |  | TRUE
58 | bus_LV_1203-1_0_3_node_87 | 0.4 | n |  | TRUE
59 | bus_LV_1203-1_0_3_node_23 | 0.4 | n |  | TRUE
60 | bus_LV_1203-1_0_3_node_25 | 0.4 | n |  | TRUE
61 | bus_LV_1203-1_0_3_node_26 | 0.4 | n |  | TRUE
62 | bus_LV_1203-1_0_3_node_28 | 0.4 | n |  | TRUE
63 | bus_LV_1203-1_0_3_node_29 | 0.4 | n |  | TRUE
64 | bus_LV_1203-1_0_3_node_30 | 0.4 | n |  | TRUE
65 | bus_LV_1203-1_0_3_node_31 | 0.4 | n |  | TRUE
66 | bus_LV_1203-1_0_3_node_32 | 0.4 | n |  | TRUE
67 | bus_LV_1203-1_0_3_node_66 | 0.4 | n |  | TRUE
68 | bus_LV_1203-1_0_3_node_64 | 0.4 | n |  | TRUE
69 | bus_LV_1203-1_0_3_node_37 | 0.4 | n |  | TRUE
70 | bus_LV_1203-1_0_3_node_38 | 0.4 | n |  | TRUE
71 | bus_LV_1203-1_0_3_node_41 | 0.4 | n |  | TRUE
72 | bus_LV_1203-1_0_3_node_40 | 0.4 | n |  | TRUE
73 | bus_LV_1203-1_0_3_node_98 | 0.4 | n |  | TRUE
74 | bus_LV_1203-1_0_3_node_42 | 0.4 | n |  | TRUE
75 | bus_LV_1203-1_0_3_node_43 | 0.4 | n |  | TRUE
76 | bus_LV_1203-1_0_3_node_44 | 0.4 | n |  | TRUE
77 | bus_LV_1203-1_0_3_node_45 | 0.4 | n |  | TRUE
78 | bus_LV_1203-1_0_3_node_46 | 0.4 | n |  | TRUE
79 | bus_LV_1203-1_0_3_node_52 | 0.4 | n |  | TRUE
80 | bus_LV_1203-1_0_3_node_93 | 0.4 | n |  | TRUE
81 | bus_LV_1203-1_0_3_node_47 | 0.4 | n |  | TRUE
82 | bus_LV_1203-1_0_3_node_48 | 0.4 | n |  | TRUE
83 | bus_LV_1203-1_0_3_node_49 | 0.4 | n |  | TRUE
84 | bus_LV_1203-1_0_3_node_50 | 0.4 | n |  | TRUE
85 | bus_LV_1203-1_0_3_node_61 | 0.4 | n |  | TRUE
86 | bus_LV_1203-1_0_3_node_60 | 0.4 | n |  | TRUE
87 | bus_LV_1203-1_0_3_node_92 | 0.4 | n |  | TRUE
88 | bus_LV_1203-1_0_3_node_99 | 0.4 | n |  | TRUE
89 | bus_LV_1203-1_0_3_node_100 | 0.4 | n |  | TRUE
90 | bus_LV_1203-1_0_3_node_101 | 0.4 | n |  | TRUE
91 | bus_LV_1203-1_0_3_node_35 | 0.4 | n |  | TRUE
92 | bus_LV_1203-1_0_3_node_56 | 0.4 | n |  | TRUE
93 | bus_LV_1203-1_0_3_node_58 | 0.4 | n |  | TRUE
94 | bus_LV_1203-1_0_3_node_65 | 0.4 | n |  | TRUE
95 | bus_LV_1203-1_0_3_node_62 | 0.4 | n |  | TRUE
96 | bus_LV_1203-1_0_3_node_63 | 0.4 | n |  | TRUE
97 | bus_LV_1203-1_0_3_node_84 | 0.4 | n |  | TRUE
98 | bus_LV_1203-1_0_3_node_104 | 0.4 | n |  | TRUE
99 | bus_LV_1203-1_0_3_node_70 | 0.4 | n |  | TRUE
100 | bus_LV_1203-1_0_3_node_85 | 0.4 | n |  | TRUE
101 | bus_LV_1203-1_0_3_node_86 | 0.4 | n |  | TRUE
102 | bus_LV_1203-1_0_3_node_106 | 0.4 | n |  | TRUE
103 | bus_LV_1203-1_0_3_node_90 | 0.4 | n |  | TRUE
104 | bus_LV_1203-1_0_3_node_91 | 0.4 | n |  | TRUE
105 | bus_MV_0_node_15 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1203-1_0_3_load_0 | 0 | 0.00031965 | 8.0111e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1203-1_0_3_load_1 | 1 | 0.00036769 | 9.2152e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1203-1_0_3_load_2 | 2 | 0.00021666 | 5.4301e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1203-1_0_3_load_3 | 3 | 0.00082513 | 0.0002068 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1203-1_0_3_load_59 | 5 | 0.00019121 | 4.7923e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1203-1_0_3_load_83 | 6 | 0.00019027 | 4.7687e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1203-1_0_3_load_57 | 7 | 0.00026136 | 6.5502e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1203-1_0_3_load_5 | 10 | 0.00037812 | 9.4765e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1203-1_0_3_load_82 | 12 | 0.00019185 | 4.8083e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1203-1_0_3_load_15 | 13 | 0.00016787 | 4.2073e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1203-1_0_3_load_71 | 14 | 0.00028946 | 7.2547e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1203-1_0_3_load_72 | 15 | 0.00022392 | 5.6119e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1203-1_0_3_load_74 | 17 | 0.0006361 | 0.00015942 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1203-1_0_3_load_75 | 18 | 0.00025659 | 6.4307e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1203-1_0_3_load_76 | 19 | 0.00020557 | 5.1521e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1203-1_0_3_load_107 | 20 | 0.00026488 | 6.6385e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1203-1_0_3_load_94 | 21 | 0.00033525 | 8.4023e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1203-1_0_3_load_102 | 23 | 0.00062509 | 0.00015666 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1203-1_0_3_load_96 | 24 | 0.00019599 | 4.912e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1203-1_0_3_load_97 | 25 | 0.0013229 | 0.00033156 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1203-1_0_3_load_55 | 27 | 0.00014105 | 3.5351e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1203-1_0_3_load_54 | 28 | 0.00031187 | 7.8162e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1203-1_0_3_load_81 | 29 | 0.00025436 | 6.3748e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1203-1_0_3_load_22 | 30 | 0.00020848 | 5.2249e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1203-1_0_3_load_7 | 31 | 0.0005359 | 0.00013431 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1203-1_0_3_load_8 | 32 | 0.00016126 | 4.0416e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1203-1_0_3_load_27 | 33 | 0.00028463 | 7.1334e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1203-1_0_3_load_9 | 34 | 0.00016406 | 4.1117e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1203-1_0_3_load_10 | 36 | 0.0001524 | 3.8195e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1203-1_0_3_load_33 | 37 | 0.00040793 | 0.00010224 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1203-1_0_3_load_11 | 39 | 0.00029865 | 7.4848e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1203-1_0_3_load_12 | 40 | 0.00018926 | 4.7433e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1203-1_0_3_load_13 | 41 | 0.00065977 | 0.00016535 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1203-1_0_3_load_14 | 42 | 0.00034548 | 8.6584e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1203-1_0_3_load_53 | 43 | 0.0018469 | 0.00046289 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1203-1_0_3_load_51 | 44 | 0.00051716 | 0.00012961 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1203-1_0_3_load_79 | 45 | 0.0001668 | 4.1804e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1203-1_0_3_load_80 | 46 | 0.00022412 | 5.6169e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1203-1_0_3_load_78 | 47 | 0.00015634 | 3.9182e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1203-1_0_3_load_17 | 48 | 0.00031979 | 8.0148e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1203-1_0_3_load_18 | 49 | 0.00035441 | 8.8822e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1203-1_0_3_load_103 | 50 | 0.00021643 | 5.4243e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1203-1_0_3_load_19 | 51 | 0.00018888 | 4.7338e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1203-1_0_3_load_20 | 52 | 0.00020926 | 5.2446e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1203-1_0_3_load_88 | 55 | 0.00021366 | 5.3548e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1203-1_0_3_load_69 | 56 | 0.00052103 | 0.00013058 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1203-1_0_3_load_89 | 57 | 0.00024764 | 6.2065e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1203-1_0_3_load_23 | 59 | 0.0002581 | 6.4687e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1203-1_0_3_load_28 | 62 | 0.00093648 | 0.0002347 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1203-1_0_3_load_30 | 64 | 0.00038971 | 9.767e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1203-1_0_3_load_31 | 65 | 0.00028167 | 7.0594e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1203-1_0_3_load_32 | 66 | 0.0004947 | 0.00012398 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1203-1_0_3_load_66 | 67 | 0.00013876 | 3.4776e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1203-1_0_3_load_64 | 68 | 0.00022163 | 5.5547e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1203-1_0_3_load_37 | 69 | 0.00067283 | 0.00016863 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1203-1_0_3_load_41 | 71 | 0.00064206 | 0.00016091 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1203-1_0_3_load_40 | 72 | 0.00046011 | 0.00011531 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1203-1_0_3_load_98 | 73 | 0.00090433 | 0.00022665 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1203-1_0_3_load_43 | 75 | 0.00058723 | 0.00014717 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1203-1_0_3_load_44 | 76 | 0.0020672 | 0.00051808 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1203-1_0_3_load_46 | 78 | 0.00069988 | 0.00017541 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1203-1_0_3_load_93 | 80 | 0.00039085 | 9.7957e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1203-1_0_3_load_47 | 81 | 0.00036792 | 9.2209e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1203-1_0_3_load_48 | 82 | 0.00038504 | 9.6501e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1203-1_0_3_load_50 | 84 | 0.00057166 | 0.00014327 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1203-1_0_3_load_61 | 85 | 0.00047896 | 0.00012004 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1203-1_0_3_load_60 | 86 | 0.0011018 | 0.00027612 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1203-1_0_3_load_92 | 87 | 0.00050807 | 0.00012733 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1203-1_0_3_load_100 | 89 | 0.0010815 | 0.00027106 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1203-1_0_3_load_101 | 90 | 0.00030909 | 7.7465e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1203-1_0_3_load_56 | 92 | 0.00026197 | 6.5655e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1203-1_0_3_load_65 | 94 | 0.00015481 | 3.8798e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1203-1_0_3_load_62 | 95 | 0.00020417 | 5.1169e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1203-1_0_3_load_63 | 96 | 0.00022259 | 5.5787e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1203-1_0_3_load_84 | 97 | 0.00038563 | 9.6649e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1203-1_0_3_load_104 | 98 | 0.00018889 | 4.734e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1203-1_0_3_load_85 | 100 | 0.00037641 | 9.4338e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1203-1_0_3_load_86 | 101 | 0.00026421 | 6.6216e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1203-1_0_3_load_106 | 102 | 0.00024268 | 6.0822e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1203-1_0_3_load_90 | 103 | 0.0012393 | 0.00031059 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1203-1_0_3_load_91 | 104 | 0.00084978 | 0.00021298 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1203-1_0_3_line_0 |  | 0 | 1 | 0.11429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1203-1_0_3_line_1 |  | 0 | 2 | 0.029513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1203-1_0_3_line_2 |  | 1 | 3 | 0.06659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1203-1_0_3_line_3 |  | 2 | 4 | 0.039057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1203-1_0_3_line_4 |  | 3 | 8 | 0.5845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1203-1_0_3_line_5 |  | 4 | 10 | 0.019236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1203-1_0_3_line_6 |  | 4 | 11 | 0.20984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1203-1_0_3_line_7 |  | 5 | 6 | 0.034711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1203-1_0_3_line_8 |  | 5 | 7 | 0.062771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1203-1_0_3_line_9 |  | 6 | 9 | 0.043883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1203-1_0_3_line_10 |  | 7 | 92 | 0.0136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1203-1_0_3_line_11 |  | 8 | 12 | 0.4716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1203-1_0_3_line_12 |  | 8 | 13 | 0.11389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1203-1_0_3_line_13 |  | 9 | 97 | 0.032194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1203-1_0_3_line_14 |  | 9 | 94 | 0.01781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1203-1_0_3_line_15 |  | 11 | 26 | 0.2026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1203-1_0_3_line_16 |  | 11 | 27 | 0.21008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1203-1_0_3_line_17 |  | 12 | 18 | 0.23126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1203-1_0_3_line_18 |  | 13 | 41 | 0.10821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1203-1_0_3_line_19 |  | 14 | 15 | 0.012561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1203-1_0_3_line_20 |  | 15 | 16 | 0.050665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1203-1_0_3_line_21 |  | 16 | 17 | 0.054392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1203-1_0_3_line_22 |  | 16 | 18 | 0.097568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1203-1_0_3_line_23 |  | 17 | 19 | 0.29758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1203-1_0_3_line_24 |  | 17 | 20 | 0.78475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1203-1_0_3_line_25 |  | 20 | 102 | 0.091204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1203-1_0_3_line_26 |  | 21 | 22 | 0.022291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1203-1_0_3_line_27 |  | 21 | 23 | 0.2506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1203-1_0_3_line_28 |  | 22 | 24 | 0.0085998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1203-1_0_3_line_29 |  | 23 | 90 | 0.012434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1203-1_0_3_line_30 |  | 24 | 25 | 0.18997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1203-1_0_3_line_31 |  | 25 | 84 | 0.14753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1203-1_0_3_line_32 |  | 26 | 29 | 0.029261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1203-1_0_3_line_33 |  | 26 | 30 | 0.15446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1203-1_0_3_line_34 |  | 27 | 28 | 0.064304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1203-1_0_3_line_35 |  | 28 | 92 | 0.045813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1203-1_0_3_line_36 |  | 30 | 51 | 0.0022299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1203-1_0_3_line_37 |  | 31 | 32 | 0.027367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1203-1_0_3_line_38 |  | 31 | 33 | 0.23366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1203-1_0_3_line_39 |  | 32 | 34 | 0.046056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1203-1_0_3_line_40 |  | 33 | 35 | 0.029664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1203-1_0_3_line_41 |  | 34 | 36 | 0.12085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1203-1_0_3_line_42 |  | 35 | 61 | 0.020527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1203-1_0_3_line_43 |  | 35 | 59 | 0.10356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1203-1_0_3_line_44 |  | 36 | 37 | 0.023469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1203-1_0_3_line_45 |  | 37 | 38 | 0.15529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1203-1_0_3_line_46 |  | 38 | 91 | 0.22769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1203-1_0_3_line_47 |  | 39 | 40 | 0.0056449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1203-1_0_3_line_48 |  | 39 | 41 | 0.0035807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1203-1_0_3_line_49 |  | 40 | 42 | 0.0018961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1203-1_0_3_line_50 |  | 42 | 43 | 0.54656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1203-1_0_3_line_51 |  | 43 | 44 | 0.022446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1203-1_0_3_line_52 |  | 44 | 83 | 0.069122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1203-1_0_3_line_53 |  | 45 | 46 | 0.018395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1203-1_0_3_line_54 |  | 45 | 47 | 0.092952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1203-1_0_3_line_55 |  | 47 | 65 | 0.04296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1203-1_0_3_line_56 |  | 48 | 49 | 0.00078544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1203-1_0_3_line_57 |  | 48 | 50 | 0.48998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1203-1_0_3_line_58 |  | 49 | 51 | 0.007711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1203-1_0_3_line_59 |  | 52 | 53 | 0.31261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1203-1_0_3_line_60 |  | 52 | 54 | 0.32038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1203-1_0_3_line_61 |  | 53 | 55 | 0.30605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1203-1_0_3_line_62 |  | 54 | 56 | 0.12627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1203-1_0_3_line_63 |  | 55 | 57 | 0.014126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1203-1_0_3_line_64 |  | 55 | 58 | 0.069567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1203-1_0_3_line_65 |  | 56 | 98 | 0.03802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1203-1_0_3_line_66 |  | 57 | 103 | 0.472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1203-1_0_3_line_67 |  | 58 | 91 | 0.38576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1203-1_0_3_line_68 |  | 59 | 60 | 0.055924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1203-1_0_3_line_69 |  | 60 | 62 | 0.01447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1203-1_0_3_line_70 |  | 60 | 63 | 0.026109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1203-1_0_3_line_71 |  | 61 | 64 | 0.042197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1203-1_0_3_line_72 |  | 61 | 65 | 0.032961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1203-1_0_3_line_73 |  | 63 | 66 | 0.035953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1203-1_0_3_line_74 |  | 64 | 67 | 0.025443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1203-1_0_3_line_75 |  | 67 | 68 | 0.028014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1203-1_0_3_line_76 |  | 68 | 96 | 0.011719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1203-1_0_3_line_77 |  | 69 | 70 | 0.047701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1203-1_0_3_line_78 |  | 70 | 71 | 0.092889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1203-1_0_3_line_79 |  | 71 | 74 | 0.12528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1203-1_0_3_line_80 |  | 72 | 73 | 0.045048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1203-1_0_3_line_81 |  | 73 | 88 | 0.087596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1203-1_0_3_line_82 |  | 74 | 75 | 0.0072625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1203-1_0_3_line_83 |  | 74 | 76 | 0.075526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1203-1_0_3_line_84 |  | 75 | 77 | 0.10357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1203-1_0_3_line_85 |  | 76 | 78 | 0.038231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1203-1_0_3_line_86 |  | 77 | 79 | 0.001903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1203-1_0_3_line_87 |  | 77 | 80 | 0.16862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1203-1_0_3_line_88 |  | 79 | 85 | 0.067655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1203-1_0_3_line_89 |  | 79 | 83 | 0.13527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1203-1_0_3_line_90 |  | 80 | 87 | 0.050126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1203-1_0_3_line_91 |  | 81 | 82 | 0.15389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1203-1_0_3_line_92 |  | 81 | 83 | 0.03324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1203-1_0_3_line_93 |  | 82 | 84 | 0.025412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1203-1_0_3_line_94 |  | 85 | 86 | 0.0077489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1203-1_0_3_line_95 |  | 88 | 89 | 0.039348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1203-1_0_3_line_96 |  | 89 | 90 | 0.022162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1203-1_0_3_line_97 |  | 93 | 94 | 0.054218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1203-1_0_3_line_98 |  | 93 | 95 | 0.016349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1203-1_0_3_line_99 |  | 95 | 96 | 0.029074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1203-1_0_3_line_100 |  | 98 | 99 | 0.018007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1203-1_0_3_line_101 |  | 99 | 100 | 0.93589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1203-1_0_3_line_102 |  | 100 | 101 | 0.70319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1203-1_0_3_line_103 |  | 103 | 104 | 0.065568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1203-1_0_3_trafo_15 | 0.63 MVA 20/0.4 kV | 105 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2688641.0405 | 1189066.7808 | 2688645.8252 | 1189075.4126 | 2688655.414 | 1189090.8531 | 2688673.0122 | 1189118.6534 | 2688682.0863 | 1189141.013 | 2688681.4797 | 1189154.6682 | 2688677.5724 | 1189169.7086
1 | 2688641.0405 | 1189066.7808 | 2688641.0405 | 1189066.7808 | 2688646.3724 | 1189052.3729 | 2688642.8912 | 1189038.6571
2 | 2688725.6246 | 1189213.2478 | 2688699.2581 | 1189197.5696 | 2688680.9172 | 1189178.7305 | 2688677.5724 | 1189169.7086
3 | 2688626.2278 | 1189003.3327 | 2688642.8912 | 1189038.6571 | 2688642.8912 | 1189038.6571
4 | 2688725.6246 | 1189213.2478 | 2689300.9565 | 1189316.3541
5 | 2688643.5864 | 1189005.6244 | 2688641.1035 | 1189007.4221 | 2688633.5212 | 1189007.9213 | 2688626.2278 | 1189003.3327
6 | 2688626.2278 | 1189003.3327 | 2688623.3627 | 1188989.2148 | 2688618.3947 | 1188979.5574 | 2688592.5144 | 1188958.7725 | 2688552.0657 | 1188940.4294 | 2688531.1077 | 1188932.37 | 2688505.9863 | 1188929.3523 | 2688496.2342 | 1188924.9165 | 2688493.69 | 1188916.9294 | 2688503.5308 | 1188895.2501 | 2688503.746 | 1188887.4039 | 2688501.9279 | 1188878.805
7 | 2688799.789 | 1188773.5274 | 2688786.853 | 1188768.6088 | 2688767.6748 | 1188760.3749 | 2688767.6748 | 1188760.3749
8 | 2688752.7088 | 1188701.6384 | 2688764.7023 | 1188718.0153 | 2688765.6947 | 1188738.0315 | 2688767.6748 | 1188760.3749
9 | 2688837.3322 | 1188761.8755 | 2688821.5028 | 1188774.2151 | 2688816.2933 | 1188778.2737 | 2688805.7796 | 1188775.8051 | 2688799.789 | 1188773.5274
10 | 2688752.7088 | 1188701.6384 | 2688747.0023 | 1188707.3129 | 2688744.6967 | 1188712.3637
11 | 2689151.217 | 1189763.5495 | 2689300.9565 | 1189316.3541
12 | 2689300.9565 | 1189316.3541 | 2689309.8325 | 1189313.4847 | 2689323.3152 | 1189297.876 | 2689345.5336 | 1189275.0041 | 2689360.363 | 1189263.2179 | 2689377.3532 | 1189254.8662 | 2689389.3058 | 1189247.2399
13 | 2688866.8857 | 1188749.5284 | 2688841.8008 | 1188758.3951 | 2688837.3322 | 1188761.8755
14 | 2688837.3322 | 1188761.8755 | 2688830.6824 | 1188745.3532
15 | 2688341.7088 | 1188921.1103 | 2688338.0327 | 1188913.3067 | 2688338.3472 | 1188891.998 | 2688339.7647 | 1188886.4043 | 2688343.0832 | 1188883.2957 | 2688347.5231 | 1188880.7041 | 2688365.2128 | 1188874.0275 | 2688373.6864 | 1188875.1755 | 2688386.4238 | 1188878.9325 | 2688395.2038 | 1188879.985 | 2688407.797 | 1188879.5595 | 2688424.3172 | 1188882.8611 | 2688432.1987 | 1188882.7774 | 2688441.9589 | 1188879.9642 | 2688454.7565 | 1188879.1305 | 2688469.1455 | 1188881.589 | 2688482.642 | 1188882.5001 | 2688501.9279 | 1188878.805
16 | 2688648.737 | 1188728.5431 | 2688501.9279 | 1188878.805
17 | 2689306.7709 | 1189919.2994 | 2689303.7088 | 1189915.9627 | 2689302.4678 | 1189901.5018 | 2689294.2536 | 1189876.9526 | 2689286.5203 | 1189861.572 | 2689249.4437 | 1189842.6962 | 2689210.7828 | 1189812.4009 | 2689176.8691 | 1189786.4905 | 2689169.0139 | 1189773.1206 | 2689151.217 | 1189763.5495
18 | 2689466.7965 | 1189206.5715 | 2689466.7965 | 1189206.5715 | 2689464.6296 | 1189203.5483 | 2689446.4917 | 1189195.2721 | 2689437.6902 | 1189193.1393 | 2689430.6514 | 1189194.0347 | 2689426.604 | 1189196.3758 | 2689410.919 | 1189211.2954 | 2689400.6244 | 1189225.3728 | 2689394.8291 | 1189237.4939 | 2689389.3058 | 1189247.2399 | 2689389.3058 | 1189247.2399
19 | 2689368.2837 | 1189947.6115 | 2689365.1901 | 1189957.4063 | 2689364.0093 | 1189959.3678
20 | 2689336.467 | 1190000.2825 | 2689344.7492 | 1189995.7366 | 2689353.2238 | 1189977.2847 | 2689364.0093 | 1189959.3678
21 | 2689336.467 | 1190000.2825 | 2689330.1705 | 1190014.8644 | 2689327.7586 | 1190053.2972
22 | 2689336.467 | 1190000.2825 | 2689340.9425 | 1189992.2109 | 2689342.7282 | 1189983.9767 | 2689342.2961 | 1189972.5631 | 2689340.109 | 1189956.5981 | 2689331.337 | 1189936.7325 | 2689326.8657 | 1189930.7175 | 2689320.0946 | 1189926.0024 | 2689306.7709 | 1189919.2994 | 2689306.7709 | 1189919.2994
23 | 2689464.5869 | 1190307.3009 | 2689433.2938 | 1190276.7474 | 2689399.1099 | 1190229.3513 | 2689382.4299 | 1190191.5895 | 2689362.7946 | 1190167.848 | 2689349.0616 | 1190142.6271 | 2689345.5149 | 1190115.0567 | 2689345.5273 | 1190090.219 | 2689342.2378 | 1190074.5378 | 2689331.8347 | 1190062.2748 | 2689327.7586 | 1190053.2972 | 2689327.7586 | 1190053.2972
24 | 2689327.7586 | 1190053.2972 | 2688597.2286 | 1190339.9344
25 | 2688597.2286 | 1190339.9344 | 2688592.904 | 1190341.5047 | 2688579.8286 | 1190340.6996 | 2688574.3716 | 1190336.3384 | 2688569.4836 | 1190332.686 | 2688567.4003 | 1190330.7095 | 2688564.8289 | 1190331.3051 | 2688562.9457 | 1190332.3001 | 2688559.1969 | 1190338.7599 | 2688550.8498 | 1190349.3097 | 2688549.3736 | 1190352.69 | 2688548.4496 | 1190356.3787 | 2688547.0069 | 1190371.4113 | 2688547.02 | 1190374.1354 | 2688548.0599 | 1190378.0755 | 2688549.2574 | 1190380.226
26 | 2690104.3357 | 1189846.8919 | 2690120.3331 | 1189854.7932 | 2690124.3879 | 1189856.6244
27 | 2690287.6109 | 1189666.4717 | 2690124.3879 | 1189856.6244
28 | 2690104.3357 | 1189846.8919 | 2690103.9159 | 1189838.3023 | 2690103.9159 | 1189838.3023
29 | 2690287.6109 | 1189666.4717 | 2690294.4079 | 1189656.0605
30 | 2690109.2688 | 1189734.7737 | 2690113.026 | 1189743.8907 | 2690124.4416 | 1189764.3199 | 2690143.7069 | 1189797.8312 | 2690151.2774 | 1189806.1616 | 2690163.6371 | 1189812.0069 | 2690170.7087 | 1189816.494 | 2690171.317 | 1189824.7195 | 2690168.2678 | 1189832.7009 | 2690164.1866 | 1189836.2862 | 2690150.2858 | 1189835.5319 | 2690127.2734 | 1189831.5385 | 2690111.3216 | 1189832.7547 | 2690103.9159 | 1189838.3023
31 | 2690142.0233 | 1189590.9278 | 2690109.2688 | 1189734.7737
32 | 2688365.6035 | 1188937.9846 | 2688352.8272 | 1188930.1467 | 2688341.7088 | 1188921.1103
33 | 2688341.7088 | 1188921.1103 | 2688337.777 | 1188923.9096 | 2688328.6573 | 1188925.1981 | 2688316.6968 | 1188924.1099 | 2688309.6286 | 1188924.9173 | 2688301.615 | 1188927.2451 | 2688295.1599 | 1188927.8614 | 2688289.6577 | 1188926.4572 | 2688280.9062 | 1188923.4707 | 2688274.3698 | 1188922.3625 | 2688266.8973 | 1188922.6526 | 2688260.5279 | 1188924.7044 | 2688257.2139 | 1188927.5129 | 2688255.4224 | 1188931.0554 | 2688254.498 | 1188937.8683 | 2688255.8475 | 1188957.5783 | 2688256.8619 | 1188964.8312 | 2688256.8634 | 1188971.969 | 2688254.0543 | 1188981.9227 | 2688249.6614 | 1188988.5844 | 2688247.8014 | 1188990.961
34 | 2688711.1599 | 1188735.3784 | 2688696.9899 | 1188736.0567 | 2688689.9969 | 1188731.7727 | 2688683.2772 | 1188729.6385 | 2688671.6307 | 1188728.4431 | 2688663.65 | 1188728.525 | 2688655.4435 | 1188729.9377 | 2688648.737 | 1188728.5431
35 | 2688711.1599 | 1188735.3784 | 2688711.5328 | 1188735.3606 | 2688722.6653 | 1188736.2372 | 2688729.3825 | 1188734.9359 | 2688740.3185 | 1188721.2782 | 2688743.3122 | 1188715.3967 | 2688744.6967 | 1188712.3637
36 | 2688246.4271 | 1188992.7171 | 2688246.4271 | 1188992.7171 | 2688247.8014 | 1188990.961
37 | 2688901.2666 | 1188406.7695 | 2688892.1383 | 1188402.1847 | 2688879.2639 | 1188394.2441 | 2688877.8692 | 1188392.7751
38 | 2688927.3268 | 1188638.9729 | 2688901.2666 | 1188406.7695
39 | 2688847.0347 | 1188368.9083 | 2688855.2942 | 1188368.4945 | 2688861.9558 | 1188367.8818 | 2688866.4349 | 1188369.3715 | 2688870.0311 | 1188375.3397 | 2688875.0349 | 1188389.7897 | 2688877.8692 | 1188392.7751
40 | 2688955.2537 | 1188648.5546 | 2688944.2705 | 1188644.2999 | 2688930.5893 | 1188640.8946 | 2688927.3268 | 1188638.9729
41 | 2688737.7474 | 1188381.4557 | 2688775.8039 | 1188388.7284 | 2688807.8442 | 1188394.507 | 2688812.7592 | 1188394.3799 | 2688816.3683 | 1188392.2876 | 2688819.3853 | 1188388.9636 | 2688826.7994 | 1188378.7783 | 2688833.1264 | 1188372.9573 | 2688838.9107 | 1188369.7745 | 2688844.3382 | 1188369.0434 | 2688847.0347 | 1188368.9083
42 | 2688967.3209 | 1188663.0207 | 2688966.8637 | 1188659.912 | 2688962.4629 | 1188657.2783 | 2688956.6374 | 1188653.4894 | 2688955.3096 | 1188651.4684 | 2688955.2537 | 1188648.5546
43 | 2688955.2537 | 1188648.5546 | 2688957.675 | 1188646.3003 | 2688962.2831 | 1188646.7912 | 2688971.9461 | 1188647.4797 | 2688982.0169 | 1188647.9407 | 2688993.127 | 1188650.841 | 2689006.021 | 1188656.9031 | 2689022.0327 | 1188669.2822 | 2689030.7261 | 1188675.6599 | 2689035.5423 | 1188677.0323 | 2689042.2397 | 1188677.5878 | 2689049.3357 | 1188675.6044
44 | 2688737.7474 | 1188381.4557 | 2688734.1755 | 1188380.7731 | 2688726.4425 | 1188378.0013 | 2688722.3768 | 1188376.4178 | 2688716.4355 | 1188372.2548
45 | 2688589.0594 | 1188315.5283 | 2688592.4701 | 1188318.5917 | 2688594.8748 | 1188322.0962 | 2688600.3227 | 1188334.4178 | 2688605.6402 | 1188341.6344 | 2688620.0249 | 1188357.8685 | 2688629.0158 | 1188365.851 | 2688633.8961 | 1188368.0691 | 2688648.6908 | 1188370.5229 | 2688662.3488 | 1188373.994 | 2688670.1122 | 1188375.2319 | 2688679.3275 | 1188374.7569 | 2688706.4268 | 1188368.5321 | 2688709.0858 | 1188368.7717 | 2688712.5534 | 1188369.5346 | 2688716.4355 | 1188372.2548
46 | 2688589.0594 | 1188315.5283 | 2688573.2143 | 1188313.9373 | 2688561.423 | 1188308.037 | 2688548.6229 | 1188301.7327 | 2688541.1692 | 1188300.6996 | 2688513.0404 | 1188300.1835 | 2688494.0069 | 1188300.6136 | 2688485.8014 | 1188301.9265 | 2688475.29 | 1188306.9744 | 2688466.8592 | 1188309.596 | 2688460.9204 | 1188309.8195 | 2688444.7833 | 1188307.8466 | 2688429.2521 | 1188306.6943 | 2688414.5984 | 1188303.9763 | 2688392.7141 | 1188302.6857 | 2688366.837 | 1188298.479
47 | 2689467.2592 | 1189210.1222 | 2689467.9885 | 1189215.7197
48 | 2689466.7965 | 1189206.5715 | 2689467.2592 | 1189210.1222
49 | 2689468.2335 | 1189217.5999 | 2689467.9885 | 1189215.7197
50 | 2689965.2935 | 1189444.891 | 2689468.2335 | 1189217.5999
51 | 2689965.2935 | 1189444.891 | 2689971.4708 | 1189441.9263 | 2689978.619 | 1189429.1812 | 2689979.0718 | 1189428.3112
52 | 2690033.3185 | 1189425.0898 | 2690019.3123 | 1189423.1668 | 2690007.09 | 1189413.6993 | 2689992.4345 | 1189408.7871 | 2689986.8351 | 1189413.3947 | 2689979.0718 | 1189428.3112
53 | 2688971.64 | 1188808.1652 | 2688988.4419 | 1188806.3692 | 2688989.8478 | 1188805.853
54 | 2689005.135 | 1188728.6453 | 2689008.5582 | 1188733.5446 | 2689012.3727 | 1188745.3309 | 2689012.187 | 1188750.6315 | 2689013.6327 | 1188763.7057 | 2689014.0275 | 1188778.1984 | 2689013.629 | 1188791.6565 | 2689002.847 | 1188801.08 | 2688989.8478 | 1188805.853
55 | 2689005.135 | 1188728.6453 | 2688996.532 | 1188716.3328 | 2688984.7405 | 1188697.7014 | 2688982.2856 | 1188692.3471
56 | 2688238.4465 | 1188995.5826 | 2688239.2235 | 1188995.4682 | 2688239.2235 | 1188995.4682
57 | 2688238.4465 | 1188995.5826 | 2688028.9924 | 1189438.5412
58 | 2688239.2235 | 1188995.4682 | 2688246.4271 | 1188992.7171
59 | 2687940.8727 | 1188717.7942 | 2687929.1482 | 1188737.4788 | 2687927.1363 | 1188749.2789 | 2687923.6196 | 1188751.8733 | 2687917.4709 | 1188752.3945 | 2687905.7763 | 1188754.4686 | 2687896.1034 | 1188758.6181 | 2687879.0015 | 1188766.3164 | 2687863.0812 | 1188777.7121 | 2687855.2645 | 1188780.6548 | 2687838.0536 | 1188796.3122 | 2687812.1868 | 1188829.9984 | 2687806.951 | 1188880.0975 | 2687821.5815 | 1188914.9783 | 2687844.4091 | 1188934.492 | 2687851.2918 | 1188946.8341
60 | 2687542.3415 | 1188862.0232 | 2687851.2918 | 1188946.8341
61 | 2687934.3716 | 1188411.8086 | 2687940.8727 | 1188717.7942
62 | 2687542.3415 | 1188862.0232 | 2687518.5728 | 1188901.0447 | 2687504.8642 | 1188927.6833 | 2687499.4931 | 1188930.8623 | 2687489.051 | 1188945.3967 | 2687489.9304 | 1188958.8179 | 2687497.5045 | 1188969.424
63 | 2687921.9516 | 1188405.08 | 2687934.3716 | 1188411.8086
64 | 2687999.3688 | 1188415.8419 | 2687982.8635 | 1188410.9074 | 2687967.3279 | 1188410.0676 | 2687955.9577 | 1188418.05 | 2687943.2914 | 1188416.6409 | 2687934.3716 | 1188411.8086
65 | 2687487.8313 | 1189001.3576 | 2687489.7004 | 1189001.1633 | 2687499.117 | 1188987.8926 | 2687501.3078 | 1188974.7497 | 2687497.5045 | 1188969.424
66 | 2687921.9516 | 1188405.08 | 2687660.7866 | 1188011.9199
67 | 2687999.3688 | 1188415.8419 | 2688366.837 | 1188298.479
68 | 2689103.1951 | 1188660.5504 | 2689049.3357 | 1188675.6044
69 | 2689103.1951 | 1188660.5504 | 2689105.535 | 1188661.2078 | 2689109.9452 | 1188664.7424 | 2689113.8208 | 1188669.8477
70 | 2689103.1951 | 1188660.5504 | 2689101.1681 | 1188652.2039 | 2689102.8027 | 1188644.8902 | 2689106.221 | 1188641.261 | 2689110.9398 | 1188639.4412
71 | 2688967.3209 | 1188663.0207 | 2688961.738 | 1188664.4721 | 2688953.0802 | 1188662.3643 | 2688940.6239 | 1188661.2453 | 2688925.7008 | 1188662.8729
72 | 2688967.3209 | 1188663.0207 | 2688974.5731 | 1188675.5252 | 2688982.2856 | 1188692.3471
73 | 2689110.9398 | 1188639.4412 | 2689119.7006 | 1188641.295 | 2689128.5796 | 1188644.9405 | 2689136.6119 | 1188653.1875 | 2689140.428 | 1188657.671
74 | 2688925.7008 | 1188662.8729 | 2688922.9499 | 1188663.1729 | 2688907.9198 | 1188667.8972 | 2688901.3071 | 1188669.9372
75 | 2688874.7658 | 1188678.859 | 2688877.6341 | 1188677.6316 | 2688892.6534 | 1188672.6069 | 2688901.3071 | 1188669.9372
76 | 2688874.7658 | 1188678.859 | 2688863.9915 | 1188683.4695
77 | 2690360.8193 | 1189372.0116 | 2690370.4446 | 1189361.9838 | 2690385.3285 | 1189355.2931 | 2690394.5101 | 1189351.4182 | 2690401.2329 | 1189348.0545
78 | 2690321.5266 | 1189287.8427 | 2690360.8193 | 1189372.0116
79 | 2690203.1501 | 1189269.8474 | 2690216.7171 | 1189268.5399 | 2690228.9934 | 1189268.3581 | 2690246.1681 | 1189270.6183 | 2690256.1741 | 1189274.794 | 2690268.5122 | 1189282.6405 | 2690285.3228 | 1189285.2734 | 2690299.902 | 1189289.6849 | 2690311.1837 | 1189294.2357 | 2690318.2098 | 1189290.1502 | 2690321.5266 | 1189287.8427
80 | 2690392.9907 | 1189497.7285 | 2690387.1822 | 1189502.7479 | 2690358.8631 | 1189527.1324
81 | 2690324.4481 | 1189602.5423 | 2690350.97 | 1189564.6073 | 2690347.8065 | 1189543.7574 | 2690354.9633 | 1189530.4904 | 2690358.8631 | 1189527.1324
82 | 2690203.1501 | 1189269.8474 | 2690197.3034 | 1189274.1556
83 | 2690203.1501 | 1189269.8474 | 2690214.1232 | 1189262.497 | 2690237.4268 | 1189257.4338 | 2690251.0438 | 1189254.337 | 2690264.1023 | 1189248.8193 | 2690274.3379 | 1189250.2113
84 | 2690143.6541 | 1189361.8431 | 2690176.1425 | 1189301.0159 | 2690190.3454 | 1189279.2827 | 2690197.3034 | 1189274.1556
85 | 2690293.1388 | 1189230.2957 | 2690292.1497 | 1189233.21 | 2690291.8207 | 1189241.3658 | 2690293.9789 | 1189247.4688 | 2690283.9632 | 1189251.5204 | 2690274.3379 | 1189250.2113
86 | 2690143.6541 | 1189361.8431 | 2690142.6911 | 1189363.4852
87 | 2690143.6541 | 1189361.8431 | 2690144.5796 | 1189344.4571 | 2690129.1583 | 1189321.5104 | 2690135.3103 | 1189296.943 | 2690127.5509 | 1189284.3961 | 2690085.0132 | 1189254.7705 | 2690064.4131 | 1189230.7416
88 | 2690142.6911 | 1189363.4852 | 2690138.1957 | 1189361.6274 | 2690129.7623 | 1189364.9693 | 2690120.9268 | 1189365.6367 | 2690113.9663 | 1189358.294 | 2690109.4917 | 1189352.0226 | 2690102.9077 | 1189348.0433 | 2690092.8777 | 1189347.9923 | 2690084.0386 | 1189350.9279
89 | 2690033.3185 | 1189425.0898 | 2690054.865 | 1189413.0617 | 2690080.1232 | 1189394.1519 | 2690092.2384 | 1189392.4887 | 2690100.1075 | 1189378.4871 | 2690126.2146 | 1189380.2144 | 2690137.1892 | 1189374.2647 | 2690141.4774 | 1189365.5682 | 2690142.6911 | 1189363.4852
90 | 2690031.7882 | 1189192.6863 | 2690064.4131 | 1189230.7416
91 | 2690064.1114 | 1189429.6891 | 2690064.1114 | 1189429.6891 | 2690111.9554 | 1189538.4333 | 2690129.393 | 1189568.8771
92 | 2690033.3185 | 1189425.0898 | 2690046.3133 | 1189432.8901 | 2690064.1114 | 1189429.6891
93 | 2690142.0233 | 1189590.9278 | 2690129.393 | 1189568.8771
94 | 2690078.0665 | 1189355.8654 | 2690084.0386 | 1189350.9279
95 | 2690324.4481 | 1189602.5423 | 2690319.2232 | 1189610.1239 | 2690313.949 | 1189619.9616 | 2690305.8326 | 1189637.1169
96 | 2690294.4079 | 1189656.0605 | 2690303.3518 | 1189642.3605 | 2690305.8326 | 1189637.1169
97 | 2688819.7706 | 1188692.5158 | 2688822.5874 | 1188718.0959 | 2688827.6942 | 1188737.9285 | 2688830.6824 | 1188745.3532
98 | 2688819.7706 | 1188692.5158 | 2688835.535 | 1188688.1814
99 | 2688835.535 | 1188688.1814 | 2688837.4958 | 1188687.6423 | 2688858.8012 | 1188685.6905 | 2688863.9915 | 1188683.4695
100 | 2687469.9208 | 1189003.2201 | 2687487.8313 | 1189001.3576
101 | 2687469.9208 | 1189003.2201 | 2687126.5557 | 1189873.8506
102 | 2687126.5557 | 1189873.8506 | 2686550.9821 | 1189469.8897
103 | 2687660.7866 | 1188011.9199 | 2687645.902 | 1188007.8478 | 2687596.3986 | 1187999.9059

## bus_geodata
| x | y | coords
0 | 2688641.0405 | 1189066.7808
1 | 2688677.5724 | 1189169.7087
2 | 2688642.8912 | 1189038.6571
3 | 2688725.6246 | 1189213.2478
4 | 2688626.2278 | 1189003.3327
5 | 2688767.6748 | 1188760.3749
6 | 2688799.789 | 1188773.5274
7 | 2688752.7088 | 1188701.6384
8 | 2689300.9565 | 1189316.3541
9 | 2688837.3322 | 1188761.8755
10 | 2688643.5864 | 1189005.6244
11 | 2688501.9279 | 1188878.805
12 | 2689151.217 | 1189763.5495
13 | 2689389.3058 | 1189247.2399
14 | 2689368.2837 | 1189947.6115
15 | 2689364.0093 | 1189959.3678
16 | 2689336.467 | 1190000.2825
17 | 2689327.7586 | 1190053.2972
18 | 2689306.7709 | 1189919.2994
19 | 2689464.5869 | 1190307.3009
20 | 2688597.2286 | 1190339.9344
21 | 2690124.3879 | 1189856.6244
22 | 2690104.3357 | 1189846.8919
23 | 2690287.6109 | 1189666.4717
24 | 2690103.9159 | 1189838.3023
25 | 2690109.2688 | 1189734.7737
26 | 2688341.7088 | 1188921.1103
27 | 2688648.737 | 1188728.5431
28 | 2688711.1599 | 1188735.3784
29 | 2688365.6035 | 1188937.9846
30 | 2688247.8014 | 1188990.961
31 | 2688901.2666 | 1188406.7695
32 | 2688877.8692 | 1188392.7751
33 | 2688927.3268 | 1188638.9729
34 | 2688847.0347 | 1188368.9083
35 | 2688955.2537 | 1188648.5546
36 | 2688737.7474 | 1188381.4557
37 | 2688716.4355 | 1188372.2548
38 | 2688589.0594 | 1188315.5283
39 | 2689467.2592 | 1189210.1222
40 | 2689467.9885 | 1189215.7197
41 | 2689466.7965 | 1189206.5715
42 | 2689468.2335 | 1189217.5999
43 | 2689965.2935 | 1189444.891
44 | 2689979.0718 | 1189428.3112
45 | 2688989.8478 | 1188805.853
46 | 2688971.64 | 1188808.1652
47 | 2689005.135 | 1188728.6453
48 | 2688238.4465 | 1188995.5826
49 | 2688239.2235 | 1188995.4682
50 | 2688028.9924 | 1189438.5412
51 | 2688246.4271 | 1188992.7171
52 | 2687851.2918 | 1188946.8341
53 | 2687940.8727 | 1188717.7942
54 | 2687542.3415 | 1188862.0232
55 | 2687934.3716 | 1188411.8086
56 | 2687497.5045 | 1188969.424
57 | 2687921.9516 | 1188405.08
58 | 2687999.3688 | 1188415.8419
59 | 2689049.3357 | 1188675.6044
60 | 2689103.1951 | 1188660.5504
61 | 2688967.3209 | 1188663.0207
62 | 2689113.8208 | 1188669.8477
63 | 2689110.9398 | 1188639.4412
64 | 2688925.7008 | 1188662.8729
65 | 2688982.2856 | 1188692.3471
66 | 2689140.428 | 1188657.671
67 | 2688901.3071 | 1188669.9372
68 | 2688874.7658 | 1188678.859
69 | 2690401.2329 | 1189348.0545
70 | 2690360.8193 | 1189372.0116
71 | 2690321.5266 | 1189287.8427
72 | 2690392.9907 | 1189497.7285
73 | 2690358.8631 | 1189527.1324
74 | 2690203.1501 | 1189269.8474
75 | 2690197.3034 | 1189274.1556
76 | 2690274.3379 | 1189250.2113
77 | 2690143.6541 | 1189361.8431
78 | 2690293.1388 | 1189230.2957
79 | 2690142.6911 | 1189363.4852
80 | 2690064.4131 | 1189230.7416
81 | 2690064.1114 | 1189429.6891
82 | 2690129.393 | 1189568.8771
83 | 2690033.3185 | 1189425.0898
84 | 2690142.0233 | 1189590.9278
85 | 2690084.0386 | 1189350.9279
86 | 2690078.0665 | 1189355.8654
87 | 2690031.7882 | 1189192.6863
88 | 2690324.4481 | 1189602.5423
89 | 2690305.8326 | 1189637.1169
90 | 2690294.4079 | 1189656.0605
91 | 2688366.837 | 1188298.479
92 | 2688744.6967 | 1188712.3637
93 | 2688819.7706 | 1188692.5158
94 | 2688830.6824 | 1188745.3532
95 | 2688835.535 | 1188688.1814
96 | 2688863.9915 | 1188683.4695
97 | 2688866.8857 | 1188749.5284
98 | 2687487.8313 | 1189001.3576
99 | 2687469.9208 | 1189003.2201
100 | 2687126.5557 | 1189873.8506
101 | 2686550.9821 | 1189469.8897
102 | 2688549.2574 | 1190380.226
103 | 2687660.7866 | 1188011.9199
104 | 2687596.3986 | 1187999.9059
105 | 2689389.3058 | 1189247.2399

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98861 | -0.2208 | 0.00031965 | 8.0111e-05
1 | 0.99007 | -0.19212 | 0.00036769 | 9.2152e-05
2 | 0.98824 | -0.22805 | 0.00021666 | 5.4301e-05
3 | 0.99095 | -0.17501 | 0.00082513 | 0.0002068
4 | 0.98776 | -0.2375 | 0 | 0
5 | 0.98114 | -0.36804 | 0.00019121 | 4.7923e-05
6 | 0.98081 | -0.37459 | 0.00019027 | 4.7687e-05
7 | 0.98175 | -0.35599 | 0.00026136 | 6.5502e-05
8 | 0.99909 | -0.017578 | 0 | 0
9 | 0.98041 | -0.38272 | 0 | 0
10 | 0.98775 | -0.23763 | 0.00037812 | 9.4765e-05
11 | 0.98524 | -0.28699 | 0 | 0
12 | 0.9981 | -0.037141 | 0.00019185 | 4.8083e-05
13 | 1 | 0 | -0.037077 | -0.0089082
14 | 0.99747 | -0.049703 | 0.00028946 | 7.2547e-05
15 | 0.99747 | -0.049639 | 0.00022392 | 5.6119e-05
16 | 0.9975 | -0.049183 | 0 | 0
17 | 0.99743 | -0.050507 | 0.0006361 | 0.00015942
18 | 0.99766 | -0.045923 | 0.00025659 | 6.4307e-05
19 | 0.99737 | -0.051604 | 0.00020557 | 5.1521e-05
20 | 0.99707 | -0.05771 | 0.00026488 | 6.6385e-05
21 | 0.98615 | -0.2679 | 0.00033525 | 8.4023e-05
22 | 0.98623 | -0.26641 | 0 | 0
23 | 0.98537 | -0.28315 | 0.00062509 | 0.00015666
24 | 0.98626 | -0.26584 | 0.00019599 | 4.912e-05
25 | 0.98694 | -0.25247 | 0.0013229 | 0.00033156
26 | 0.98495 | -0.2927 | 0 | 0
27 | 0.98302 | -0.33082 | 0.00014105 | 3.5351e-05
28 | 0.98235 | -0.3441 | 0.00031187 | 7.8162e-05
29 | 0.98495 | -0.29283 | 0.00025436 | 6.3748e-05
30 | 0.98477 | -0.29633 | 0.00020848 | 5.2249e-05
31 | 0.97701 | -0.45077 | 0.0005359 | 0.00013431
32 | 0.97689 | -0.45333 | 0.00016126 | 4.0416e-05
33 | 0.97821 | -0.42658 | 0.00028463 | 7.1334e-05
34 | 0.97668 | -0.45752 | 0.00016406 | 4.1117e-05
35 | 0.97837 | -0.42336 | 0 | 0
36 | 0.97616 | -0.46813 | 0.0001524 | 3.8195e-05
37 | 0.97606 | -0.47013 | 0.00040793 | 0.00010224
38 | 0.97547 | -0.48218 | 0 | 0
39 | 0.9982 | -0.034416 | 0.00029865 | 7.4848e-05
40 | 0.99811 | -0.036064 | 0.00018926 | 4.7433e-05
41 | 0.99826 | -0.033352 | 0.00065977 | 0.00016535
42 | 0.99809 | -0.036612 | 0.00034548 | 8.6584e-05
43 | 0.99002 | -0.19229 | 0.0018469 | 0.00046289
44 | 0.98973 | -0.198 | 0.00051716 | 0.00012961
45 | 0.97843 | -0.4221 | 0.0001668 | 4.1804e-05
46 | 0.97843 | -0.42217 | 0.00022412 | 5.6169e-05
47 | 0.97847 | -0.42143 | 0.00015634 | 3.9182e-05
48 | 0.98476 | -0.29651 | 0.00031979 | 8.0148e-05
49 | 0.98476 | -0.2965 | 0.00035441 | 8.8822e-05
50 | 0.98467 | -0.29848 | 0.00021643 | 5.4243e-05
51 | 0.98477 | -0.29637 | 0.00018888 | 4.7338e-05
52 | 0.97197 | -0.55387 | 0.00020926 | 5.2446e-05
53 | 0.97242 | -0.54446 | 0 | 0
54 | 0.97157 | -0.56223 | 0 | 0
55 | 0.97286 | -0.5352 | 0.00021366 | 5.3548e-05
56 | 0.97141 | -0.56551 | 0.00052103 | 0.00013058
57 | 0.97283 | -0.53581 | 0.00024764 | 6.2065e-05
58 | 0.97313 | -0.5298 | 0 | 0
59 | 0.97821 | -0.42656 | 0.0002581 | 6.4687e-05
60 | 0.97813 | -0.42802 | 0 | 0
61 | 0.97851 | -0.4205 | 0 | 0
62 | 0.97812 | -0.42827 | 0.00093648 | 0.0002347
63 | 0.97812 | -0.42826 | 0 | 0
64 | 0.97884 | -0.41398 | 0.00038971 | 9.767e-05
65 | 0.97849 | -0.421 | 0.00028167 | 7.0594e-05
66 | 0.97811 | -0.42858 | 0.0004947 | 0.00012398
67 | 0.97905 | -0.40986 | 0.00013876 | 3.4776e-05
68 | 0.97928 | -0.40527 | 0.00022163 | 5.5547e-05
69 | 0.98725 | -0.24632 | 0.00067283 | 0.00016863
70 | 0.98728 | -0.24574 | 0 | 0
71 | 0.98734 | -0.24462 | 0.00064206 | 0.00016091
72 | 0.98511 | -0.28823 | 0.00046011 | 0.00011531
73 | 0.98513 | -0.28786 | 0.00090433 | 0.00022665
74 | 0.98749 | -0.24166 | 0 | 0
75 | 0.98752 | -0.24113 | 0.00058723 | 0.00014717
76 | 0.9873 | -0.2454 | 0.0020672 | 0.00051808
77 | 0.98796 | -0.23246 | 0 | 0
78 | 0.98728 | -0.24588 | 0.00069988 | 0.00017541
79 | 0.98797 | -0.23227 | 0 | 0
80 | 0.98782 | -0.23518 | 0.00039085 | 9.7957e-05
81 | 0.98866 | -0.21886 | 0.00036792 | 9.2209e-05
82 | 0.98778 | -0.23595 | 0.00038504 | 9.6501e-05
83 | 0.98886 | -0.21495 | 0 | 0
84 | 0.98765 | -0.2386 | 0.00057166 | 0.00014327
85 | 0.98787 | -0.23418 | 0.00047896 | 0.00012004
86 | 0.98787 | -0.23434 | 0.0011018 | 0.00027612
87 | 0.9878 | -0.23564 | 0.00050807 | 0.00012733
88 | 0.98524 | -0.28571 | 0 | 0
89 | 0.98529 | -0.28474 | 0.0010815 | 0.00027106
90 | 0.98534 | -0.28376 | 0.00030909 | 7.7465e-05
91 | 0.9746 | -0.49985 | 0 | 0
92 | 0.98189 | -0.35332 | 0.00026197 | 6.5655e-05
93 | 0.97977 | -0.39542 | 0 | 0
94 | 0.98025 | -0.38589 | 0.00015481 | 3.8798e-05
95 | 0.97962 | -0.39829 | 0.00020417 | 5.1169e-05
96 | 0.97937 | -0.4033 | 0.00022259 | 5.5787e-05
97 | 0.98039 | -0.38294 | 0.00038563 | 9.6649e-05
98 | 0.97138 | -0.56613 | 0.00018889 | 4.734e-05
99 | 0.97137 | -0.56636 | 0 | 0
100 | 0.97082 | -0.57809 | 0.00037641 | 9.4338e-05
101 | 0.97065 | -0.58167 | 0.00026421 | 6.6216e-05
102 | 0.99705 | -0.058101 | 0.00024268 | 6.0822e-05
103 | 0.97191 | -0.55407 | 0.0012393 | 0.00031059
104 | 0.97186 | -0.5551 | 0.00084978 | 0.00021298
105 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.014004 | -0.0034759 | 0.014023 | 0.0034866 | 1.9019e-05 | 1.0705e-05 | 0.021066 | 0.021066 | 0.021066 | 0.98861 | -0.2208 | 0.99007 | -0.19212 | 5.7874
1 | 0.013684 | 0.0033958 | -0.01368 | -0.0033931 | 4.6899e-06 | 2.6232e-06 | 0.020585 | 0.020585 | 0.020585 | 0.98861 | -0.2208 | 0.98824 | -0.22805 | 5.6553
2 | -0.014391 | -0.0035787 | 0.014402 | 0.0035853 | 1.167e-05 | 6.6118e-06 | 0.021618 | 0.021618 | 0.021618 | 0.99007 | -0.19212 | 0.99095 | -0.17501 | 5.9391
3 | 0.013463 | 0.0033388 | -0.013457 | -0.0033355 | 6.0114e-06 | 3.3471e-06 | 0.020259 | 0.020259 | 0.020259 | 0.98824 | -0.22805 | 0.98776 | -0.2375 | 5.5657
4 | -0.015227 | -0.0037921 | 0.015342 | 0.0038578 | 0.0001145 | 6.5688e-05 | 0.022857 | 0.022854 | 0.022857 | 0.99095 | -0.17501 | 0.99909 | -0.017578 | 6.2794
5 | 0.00037812 | 9.452e-05 | -0.00037812 | -9.4765e-05 | 2.3402e-09 | -2.4472e-07 | 0.00056953 | 0.00056962 | 0.00056962 | 0.98776 | -0.2375 | 0.98775 | -0.23763 | 0.15649
6 | 0.013079 | 0.003241 | -0.013048 | -0.0032241 | 3.0509e-05 | 1.6846e-05 | 0.01969 | 0.019691 | 0.019691 | 0.98776 | -0.2375 | 0.98524 | -0.28699 | 5.4095
7 | 0.010295 | 0.0025334 | -0.010292 | -0.0025318 | 3.1664e-06 | 1.5883e-06 | 0.015597 | 0.015597 | 0.015597 | 0.98114 | -0.36804 | 0.98081 | -0.37459 | 4.2849
8 | -0.010486 | -0.0025813 | 0.010492 | 0.0025843 | 5.9409e-06 | 3.009e-06 | 0.015887 | 0.015887 | 0.015887 | 0.98114 | -0.36804 | 0.98175 | -0.35599 | 4.3645
9 | 0.010101 | 0.0024841 | -0.010098 | -0.0024822 | 3.8565e-06 | 1.9145e-06 | 0.015308 | 0.015308 | 0.015308 | 0.98081 | -0.37459 | 0.98041 | -0.38272 | 4.2056
10 | -0.010753 | -0.0026498 | 0.010755 | 0.0026505 | 1.3521e-06 | 6.9336e-07 | 0.016283 | 0.016283 | 0.016283 | 0.98175 | -0.35599 | 0.98189 | -0.35332 | 4.4733
11 | 0.0023146 | 0.00055414 | -0.0023125 | -0.00055897 | 2.092e-06 | -4.8308e-06 | 0.0034383 | 0.0034404 | 0.0034404 | 0.99909 | -0.017578 | 0.9981 | -0.037141 | 0.94517
12 | -0.017657 | -0.004412 | 0.017671 | 0.0044184 | 1.4762e-05 | 6.4621e-06 | 0.026293 | 0.026291 | 0.026293 | 0.99909 | -0.017578 | 1 | 0 | 3.6116
13 | 0.00038564 | 9.6246e-05 | -0.00038563 | -9.6649e-05 | 4.1349e-09 | -4.0332e-07 | 0.00058516 | 0.00058531 | 0.00058531 | 0.98041 | -0.38272 | 0.98039 | -0.38294 | 0.1608
14 | 0.009712 | 0.002386 | -0.0097105 | -0.0023853 | 1.4478e-06 | 7.0205e-07 | 0.014723 | 0.014723 | 0.014723 | 0.98041 | -0.38272 | 0.98025 | -0.38589 | 4.0449
15 | 0.001543 | 0.00037568 | -0.0015426 | -0.000378 | 4.1139e-07 | -2.316e-06 | 0.0023265 | 0.0023274 | 0.0023274 | 0.98524 | -0.28699 | 0.98495 | -0.2927 | 0.6394
16 | 0.011505 | 0.0028484 | -0.011482 | -0.0028359 | 2.3754e-05 | 1.2533e-05 | 0.017364 | 0.017365 | 0.017365 | 0.98524 | -0.28699 | 0.98302 | -0.33082 | 4.7706
17 | 0.0021206 | 0.00051089 | -0.0021198 | -0.00051336 | 8.632e-07 | -2.4687e-06 | 0.0031544 | 0.0031554 | 0.0031554 | 0.9981 | -0.037141 | 0.99766 | -0.045923 | 0.86688
18 | 0.017756 | 0.0044897 | -0.017728 | -0.004473 | 2.8358e-05 | 1.6732e-05 | 0.026435 | 0.026436 | 0.026436 | 1 | 0 | 0.99826 | -0.033352 | 7.2626
19 | -0.00028946 | -7.2547e-05 | 0.00028947 | 7.2383e-05 | 8.7823e-10 | -1.634e-07 | 0.00043182 | 0.00043176 | 0.00043182 | 0.99747 | -0.049703 | 0.99747 | -0.049639 | 0.11863
20 | -0.00051338 | -0.0001285 | 0.00051339 | 0.00012785 | 1.1139e-08 | -6.5423e-07 | 0.0007658 | 0.00076557 | 0.0007658 | 0.99747 | -0.049639 | 0.9975 | -0.049183 | 0.21038
21 | 0.0013495 | 0.0003223 | -0.0013494 | -0.00032295 | 8.2222e-08 | -6.5734e-07 | 0.0020076 | 0.0020079 | 0.0020079 | 0.9975 | -0.049183 | 0.99743 | -0.050507 | 0.55162
22 | -0.0018629 | -0.00045014 | 0.0018632 | 0.00044905 | 2.8134e-07 | -1.0938e-06 | 0.0027732 | 0.0027727 | 0.0027732 | 0.9975 | -0.049183 | 0.99766 | -0.045923 | 0.76186
23 | 0.00020558 | 4.7644e-05 | -0.00020557 | -5.1521e-05 | 1.0451e-08 | -3.8771e-06 | 0.00030538 | 0.0003067 | 0.0003067 | 0.99743 | -0.050507 | 0.99737 | -0.051604 | 0.084258
24 | 0.00050773 | 0.00011589 | -0.00050757 | -0.00012602 | 1.6789e-07 | -1.0131e-05 | 0.00075364 | 0.00075707 | 0.00075707 | 0.99743 | -0.050507 | 0.99707 | -0.05771 | 0.20799
25 | 0.00024269 | 5.9636e-05 | -0.00024268 | -6.0822e-05 | 4.4814e-09 | -1.1866e-06 | 0.00036177 | 0.00036219 | 0.00036219 | 0.99707 | -0.05771 | 0.99705 | -0.058101 | 0.099502
26 | -0.0037183 | -0.00092717 | 0.0037185 | 0.00092706 | 2.6297e-07 | -1.1612e-07 | 0.0056089 | 0.0056088 | 0.0056089 | 0.98615 | -0.2679 | 0.98623 | -0.26641 | 1.5409
27 | 0.003383 | 0.00084315 | -0.0033806 | -0.00084478 | 2.4477e-06 | -1.6282e-06 | 0.005103 | 0.0051041 | 0.0051041 | 0.98615 | -0.2679 | 0.98537 | -0.28315 | 1.4022
28 | -0.0037185 | -0.00092706 | 0.0037186 | 0.00092701 | 1.0145e-07 | -4.4812e-08 | 0.0056088 | 0.0056087 | 0.0056088 | 0.98623 | -0.26641 | 0.98626 | -0.26584 | 1.5409
29 | 0.0027555 | 0.00068811 | -0.0027554 | -0.00068822 | 8.0697e-08 | -1.0673e-07 | 0.0041602 | 0.0041602 | 0.0041602 | 0.98537 | -0.28315 | 0.98534 | -0.28376 | 1.1429
30 | -0.0039146 | -0.00097613 | 0.0039171 | 0.00097529 | 2.4833e-06 | -8.3669e-07 | 0.0059044 | 0.0059036 | 0.0059044 | 0.98626 | -0.26584 | 0.98694 | -0.25247 | 1.6221
31 | -0.00524 | -0.0013069 | 0.0052435 | 0.0013072 | 3.4508e-06 | 3.2194e-07 | 0.0078982 | 0.0078975 | 0.0078982 | 0.98694 | -0.25247 | 0.98765 | -0.2386 | 2.1698
32 | 0.00025436 | 6.3376e-05 | -0.00025436 | -6.3748e-05 | 1.6197e-09 | -3.7138e-07 | 0.00038414 | 0.00038427 | 0.00038427 | 0.98495 | -0.2927 | 0.98495 | -0.29283 | 0.10557
33 | 0.0012882 | 0.00031462 | -0.001288 | -0.00031645 | 2.1882e-07 | -1.8255e-06 | 0.0019433 | 0.001944 | 0.001944 | 0.98495 | -0.2927 | 0.98477 | -0.29633 | 0.53406
34 | 0.01134 | 0.0028006 | -0.011333 | -0.0027968 | 7.0938e-06 | 3.7254e-06 | 0.017152 | 0.017152 | 0.017152 | 0.98302 | -0.33082 | 0.98235 | -0.3441 | 4.712
35 | 0.011022 | 0.0027187 | -0.011017 | -0.0027162 | 4.7795e-06 | 2.4791e-06 | 0.016679 | 0.01668 | 0.01668 | 0.98235 | -0.3441 | 0.98189 | -0.35332 | 4.5823
36 | 0.0010795 | 0.0002642 | -0.0010795 | -0.00026423 | 2.219e-09 | -2.6951e-08 | 0.001629 | 0.001629 | 0.001629 | 0.98477 | -0.29633 | 0.98477 | -0.29637 | 0.44752
37 | 0.0050168 | 0.0012113 | -0.0050162 | -0.0012113 | 5.966e-07 | 3.9154e-08 | 0.0076245 | 0.0076246 | 0.0076246 | 0.97701 | -0.45077 | 0.97689 | -0.45333 | 2.0947
38 | -0.0055527 | -0.0013456 | 0.005559 | 0.0013467 | 6.2419e-06 | 1.0651e-06 | 0.0084407 | 0.0084396 | 0.0084407 | 0.97701 | -0.45077 | 0.97821 | -0.42658 | 2.3189
39 | 0.004855 | 0.0011709 | -0.004854 | -0.0011708 | 9.4043e-07 | 2.538e-08 | 0.007379 | 0.0073792 | 0.0073792 | 0.97689 | -0.45333 | 0.97668 | -0.45752 | 2.0273
40 | -0.0058436 | -0.001418 | 0.0058445 | 0.0014182 | 8.7569e-07 | 1.8799e-07 | 0.0088726 | 0.0088725 | 0.0088726 | 0.97821 | -0.42658 | 0.97837 | -0.42336 | 2.4375
41 | 0.00469 | 0.0011297 | -0.0046877 | -0.0011298 | 2.3036e-06 | -3.73e-08 | 0.0071292 | 0.0071298 | 0.0071298 | 0.97668 | -0.45752 | 0.97616 | -0.46813 | 1.9587
42 | -0.0075341 | -0.0018389 | 0.0075351 | 0.0018393 | 1.0076e-06 | 3.8707e-07 | 0.011441 | 0.011441 | 0.011441 | 0.97837 | -0.42336 | 0.97851 | -0.4205 | 3.1432
43 | 0.0016897 | 0.00042066 | -0.0016894 | -0.00042179 | 2.5631e-07 | -1.1362e-06 | 0.0025688 | 0.0025693 | 0.0025693 | 0.97837 | -0.42336 | 0.97821 | -0.42656 | 0.70585
44 | 0.0045353 | 0.0010916 | -0.0045348 | -0.0010916 | 4.1871e-07 | -2.5386e-08 | 0.0068975 | 0.0068976 | 0.0068976 | 0.97616 | -0.46813 | 0.97606 | -0.47013 | 1.8949
45 | 0.0041269 | 0.00098936 | -0.0041246 | -0.00098983 | 2.2937e-06 | -4.7173e-07 | 0.0062757 | 0.0062764 | 0.0062764 | 0.97606 | -0.47013 | 0.97547 | -0.48218 | 1.7243
46 | 0.0041246 | 0.00098983 | -0.0041212 | -0.00099052 | 3.3641e-06 | -6.8685e-07 | 0.0062764 | 0.0062774 | 0.0062774 | 0.97547 | -0.48218 | 0.9746 | -0.49985 | 1.7245
47 | 0.016769 | 0.0042322 | -0.016767 | -0.0042315 | 1.3238e-06 | 7.7344e-07 | 0.025007 | 0.025007 | 0.025007 | 0.9982 | -0.034416 | 0.99811 | -0.036064 | 6.8701
48 | -0.017067 | -0.0043071 | 0.017068 | 0.0043076 | 8.6989e-07 | 5.0992e-07 | 0.025453 | 0.025452 | 0.025453 | 0.9982 | -0.034416 | 0.99826 | -0.033352 | 6.9924
49 | 0.016578 | 0.004184 | -0.016578 | -0.0041838 | 4.3467e-07 | 2.5341e-07 | 0.024725 | 0.024725 | 0.024725 | 0.99811 | -0.036064 | 0.99809 | -0.036612 | 6.7926
50 | 0.016232 | 0.0040972 | -0.016112 | -0.0040274 | 0.00012015 | 6.9808e-05 | 0.02421 | 0.024213 | 0.024213 | 0.99809 | -0.036612 | 0.99002 | -0.19229 | 6.6518
51 | 0.014265 | 0.0035645 | -0.014261 | -0.0035623 | 3.8679e-06 | 2.1869e-06 | 0.021437 | 0.021437 | 0.021437 | 0.99002 | -0.19229 | 0.98973 | -0.198 | 5.8892
52 | 0.013744 | 0.0034327 | -0.013733 | -0.0034265 | 1.1063e-05 | 6.193e-06 | 0.020659 | 0.02066 | 0.02066 | 0.98973 | -0.198 | 0.98886 | -0.21495 | 5.6757
53 | 0.00022412 | 5.5939e-05 | -0.00022412 | -5.6169e-05 | 8.0121e-10 | -2.3052e-07 | 0.00034076 | 0.00034084 | 0.00034084 | 0.97843 | -0.4221 | 0.97843 | -0.42217 | 0.093638
54 | -0.00039092 | -9.7743e-05 | 0.00039093 | 9.6584e-05 | 1.2308e-08 | -1.1596e-06 | 0.00059444 | 0.00059402 | 0.00059444 | 0.97843 | -0.4221 | 0.97847 | -0.42143 | 0.16331
55 | -0.00054727 | -0.00013577 | 0.00054728 | 0.00013523 | 1.1143e-08 | -5.3247e-07 | 0.00083177 | 0.00083158 | 0.00083177 | 0.97847 | -0.42143 | 0.97849 | -0.421 | 0.22851
56 | -0.00053625 | -0.00012817 | 0.00053625 | 0.00012816 | 1.9236e-10 | -9.8699e-09 | 0.00080812 | 0.00080811 | 0.00080812 | 0.98476 | -0.29651 | 0.98476 | -0.2965 | 0.22201
57 | 0.00021645 | 4.8023e-05 | -0.00021643 | -5.4243e-05 | 1.9526e-08 | -6.2207e-06 | 0.00032497 | 0.00032707 | 0.00032707 | 0.98476 | -0.29651 | 0.98467 | -0.29848 | 0.089855
58 | -0.00089065 | -0.00021698 | 0.00089066 | 0.00021689 | 5.2201e-09 | -9.4763e-08 | 0.0013436 | 0.0013436 | 0.0013436 | 0.98476 | -0.2965 | 0.98477 | -0.29637 | 0.36912
59 | -0.0015609 | -0.00036514 | 0.0015616 | 0.00036169 | 6.6397e-07 | -3.4514e-06 | 0.0023805 | 0.0023792 | 0.0023805 | 0.97197 | -0.55387 | 0.97242 | -0.54446 | 0.654
60 | 0.0013517 | 0.0003127 | -0.0013511 | -0.00031634 | 5.1028e-07 | -3.6426e-06 | 0.0020602 | 0.0020616 | 0.0020616 | 0.97197 | -0.55387 | 0.97157 | -0.56223 | 0.56636
61 | -0.0015616 | -0.00036169 | 0.0015622 | 0.00035831 | 6.4934e-07 | -3.3829e-06 | 0.0023792 | 0.002378 | 0.0023792 | 0.97242 | -0.54446 | 0.97286 | -0.5352 | 0.65364
62 | 0.0013511 | 0.00031634 | -0.0013509 | -0.00031777 | 2.013e-07 | -1.4346e-06 | 0.0020616 | 0.0020621 | 0.0020621 | 0.97157 | -0.56223 | 0.97141 | -0.56551 | 0.56651
63 | 0.0023386 | 0.00058002 | -0.0023386 | -0.00058015 | 6.7693e-08 | -1.3207e-07 | 0.0035748 | 0.0035748 | 0.0035748 | 0.97286 | -0.5352 | 0.97283 | -0.53581 | 0.9821
64 | -0.0041145 | -0.00099187 | 0.0041155 | 0.00099167 | 1.0286e-06 | -2.0575e-07 | 0.0062793 | 0.006279 | 0.0062793 | 0.97286 | -0.5352 | 0.97313 | -0.5298 | 1.7251
65 | 0.00082992 | 0.00018719 | -0.00082989 | -0.00018765 | 2.2786e-08 | -4.5609e-07 | 0.0012641 | 0.0012643 | 0.0012643 | 0.97141 | -0.56551 | 0.97138 | -0.56613 | 0.34733
66 | 0.0020909 | 0.00051808 | -0.0020891 | -0.00052278 | 1.8092e-06 | -4.697e-06 | 0.0031961 | 0.0031982 | 0.0031982 | 0.97283 | -0.53581 | 0.97191 | -0.55407 | 0.87862
67 | -0.0041155 | -0.00099167 | 0.0041212 | 0.00099052 | 5.7018e-06 | -1.1506e-06 | 0.006279 | 0.0062774 | 0.006279 | 0.97313 | -0.5298 | 0.9746 | -0.49985 | 1.725
68 | 0.0014313 | 0.00035711 | -0.0014312 | -0.00035774 | 9.9372e-08 | -6.384e-07 | 0.0021767 | 0.0021769 | 0.0021769 | 0.97821 | -0.42656 | 0.97813 | -0.42802 | 0.59806
69 | 0.00093649 | 0.00023453 | -0.00093648 | -0.0002347 | 1.1013e-08 | -1.7457e-07 | 0.0014246 | 0.0014247 | 0.0014247 | 0.97813 | -0.42802 | 0.97812 | -0.42827 | 0.39139
70 | 0.00049472 | 0.00012321 | -0.00049471 | -0.00012354 | 5.5424e-09 | -3.2416e-07 | 0.00075232 | 0.00075244 | 0.00075244 | 0.97813 | -0.42802 | 0.97812 | -0.42826 | 0.20671
71 | -0.0083641 | -0.0020447 | 0.0083667 | 0.0020458 | 2.5526e-06 | 1.1034e-06 | 0.012701 | 0.012701 | 0.012701 | 0.97851 | -0.4205 | 0.97884 | -0.41398 | 3.4893
72 | 0.00082898 | 0.00020543 | -0.00082896 | -0.00020583 | 1.9619e-08 | -4.0147e-07 | 0.0012598 | 0.0012599 | 0.0012599 | 0.97851 | -0.4205 | 0.97849 | -0.421 | 0.34614
73 | 0.00049471 | 0.00012354 | -0.0004947 | -0.00012398 | 7.6349e-09 | -4.4637e-07 | 0.00075244 | 0.0007526 | 0.0007526 | 0.97812 | -0.42826 | 0.97811 | -0.42858 | 0.20676
74 | -0.0087564 | -0.0021435 | 0.0087581 | 0.0021442 | 1.686e-06 | 7.5913e-07 | 0.013293 | 0.013293 | 0.013293 | 0.97884 | -0.41398 | 0.97905 | -0.40986 | 3.652
75 | -0.0088968 | -0.002179 | 0.0088987 | 0.0021799 | 1.9157e-06 | 8.7366e-07 | 0.013504 | 0.013504 | 0.013504 | 0.97905 | -0.40986 | 0.97928 | -0.40527 | 3.7099
76 | -0.0091204 | -0.0022354 | 0.0091212 | 0.0022358 | 8.4186e-07 | 3.9133e-07 | 0.013841 | 0.013841 | 0.013841 | 0.97928 | -0.40527 | 0.97937 | -0.4033 | 3.8024
77 | -0.00067283 | -0.00016863 | 0.00067285 | 0.00016803 | 1.8392e-08 | -5.982e-07 | 0.0010141 | 0.0010139 | 0.0010141 | 0.98725 | -0.24632 | 0.98728 | -0.24574 | 0.2786
78 | -0.00067285 | -0.00016803 | 0.00067289 | 0.00016686 | 3.5793e-08 | -1.165e-06 | 0.0010139 | 0.0010135 | 0.0010139 | 0.98728 | -0.24574 | 0.98734 | -0.24462 | 0.27854
79 | -0.0013149 | -0.00032778 | 0.0013151 | 0.00032629 | 1.8433e-07 | -1.4844e-06 | 0.0019811 | 0.0019806 | 0.0019811 | 0.98734 | -0.24462 | 0.98749 | -0.24166 | 0.54426
80 | -0.00046011 | -0.00011531 | 0.00046012 | 0.00011475 | 8.1573e-09 | -5.6832e-07 | 0.000695 | 0.0006948 | 0.000695 | 0.98511 | -0.28823 | 0.98513 | -0.28786 | 0.19093
81 | -0.0013645 | -0.00034139 | 0.0013646 | 0.00034037 | 1.3947e-07 | -1.0261e-06 | 0.0020608 | 0.0020604 | 0.0020608 | 0.98513 | -0.28786 | 0.98524 | -0.28571 | 0.56614
82 | -0.0040827 | -0.0010187 | 0.0040828 | 0.0010186 | 1.0302e-07 | -2.6979e-08 | 0.0061504 | 0.0061504 | 0.0061504 | 0.98749 | -0.24166 | 0.98752 | -0.24113 | 1.6897
83 | 0.0027676 | 0.00069236 | -0.0027671 | -0.00069301 | 4.9251e-07 | -6.5082e-07 | 0.0041699 | 0.0041702 | 0.0041702 | 0.98749 | -0.24166 | 0.9873 | -0.2454 | 1.1457
84 | -0.00467 | -0.0011658 | 0.0046719 | 0.0011657 | 1.9221e-06 | -9.5446e-08 | 0.0070353 | 0.0070348 | 0.0070353 | 0.98752 | -0.24113 | 0.98796 | -0.23246 | 1.9328
85 | 0.00069989 | 0.00017493 | -0.00069988 | -0.00017541 | 1.595e-08 | -4.7869e-07 | 0.0010547 | 0.0010549 | 0.0010549 | 0.9873 | -0.2454 | 0.98728 | -0.24588 | 0.28979
86 | -0.005571 | -0.0013883 | 0.005571 | 0.0013883 | 5.0209e-08 | 7.7647e-09 | 0.0083879 | 0.0083879 | 0.0083879 | 0.98796 | -0.23246 | 0.98797 | -0.23227 | 2.3044
87 | 0.00089905 | 0.00022257 | -0.00089893 | -0.00022466 | 1.1584e-07 | -2.0848e-06 | 0.0013531 | 0.0013539 | 0.0013539 | 0.98796 | -0.23246 | 0.98782 | -0.23518 | 0.37195
88 | 0.0015809 | 0.00039529 | -0.0015807 | -0.00039607 | 1.4381e-07 | -7.7424e-07 | 0.0023807 | 0.002381 | 0.002381 | 0.98797 | -0.23227 | 0.98787 | -0.23418 | 0.65411
89 | -0.0071519 | -0.0017836 | 0.0071578 | 0.0017856 | 5.8822e-06 | 2.0308e-06 | 0.010769 | 0.010768 | 0.010769 | 0.98797 | -0.23227 | 0.98886 | -0.21495 | 2.9584
90 | 0.00050808 | 0.0001267 | -0.00050807 | -0.00012733 | 1.1007e-08 | -6.3464e-07 | 0.00076512 | 0.00076535 | 0.00076535 | 0.98782 | -0.23518 | 0.9878 | -0.23564 | 0.21026
91 | 0.006206 | 0.0015483 | -0.0062009 | -0.0015471 | 5.0324e-06 | 1.2491e-06 | 0.009338 | 0.0093387 | 0.0093387 | 0.98866 | -0.21886 | 0.98778 | -0.23595 | 2.5656
92 | -0.0065739 | -0.0016405 | 0.0065751 | 0.0016409 | 1.2196e-06 | 3.5423e-07 | 0.0098918 | 0.0098916 | 0.0098918 | 0.98866 | -0.21886 | 0.98886 | -0.21495 | 2.7175
93 | 0.0058159 | 0.0014506 | -0.0058152 | -0.0014504 | 7.3105e-07 | 1.4263e-07 | 0.0087587 | 0.0087588 | 0.0087588 | 0.98778 | -0.23595 | 0.98765 | -0.2386 | 2.4063
94 | 0.0011018 | 0.00027603 | -0.0011018 | -0.00027612 | 8.0029e-09 | -9.4087e-08 | 0.0016595 | 0.0016596 | 0.0016596 | 0.98787 | -0.23418 | 0.98787 | -0.23434 | 0.45592
95 | -0.0013646 | -0.00034037 | 0.0013647 | 0.00033991 | 6.2634e-08 | -4.6104e-07 | 0.0020604 | 0.0020602 | 0.0020604 | 0.98524 | -0.28571 | 0.98529 | -0.28474 | 0.56604
96 | -0.0024462 | -0.00061097 | 0.0024463 | 0.00061076 | 1.1338e-07 | -2.0971e-07 | 0.0036936 | 0.0036935 | 0.0036936 | 0.98529 | -0.28474 | 0.98534 | -0.28376 | 1.0147
97 | -0.0095514 | -0.0023444 | 0.0095557 | 0.0023465 | 4.268e-06 | 2.0484e-06 | 0.014489 | 0.014488 | 0.014489 | 0.97977 | -0.39542 | 0.98025 | -0.38589 | 3.9804
98 | 0.0095514 | 0.0023444 | -0.0095502 | -0.0023438 | 1.287e-06 | 6.1783e-07 | 0.014489 | 0.014489 | 0.014489 | 0.97977 | -0.39542 | 0.97962 | -0.39829 | 3.9804
99 | 0.009346 | 0.0022926 | -0.0093438 | -0.0022916 | 2.1918e-06 | 1.0368e-06 | 0.014179 | 0.014179 | 0.014179 | 0.97962 | -0.39829 | 0.97937 | -0.4033 | 3.8953
100 | 0.000641 | 0.00014031 | -0.000641 | -0.00014052 | 6.4199e-09 | -2.188e-07 | 0.00097502 | 0.00097509 | 0.00097509 | 0.97138 | -0.56613 | 0.97137 | -0.56636 | 0.26788
101 | 0.000641 | 0.00014052 | -0.00064066 | -0.00015189 | 3.3498e-07 | -1.1364e-05 | 0.00097509 | 0.00097891 | 0.00097891 | 0.97137 | -0.56636 | 0.97082 | -0.57809 | 0.26893
102 | 0.00026425 | 5.7551e-05 | -0.00026421 | -6.6216e-05 | 4.2935e-08 | -8.6658e-06 | 0.00040209 | 0.00040503 | 0.00040503 | 0.97082 | -0.57809 | 0.97065 | -0.58167 | 0.11127
103 | 0.00084983 | 0.00021219 | -0.00084978 | -0.00021298 | 4.1615e-08 | -7.8588e-07 | 0.0013008 | 0.0013011 | 0.0013011 | 0.97191 | -0.55407 | 0.97186 | -0.5551 | 0.35745

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.037245 | 0.0089503

## res_load
| p_mw | q_mvar
0 | 0.00031965 | 8.0111e-05
1 | 0.00036769 | 9.2152e-05
2 | 0.00021666 | 5.4301e-05
3 | 0.00082513 | 0.0002068
4 | 0.00019121 | 4.7923e-05
5 | 0.00019027 | 4.7687e-05
6 | 0.00026136 | 6.5502e-05
7 | 0.00037812 | 9.4765e-05
8 | 0.00019185 | 4.8083e-05
9 | 0.00016787 | 4.2073e-05
10 | 0.00028946 | 7.2547e-05
11 | 0.00022392 | 5.6119e-05
12 | 0.0006361 | 0.00015942
13 | 0.00025659 | 6.4307e-05
14 | 0.00020557 | 5.1521e-05
15 | 0.00026488 | 6.6385e-05
16 | 0.00033525 | 8.4023e-05
17 | 0.00062509 | 0.00015666
18 | 0.00019599 | 4.912e-05
19 | 0.0013229 | 0.00033156
20 | 0.00014105 | 3.5351e-05
21 | 0.00031187 | 7.8162e-05
22 | 0.00025436 | 6.3748e-05
23 | 0.00020848 | 5.2249e-05
24 | 0.0005359 | 0.00013431
25 | 0.00016126 | 4.0416e-05
26 | 0.00028463 | 7.1334e-05
27 | 0.00016406 | 4.1117e-05
28 | 0.0001524 | 3.8195e-05
29 | 0.00040793 | 0.00010224
30 | 0.00029865 | 7.4848e-05
31 | 0.00018926 | 4.7433e-05
32 | 0.00065977 | 0.00016535
33 | 0.00034548 | 8.6584e-05
34 | 0.0018469 | 0.00046289
35 | 0.00051716 | 0.00012961
36 | 0.0001668 | 4.1804e-05
37 | 0.00022412 | 5.6169e-05
38 | 0.00015634 | 3.9182e-05
39 | 0.00031979 | 8.0148e-05
40 | 0.00035441 | 8.8822e-05
41 | 0.00021643 | 5.4243e-05
42 | 0.00018888 | 4.7338e-05
43 | 0.00020926 | 5.2446e-05
44 | 0.00021366 | 5.3548e-05
45 | 0.00052103 | 0.00013058
46 | 0.00024764 | 6.2065e-05
47 | 0.0002581 | 6.4687e-05
48 | 0.00093648 | 0.0002347
49 | 0.00038971 | 9.767e-05
50 | 0.00028167 | 7.0594e-05
51 | 0.0004947 | 0.00012398
52 | 0.00013876 | 3.4776e-05
53 | 0.00022163 | 5.5547e-05
54 | 0.00067283 | 0.00016863
55 | 0.00064206 | 0.00016091
56 | 0.00046011 | 0.00011531
57 | 0.00090433 | 0.00022665
58 | 0.00058723 | 0.00014717
59 | 0.0020672 | 0.00051808
60 | 0.00069988 | 0.00017541
61 | 0.00039085 | 9.7957e-05
62 | 0.00036792 | 9.2209e-05
63 | 0.00038504 | 9.6501e-05
64 | 0.00057166 | 0.00014327
65 | 0.00047896 | 0.00012004
66 | 0.0011018 | 0.00027612
67 | 0.00050807 | 0.00012733
68 | 0.0010815 | 0.00027106
69 | 0.00030909 | 7.7465e-05
70 | 0.00026197 | 6.5655e-05
71 | 0.00015481 | 3.8798e-05
72 | 0.00020417 | 5.1169e-05
73 | 0.00022259 | 5.5787e-05
74 | 0.00038563 | 9.6649e-05
75 | 0.00018889 | 4.734e-05
76 | 0.00037641 | 9.4338e-05
77 | 0.00026421 | 6.6216e-05
78 | 0.00024268 | 6.0822e-05
79 | 0.0012393 | 0.00031059
80 | 0.00084978 | 0.00021298

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1