## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1203-2_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1203-2_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1203-2_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1203-2_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1203-2_0_5_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1203-2_0_5_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1203-2_0_5_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_1203-2_0_5_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_1203-2_0_5_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_1203-2_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1203-2_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1203-2_0_5_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_1203-2_0_5_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_1203-2_0_5_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_1203-2_0_5_node_28 | 0.4 | n |  | TRUE
15 | bus_LV_1203-2_0_5_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_1203-2_0_5_node_34 | 0.4 | n |  | TRUE
17 | bus_LV_1203-2_0_5_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_1203-2_0_5_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1203-2_0_5_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_1203-2_0_5_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1203-2_0_5_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_1203-2_0_5_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_1203-2_0_5_node_37 | 0.4 | n |  | TRUE
24 | bus_LV_1203-2_0_5_node_63 | 0.4 | n |  | TRUE
25 | bus_LV_1203-2_0_5_node_38 | 0.4 | n |  | TRUE
26 | bus_LV_1203-2_0_5_node_45 | 0.4 | n |  | TRUE
27 | bus_LV_1203-2_0_5_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1203-2_0_5_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1203-2_0_5_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1203-2_0_5_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_1203-2_0_5_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_1203-2_0_5_node_53 | 0.4 | n |  | TRUE
33 | bus_LV_1203-2_0_5_node_51 | 0.4 | n |  | TRUE
34 | bus_LV_1203-2_0_5_node_43 | 0.4 | n |  | TRUE
35 | bus_LV_1203-2_0_5_node_134 | 0.4 | n |  | TRUE
36 | bus_LV_1203-2_0_5_node_44 | 0.4 | n |  | TRUE
37 | bus_LV_1203-2_0_5_node_132 | 0.4 | n |  | TRUE
38 | bus_LV_1203-2_0_5_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_1203-2_0_5_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_1203-2_0_5_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_1203-2_0_5_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_1203-2_0_5_node_31 | 0.4 | n |  | TRUE
43 | bus_LV_1203-2_0_5_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_1203-2_0_5_node_60 | 0.4 | n |  | TRUE
45 | bus_LV_1203-2_0_5_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_1203-2_0_5_node_46 | 0.4 | n |  | TRUE
47 | bus_LV_1203-2_0_5_node_47 | 0.4 | n |  | TRUE
48 | bus_LV_1203-2_0_5_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_1203-2_0_5_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_1203-2_0_5_node_41 | 0.4 | n |  | TRUE
51 | bus_LV_1203-2_0_5_node_55 | 0.4 | n |  | TRUE
52 | bus_LV_1203-2_0_5_node_42 | 0.4 | n |  | TRUE
53 | bus_LV_1203-2_0_5_node_56 | 0.4 | n |  | TRUE
54 | bus_LV_1203-2_0_5_node_52 | 0.4 | n |  | TRUE
55 | bus_LV_1203-2_0_5_node_48 | 0.4 | n |  | TRUE
56 | bus_LV_1203-2_0_5_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_1203-2_0_5_node_50 | 0.4 | n |  | TRUE
58 | bus_LV_1203-2_0_5_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_1203-2_0_5_node_57 | 0.4 | n |  | TRUE
60 | bus_LV_1203-2_0_5_node_58 | 0.4 | n |  | TRUE
61 | bus_LV_1203-2_0_5_node_61 | 0.4 | n |  | TRUE
62 | bus_LV_1203-2_0_5_node_64 | 0.4 | n |  | TRUE
63 | bus_LV_1203-2_0_5_node_59 | 0.4 | n |  | TRUE
64 | bus_LV_1203-2_0_5_node_62 | 0.4 | n |  | TRUE
65 | bus_LV_1203-2_0_5_node_141 | 0.4 | n |  | TRUE
66 | bus_LV_1203-2_0_5_node_69 | 0.4 | n |  | TRUE
67 | bus_LV_1203-2_0_5_node_142 | 0.4 | n |  | TRUE
68 | bus_LV_1203-2_0_5_node_67 | 0.4 | n |  | TRUE
69 | bus_LV_1203-2_0_5_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_1203-2_0_5_node_66 | 0.4 | n |  | TRUE
71 | bus_LV_1203-2_0_5_node_68 | 0.4 | n |  | TRUE
72 | bus_LV_1203-2_0_5_node_70 | 0.4 | n |  | TRUE
73 | bus_LV_1203-2_0_5_node_71 | 0.4 | n |  | TRUE
74 | bus_LV_1203-2_0_5_node_72 | 0.4 | n |  | TRUE
75 | bus_LV_1203-2_0_5_node_113 | 0.4 | n |  | TRUE
76 | bus_LV_1203-2_0_5_node_114 | 0.4 | n |  | TRUE
77 | bus_LV_1203-2_0_5_node_73 | 0.4 | n |  | TRUE
78 | bus_LV_1203-2_0_5_node_74 | 0.4 | n |  | TRUE
79 | bus_LV_1203-2_0_5_node_76 | 0.4 | n |  | TRUE
80 | bus_LV_1203-2_0_5_node_75 | 0.4 | n |  | TRUE
81 | bus_LV_1203-2_0_5_node_77 | 0.4 | n |  | TRUE
82 | bus_LV_1203-2_0_5_node_78 | 0.4 | n |  | TRUE
83 | bus_LV_1203-2_0_5_node_115 | 0.4 | n |  | TRUE
84 | bus_LV_1203-2_0_5_node_93 | 0.4 | n |  | TRUE
85 | bus_LV_1203-2_0_5_node_85 | 0.4 | n |  | TRUE
86 | bus_LV_1203-2_0_5_node_116 | 0.4 | n |  | TRUE
87 | bus_LV_1203-2_0_5_node_90 | 0.4 | n |  | TRUE
88 | bus_LV_1203-2_0_5_node_84 | 0.4 | n |  | TRUE
89 | bus_LV_1203-2_0_5_node_79 | 0.4 | n |  | TRUE
90 | bus_LV_1203-2_0_5_node_80 | 0.4 | n |  | TRUE
91 | bus_LV_1203-2_0_5_node_81 | 0.4 | n |  | TRUE
92 | bus_LV_1203-2_0_5_node_82 | 0.4 | n |  | TRUE
93 | bus_LV_1203-2_0_5_node_83 | 0.4 | n |  | TRUE
94 | bus_LV_1203-2_0_5_node_94 | 0.4 | n |  | TRUE
95 | bus_LV_1203-2_0_5_node_112 | 0.4 | n |  | TRUE
96 | bus_LV_1203-2_0_5_node_129 | 0.4 | n |  | TRUE
97 | bus_LV_1203-2_0_5_node_127 | 0.4 | n |  | TRUE
98 | bus_LV_1203-2_0_5_node_110 | 0.4 | n |  | TRUE
99 | bus_LV_1203-2_0_5_node_86 | 0.4 | n |  | TRUE
100 | bus_LV_1203-2_0_5_node_87 | 0.4 | n |  | TRUE
101 | bus_LV_1203-2_0_5_node_88 | 0.4 | n |  | TRUE
102 | bus_LV_1203-2_0_5_node_119 | 0.4 | n |  | TRUE
103 | bus_LV_1203-2_0_5_node_128 | 0.4 | n |  | TRUE
104 | bus_LV_1203-2_0_5_node_130 | 0.4 | n |  | TRUE
105 | bus_LV_1203-2_0_5_node_124 | 0.4 | n |  | TRUE
106 | bus_LV_1203-2_0_5_node_118 | 0.4 | n |  | TRUE
107 | bus_LV_1203-2_0_5_node_89 | 0.4 | n |  | TRUE
108 | bus_LV_1203-2_0_5_node_92 | 0.4 | n |  | TRUE
109 | bus_LV_1203-2_0_5_node_103 | 0.4 | n |  | TRUE
110 | bus_LV_1203-2_0_5_node_100 | 0.4 | n |  | TRUE
111 | bus_LV_1203-2_0_5_node_120 | 0.4 | n |  | TRUE
112 | bus_LV_1203-2_0_5_node_101 | 0.4 | n |  | TRUE
113 | bus_LV_1203-2_0_5_node_143 | 0.4 | n |  | TRUE
114 | bus_LV_1203-2_0_5_node_126 | 0.4 | n |  | TRUE
115 | bus_LV_1203-2_0_5_node_95 | 0.4 | n |  | TRUE
116 | bus_LV_1203-2_0_5_node_96 | 0.4 | n |  | TRUE
117 | bus_LV_1203-2_0_5_node_97 | 0.4 | n |  | TRUE
118 | bus_LV_1203-2_0_5_node_98 | 0.4 | n |  | TRUE
119 | bus_LV_1203-2_0_5_node_99 | 0.4 | n |  | TRUE
120 | bus_LV_1203-2_0_5_node_105 | 0.4 | n |  | TRUE
121 | bus_LV_1203-2_0_5_node_106 | 0.4 | n |  | TRUE
122 | bus_LV_1203-2_0_5_node_102 | 0.4 | n |  | TRUE
123 | bus_LV_1203-2_0_5_node_104 | 0.4 | n |  | TRUE
124 | bus_LV_1203-2_0_5_node_123 | 0.4 | n |  | TRUE
125 | bus_LV_1203-2_0_5_node_121 | 0.4 | n |  | TRUE
126 | bus_LV_1203-2_0_5_node_107 | 0.4 | n |  | TRUE
127 | bus_LV_1203-2_0_5_node_108 | 0.4 | n |  | TRUE
128 | bus_LV_1203-2_0_5_node_109 | 0.4 | n |  | TRUE
129 | bus_LV_1203-2_0_5_node_111 | 0.4 | n |  | TRUE
130 | bus_LV_1203-2_0_5_node_117 | 0.4 | n |  | TRUE
131 | bus_LV_1203-2_0_5_node_122 | 0.4 | n |  | TRUE
132 | bus_LV_1203-2_0_5_node_133 | 0.4 | n |  | TRUE
133 | bus_LV_1203-2_0_5_node_135 | 0.4 | n |  | TRUE
134 | bus_LV_1203-2_0_5_node_131 | 0.4 | n |  | TRUE
135 | bus_LV_1203-2_0_5_node_125 | 0.4 | n |  | TRUE
136 | bus_LV_1203-2_0_5_node_137 | 0.4 | n |  | TRUE
137 | bus_LV_1203-2_0_5_node_140 | 0.4 | n |  | TRUE
138 | bus_LV_1203-2_0_5_node_138 | 0.4 | n |  | TRUE
139 | bus_LV_1203-2_0_5_node_139 | 0.4 | n |  | TRUE
140 | bus_MV_11_0_node_64 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1203-2_0_5_load_0 | 0 | 0.01039 | 0.0026041 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1203-2_0_5_load_1 | 1 | 0.0039111 | 0.00098021 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1203-2_0_5_load_4 | 3 | 0.0096402 | 0.0024161 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1203-2_0_5_load_5 | 4 | 0.0077224 | 0.0019354 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1203-2_0_5_load_6 | 5 | 0.0093083 | 0.0023329 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1203-2_0_5_load_15 | 7 | 0.0033817 | 0.00084753 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1203-2_0_5_load_13 | 8 | 0.0076233 | 0.0019106 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1203-2_0_5_load_7 | 9 | 0.0080518 | 0.002018 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1203-2_0_5_load_10 | 11 | 0.0040686 | 0.0010197 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1203-2_0_5_load_11 | 12 | 0.0034223 | 0.0008577 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1203-2_0_5_load_12 | 13 | 0.0041836 | 0.0010485 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1203-2_0_5_load_28 | 14 | 0.0076788 | 0.0019245 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1203-2_0_5_load_26 | 15 | 0.0050942 | 0.0012767 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1203-2_0_5_load_34 | 16 | 0.013441 | 0.0033686 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1203-2_0_5_load_35 | 17 | 0.003527 | 0.00088396 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1203-2_0_5_load_16 | 18 | 0.002163 | 0.00054211 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1203-2_0_5_load_18 | 20 | 0.004531 | 0.0011356 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1203-2_0_5_load_19 | 21 | 0.0027944 | 0.00070034 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1203-2_0_5_load_37 | 23 | 0.0038319 | 0.00096037 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1203-2_0_5_load_63 | 24 | 0.0028945 | 0.00072543 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1203-2_0_5_load_21 | 27 | 0.0046438 | 0.0011638 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1203-2_0_5_load_22 | 28 | 0.0028396 | 0.00071167 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1203-2_0_5_load_24 | 30 | 0.0015935 | 0.00039937 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1203-2_0_5_load_25 | 31 | 0.0027057 | 0.0006781 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1203-2_0_5_load_53 | 32 | 0.0011825 | 0.00029637 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1203-2_0_5_load_51 | 33 | 0.0020075 | 0.00050312 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1203-2_0_5_load_43 | 34 | 0.0017 | 0.00042605 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1203-2_0_5_load_134 | 35 | 0.0054082 | 0.0013554 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1203-2_0_5_load_44 | 36 | 0.015827 | 0.0039665 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1203-2_0_5_load_132 | 37 | 0.0054182 | 0.0013579 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1203-2_0_5_load_27 | 38 | 0.0061963 | 0.0015529 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1203-2_0_5_load_32 | 40 | 0.0057789 | 0.0014483 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1203-2_0_5_load_30 | 41 | 0.010908 | 0.0027339 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1203-2_0_5_load_31 | 42 | 0.0045168 | 0.001132 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1203-2_0_5_load_33 | 43 | 0.0086028 | 0.0021561 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1203-2_0_5_load_60 | 44 | 0.02622 | 0.0065713 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1203-2_0_5_load_36 | 45 | 0.0071119 | 0.0017824 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1203-2_0_5_load_46 | 46 | 0.007807 | 0.0019566 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1203-2_0_5_load_47 | 47 | 0.0059996 | 0.0015037 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1203-2_0_5_load_39 | 48 | 0.0039025 | 0.00097807 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1203-2_0_5_load_40 | 49 | 0.0031385 | 0.00078659 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1203-2_0_5_load_41 | 50 | 0.003696 | 0.0009263 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1203-2_0_5_load_55 | 51 | 0.0027617 | 0.00069216 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1203-2_0_5_load_42 | 52 | 0.0065787 | 0.0016488 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1203-2_0_5_load_56 | 53 | 0.0024485 | 0.00061365 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1203-2_0_5_load_52 | 54 | 0.0036169 | 0.00090647 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1203-2_0_5_load_48 | 55 | 0.0071666 | 0.0017961 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1203-2_0_5_load_49 | 56 | 0.010247 | 0.002568 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1203-2_0_5_load_50 | 57 | 0.0076537 | 0.0019182 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1203-2_0_5_load_54 | 58 | 0.0017868 | 0.00044782 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1203-2_0_5_load_57 | 59 | 0.0032554 | 0.00081588 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1203-2_0_5_load_58 | 60 | 0.0021767 | 0.00054553 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1203-2_0_5_load_62 | 64 | 0.0037258 | 0.00093378 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1203-2_0_5_load_141 | 65 | 0.0062027 | 0.0015545 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1203-2_0_5_load_69 | 66 | 0.001565 | 0.00039223 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1203-2_0_5_load_67 | 68 | 0.0085671 | 0.0021471 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1203-2_0_5_load_65 | 69 | 0.0017629 | 0.00044183 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1203-2_0_5_load_68 | 71 | 0.0027106 | 0.00067935 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1203-2_0_5_load_70 | 72 | 0.0012973 | 0.00032513 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1203-2_0_5_load_71 | 73 | 0.00088619 | 0.0002221 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1203-2_0_5_load_72 | 74 | 0.00066555 | 0.0001668 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1203-2_0_5_load_113 | 75 | 0.0068458 | 0.0017157 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1203-2_0_5_load_73 | 77 | 0.0061139 | 0.0015323 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1203-2_0_5_load_74 | 78 | 0.0099097 | 0.0024836 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1203-2_0_5_load_76 | 79 | 0.0064299 | 0.0016115 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1203-2_0_5_load_75 | 80 | 0.0068746 | 0.0017229 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1203-2_0_5_load_77 | 81 | 0.007494 | 0.0018782 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1203-2_0_5_load_78 | 82 | 0.0082688 | 0.0020724 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1203-2_0_5_load_115 | 83 | 0.003644 | 0.00091326 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1203-2_0_5_load_93 | 84 | 0.0043304 | 0.0010853 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1203-2_0_5_load_85 | 85 | 0.0062127 | 0.001557 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1203-2_0_5_load_116 | 86 | 0.0075808 | 0.0018999 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1203-2_0_5_load_84 | 88 | 0.0059036 | 0.0014796 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1203-2_0_5_load_79 | 89 | 0.0053947 | 0.001352 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1203-2_0_5_load_80 | 90 | 0.0036354 | 0.00091111 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1203-2_0_5_load_81 | 91 | 0.0014259 | 0.00035737 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1203-2_0_5_load_82 | 92 | 0.0036356 | 0.00091118 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1203-2_0_5_load_83 | 93 | 0.001763 | 0.00044185 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1203-2_0_5_load_112 | 95 | 0.0020366 | 0.00051041 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1203-2_0_5_load_129 | 96 | 0.0022336 | 0.00055979 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1203-2_0_5_load_127 | 97 | 0.0040404 | 0.0010126 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1203-2_0_5_load_128 | 103 | 0.0057204 | 0.0014337 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1203-2_0_5_load_130 | 104 | 0.010207 | 0.0025581 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1203-2_0_5_load_124 | 105 | 0.0024988 | 0.00062625 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1203-2_0_5_load_118 | 106 | 0.0061268 | 0.0015355 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1203-2_0_5_load_89 | 107 | 0.004207 | 0.0010544 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1203-2_0_5_load_103 | 109 | 0.0020398 | 0.00051122 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1203-2_0_5_load_100 | 110 | 0.0026326 | 0.00065978 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1203-2_0_5_load_120 | 111 | 0.0022612 | 0.00056671 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1203-2_0_5_load_101 | 112 | 0.0034233 | 0.00085795 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1203-2_0_5_load_143 | 113 | 0.0013544 | 0.00033945 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1203-2_0_5_load_126 | 114 | 0.0026783 | 0.00067126 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1203-2_0_5_load_95 | 115 | 0.0014778 | 0.00037038 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1203-2_0_5_load_96 | 116 | 0.0024857 | 0.00062297 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1203-2_0_5_load_97 | 117 | 0.0037941 | 0.00095089 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1203-2_0_5_load_98 | 118 | 0.0030246 | 0.00075804 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1203-2_0_5_load_99 | 119 | 0.0044617 | 0.0011182 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1203-2_0_5_load_105 | 120 | 0.0044761 | 0.0011218 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1203-2_0_5_load_102 | 122 | 0.0032032 | 0.00080279 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1203-2_0_5_load_104 | 123 | 0.0040113 | 0.0010053 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1203-2_0_5_load_123 | 124 | 0.0056338 | 0.001412 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1203-2_0_5_load_121 | 125 | 0.0057764 | 0.0014477 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1203-2_0_5_load_107 | 126 | 0.0027625 | 0.00069234 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1203-2_0_5_load_108 | 127 | 0.0039664 | 0.00099407 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1203-2_0_5_load_109 | 128 | 0.0051754 | 0.0012971 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1203-2_0_5_load_111 | 129 | 0.0030033 | 0.00075271 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1203-2_0_5_load_117 | 130 | 0.0065528 | 0.0016423 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1203-2_0_5_load_122 | 131 | 0.0043203 | 0.0010828 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1203-2_0_5_load_135 | 133 | 0.0029866 | 0.00074852 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1203-2_0_5_load_131 | 134 | 0.00101 | 0.00025314 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1203-2_0_5_load_125 | 135 | 0.001628 | 0.00040801 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1203-2_0_5_load_140 | 137 | 0.013059 | 0.003273 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1203-2_0_5_load_138 | 138 | 0.0043649 | 0.0010939 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1203-2_0_5_load_139 | 139 | 0.001968 | 0.00049324 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1203-2_0_5_line_0 |  | 0 | 1 | 0.023527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1203-2_0_5_line_1 |  | 1 | 2 | 0.011946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1203-2_0_5_line_2 |  | 2 | 3 | 0.052719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1203-2_0_5_line_3 |  | 3 | 4 | 0.014185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1203-2_0_5_line_4 |  | 4 | 5 | 0.0079349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1203-2_0_5_line_5 |  | 5 | 6 | 0.0097815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_1203-2_0_5_line_6 |  | 6 | 7 | 0.029924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_1203-2_0_5_line_7 |  | 6 | 8 | 0.015447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_1203-2_0_5_line_8 |  | 7 | 16 | 0.018007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_1203-2_0_5_line_9 |  | 8 | 13 | 0.0048303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_1203-2_0_5_line_10 |  | 9 | 10 | 0.017612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1203-2_0_5_line_11 |  | 10 | 11 | 0.01233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_1203-2_0_5_line_12 |  | 10 | 12 | 0.029904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_1203-2_0_5_line_13 |  | 11 | 13 | 0.033951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_1203-2_0_5_line_14 |  | 12 | 14 | 0.032595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_1203-2_0_5_line_15 |  | 14 | 15 | 0.037699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_1203-2_0_5_line_16 |  | 15 | 38 | 0.026267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_1203-2_0_5_line_17 |  | 16 | 17 | 0.0026364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_1203-2_0_5_line_18 |  | 17 | 45 | 0.018035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_1203-2_0_5_line_19 |  | 18 | 19 | 0.010118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1203-2_0_5_line_20 |  | 18 | 20 | 0.02348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1203-2_0_5_line_21 |  | 19 | 21 | 0.011099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_1203-2_0_5_line_22 |  | 19 | 22 | 0.022164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_1203-2_0_5_line_23 |  | 21 | 23 | 0.0042416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_1203-2_0_5_line_24 |  | 22 | 24 | 0.04167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_1203-2_0_5_line_25 |  | 23 | 25 | 0.015785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_1203-2_0_5_line_26 |  | 24 | 26 | 0.011435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_1203-2_0_5_line_27 |  | 25 | 48 | 0.021475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1203-2_0_5_line_28 |  | 25 | 49 | 0.0036852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_1203-2_0_5_line_29 |  | 26 | 39 | 0.028979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_1203-2_0_5_line_30 |  | 27 | 28 | 0.0044257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_1203-2_0_5_line_31 |  | 27 | 29 | 0.02546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_1203-2_0_5_line_32 |  | 29 | 30 | 0.002539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_1203-2_0_5_line_33 |  | 29 | 31 | 0.0088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_1203-2_0_5_line_34 |  | 30 | 34 | 0.021118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_1203-2_0_5_line_35 |  | 31 | 35 | 0.014112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_1203-2_0_5_line_36 |  | 32 | 33 | 0.022575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1203-2_0_5_line_37 |  | 33 | 54 | 0.024352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_1203-2_0_5_line_38 |  | 33 | 34 | 0.045638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_1203-2_0_5_line_39 |  | 34 | 36 | 0.0061297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1203-2_0_5_line_40 |  | 35 | 37 | 0.036066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_1203-2_0_5_line_41 |  | 37 | 134 | 0.0017516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_1203-2_0_5_line_42 |  | 38 | 39 | 0.035231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_1203-2_0_5_line_43 |  | 39 | 40 | 0.017184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_1203-2_0_5_line_44 |  | 40 | 41 | 0.0057498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_1203-2_0_5_line_45 |  | 41 | 42 | 0.02394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_1203-2_0_5_line_46 |  | 42 | 43 | 0.0012135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1203-2_0_5_line_47 |  | 43 | 44 | 0.034645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1203-2_0_5_line_48 |  | 45 | 46 | 0.0067508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_1203-2_0_5_line_49 |  | 46 | 47 | 0.016619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_1203-2_0_5_line_50 |  | 47 | 55 | 0.0083636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_1203-2_0_5_line_51 |  | 48 | 50 | 0.0077021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1203-2_0_5_line_52 |  | 49 | 51 | 0.025954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_1203-2_0_5_line_53 |  | 50 | 52 | 0.0093541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1203-2_0_5_line_54 |  | 51 | 53 | 0.0001765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_1203-2_0_5_line_55 |  | 53 | 61 | 0.025333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_1203-2_0_5_line_56 |  | 54 | 58 | 0.026812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_1203-2_0_5_line_57 |  | 55 | 56 | 0.015717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_1203-2_0_5_line_58 |  | 56 | 57 | 0.0052016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1203-2_0_5_line_59 |  | 58 | 59 | 0.0078002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_1203-2_0_5_line_60 |  | 59 | 60 | 0.015322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_1203-2_0_5_line_61 |  | 60 | 63 | 0.02041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_1203-2_0_5_line_62 |  | 61 | 62 | 0.023705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_1203-2_0_5_line_63 |  | 61 | 63 | 0.048393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_1203-2_0_5_line_64 |  | 62 | 66 | 0.019677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_1203-2_0_5_line_65 |  | 63 | 64 | 0.017519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_1203-2_0_5_line_66 |  | 64 | 65 | 0.022209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_1203-2_0_5_line_67 |  | 65 | 67 | 0.019802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_1203-2_0_5_line_68 |  | 66 | 68 | 0.03366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_1203-2_0_5_line_69 |  | 67 | 137 | 0.050657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_1203-2_0_5_line_70 |  | 68 | 70 | 0.019821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1203-2_0_5_line_71 |  | 69 | 70 | 0.032129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1203-2_0_5_line_72 |  | 70 | 71 | 0.026866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1203-2_0_5_line_73 |  | 72 | 73 | 0.02025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1203-2_0_5_line_74 |  | 72 | 74 | 0.0092416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1203-2_0_5_line_75 |  | 74 | 75 | 0.15282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1203-2_0_5_line_76 |  | 75 | 76 | 0.016992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_1203-2_0_5_line_77 |  | 76 | 119 | 0.0049362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_1203-2_0_5_line_78 |  | 77 | 78 | 0.0020635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1203-2_0_5_line_79 |  | 78 | 79 | 0.023372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_1203-2_0_5_line_80 |  | 79 | 83 | 0.012231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_1203-2_0_5_line_81 |  | 80 | 81 | 0.01773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_1203-2_0_5_line_82 |  | 80 | 82 | 0.022055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
83 | LV_1203-2_0_5_line_83 |  | 81 | 84 | 0.0018767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
84 | LV_1203-2_0_5_line_84 |  | 82 | 85 | 0.019766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_1203-2_0_5_line_85 |  | 83 | 86 | 0.0107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
86 | LV_1203-2_0_5_line_86 |  | 84 | 87 | 0.020464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_1203-2_0_5_line_87 |  | 85 | 88 | 0.020071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_1203-2_0_5_line_88 |  | 86 | 130 | 0.0022239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_1203-2_0_5_line_89 |  | 87 | 108 | 0.017543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_1203-2_0_5_line_90 |  | 87 | 107 | 0.046697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1203-2_0_5_line_91 |  | 88 | 99 | 0.014822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
92 | LV_1203-2_0_5_line_92 |  | 89 | 90 | 0.015488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_1203-2_0_5_line_93 |  | 89 | 91 | 0.012602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
94 | LV_1203-2_0_5_line_94 |  | 90 | 92 | 0.0062581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_1203-2_0_5_line_95 |  | 91 | 93 | 0.0058478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_1203-2_0_5_line_96 |  | 92 | 94 | 0.0097204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_1203-2_0_5_line_97 |  | 93 | 95 | 0.0095106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_1203-2_0_5_line_98 |  | 94 | 96 | 0.0058261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
99 | LV_1203-2_0_5_line_99 |  | 94 | 97 | 0.02254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_1203-2_0_5_line_100 |  | 95 | 98 | 0.010895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_1203-2_0_5_line_101 |  | 97 | 113 | 0.16917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
102 | LV_1203-2_0_5_line_102 |  | 97 | 114 | 0.023268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
103 | LV_1203-2_0_5_line_103 |  | 98 | 129 | 0.012056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_1203-2_0_5_line_104 |  | 98 | 128 | 0.018861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_1203-2_0_5_line_105 |  | 99 | 100 | 0.021511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
106 | LV_1203-2_0_5_line_106 |  | 99 | 101 | 0.022454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
107 | LV_1203-2_0_5_line_107 |  | 100 | 102 | 0.026673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
108 | LV_1203-2_0_5_line_108 |  | 100 | 103 | 0.01504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
109 | LV_1203-2_0_5_line_109 |  | 101 | 104 | 0.011346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
110 | LV_1203-2_0_5_line_110 |  | 102 | 105 | 0.012543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
111 | LV_1203-2_0_5_line_111 |  | 102 | 106 | 0.011825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_1203-2_0_5_line_112 |  | 105 | 129 | 0.0030227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
113 | LV_1203-2_0_5_line_113 |  | 106 | 130 | 0.02212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
114 | LV_1203-2_0_5_line_114 |  | 108 | 109 | 0.010555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
115 | LV_1203-2_0_5_line_115 |  | 108 | 110 | 0.01374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
116 | LV_1203-2_0_5_line_116 |  | 109 | 111 | 0.018503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
117 | LV_1203-2_0_5_line_117 |  | 110 | 112 | 0.0052992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
118 | LV_1203-2_0_5_line_118 |  | 111 | 125 | 0.071566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
119 | LV_1203-2_0_5_line_119 |  | 112 | 122 | 0.016733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
120 | LV_1203-2_0_5_line_120 |  | 114 | 135 | 0.0080096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
121 | LV_1203-2_0_5_line_121 |  | 115 | 116 | 0.010185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
122 | LV_1203-2_0_5_line_122 |  | 115 | 117 | 0.017641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
123 | LV_1203-2_0_5_line_123 |  | 116 | 118 | 0.019542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
124 | LV_1203-2_0_5_line_124 |  | 117 | 119 | 0.0076579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
125 | LV_1203-2_0_5_line_125 |  | 118 | 120 | 0.0222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
126 | LV_1203-2_0_5_line_126 |  | 120 | 121 | 0.0042915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
127 | LV_1203-2_0_5_line_127 |  | 121 | 126 | 0.0079272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
128 | LV_1203-2_0_5_line_128 |  | 121 | 127 | 0.035633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
129 | LV_1203-2_0_5_line_129 |  | 122 | 123 | 0.0073435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
130 | LV_1203-2_0_5_line_130 |  | 123 | 124 | 0.027279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
131 | LV_1203-2_0_5_line_131 |  | 124 | 126 | 0.016786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
132 | LV_1203-2_0_5_line_132 |  | 125 | 131 | 0.0092645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
133 | LV_1203-2_0_5_line_133 |  | 131 | 132 | 0.0056665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
134 | LV_1203-2_0_5_line_134 |  | 132 | 133 | 0.007607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_1203-2_0_5_line_135 |  | 132 | 134 | 0.026804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
136 | LV_1203-2_0_5_line_136 |  | 136 | 137 | 0.016716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
137 | LV_1203-2_0_5_line_137 |  | 136 | 138 | 0.024882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
138 | LV_1203-2_0_5_line_138 |  | 138 | 139 | 0.042827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1203-2_0_5_trafo_22 | 0.63 MVA 20/0.4 kV | 140 | 28 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2690819.5151 | 1190975.9655 | 2690838.077 | 1190986.4152 | 2690839.5051 | 1190988.1225
1 | 2690847.9353 | 1190996.5824 | 2690842.8577 | 1190991.4799 | 2690839.9045 | 1190988.5999 | 2690839.5051 | 1190988.1225
2 | 2690861.7886 | 1191047.4489 | 2690847.9353 | 1190996.5824
3 | 2690861.7886 | 1191047.4489 | 2690875.9055 | 1191046.0609
4 | 2690875.9055 | 1191046.0609 | 2690883.8023 | 1191045.2844
5 | 2690893.5369 | 1191044.3273 | 2690883.8023 | 1191045.2844
6 | 2690893.5369 | 1191044.3273 | 2690895.5548 | 1191065.0934 | 2690891.5306 | 1191073.2104
7 | 2690893.5369 | 1191044.3273 | 2690908.8227 | 1191042.1036
8 | 2690883.5323 | 1191089.3431 | 2690891.5306 | 1191073.2104
9 | 2690908.8227 | 1191042.1036 | 2690913.6027 | 1191041.4083
10 | 2690956.5669 | 1191053.157 | 2690965.1393 | 1191037.7723
11 | 2690956.5669 | 1191053.157 | 2690945.4646 | 1191047.7943
12 | 2690956.5669 | 1191053.157 | 2690944.3425 | 1191080.4478
13 | 2690945.4646 | 1191047.7943 | 2690927.9289 | 1191039.3242 | 2690913.6027 | 1191041.4083
14 | 2690944.3425 | 1191080.4478 | 2690931.0178 | 1191110.1952
15 | 2690931.0178 | 1191110.1952 | 2690915.6066 | 1191144.6005
16 | 2690904.8689 | 1191168.572 | 2690915.6066 | 1191144.6005
17 | 2690882.3613 | 1191091.7051 | 2690883.5323 | 1191089.3431
18 | 2690882.3613 | 1191091.7051 | 2690877.8781 | 1191100.7478 | 2690872.9642 | 1191106.9869
19 | 2690824.2047 | 1191243.1351 | 2690829.2523 | 1191234.3655
20 | 2690840.9655 | 1191214.0153 | 2690829.2523 | 1191234.3655
21 | 2690824.2047 | 1191243.1351 | 2690814.3966 | 1191237.9391
22 | 2690837.3852 | 1191260.9798 | 2690824.2047 | 1191243.1351
23 | 2690810.6484 | 1191235.9535 | 2690814.3966 | 1191237.9391
24 | 2690837.3852 | 1191260.9798 | 2690859.488 | 1191247.1508 | 2690869.2772 | 1191235.0084
25 | 2690796.6995 | 1191228.5641 | 2690810.6484 | 1191235.9535
26 | 2690876.4542 | 1191226.1061 | 2690869.2772 | 1191235.0084
27 | 2690796.6995 | 1191228.5641 | 2690807.0365 | 1191209.7407
28 | 2690796.6995 | 1191228.5641 | 2690794.7045 | 1191231.6625
29 | 2690890.4667 | 1191200.7249 | 2690876.4542 | 1191226.1061
30 | 2690756.9478 | 1191138.8593 | 2690759.2973 | 1191135.1088
31 | 2690743.4315 | 1191160.4351 | 2690756.9478 | 1191138.8593
32 | 2690743.4315 | 1191160.4351 | 2690742.1973 | 1191162.6539
33 | 2690743.4315 | 1191160.4351 | 2690734.8461 | 1191158.5031
34 | 2690742.1973 | 1191162.6539 | 2690731.9318 | 1191181.1088
35 | 2690721.0785 | 1191155.405 | 2690734.8461 | 1191158.5031
36 | 2690771.782 | 1191203.3518 | 2690783.9883 | 1191184.3617
37 | 2690771.782 | 1191203.3518 | 2690758.6147 | 1191223.837
38 | 2690771.782 | 1191203.3518 | 2690731.9318 | 1191181.1088
39 | 2690728.9521 | 1191186.4656 | 2690731.9318 | 1191181.1088
40 | 2690721.0785 | 1191155.405 | 2690685.8921 | 1191147.4869
41 | 2690685.8921 | 1191147.4869 | 2690684.1833 | 1191147.1024
42 | 2690890.4667 | 1191200.7249 | 2690904.8689 | 1191168.572
43 | 2690890.4667 | 1191200.7249 | 2690875.7783 | 1191191.8069
44 | 2690870.8635 | 1191188.8229 | 2690875.7783 | 1191191.8069
45 | 2690870.8635 | 1191188.8229 | 2690850.3997 | 1191176.3984
46 | 2690849.3624 | 1191175.7686 | 2690850.3997 | 1191176.3984
47 | 2690817.4261 | 1191171.2753 | 2690830.7068 | 1191177.0027 | 2690844.3001 | 1191172.6951 | 2690849.3624 | 1191175.7686
48 | 2690868.7872 | 1191112.2904 | 2690872.9642 | 1191106.9869
49 | 2690868.7872 | 1191112.2904 | 2690863.5398 | 1191118.9528 | 2690857.0196 | 1191123.8227
50 | 2690850.3188 | 1191128.8275 | 2690857.0196 | 1191123.8227
51 | 2690810.744 | 1191202.9897 | 2690807.0365 | 1191209.7407
52 | 2690794.7045 | 1191231.6625 | 2690780.6545 | 1191253.4846
53 | 2690815.2466 | 1191194.7905 | 2690810.744 | 1191202.9897
54 | 2690780.559 | 1191253.633 | 2690780.6545 | 1191253.4846
55 | 2690768.5622 | 1191275.7452 | 2690770.8029 | 1191268.7858 | 2690780.559 | 1191253.633
56 | 2690758.6147 | 1191223.837 | 2690744.1172 | 1191246.3918
57 | 2690837.7263 | 1191138.2327 | 2690850.3188 | 1191128.8275
58 | 2690833.5588 | 1191141.3454 | 2690837.7263 | 1191138.2327
59 | 2690739.8995 | 1191252.9535 | 2690744.1172 | 1191246.3918
60 | 2690739.8995 | 1191252.9535 | 2690731.6151 | 1191265.8422
61 | 2690720.5792 | 1191283.0113 | 2690731.6151 | 1191265.8422
62 | 2690768.5622 | 1191275.7452 | 2690783.6419 | 1191273.4613 | 2690779.7231 | 1191280.9511
63 | 2690768.5622 | 1191275.7452 | 2690720.5792 | 1191283.0113
64 | 2690779.7231 | 1191280.9511 | 2690797.0713 | 1191290.2369
65 | 2690720.5792 | 1191283.0113 | 2690703.2572 | 1191285.632
66 | 2690703.2572 | 1191285.632 | 2690681.298 | 1191288.9541
67 | 2690661.7413 | 1191292.059 | 2690671.3507 | 1191290.4591 | 2690681.298 | 1191288.9541
68 | 2690797.0713 | 1191290.2369 | 2690797.8087 | 1191290.6316 | 2690800.6797 | 1191304.9509 | 2690808.6141 | 1191308.707 | 2690817.159 | 1191312.7215
69 | 2690661.7413 | 1191292.059 | 2690661.6353 | 1191286.9764 | 2690661.0822 | 1191259.5727 | 2690660.0108 | 1191241.4399
70 | 2690835.0989 | 1191321.1501 | 2690817.159 | 1191312.7215
71 | 2690835.0989 | 1191321.1501 | 2690838.7866 | 1191312.3115 | 2690852.2254 | 1191294.201
72 | 2690835.0989 | 1191321.1501 | 2690824.7532 | 1191345.9444
73 | 2690325.2321 | 1191028.304 | 2690344.1897 | 1191021.1851
74 | 2690352.8415 | 1191017.9363 | 2690344.1897 | 1191021.1851
75 | 2690498.2223 | 1190970.8466 | 2690352.8415 | 1191017.9363
76 | 2690513.6174 | 1190972.992 | 2690511.4951 | 1190975.1613 | 2690500.65 | 1190971.7063 | 2690498.2223 | 1190970.8466
77 | 2690513.6174 | 1190972.992 | 2690517.0732 | 1190969.4673
78 | 2690651.966 | 1190968.5857 | 2690650.0777 | 1190967.7535
79 | 2690628.3595 | 1190959.1722 | 2690638.6086 | 1190962.6989 | 2690650.0777 | 1190967.7535
80 | 2690628.3595 | 1190959.1722 | 2690622.3511 | 1190957.1047 | 2690617.6993 | 1190956.1003 | 2690617.2983 | 1190955.0568
81 | 2690679.7881 | 1190970.761 | 2690682.2282 | 1190981.338 | 2690682.8658 | 1190988.1832
82 | 2690679.7881 | 1190970.761 | 2690670.8265 | 1190950.6087
83 | 2690683.0399 | 1190990.0519 | 2690682.8658 | 1190988.1832
84 | 2690663.1878 | 1190932.4004 | 2690664.2426 | 1190935.8033 | 2690670.8265 | 1190950.6087
85 | 2690617.2983 | 1190955.0568 | 2690614.9407 | 1190948.9207 | 2690614.778 | 1190944.7972
86 | 2690681.6656 | 1191010.4036 | 2690683.4219 | 1190994.1532 | 2690683.0399 | 1190990.0519
87 | 2690657.9361 | 1190913.0812 | 2690658.4117 | 1190916.9919 | 2690663.1878 | 1190932.4004
88 | 2690614.6904 | 1190942.5751 | 2690614.778 | 1190944.7972
89 | 2690681.6656 | 1191010.4036 | 2690677.1155 | 1191027.3454
90 | 2690681.6656 | 1191010.4036 | 2690719.5545 | 1191016.6928 | 2690727.7071 | 1191018.193
91 | 2690656.1468 | 1190898.3679 | 2690657.9361 | 1190913.0812
92 | 2690545.2542 | 1190907.5724 | 2690539.7953 | 1190903.5659 | 2690533.4231 | 1190897.6185
93 | 2690545.2542 | 1190907.5724 | 2690549.8339 | 1190910.9336 | 2690556.5152 | 1190912.7402
94 | 2690533.4231 | 1190897.6185 | 2690528.8481 | 1190893.3486
95 | 2690556.5152 | 1190912.7402 | 2690562.1603 | 1190914.2666
96 | 2690521.0524 | 1190887.828 | 2690524.1993 | 1190889.0097 | 2690528.8481 | 1190893.3486
97 | 2690562.1603 | 1190914.2666 | 2690562.1603 | 1190914.2666 | 2690571.6708 | 1190914.3173
98 | 2690521.0524 | 1190887.828 | 2690522.2765 | 1190882.132
99 | 2690521.0524 | 1190887.828 | 2690516.3369 | 1190887.501 | 2690504.5561 | 1190891.4476 | 2690500.376 | 1190894.8488
100 | 2690582.5657 | 1190914.3754 | 2690571.6708 | 1190914.3173
101 | 2690500.376 | 1190894.8488 | 2690421.5393 | 1190745.1667
102 | 2690482.3274 | 1190909.5342 | 2690482.3274 | 1190909.5342 | 2690500.376 | 1190894.8488
103 | 2690582.5657 | 1190914.3754 | 2690585.6235 | 1190914.3883 | 2690594.4158 | 1190912.4729
104 | 2690582.5657 | 1190914.3754 | 2690579.0401 | 1190897.4112 | 2690579.6815 | 1190896.0178
105 | 2690656.1468 | 1190898.3679 | 2690644.6921 | 1190898.4056 | 2690634.7218 | 1190900.1224
106 | 2690656.1468 | 1190898.3679 | 2690656.1381 | 1190897.4339 | 2690663.0814 | 1190897.6947 | 2690668.5393 | 1190899.3562 | 2690675.7282 | 1190904.5462
107 | 2690609.6252 | 1190909.1594 | 2690630.9982 | 1190900.7664 | 2690634.7218 | 1190900.1224
108 | 2690634.7218 | 1190900.1224 | 2690628.2428 | 1190886.5494
109 | 2690675.7282 | 1190904.5462 | 2690683.2236 | 1190911.1417 | 2690684.1298 | 1190912.1579
110 | 2690609.6252 | 1190909.1594 | 2690597.3692 | 1190911.8294
111 | 2690609.6252 | 1190909.1594 | 2690612.3074 | 1190920.6764
112 | 2690594.4158 | 1190912.4729 | 2690597.3692 | 1190911.8294
113 | 2690614.6904 | 1190942.5751 | 2690614.1362 | 1190928.5289 | 2690612.3074 | 1190920.6764
114 | 2690677.1155 | 1191027.3454 | 2690674.3694 | 1191037.5372
115 | 2690677.1155 | 1191027.3454 | 2690663.5497 | 1191025.1644
116 | 2690670.4634 | 1191055.6184 | 2690673.6248 | 1191040.3008 | 2690674.3694 | 1191037.5372
117 | 2690663.5497 | 1191025.1644 | 2690662.6085 | 1191025.0131 | 2690658.4016 | 1191023.9227
118 | 2690670.4634 | 1191055.6184 | 2690660.1511 | 1191126.4377
119 | 2690658.4016 | 1191023.9227 | 2690642.3804 | 1191019.7701 | 2690642.2211 | 1191019.6811
120 | 2690482.3274 | 1190909.5342 | 2690475.3009 | 1190913.3788
121 | 2690537.8608 | 1190971.2046 | 2690544.6625 | 1190975.9968 | 2690546.3483 | 1190976.7931
122 | 2690522.2287 | 1190963.8053 | 2690529.6321 | 1190965.4071 | 2690537.8608 | 1190971.2046
123 | 2690564.0178 | 1190985.1406 | 2690546.3483 | 1190976.7931
124 | 2690522.2287 | 1190963.8053 | 2690522.2287 | 1190963.8053 | 2690517.3662 | 1190969.1685 | 2690517.0732 | 1190969.4673
125 | 2690585.1152 | 1190992.0268 | 2690564.8184 | 1190985.5188 | 2690564.0178 | 1190985.1406
126 | 2690589.2018 | 1190993.3372 | 2690585.1152 | 1190992.0268
127 | 2690589.2018 | 1190993.3372 | 2690596.7491 | 1190995.7621
128 | 2690589.2018 | 1190993.3372 | 2690577.7413 | 1190999.8123 | 2690567.7362 | 1191010.3899 | 2690559.9731 | 1191011.9068
129 | 2690635.8103 | 1191016.0993 | 2690642.2211 | 1191019.6811
130 | 2690611.7691 | 1191003.2163 | 2690624.217 | 1191009.622 | 2690635.8103 | 1191016.0993
131 | 2690611.7691 | 1191003.2163 | 2690598.1719 | 1190996.2192 | 2690596.7491 | 1190995.7621
132 | 2690660.1511 | 1191126.4377 | 2690658.8372 | 1191135.6086
133 | 2690658.0336 | 1191141.2178 | 2690658.8372 | 1191135.6086
134 | 2690658.0336 | 1191141.2178 | 2690657.2134 | 1191148.7805
135 | 2690658.0336 | 1191141.2178 | 2690684.1833 | 1191147.1024
136 | 2690659.0248 | 1191224.7527 | 2690660.0108 | 1191241.4399
137 | 2690659.0248 | 1191224.7527 | 2690635.1406 | 1191217.7755
138 | 2690595.0655 | 1191202.8593 | 2690607.6048 | 1191208.7084 | 2690635.1406 | 1191217.7755

## bus_geodata
| x | y | coords
0 | 2690819.5151 | 1190975.9655
1 | 2690839.5051 | 1190988.1225
2 | 2690847.9353 | 1190996.5824
3 | 2690861.7886 | 1191047.4489
4 | 2690875.9055 | 1191046.0609
5 | 2690883.8023 | 1191045.2844
6 | 2690893.5369 | 1191044.3273
7 | 2690891.5306 | 1191073.2104
8 | 2690908.8227 | 1191042.1036
9 | 2690965.1393 | 1191037.7723
10 | 2690956.5669 | 1191053.157
11 | 2690945.4646 | 1191047.7943
12 | 2690944.3425 | 1191080.4478
13 | 2690913.6027 | 1191041.4083
14 | 2690931.0178 | 1191110.1952
15 | 2690915.6066 | 1191144.6005
16 | 2690883.5323 | 1191089.3431
17 | 2690882.3613 | 1191091.7051
18 | 2690829.2523 | 1191234.3655
19 | 2690824.2047 | 1191243.1351
20 | 2690840.9655 | 1191214.0153
21 | 2690814.3966 | 1191237.9391
22 | 2690837.3852 | 1191260.9798
23 | 2690810.6484 | 1191235.9535
24 | 2690869.2772 | 1191235.0084
25 | 2690796.6995 | 1191228.5641
26 | 2690876.4542 | 1191226.1061
27 | 2690756.9478 | 1191138.8593
28 | 2690759.2973 | 1191135.1088
29 | 2690743.4315 | 1191160.4351
30 | 2690742.1973 | 1191162.6539
31 | 2690734.8461 | 1191158.5031
32 | 2690783.9883 | 1191184.3617
33 | 2690771.782 | 1191203.3519
34 | 2690731.9318 | 1191181.1088
35 | 2690721.0785 | 1191155.405
36 | 2690728.9521 | 1191186.4656
37 | 2690685.8921 | 1191147.4869
38 | 2690904.8689 | 1191168.572
39 | 2690890.4667 | 1191200.7249
40 | 2690875.7783 | 1191191.8069
41 | 2690870.8635 | 1191188.8229
42 | 2690850.3997 | 1191176.3984
43 | 2690849.3624 | 1191175.7686
44 | 2690817.4261 | 1191171.2753
45 | 2690872.9642 | 1191106.9869
46 | 2690868.7872 | 1191112.2904
47 | 2690857.0196 | 1191123.8227
48 | 2690807.0365 | 1191209.7407
49 | 2690794.7045 | 1191231.6625
50 | 2690810.744 | 1191202.9897
51 | 2690780.6545 | 1191253.4846
52 | 2690815.2466 | 1191194.7905
53 | 2690780.559 | 1191253.633
54 | 2690758.6147 | 1191223.837
55 | 2690850.3188 | 1191128.8275
56 | 2690837.7263 | 1191138.2327
57 | 2690833.5588 | 1191141.3454
58 | 2690744.1172 | 1191246.3918
59 | 2690739.8995 | 1191252.9535
60 | 2690731.6151 | 1191265.8422
61 | 2690768.5622 | 1191275.7452
62 | 2690779.7231 | 1191280.9511
63 | 2690720.5792 | 1191283.0113
64 | 2690703.2572 | 1191285.632
65 | 2690681.298 | 1191288.9541
66 | 2690797.0713 | 1191290.2369
67 | 2690661.7413 | 1191292.059
68 | 2690817.159 | 1191312.7215
69 | 2690852.2254 | 1191294.201
70 | 2690835.0989 | 1191321.1501
71 | 2690824.7532 | 1191345.9444
72 | 2690344.1897 | 1191021.1851
73 | 2690325.2321 | 1191028.304
74 | 2690352.8415 | 1191017.9363
75 | 2690498.2223 | 1190970.8466
76 | 2690513.6174 | 1190972.992
77 | 2690651.966 | 1190968.5857
78 | 2690650.0777 | 1190967.7535
79 | 2690628.3595 | 1190959.1722
80 | 2690679.7881 | 1190970.761
81 | 2690682.8658 | 1190988.1832
82 | 2690670.8265 | 1190950.6087
83 | 2690617.2983 | 1190955.0568
84 | 2690683.0399 | 1190990.0519
85 | 2690663.1878 | 1190932.4004
86 | 2690614.778 | 1190944.7972
87 | 2690681.6656 | 1191010.4036
88 | 2690657.9361 | 1190913.0812
89 | 2690545.2542 | 1190907.5724
90 | 2690533.4231 | 1190897.6185
91 | 2690556.5152 | 1190912.7402
92 | 2690528.8481 | 1190893.3486
93 | 2690562.1603 | 1190914.2666
94 | 2690521.0524 | 1190887.828
95 | 2690571.6708 | 1190914.3173
96 | 2690522.2765 | 1190882.132
97 | 2690500.376 | 1190894.8488
98 | 2690582.5657 | 1190914.3754
99 | 2690656.1468 | 1190898.3679
100 | 2690634.7218 | 1190900.1224
101 | 2690675.7282 | 1190904.5462
102 | 2690609.6252 | 1190909.1594
103 | 2690628.2428 | 1190886.5494
104 | 2690684.1298 | 1190912.1579
105 | 2690597.3692 | 1190911.8294
106 | 2690612.3074 | 1190920.6764
107 | 2690727.7071 | 1191018.193
108 | 2690677.1155 | 1191027.3454
109 | 2690674.3694 | 1191037.5372
110 | 2690663.5497 | 1191025.1644
111 | 2690670.4634 | 1191055.6184
112 | 2690658.4016 | 1191023.9227
113 | 2690421.5393 | 1190745.1667
114 | 2690482.3274 | 1190909.5342
115 | 2690537.8608 | 1190971.2046
116 | 2690546.3483 | 1190976.7931
117 | 2690522.2287 | 1190963.8053
118 | 2690564.0178 | 1190985.1406
119 | 2690517.0732 | 1190969.4673
120 | 2690585.1152 | 1190992.0268
121 | 2690589.2018 | 1190993.3372
122 | 2690642.2211 | 1191019.6811
123 | 2690635.8103 | 1191016.0993
124 | 2690611.7691 | 1191003.2163
125 | 2690660.1511 | 1191126.4377
126 | 2690596.7491 | 1190995.7621
127 | 2690559.9731 | 1191011.9068
128 | 2690579.6815 | 1190896.0178
129 | 2690594.4158 | 1190912.4729
130 | 2690614.6904 | 1190942.5751
131 | 2690658.8372 | 1191135.6086
132 | 2690658.0336 | 1191141.2178
133 | 2690657.2134 | 1191148.7805
134 | 2690684.1833 | 1191147.1024
135 | 2690475.3009 | 1190913.3788
136 | 2690659.0248 | 1191224.7527
137 | 2690660.0108 | 1191241.4399
138 | 2690635.1406 | 1191217.7755
139 | 2690595.0655 | 1191202.8593
140 | 2690763.1641 | 1191128.9364

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97 | -0.57927 | 0.01039 | 0.0026041
1 | 0.97023 | -0.57474 | 0.0039111 | 0.00098021
2 | 0.97039 | -0.57158 | 0 | 0
3 | 0.97109 | -0.55763 | 0.0096402 | 0.0024161
4 | 0.97141 | -0.55136 | 0.0077224 | 0.0019354
5 | 0.97153 | -0.54904 | 0.0093083 | 0.0023329
6 | 0.9716 | -0.54756 | 0 | 0
7 | 0.97123 | -0.55489 | 0.0033817 | 0.00084753
8 | 0.97191 | -0.54144 | 0.0076233 | 0.0019106
9 | 0.97292 | -0.52149 | 0.0080518 | 0.002018
10 | 0.97306 | -0.51888 | 0 | 0
11 | 0.97277 | -0.52447 | 0.0040686 | 0.0010197
12 | 0.97379 | -0.50444 | 0.0034223 | 0.0008577
13 | 0.97202 | -0.53939 | 0.0041836 | 0.0010485
14 | 0.97461 | -0.48831 | 0.0076788 | 0.0019245
15 | 0.97561 | -0.46863 | 0.0050942 | 0.0012767
16 | 0.97102 | -0.55908 | 0.013441 | 0.0033686
17 | 0.971 | -0.55956 | 0.003527 | 0.00088396
18 | 0.98139 | -0.35578 | 0.002163 | 0.00054211
19 | 0.98145 | -0.35455 | 0 | 0
20 | 0.98129 | -0.3577 | 0.004531 | 0.0011356
21 | 0.98191 | -0.34574 | 0.0027944 | 0.00070034
22 | 0.98058 | -0.37162 | 0 | 0
23 | 0.98208 | -0.34234 | 0.0038319 | 0.00096037
24 | 0.97892 | -0.4038 | 0.0028945 | 0.00072543
25 | 0.98275 | -0.32946 | 0 | 0
26 | 0.97848 | -0.41252 | 0 | 0
27 | 0.99954 | -0.0086979 | 0.0046438 | 0.0011638
28 | 1 | 0 | -0.57428 | -0.14706
29 | 0.99691 | -0.058476 | 0 | 0
30 | 0.99675 | -0.061377 | 0.0015935 | 0.00039937
31 | 0.99653 | -0.065678 | 0.0027057 | 0.0006781
32 | 0.99286 | -0.13523 | 0.0011825 | 0.00029637
33 | 0.99288 | -0.13475 | 0.0020075 | 0.00050312
34 | 0.99548 | -0.085418 | 0.0017 | 0.00042605
35 | 0.99593 | -0.077105 | 0.0054082 | 0.0013554
36 | 0.9954 | -0.087124 | 0.015827 | 0.0039665
37 | 0.99444 | -0.10568 | 0.0054182 | 0.0013579
38 | 0.97633 | -0.45446 | 0.0061963 | 0.0015529
39 | 0.97734 | -0.43468 | 0 | 0
40 | 0.97717 | -0.43819 | 0.0057789 | 0.0014483
41 | 0.97711 | -0.43925 | 0.010908 | 0.0027339
42 | 0.97682 | -0.44498 | 0.0045168 | 0.001132
43 | 0.97678 | -0.44575 | 0.0086028 | 0.0021561
44 | 0.97594 | -0.46236 | 0.02622 | 0.0065713
45 | 0.97084 | -0.56263 | 0.0071119 | 0.0017824
46 | 0.97079 | -0.5636 | 0.007807 | 0.0019566
47 | 0.9707 | -0.56551 | 0.0059996 | 0.0015037
48 | 0.98247 | -0.33495 | 0.0039025 | 0.00097807
49 | 0.98291 | -0.32626 | 0.0031385 | 0.00078659
50 | 0.98239 | -0.33638 | 0.003696 | 0.0009263
51 | 0.98409 | -0.30351 | 0.0027617 | 0.00069216
52 | 0.98234 | -0.33749 | 0.0065787 | 0.0016488
53 | 0.9841 | -0.30335 | 0.0024485 | 0.00061365
54 | 0.99151 | -0.16091 | 0.0036169 | 0.00090647
55 | 0.97066 | -0.56629 | 0.0071666 | 0.0017961
56 | 0.97059 | -0.56759 | 0.010247 | 0.002568
57 | 0.97055 | -0.56833 | 0.0076537 | 0.0019182
58 | 0.99002 | -0.18945 | 0.0017868 | 0.00044782
59 | 0.98959 | -0.19771 | 0.0032554 | 0.00081588
60 | 0.98875 | -0.2138 | 0.0021767 | 0.00054553
61 | 0.98527 | -0.28072 | 0 | 0
62 | 0.9852 | -0.28196 | 0 | 0
63 | 0.98764 | -0.23511 | 0 | 0
64 | 0.98754 | -0.23694 | 0.0037258 | 0.00093378
65 | 0.98744 | -0.23898 | 0.0062027 | 0.0015545
66 | 0.98515 | -0.283 | 0.001565 | 0.00039223
67 | 0.98737 | -0.24035 | 0 | 0
68 | 0.98505 | -0.28497 | 0.0085671 | 0.0021471
69 | 0.98492 | -0.28758 | 0.0017629 | 0.00044183
70 | 0.98497 | -0.28656 | 0 | 0
71 | 0.9849 | -0.28787 | 0.0027106 | 0.00067935
72 | 0.98733 | -0.24309 | 0.0012973 | 0.00032513
73 | 0.98732 | -0.24341 | 0.00088619 | 0.0002221
74 | 0.98735 | -0.24273 | 0.00066555 | 0.0001668
75 | 0.98775 | -0.23494 | 0.0068458 | 0.0017157
76 | 0.98783 | -0.23347 | 0 | 0
77 | 0.98458 | -0.29677 | 0.0061139 | 0.0015323
78 | 0.98459 | -0.29654 | 0.0099097 | 0.0024836
79 | 0.98467 | -0.29486 | 0.0064299 | 0.0016115
80 | 0.98745 | -0.2408 | 0.0068746 | 0.0017229
81 | 0.98787 | -0.23255 | 0.007494 | 0.0018782
82 | 0.98695 | -0.25052 | 0.0082688 | 0.0020724
83 | 0.98472 | -0.29387 | 0.003644 | 0.00091326
84 | 0.98792 | -0.23163 | 0.0043304 | 0.0010853
85 | 0.98653 | -0.25866 | 0.0062127 | 0.001557
86 | 0.98478 | -0.29287 | 0.0075808 | 0.0018999
87 | 0.98845 | -0.22126 | 0 | 0
88 | 0.98613 | -0.26649 | 0.0059036 | 0.0014796
89 | 0.98467 | -0.29498 | 0.0053947 | 0.001352
90 | 0.98461 | -0.29605 | 0.0036354 | 0.00091111
91 | 0.98473 | -0.29386 | 0.0014259 | 0.00035737
92 | 0.9846 | -0.2964 | 0.0036356 | 0.00091118
93 | 0.98475 | -0.29331 | 0.001763 | 0.00044185
94 | 0.98457 | -0.29682 | 0 | 0
95 | 0.9848 | -0.29236 | 0.0020366 | 0.00051041
96 | 0.98457 | -0.29693 | 0.0022336 | 0.00055979
97 | 0.98453 | -0.29761 | 0.0040404 | 0.0010126
98 | 0.98486 | -0.29119 | 0 | 0
99 | 0.98585 | -0.27195 | 0 | 0
100 | 0.98548 | -0.2791 | 0 | 0
101 | 0.98581 | -0.27277 | 0 | 0
102 | 0.98505 | -0.28743 | 0 | 0
103 | 0.98546 | -0.27941 | 0.0057204 | 0.0014337
104 | 0.98578 | -0.27319 | 0.010207 | 0.0025581
105 | 0.98496 | -0.28926 | 0.0024988 | 0.00062625
106 | 0.98495 | -0.2894 | 0.0061268 | 0.0015355
107 | 0.98827 | -0.22477 | 0.004207 | 0.0010544
108 | 0.98893 | -0.21211 | 0 | 0
109 | 0.98932 | -0.20454 | 0.0020398 | 0.00051122
110 | 0.98879 | -0.21481 | 0.0026326 | 0.00065978
111 | 0.99001 | -0.19116 | 0.0022612 | 0.00056671
112 | 0.98874 | -0.2158 | 0.0034233 | 0.00085795
113 | 0.98449 | -0.29844 | 0.0013544 | 0.00033945
114 | 0.98452 | -0.29797 | 0.0026783 | 0.00067126
115 | 0.98791 | -0.23178 | 0.0014778 | 0.00037038
116 | 0.98795 | -0.23107 | 0.0024857 | 0.00062297
117 | 0.98786 | -0.23291 | 0.0037941 | 0.00095089
118 | 0.98803 | -0.22954 | 0.0030246 | 0.00075804
119 | 0.98784 | -0.2333 | 0.0044617 | 0.0011182
120 | 0.98813 | -0.22756 | 0.0044761 | 0.0011218
121 | 0.98815 | -0.22711 | 0 | 0
122 | 0.98859 | -0.21873 | 0.0032032 | 0.00080279
123 | 0.98852 | -0.21993 | 0.0040113 | 0.0010053
124 | 0.98831 | -0.224 | 0.0056338 | 0.001412
125 | 0.99271 | -0.13897 | 0.0057764 | 0.0014477
126 | 0.9882 | -0.22617 | 0.0027625 | 0.00069234
127 | 0.98813 | -0.22762 | 0.0039664 | 0.00099407
128 | 0.98484 | -0.29154 | 0.0051754 | 0.0012971
129 | 0.98494 | -0.28967 | 0.0030033 | 0.00075271
130 | 0.98479 | -0.2926 | 0.0065528 | 0.0016423
131 | 0.99307 | -0.13204 | 0.0043203 | 0.0010828
132 | 0.99329 | -0.12773 | 0 | 0
133 | 0.99329 | -0.12783 | 0.0029866 | 0.00074852
134 | 0.99437 | -0.10704 | 0.00101 | 0.00025314
135 | 0.98451 | -0.29808 | 0.001628 | 0.00040801
136 | 0.98717 | -0.24425 | 0 | 0
137 | 0.98719 | -0.24387 | 0.013059 | 0.003273
138 | 0.98714 | -0.24481 | 0.0043649 | 0.0010939
139 | 0.98712 | -0.24512 | 0.001968 | 0.00049324
140 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.01039 | -0.0026041 | 0.010393 | 0.0026052 | 2.2415e-06 | 1.1441e-06 | 0.015939 | 0.015939 | 0.015939 | 0.97 | -0.57927 | 0.97023 | -0.57474 | 4.3789
1 | -0.014304 | -0.0035854 | 0.014306 | 0.0035867 | 2.1559e-06 | 1.2322e-06 | 0.021937 | 0.021937 | 0.021937 | 0.97023 | -0.57474 | 0.97039 | -0.57158 | 6.0268
2 | -0.014306 | -0.0035867 | 0.014315 | 0.0035921 | 9.5141e-06 | 5.4373e-06 | 0.021937 | 0.021937 | 0.021937 | 0.97039 | -0.57158 | 0.97109 | -0.55763 | 6.0268
3 | -0.023956 | -0.0060082 | 0.023963 | 0.0060126 | 7.1681e-06 | 4.412e-06 | 0.036709 | 0.036709 | 0.036709 | 0.97109 | -0.55763 | 0.97141 | -0.55136 | 10.0849
4 | -0.031685 | -0.007948 | 0.031689 | 0.00795 | 3.5052e-06 | 2.0468e-06 | 0.048538 | 0.048538 | 0.048538 | 0.97141 | -0.55136 | 0.97153 | -0.54904 | 6.6673
5 | -0.040997 | -0.010283 | 0.041 | 0.010284 | 2.8928e-06 | 1.2457e-06 | 0.062795 | 0.062795 | 0.062795 | 0.97153 | -0.54904 | 0.9716 | -0.54756 | 3.4503
6 | 0.066386 | 0.01665 | -0.066363 | -0.016637 | 2.3201e-05 | 1.2996e-05 | 0.10167 | 0.10168 | 0.10168 | 0.9716 | -0.54756 | 0.97123 | -0.55489 | 5.5866
7 | -0.10739 | -0.026935 | 0.10742 | 0.026954 | 3.1338e-05 | 1.9099e-05 | 0.16447 | 0.16447 | 0.16447 | 0.9716 | -0.54756 | 0.97191 | -0.54144 | 9.0368
8 | 0.062981 | 0.01579 | -0.062968 | -0.015783 | 1.2575e-05 | 6.9339e-06 | 0.096494 | 0.096495 | 0.096495 | 0.97123 | -0.55489 | 0.97102 | -0.55908 | 5.3019
9 | -0.11504 | -0.028864 | 0.11505 | 0.028871 | 1.124e-05 | 6.894e-06 | 0.17614 | 0.17614 | 0.17614 | 0.97191 | -0.54144 | 0.97202 | -0.53939 | 9.678
10 | -0.0080518 | -0.002018 | 0.0080528 | 0.0020184 | 1.0016e-06 | 4.2225e-07 | 0.012315 | 0.012315 | 0.012315 | 0.97292 | -0.52149 | 0.97306 | -0.51888 | 3.3831
11 | 0.12342 | 0.031012 | -0.12339 | -0.030992 | 3.2951e-05 | 2.0323e-05 | 0.18877 | 0.18877 | 0.18877 | 0.97306 | -0.51888 | 0.97277 | -0.52447 | 10.3718
12 | -0.13147 | -0.03303 | 0.13157 | 0.033087 | 9.0684e-05 | 5.6179e-05 | 0.20108 | 0.20108 | 0.20108 | 0.97306 | -0.51888 | 0.97379 | -0.50444 | 11.0485
13 | 0.11932 | 0.029972 | -0.11924 | -0.02992 | 8.485e-05 | 5.2198e-05 | 0.18254 | 0.18254 | 0.18254 | 0.97277 | -0.52447 | 0.97202 | -0.53939 | 10.0299
14 | -0.13499 | -0.033944 | 0.13509 | 0.034009 | 0.00010405 | 6.4565e-05 | 0.20631 | 0.20631 | 0.20631 | 0.97379 | -0.50444 | 0.97461 | -0.48831 | 11.3358
15 | -0.14277 | -0.035933 | 0.1429 | 0.036017 | 0.00013441 | 8.3673e-05 | 0.21803 | 0.21803 | 0.21803 | 0.97461 | -0.48831 | 0.97561 | -0.46863 | 11.9799
16 | -0.148 | -0.037294 | 0.1481 | 0.037356 | 0.00010044 | 6.2643e-05 | 0.2258 | 0.2258 | 0.2258 | 0.97561 | -0.46863 | 0.97633 | -0.45446 | 12.4067
17 | 0.049527 | 0.012414 | -0.049526 | -0.012414 | 1.139e-06 | 5.6591e-07 | 0.075898 | 0.075898 | 0.075898 | 0.97102 | -0.55908 | 0.971 | -0.55956 | 4.1702
18 | 0.045999 | 0.01153 | -0.045992 | -0.011527 | 6.7214e-06 | 3.1865e-06 | 0.070493 | 0.070493 | 0.070493 | 0.971 | -0.55956 | 0.97084 | -0.56263 | 3.8732
19 | -0.0066945 | -0.0016777 | 0.0066949 | 0.0016778 | 3.9093e-07 | 1.2234e-07 | 0.01015 | 0.01015 | 0.01015 | 0.98139 | -0.35578 | 0.98145 | -0.35455 | 2.7885
20 | 0.0045314 | 0.0011355 | -0.004531 | -0.0011356 | 4.1566e-07 | -3.0635e-08 | 0.0068707 | 0.0068708 | 0.0068708 | 0.98139 | -0.35578 | 0.98129 | -0.3577 | 1.8876
21 | -0.22092 | -0.055988 | 0.22101 | 0.056047 | 9.3516e-05 | 5.9148e-05 | 0.33517 | 0.33517 | 0.33517 | 0.98145 | -0.35455 | 0.98191 | -0.34574 | 18.4158
22 | 0.21422 | 0.05431 | -0.21405 | -0.054199 | 0.0001756 | 0.00011098 | 0.32502 | 0.32502 | 0.32502 | 0.98145 | -0.35455 | 0.98058 | -0.37162 | 17.8581
23 | -0.22381 | -0.056747 | 0.22384 | 0.05677 | 3.6645e-05 | 2.3185e-05 | 0.3394 | 0.3394 | 0.3394 | 0.98191 | -0.34574 | 0.98208 | -0.34234 | 18.6484
24 | 0.21405 | 0.054199 | -0.21372 | -0.05399 | 0.00033014 | 0.00020866 | 0.32502 | 0.32502 | 0.32502 | 0.98058 | -0.37162 | 0.97892 | -0.4038 | 17.8582
25 | -0.22768 | -0.057731 | 0.22782 | 0.05782 | 0.00014108 | 8.9294e-05 | 0.34521 | 0.34521 | 0.34521 | 0.98208 | -0.34234 | 0.98275 | -0.32946 | 18.9674
26 | 0.21082 | 0.053265 | -0.21074 | -0.053209 | 8.8161e-05 | 5.5705e-05 | 0.32062 | 0.32062 | 0.32062 | 0.97892 | -0.4038 | 0.97848 | -0.41252 | 17.6164
27 | 0.014182 | 0.0035557 | -0.014178 | -0.0035536 | 3.7136e-06 | 2.1047e-06 | 0.021474 | 0.021474 | 0.021474 | 0.98275 | -0.32946 | 0.98247 | -0.33495 | 5.8995
28 | -0.242 | -0.061376 | 0.24204 | 0.061399 | 3.7162e-05 | 2.355e-05 | 0.36668 | 0.36668 | 0.36668 | 0.98275 | -0.32946 | 0.98291 | -0.32626 | 20.1473
29 | 0.21074 | 0.053209 | -0.21051 | -0.053068 | 0.00022342 | 0.00014117 | 0.32062 | 0.32062 | 0.32062 | 0.97848 | -0.41252 | 0.97734 | -0.43468 | 17.6165
30 | -0.57239 | -0.1469 | 0.57263 | 0.14706 | 0.00024171 | 0.0001544 | 0.85335 | 0.85335 | 0.85335 | 0.99954 | -0.0086979 | 1 | 0 | 46.8871
31 | 0.56775 | 0.14574 | -0.56638 | -0.14487 | 0.0013681 | 0.00087389 | 0.84643 | 0.84643 | 0.84643 | 0.99954 | -0.0086979 | 0.99691 | -0.058476 | 46.5073
32 | 0.33124 | 0.085194 | -0.33119 | -0.085165 | 4.6696e-05 | 2.972e-05 | 0.4952 | 0.4952 | 0.4952 | 0.99691 | -0.058476 | 0.99675 | -0.061377 | 27.2086
33 | 0.23514 | 0.059671 | -0.23506 | -0.059619 | 8.1423e-05 | 5.1537e-05 | 0.35124 | 0.35124 | 0.35124 | 0.99691 | -0.058476 | 0.99653 | -0.065678 | 19.2988
34 | 0.3296 | 0.084765 | -0.32922 | -0.084521 | 0.00038467 | 0.00024481 | 0.49282 | 0.49282 | 0.49282 | 0.99675 | -0.061377 | 0.99548 | -0.085418 | 27.078
35 | 0.23235 | 0.058941 | -0.23222 | -0.058861 | 0.00012758 | 8.0736e-05 | 0.3472 | 0.3472 | 0.3472 | 0.99653 | -0.065678 | 0.99593 | -0.077105 | 19.0768
36 | -0.0011825 | -0.00029637 | 0.0011826 | 0.00029609 | 2.6588e-08 | -2.7494e-07 | 0.0017723 | 0.0017722 | 0.0017723 | 0.99286 | -0.13523 | 0.99288 | -0.13475 | 0.48689
37 | 0.30775 | 0.078854 | -0.30736 | -0.078606 | 0.00038956 | 0.00024775 | 0.46184 | 0.46184 | 0.46184 | 0.99288 | -0.13475 | 0.99151 | -0.16091 | 25.3758
38 | -0.31094 | -0.079653 | 0.31169 | 0.080127 | 0.00074526 | 0.00047401 | 0.46662 | 0.46662 | 0.46662 | 0.99288 | -0.13475 | 0.99548 | -0.085418 | 25.6385
39 | 0.015828 | 0.0039672 | -0.015827 | -0.0039665 | 1.2867e-06 | 7.4378e-07 | 0.023659 | 0.023659 | 0.023659 | 0.99548 | -0.085418 | 0.9954 | -0.087124 | 6.4997
40 | 0.22682 | 0.057505 | -0.2265 | -0.057308 | 0.00031107 | 0.00019674 | 0.33912 | 0.33912 | 0.33912 | 0.99593 | -0.077105 | 0.99444 | -0.10568 | 18.6329
41 | 0.22109 | 0.05595 | -0.22107 | -0.055941 | 1.4394e-05 | 9.0985e-06 | 0.33101 | 0.33101 | 0.33101 | 0.99444 | -0.10568 | 0.99437 | -0.10704 | 18.1874
42 | -0.1543 | -0.038909 | 0.15444 | 0.039001 | 0.00014623 | 9.138e-05 | 0.23525 | 0.23524 | 0.23525 | 0.97633 | -0.45446 | 0.97734 | -0.43468 | 12.9256
43 | 0.056072 | 0.014067 | -0.056062 | -0.014063 | 9.3937e-06 | 4.9355e-06 | 0.085375 | 0.085375 | 0.085375 | 0.97734 | -0.43468 | 0.97717 | -0.43819 | 4.6909
44 | 0.050283 | 0.012614 | -0.050281 | -0.012613 | 2.5286e-06 | 1.2582e-06 | 0.076575 | 0.076575 | 0.076575 | 0.97717 | -0.43819 | 0.97711 | -0.43925 | 4.2074
45 | 0.039372 | 0.009879 | -0.039361 | -0.009873 | 1.076e-05 | 5.987e-06 | 0.059963 | 0.059963 | 0.059963 | 0.97711 | -0.43925 | 0.97682 | -0.44498 | 5.4911
46 | 0.034845 | 0.008741 | -0.034843 | -0.0087402 | 1.2823e-06 | 8.0545e-07 | 0.053083 | 0.053083 | 0.053083 | 0.97682 | -0.44498 | 0.97678 | -0.44575 | 14.5832
47 | 0.026241 | 0.0065842 | -0.02622 | -0.0065713 | 2.0763e-05 | 1.2855e-05 | 0.039977 | 0.039978 | 0.039978 | 0.97678 | -0.44575 | 0.97594 | -0.46236 | 10.9828
48 | 0.038881 | 0.0097443 | -0.038879 | -0.0097435 | 1.7981e-06 | 7.3339e-07 | 0.059592 | 0.059593 | 0.059593 | 0.97084 | -0.56263 | 0.97079 | -0.5636 | 3.2743
49 | 0.031072 | 0.0077869 | -0.031069 | -0.0077861 | 2.8272e-06 | 7.8212e-07 | 0.047626 | 0.047627 | 0.047627 | 0.97079 | -0.5636 | 0.9707 | -0.56551 | 2.6168
50 | 0.025069 | 0.0062825 | -0.025068 | -0.0062824 | 9.2637e-07 | 7.5958e-08 | 0.038429 | 0.03843 | 0.03843 | 0.9707 | -0.56551 | 0.97066 | -0.56629 | 2.1115
51 | 0.010276 | 0.0025755 | -0.010275 | -0.0025752 | 6.996e-07 | 3.5022e-07 | 0.015563 | 0.015563 | 0.015563 | 0.98247 | -0.33495 | 0.98239 | -0.33638 | 4.2757
52 | -0.24518 | -0.062186 | 0.24544 | 0.062356 | 0.00026855 | 0.00017022 | 0.37143 | 0.37143 | 0.37143 | 0.98291 | -0.32626 | 0.98409 | -0.30351 | 20.4084
53 | 0.0065791 | 0.0016489 | -0.0065787 | -0.0016488 | 3.4834e-07 | 1.0451e-07 | 0.0099652 | 0.0099653 | 0.0099653 | 0.98239 | -0.33638 | 0.98234 | -0.33749 | 2.7377
54 | -0.24821 | -0.063048 | 0.24821 | 0.06305 | 1.8676e-06 | 1.184e-06 | 0.37561 | 0.37561 | 0.37561 | 0.98409 | -0.30351 | 0.9841 | -0.30335 | 20.6378
55 | -0.25066 | -0.063663 | 0.25093 | 0.063837 | 0.00027336 | 0.00017334 | 0.37931 | 0.37931 | 0.37931 | 0.9841 | -0.30335 | 0.98527 | -0.28072 | 20.8412
56 | 0.30375 | 0.0777 | -0.30333 | -0.077433 | 0.0004189 | 0.00026637 | 0.45641 | 0.45641 | 0.45641 | 0.99151 | -0.16091 | 0.99002 | -0.18945 | 25.0776
57 | 0.017902 | 0.0044863 | -0.017901 | -0.0044864 | 1.1097e-06 | -6.6813e-08 | 0.027443 | 0.027444 | 0.027444 | 0.97066 | -0.56629 | 0.97059 | -0.56759 | 1.8849
58 | 0.007654 | 0.0019183 | -0.0076537 | -0.0019182 | 2.6859e-07 | 1.0761e-07 | 0.011734 | 0.011734 | 0.011734 | 0.97059 | -0.56759 | 0.97055 | -0.56833 | 3.2237
59 | 0.30154 | 0.076986 | -0.30142 | -0.076909 | 0.00012044 | 7.6578e-05 | 0.45373 | 0.45373 | 0.45373 | 0.99002 | -0.18945 | 0.98959 | -0.19771 | 24.9301
60 | 0.29817 | 0.076093 | -0.29793 | -0.075946 | 0.00023149 | 0.00014717 | 0.44883 | 0.44883 | 0.44883 | 0.98959 | -0.19771 | 0.98875 | -0.2138 | 24.6612
61 | 0.29576 | 0.0754 | -0.29545 | -0.075207 | 0.00030389 | 0.00019318 | 0.44556 | 0.44556 | 0.44556 | 0.98875 | -0.2138 | 0.98764 | -0.23511 | 24.4812
62 | 0.014609 | 0.0036572 | -0.014608 | -0.0036582 | 8.6537e-07 | -9.5554e-07 | 0.022062 | 0.022063 | 0.022063 | 0.98527 | -0.28072 | 0.9852 | -0.28196 | 1.2122
63 | -0.26554 | -0.067494 | 0.26612 | 0.067865 | 0.0005847 | 0.00037112 | 0.40137 | 0.40137 | 0.40137 | 0.98527 | -0.28072 | 0.98764 | -0.23511 | 22.0534
64 | 0.014608 | 0.0036582 | -0.014608 | -0.003659 | 7.1837e-07 | -7.9301e-07 | 0.022063 | 0.022063 | 0.022063 | 0.9852 | -0.28196 | 0.98515 | -0.283 | 1.2123
65 | 0.029331 | 0.0073424 | -0.029328 | -0.0073419 | 2.5656e-06 | 5.2111e-07 | 0.044188 | 0.044188 | 0.044188 | 0.98764 | -0.23511 | 0.98754 | -0.23694 | 2.4279
66 | 0.025602 | 0.0064081 | -0.0256 | -0.0064079 | 2.4785e-06 | 1.6563e-07 | 0.038574 | 0.038575 | 0.038575 | 0.98754 | -0.23694 | 0.98744 | -0.23898 | 2.1195
67 | 0.019397 | 0.0048534 | -0.019396 | -0.0048538 | 1.2687e-06 | -4.5445e-07 | 0.029228 | 0.029228 | 0.029228 | 0.98744 | -0.23898 | 0.98737 | -0.24035 | 1.6059
68 | 0.013042 | 0.0032667 | -0.013041 | -0.0032677 | 1.2246e-06 | -9.304e-07 | 0.019699 | 0.0197 | 0.0197 | 0.98515 | -0.283 | 0.98505 | -0.28497 | 1.353
69 | 0.019396 | 0.0048538 | -0.019393 | -0.004855 | 3.2458e-06 | -1.1616e-06 | 0.029228 | 0.029229 | 0.029229 | 0.98737 | -0.24035 | 0.98719 | -0.24387 | 1.606
70 | 0.0044741 | 0.0011206 | -0.0044738 | -0.0011206 | 3.3951e-07 | -3.5019e-08 | 0.0067583 | 0.0067584 | 0.0067584 | 0.98505 | -0.28497 | 0.98497 | -0.28656 | 1.8567
71 | -0.0017629 | -0.00044183 | 0.001763 | 0.00044148 | 8.5465e-08 | -3.5421e-07 | 0.0026634 | 0.0026633 | 0.0026634 | 0.98492 | -0.28758 | 0.98497 | -0.28656 | 0.73171
72 | 0.0027108 | 0.00067911 | -0.0027106 | -0.00067935 | 1.6896e-07 | -2.3379e-07 | 0.0040952 | 0.0040953 | 0.0040953 | 0.98497 | -0.28656 | 0.9849 | -0.28787 | 1.1251
73 | 0.00088621 | 0.00022185 | -0.00088619 | -0.0002221 | 1.3545e-08 | -2.5031e-07 | 0.0013355 | 0.0013356 | 0.0013356 | 0.98733 | -0.24309 | 0.98732 | -0.24341 | 0.36693
74 | -0.0021835 | -0.00054698 | 0.0021835 | 0.00054688 | 3.7526e-08 | -9.4177e-08 | 0.0032906 | 0.0032906 | 0.0032906 | 0.98733 | -0.24309 | 0.98735 | -0.24273 | 0.90402
75 | -0.0028491 | -0.00071368 | 0.0028501 | 0.00071241 | 1.0563e-06 | -1.2792e-06 | 0.0042936 | 0.0042929 | 0.0042936 | 0.98735 | -0.24273 | 0.98775 | -0.23494 | 1.1796
76 | -0.0096959 | -0.0024281 | 0.0096966 | 0.0024281 | 6.7968e-07 | -3.5576e-11 | 0.014606 | 0.014606 | 0.014606 | 0.98775 | -0.23494 | 0.98783 | -0.23347 | 2.0063
77 | -0.0096966 | -0.0024281 | 0.0096967 | 0.0024279 | 7.8976e-08 | -2.6542e-07 | 0.014606 | 0.014606 | 0.014606 | 0.98783 | -0.23347 | 0.98784 | -0.2333 | 0.80251
78 | -0.0061139 | -0.0015323 | 0.006114 | 0.0015323 | 6.6069e-08 | 1.6041e-08 | 0.0092402 | 0.0092402 | 0.0092402 | 0.98458 | -0.29677 | 0.98459 | -0.29654 | 2.5385
79 | -0.016024 | -0.0040159 | 0.016025 | 0.0040156 | 1.285e-06 | -3.6671e-07 | 0.024217 | 0.024216 | 0.024217 | 0.98459 | -0.29654 | 0.98467 | -0.29486 | 1.6632
80 | -0.022455 | -0.005627 | 0.022456 | 0.0056269 | 1.0563e-06 | -1.0195e-07 | 0.033933 | 0.033933 | 0.033933 | 0.98467 | -0.29486 | 0.98472 | -0.29387 | 1.8645
81 | -0.13031 | -0.032725 | 0.13036 | 0.032757 | 5.1289e-05 | 3.1691e-05 | 0.1964 | 0.1964 | 0.1964 | 0.98745 | -0.2408 | 0.98787 | -0.23255 | 10.791
82 | 0.12344 | 0.031002 | -0.12338 | -0.030967 | 5.7249e-05 | 3.5229e-05 | 0.18604 | 0.18604 | 0.18604 | 0.98745 | -0.2408 | 0.98695 | -0.25052 | 10.2218
83 | -0.13786 | -0.034635 | 0.13786 | 0.034639 | 6.0711e-06 | 3.7654e-06 | 0.20768 | 0.20768 | 0.20768 | 0.98787 | -0.23255 | 0.98792 | -0.23163 | 11.4112
84 | 0.11511 | 0.028894 | -0.11507 | -0.028867 | 4.4661e-05 | 2.7321e-05 | 0.17357 | 0.17357 | 0.17357 | 0.98695 | -0.25052 | 0.98653 | -0.25866 | 9.5368
85 | -0.0261 | -0.0065402 | 0.026101 | 0.0065403 | 1.2483e-06 | 1.1824e-07 | 0.039439 | 0.039439 | 0.039439 | 0.98472 | -0.29387 | 0.98478 | -0.29287 | 2.167
86 | -0.14219 | -0.035724 | 0.14227 | 0.035768 | 7.0423e-05 | 4.376e-05 | 0.21421 | 0.21421 | 0.21421 | 0.98792 | -0.23163 | 0.98845 | -0.22126 | 11.7696
87 | 0.10885 | 0.02731 | -0.10881 | -0.027285 | 4.0587e-05 | 2.4695e-05 | 0.1642 | 0.1642 | 0.1642 | 0.98653 | -0.25866 | 0.98613 | -0.26649 | 9.022
88 | -0.033682 | -0.0084403 | 0.033682 | 0.0084404 | 4.3201e-07 | 1.3502e-07 | 0.050894 | 0.050894 | 0.050894 | 0.98478 | -0.29287 | 0.98479 | -0.2926 | 2.7964
89 | -0.14647 | -0.036822 | 0.14654 | 0.036862 | 6.3994e-05 | 3.9831e-05 | 0.22054 | 0.22054 | 0.22054 | 0.98845 | -0.22126 | 0.98893 | -0.21211 | 12.1176
90 | 0.0042077 | 0.0010542 | -0.004207 | -0.0010544 | 7.026e-07 | -1.4879e-07 | 0.0063341 | 0.0063343 | 0.0063343 | 0.98845 | -0.22126 | 0.98827 | -0.22477 | 1.7402
91 | 0.10291 | 0.025806 | -0.10288 | -0.02579 | 2.6807e-05 | 1.6212e-05 | 0.15529 | 0.15529 | 0.15529 | 0.98613 | -0.26649 | 0.98585 | -0.27195 | 8.5325
92 | 0.019208 | 0.0047987 | -0.019207 | -0.004799 | 9.7832e-07 | -3.5885e-07 | 0.029021 | 0.029021 | 0.029021 | 0.98467 | -0.29498 | 0.98461 | -0.29605 | 1.5946
93 | -0.024602 | -0.0061507 | 0.024604 | 0.0061507 | 1.3061e-06 | 3.4338e-08 | 0.037173 | 0.037173 | 0.037173 | 0.98467 | -0.29498 | 0.98473 | -0.29386 | 2.0425
94 | 0.015571 | 0.0038879 | -0.015571 | -0.0038881 | 2.5981e-07 | -2.3169e-07 | 0.023527 | 0.023527 | 0.023527 | 0.98461 | -0.29605 | 0.9846 | -0.2964 | 1.2927
95 | -0.02603 | -0.0065081 | 0.02603 | 0.0065082 | 6.7835e-07 | 6.2167e-08 | 0.039328 | 0.039328 | 0.039328 | 0.98473 | -0.29386 | 0.98475 | -0.29331 | 2.1609
96 | 0.011935 | 0.002977 | -0.011935 | -0.0029774 | 2.3708e-07 | -4.6639e-07 | 0.018033 | 0.018033 | 0.018033 | 0.9846 | -0.2964 | 0.98457 | -0.29682 | 0.99083
97 | -0.027793 | -0.00695 | 0.027795 | 0.0069502 | 1.2578e-06 | 1.9995e-07 | 0.041992 | 0.041991 | 0.041992 | 0.98475 | -0.29331 | 0.9848 | -0.29236 | 2.3072
98 | 0.0022336 | 0.00055965 | -0.0022336 | -0.00055979 | 1.2448e-08 | -1.4022e-07 | 0.0033756 | 0.0033757 | 0.0033757 | 0.98457 | -0.29682 | 0.98457 | -0.29693 | 0.46369
99 | 0.0097017 | 0.0024178 | -0.0097013 | -0.002419 | 3.6321e-07 | -1.2008e-06 | 0.014658 | 0.014658 | 0.014658 | 0.98457 | -0.29682 | 0.98453 | -0.29761 | 0.80539
100 | -0.029831 | -0.0074606 | 0.029833 | 0.007461 | 1.6597e-06 | 3.6907e-07 | 0.045069 | 0.045068 | 0.045069 | 0.9848 | -0.29236 | 0.98486 | -0.29119 | 2.4763
101 | 0.0013545 | 0.00032873 | -0.0013544 | -0.00033945 | 5.3075e-08 | -1.0722e-05 | 0.0020434 | 0.0020471 | 0.0020471 | 0.98453 | -0.29761 | 0.98449 | -0.29844 | 0.11248
102 | 0.0043064 | 0.0010776 | -0.0043063 | -0.0010791 | 7.3921e-08 | -1.4321e-06 | 0.0065081 | 0.0065086 | 0.0065086 | 0.98453 | -0.29761 | 0.98452 | -0.29797 | 0.35762
103 | -0.035008 | -0.0087569 | 0.035011 | 0.0087578 | 2.5292e-06 | 8.5154e-07 | 0.052888 | 0.052887 | 0.052888 | 0.98486 | -0.29119 | 0.98494 | -0.28967 | 2.9059
104 | 0.0051755 | 0.0012959 | -0.0051754 | -0.0012971 | 8.6488e-08 | -1.1446e-06 | 0.0078191 | 0.0078195 | 0.0078195 | 0.98486 | -0.29119 | 0.98484 | -0.29154 | 0.42965
105 | 0.092676 | 0.023233 | -0.092645 | -0.023214 | 3.157e-05 | 1.8834e-05 | 0.13989 | 0.13989 | 0.13989 | 0.98585 | -0.27195 | 0.98548 | -0.2791 | 7.6861
106 | 0.010208 | 0.0025563 | -0.010207 | -0.0025575 | 3.9973e-07 | -1.1756e-06 | 0.015406 | 0.015407 | 0.015407 | 0.98585 | -0.27195 | 0.98581 | -0.27277 | 0.84653
107 | 0.086924 | 0.021782 | -0.08689 | -0.021761 | 3.4461e-05 | 2.0357e-05 | 0.13125 | 0.13125 | 0.13125 | 0.98548 | -0.2791 | 0.98505 | -0.28743 | 7.2115
108 | 0.0057205 | 0.0014328 | -0.0057204 | -0.0014337 | 8.4156e-08 | -9.0426e-07 | 0.0086373 | 0.0086376 | 0.0086376 | 0.98548 | -0.2791 | 0.98546 | -0.27941 | 0.47459
109 | 0.010207 | 0.0025575 | -0.010207 | -0.0025581 | 2.0199e-07 | -5.9397e-07 | 0.015407 | 0.015407 | 0.015407 | 0.98581 | -0.27277 | 0.98578 | -0.27319 | 0.84654
110 | 0.040517 | 0.010138 | -0.040514 | -0.010137 | 3.5235e-06 | 1.4567e-06 | 0.061199 | 0.0612 | 0.0612 | 0.98505 | -0.28743 | 0.98496 | -0.28926 | 3.3626
111 | 0.046373 | 0.011623 | -0.046368 | -0.011621 | 4.352e-06 | 2.0327e-06 | 0.07005 | 0.070051 | 0.070051 | 0.98505 | -0.28743 | 0.98495 | -0.2894 | 3.8489
112 | 0.038015 | 0.0095108 | -0.038014 | -0.0095105 | 7.4757e-07 | 2.8609e-07 | 0.057425 | 0.057425 | 0.057425 | 0.98496 | -0.28926 | 0.98494 | -0.28967 | 3.1552
113 | 0.040241 | 0.010085 | -0.040235 | -0.010083 | 6.1316e-06 | 2.5168e-06 | 0.060795 | 0.060795 | 0.060795 | 0.98495 | -0.2894 | 0.98479 | -0.2926 | 3.3404
114 | -0.20163 | -0.050667 | 0.2017 | 0.050713 | 7.2886e-05 | 4.597e-05 | 0.30343 | 0.30343 | 0.30343 | 0.98893 | -0.21211 | 0.98932 | -0.20454 | 16.672
115 | 0.055089 | 0.013806 | -0.055082 | -0.013802 | 7.0804e-06 | 3.6502e-06 | 0.08289 | 0.082891 | 0.082891 | 0.98893 | -0.21211 | 0.98879 | -0.21481 | 4.5544
116 | -0.20374 | -0.051225 | 0.20387 | 0.051307 | 0.00013036 | 8.2242e-05 | 0.3065 | 0.3065 | 0.3065 | 0.98932 | -0.20454 | 0.99001 | -0.19116 | 16.8405
117 | 0.052449 | 0.013142 | -0.052446 | -0.013141 | 2.476e-06 | 1.2448e-06 | 0.078929 | 0.078929 | 0.078929 | 0.98879 | -0.21481 | 0.98874 | -0.2158 | 4.3368
118 | -0.20613 | -0.051874 | 0.20665 | 0.052199 | 0.00051546 | 0.00032528 | 0.3099 | 0.30989 | 0.3099 | 0.99001 | -0.19116 | 0.99271 | -0.13897 | 17.0272
119 | 0.049023 | 0.012283 | -0.049016 | -0.01228 | 6.831e-06 | 3.299e-06 | 0.073777 | 0.073778 | 0.073778 | 0.98874 | -0.2158 | 0.98859 | -0.21873 | 4.0537
120 | 0.001628 | 0.00040782 | -0.001628 | -0.00040801 | 9.0925e-09 | -1.9788e-07 | 0.0024605 | 0.0024606 | 0.0024606 | 0.98452 | -0.29797 | 0.98451 | -0.29808 | 0.338
121 | -0.019432 | -0.0048665 | 0.019432 | 0.0048663 | 6.5428e-07 | -2.3332e-07 | 0.029267 | 0.029267 | 0.029267 | 0.98791 | -0.23178 | 0.98795 | -0.23107 | 1.6081
122 | 0.017954 | 0.0044961 | -0.017953 | -0.0044966 | 9.6744e-07 | -5.1013e-07 | 0.027041 | 0.027041 | 0.027041 | 0.98791 | -0.23178 | 0.98786 | -0.23291 | 1.4858
123 | -0.021918 | -0.0054892 | 0.021919 | 0.005489 | 1.5971e-06 | -2.2915e-07 | 0.03301 | 0.03301 | 0.03301 | 0.98795 | -0.23107 | 0.98803 | -0.22954 | 1.8138
124 | 0.014159 | 0.0035457 | -0.014158 | -0.0035461 | 2.6122e-07 | -3.2302e-07 | 0.021326 | 0.021326 | 0.021326 | 0.98786 | -0.23291 | 0.98784 | -0.2333 | 1.1718
125 | -0.024944 | -0.006247 | 0.024946 | 0.0062471 | 2.3495e-06 | 8.1965e-08 | 0.037565 | 0.037565 | 0.037565 | 0.98803 | -0.22954 | 0.98813 | -0.22756 | 2.064
126 | -0.029422 | -0.0073689 | 0.029423 | 0.0073691 | 6.3181e-07 | 1.2948e-07 | 0.044305 | 0.044305 | 0.044305 | 0.98813 | -0.22756 | 0.98815 | -0.22711 | 2.4344
127 | -0.03339 | -0.0083609 | 0.033391 | 0.0083614 | 1.5029e-06 | 4.5407e-07 | 0.050277 | 0.050277 | 0.050277 | 0.98815 | -0.22711 | 0.9882 | -0.22617 | 2.7625
128 | 0.0039665 | 0.00099185 | -0.0039664 | -0.00099407 | 9.5331e-08 | -2.2213e-06 | 0.0059722 | 0.005973 | 0.005973 | 0.98815 | -0.22711 | 0.98813 | -0.22762 | 0.32818
129 | 0.045813 | 0.011477 | -0.045811 | -0.011476 | 2.6188e-06 | 1.2053e-06 | 0.068956 | 0.068956 | 0.068956 | 0.98859 | -0.21873 | 0.98852 | -0.21993 | 3.7888
130 | 0.041799 | 0.01047 | -0.041791 | -0.010467 | 8.0994e-06 | 3.4354e-06 | 0.062918 | 0.062919 | 0.062919 | 0.98852 | -0.21993 | 0.98831 | -0.224 | 3.4571
131 | 0.036157 | 0.009055 | -0.036154 | -0.0090537 | 3.7308e-06 | 1.3123e-06 | 0.054436 | 0.054437 | 0.054437 | 0.98831 | -0.224 | 0.9882 | -0.22617 | 2.991
132 | -0.21242 | -0.053646 | 0.21249 | 0.053691 | 7.0509e-05 | 4.4527e-05 | 0.31855 | 0.31855 | 0.31855 | 0.99271 | -0.13897 | 0.99307 | -0.13204 | 17.5029
133 | -0.21681 | -0.054774 | 0.21686 | 0.054802 | 4.4897e-05 | 2.8367e-05 | 0.32503 | 0.32503 | 0.32503 | 0.99307 | -0.13204 | 0.99329 | -0.12773 | 17.8586
134 | 0.0029866 | 0.00074814 | -0.0029866 | -0.00074852 | 1.4276e-08 | -3.8472e-07 | 0.004474 | 0.0044742 | 0.0044742 | 0.99329 | -0.12773 | 0.99329 | -0.12783 | 0.30729
135 | -0.21984 | -0.05555 | 0.22006 | 0.055688 | 0.00021826 | 0.00013795 | 0.3295 | 0.3295 | 0.3295 | 0.99329 | -0.12773 | 0.99437 | -0.10704 | 18.1044
136 | -0.0063331 | -0.001583 | 0.0063332 | 0.001582 | 1.1421e-07 | -9.9549e-07 | 0.0095447 | 0.0095443 | 0.0095447 | 0.98717 | -0.24425 | 0.98719 | -0.24387 | 0.52444
137 | 0.0063331 | 0.001583 | -0.0063329 | -0.0015845 | 1.7002e-07 | -1.4817e-06 | 0.0095447 | 0.0095453 | 0.0095453 | 0.98717 | -0.24425 | 0.98714 | -0.24481 | 0.52447
138 | 0.0019681 | 0.00049052 | -0.001968 | -0.00049324 | 2.826e-08 | -2.7194e-06 | 0.0029657 | 0.0029667 | 0.0029667 | 0.98714 | -0.24481 | 0.98712 | -0.24512 | 0.163

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57712 | 0.14777

## res_load
| p_mw | q_mvar
0 | 0.01039 | 0.0026041
1 | 0.0039111 | 0.00098021
2 | 0.0096402 | 0.0024161
3 | 0.0077224 | 0.0019354
4 | 0.0093083 | 0.0023329
5 | 0.0033817 | 0.00084753
6 | 0.0076233 | 0.0019106
7 | 0.0080518 | 0.002018
8 | 0.0040686 | 0.0010197
9 | 0.0034223 | 0.0008577
10 | 0.0041836 | 0.0010485
11 | 0.0076788 | 0.0019245
12 | 0.0050942 | 0.0012767
13 | 0.013441 | 0.0033686
14 | 0.003527 | 0.00088396
15 | 0.002163 | 0.00054211
16 | 0.004531 | 0.0011356
17 | 0.0027944 | 0.00070034
18 | 0.0038319 | 0.00096037
19 | 0.0028945 | 0.00072543
20 | 0.0046438 | 0.0011638
21 | 0.0028396 | 0.00071167
22 | 0.0015935 | 0.00039937
23 | 0.0027057 | 0.0006781
24 | 0.0011825 | 0.00029637
25 | 0.0020075 | 0.00050312
26 | 0.0017 | 0.00042605
27 | 0.0054082 | 0.0013554
28 | 0.015827 | 0.0039665
29 | 0.0054182 | 0.0013579
30 | 0.0061963 | 0.0015529
31 | 0.0057789 | 0.0014483
32 | 0.010908 | 0.0027339
33 | 0.0045168 | 0.001132
34 | 0.0086028 | 0.0021561
35 | 0.02622 | 0.0065713
36 | 0.0071119 | 0.0017824
37 | 0.007807 | 0.0019566
38 | 0.0059996 | 0.0015037
39 | 0.0039025 | 0.00097807
40 | 0.0031385 | 0.00078659
41 | 0.003696 | 0.0009263
42 | 0.0027617 | 0.00069216
43 | 0.0065787 | 0.0016488
44 | 0.0024485 | 0.00061365
45 | 0.0036169 | 0.00090647
46 | 0.0071666 | 0.0017961
47 | 0.010247 | 0.002568
48 | 0.0076537 | 0.0019182
49 | 0.0017868 | 0.00044782
50 | 0.0032554 | 0.00081588
51 | 0.0021767 | 0.00054553
52 | 0.0037258 | 0.00093378
53 | 0.0062027 | 0.0015545
54 | 0.001565 | 0.00039223
55 | 0.0085671 | 0.0021471
56 | 0.0017629 | 0.00044183
57 | 0.0027106 | 0.00067935
58 | 0.0012973 | 0.00032513
59 | 0.00088619 | 0.0002221
60 | 0.00066555 | 0.0001668
61 | 0.0068458 | 0.0017157
62 | 0.0061139 | 0.0015323
63 | 0.0099097 | 0.0024836
64 | 0.0064299 | 0.0016115
65 | 0.0068746 | 0.0017229
66 | 0.007494 | 0.0018782
67 | 0.0082688 | 0.0020724
68 | 0.003644 | 0.00091326
69 | 0.0043304 | 0.0010853
70 | 0.0062127 | 0.001557
71 | 0.0075808 | 0.0018999
72 | 0.0059036 | 0.0014796
73 | 0.0053947 | 0.001352
74 | 0.0036354 | 0.00091111
75 | 0.0014259 | 0.00035737
76 | 0.0036356 | 0.00091118
77 | 0.001763 | 0.00044185
78 | 0.0020366 | 0.00051041
79 | 0.0022336 | 0.00055979
80 | 0.0040404 | 0.0010126
81 | 0.0057204 | 0.0014337
82 | 0.010207 | 0.0025581
83 | 0.0024988 | 0.00062625
84 | 0.0061268 | 0.0015355
85 | 0.004207 | 0.0010544
86 | 0.0020398 | 0.00051122
87 | 0.0026326 | 0.00065978
88 | 0.0022612 | 0.00056671
89 | 0.0034233 | 0.00085795
90 | 0.0013544 | 0.00033945
91 | 0.0026783 | 0.00067126
92 | 0.0014778 | 0.00037038
93 | 0.0024857 | 0.00062297
94 | 0.0037941 | 0.00095089
95 | 0.0030246 | 0.00075804
96 | 0.0044617 | 0.0011182
97 | 0.0044761 | 0.0011218
98 | 0.0032032 | 0.00080279
99 | 0.0040113 | 0.0010053
100 | 0.0056338 | 0.001412
101 | 0.0057764 | 0.0014477
102 | 0.0027625 | 0.00069234
103 | 0.0039664 | 0.00099407
104 | 0.0051754 | 0.0012971
105 | 0.0030033 | 0.00075271
106 | 0.0065528 | 0.0016423
107 | 0.0043203 | 0.0010828
108 | 0.0029866 | 0.00074852
109 | 0.00101 | 0.00025314
110 | 0.001628 | 0.00040801
111 | 0.013059 | 0.003273
112 | 0.0043649 | 0.0010939
113 | 0.001968 | 0.00049324

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1