## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1203-4_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1203-4_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1203-4_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1203-4_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1203-4_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1203-4_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1203-4_0_6_node_80 | 0.4 | n |  | TRUE
7 | bus_LV_1203-4_0_6_node_95 | 0.4 | n |  | TRUE
8 | bus_LV_1203-4_0_6_node_78 | 0.4 | n |  | TRUE
9 | bus_LV_1203-4_0_6_node_106 | 0.4 | n |  | TRUE
10 | bus_LV_1203-4_0_6_node_105 | 0.4 | n |  | TRUE
11 | bus_LV_1203-4_0_6_node_108 | 0.4 | n |  | TRUE
12 | bus_LV_1203-4_0_6_node_107 | 0.4 | n |  | TRUE
13 | bus_LV_1203-4_0_6_node_96 | 0.4 | n |  | TRUE
14 | bus_LV_1203-4_0_6_node_109 | 0.4 | n |  | TRUE
15 | bus_LV_1203-4_0_6_node_76 | 0.4 | n |  | TRUE
16 | bus_LV_1203-4_0_6_node_77 | 0.4 | n |  | TRUE
17 | bus_LV_1203-4_0_6_node_44 | 0.4 | n |  | TRUE
18 | bus_LV_1203-4_0_6_node_6 | 0.4 | n |  | TRUE
19 | bus_LV_1203-4_0_6_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_1203-4_0_6_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_1203-4_0_6_node_8 | 0.4 | n |  | TRUE
22 | bus_LV_1203-4_0_6_node_91 | 0.4 | n |  | TRUE
23 | bus_LV_1203-4_0_6_node_90 | 0.4 | n |  | TRUE
24 | bus_LV_1203-4_0_6_node_9 | 0.4 | n |  | TRUE
25 | bus_LV_1203-4_0_6_node_10 | 0.4 | n |  | TRUE
26 | bus_LV_1203-4_0_6_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_1203-4_0_6_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_1203-4_0_6_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_1203-4_0_6_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_1203-4_0_6_node_43 | 0.4 | n |  | TRUE
31 | bus_LV_1203-4_0_6_node_64 | 0.4 | n |  | TRUE
32 | bus_LV_1203-4_0_6_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_1203-4_0_6_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_1203-4_0_6_node_82 | 0.4 | n |  | TRUE
35 | bus_LV_1203-4_0_6_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_1203-4_0_6_node_65 | 0.4 | n |  | TRUE
37 | bus_LV_1203-4_0_6_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_1203-4_0_6_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_1203-4_0_6_node_15 | 0.4 | n |  | TRUE
40 | bus_LV_1203-4_0_6_node_16 | 0.4 | n |  | TRUE
41 | bus_LV_1203-4_0_6_node_17 | 0.4 | n |  | TRUE
42 | bus_LV_1203-4_0_6_node_18 | 0.4 | n |  | TRUE
43 | bus_LV_1203-4_0_6_node_19 | 0.4 | n |  | TRUE
44 | bus_LV_1203-4_0_6_node_74 | 0.4 | n |  | TRUE
45 | bus_LV_1203-4_0_6_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_1203-4_0_6_node_75 | 0.4 | n |  | TRUE
47 | bus_LV_1203-4_0_6_node_38 | 0.4 | n |  | TRUE
48 | bus_LV_1203-4_0_6_node_22 | 0.4 | n |  | TRUE
49 | bus_LV_1203-4_0_6_node_23 | 0.4 | n |  | TRUE
50 | bus_LV_1203-4_0_6_node_24 | 0.4 | n |  | TRUE
51 | bus_LV_1203-4_0_6_node_55 | 0.4 | n |  | TRUE
52 | bus_LV_1203-4_0_6_node_51 | 0.4 | n |  | TRUE
53 | bus_LV_1203-4_0_6_node_103 | 0.4 | n |  | TRUE
54 | bus_LV_1203-4_0_6_node_98 | 0.4 | n |  | TRUE
55 | bus_LV_1203-4_0_6_node_102 | 0.4 | n |  | TRUE
56 | bus_LV_1203-4_0_6_node_25 | 0.4 | n |  | TRUE
57 | bus_LV_1203-4_0_6_node_26 | 0.4 | n |  | TRUE
58 | bus_LV_1203-4_0_6_node_27 | 0.4 | n |  | TRUE
59 | bus_LV_1203-4_0_6_node_28 | 0.4 | n |  | TRUE
60 | bus_LV_1203-4_0_6_node_29 | 0.4 | n |  | TRUE
61 | bus_LV_1203-4_0_6_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_1203-4_0_6_node_70 | 0.4 | n |  | TRUE
63 | bus_LV_1203-4_0_6_node_35 | 0.4 | n |  | TRUE
64 | bus_LV_1203-4_0_6_node_57 | 0.4 | n |  | TRUE
65 | bus_LV_1203-4_0_6_node_58 | 0.4 | n |  | TRUE
66 | bus_LV_1203-4_0_6_node_49 | 0.4 | n |  | TRUE
67 | bus_LV_1203-4_0_6_node_34 | 0.4 | n |  | TRUE
68 | bus_LV_1203-4_0_6_node_36 | 0.4 | n |  | TRUE
69 | bus_LV_1203-4_0_6_node_39 | 0.4 | n |  | TRUE
70 | bus_LV_1203-4_0_6_node_40 | 0.4 | n |  | TRUE
71 | bus_LV_1203-4_0_6_node_42 | 0.4 | n |  | TRUE
72 | bus_LV_1203-4_0_6_node_83 | 0.4 | n |  | TRUE
73 | bus_LV_1203-4_0_6_node_81 | 0.4 | n |  | TRUE
74 | bus_LV_1203-4_0_6_node_45 | 0.4 | n |  | TRUE
75 | bus_LV_1203-4_0_6_node_50 | 0.4 | n |  | TRUE
76 | bus_LV_1203-4_0_6_node_84 | 0.4 | n |  | TRUE
77 | bus_LV_1203-4_0_6_node_46 | 0.4 | n |  | TRUE
78 | bus_LV_1203-4_0_6_node_47 | 0.4 | n |  | TRUE
79 | bus_LV_1203-4_0_6_node_48 | 0.4 | n |  | TRUE
80 | bus_LV_1203-4_0_6_node_142 | 0.4 | n |  | TRUE
81 | bus_LV_1203-4_0_6_node_88 | 0.4 | n |  | TRUE
82 | bus_LV_1203-4_0_6_node_89 | 0.4 | n |  | TRUE
83 | bus_LV_1203-4_0_6_node_87 | 0.4 | n |  | TRUE
84 | bus_LV_1203-4_0_6_node_92 | 0.4 | n |  | TRUE
85 | bus_LV_1203-4_0_6_node_93 | 0.4 | n |  | TRUE
86 | bus_LV_1203-4_0_6_node_94 | 0.4 | n |  | TRUE
87 | bus_LV_1203-4_0_6_node_104 | 0.4 | n |  | TRUE
88 | bus_LV_1203-4_0_6_node_52 | 0.4 | n |  | TRUE
89 | bus_LV_1203-4_0_6_node_53 | 0.4 | n |  | TRUE
90 | bus_LV_1203-4_0_6_node_54 | 0.4 | n |  | TRUE
91 | bus_LV_1203-4_0_6_node_61 | 0.4 | n |  | TRUE
92 | bus_LV_1203-4_0_6_node_85 | 0.4 | n |  | TRUE
93 | bus_LV_1203-4_0_6_node_69 | 0.4 | n |  | TRUE
94 | bus_LV_1203-4_0_6_node_63 | 0.4 | n |  | TRUE
95 | bus_LV_1203-4_0_6_node_59 | 0.4 | n |  | TRUE
96 | bus_LV_1203-4_0_6_node_86 | 0.4 | n |  | TRUE
97 | bus_LV_1203-4_0_6_node_67 | 0.4 | n |  | TRUE
98 | bus_LV_1203-4_0_6_node_72 | 0.4 | n |  | TRUE
99 | bus_LV_1203-4_0_6_node_71 | 0.4 | n |  | TRUE
100 | bus_LV_1203-4_0_6_node_60 | 0.4 | n |  | TRUE
101 | bus_LV_1203-4_0_6_node_62 | 0.4 | n |  | TRUE
102 | bus_LV_1203-4_0_6_node_66 | 0.4 | n |  | TRUE
103 | bus_LV_1203-4_0_6_node_73 | 0.4 | n |  | TRUE
104 | bus_LV_1203-4_0_6_node_121 | 0.4 | n |  | TRUE
105 | bus_LV_1203-4_0_6_node_110 | 0.4 | n |  | TRUE
106 | bus_LV_1203-4_0_6_node_111 | 0.4 | n |  | TRUE
107 | bus_LV_1203-4_0_6_node_112 | 0.4 | n |  | TRUE
108 | bus_LV_1203-4_0_6_node_131 | 0.4 | n |  | TRUE
109 | bus_LV_1203-4_0_6_node_130 | 0.4 | n |  | TRUE
110 | bus_LV_1203-4_0_6_node_79 | 0.4 | n |  | TRUE
111 | bus_LV_1203-4_0_6_node_135 | 0.4 | n |  | TRUE
112 | bus_LV_1203-4_0_6_node_134 | 0.4 | n |  | TRUE
113 | bus_LV_1203-4_0_6_node_132 | 0.4 | n |  | TRUE
114 | bus_LV_1203-4_0_6_node_133 | 0.4 | n |  | TRUE
115 | bus_LV_1203-4_0_6_node_99 | 0.4 | n |  | TRUE
116 | bus_LV_1203-4_0_6_node_100 | 0.4 | n |  | TRUE
117 | bus_LV_1203-4_0_6_node_101 | 0.4 | n |  | TRUE
118 | bus_LV_1203-4_0_6_node_119 | 0.4 | n |  | TRUE
119 | bus_LV_1203-4_0_6_node_141 | 0.4 | n |  | TRUE
120 | bus_LV_1203-4_0_6_node_113 | 0.4 | n |  | TRUE
121 | bus_LV_1203-4_0_6_node_115 | 0.4 | n |  | TRUE
122 | bus_LV_1203-4_0_6_node_125 | 0.4 | n |  | TRUE
123 | bus_LV_1203-4_0_6_node_129 | 0.4 | n |  | TRUE
124 | bus_LV_1203-4_0_6_node_126 | 0.4 | n |  | TRUE
125 | bus_LV_1203-4_0_6_node_127 | 0.4 | n |  | TRUE
126 | bus_LV_1203-4_0_6_node_124 | 0.4 | n |  | TRUE
127 | bus_LV_1203-4_0_6_node_116 | 0.4 | n |  | TRUE
128 | bus_LV_1203-4_0_6_node_117 | 0.4 | n |  | TRUE
129 | bus_LV_1203-4_0_6_node_118 | 0.4 | n |  | TRUE
130 | bus_LV_1203-4_0_6_node_120 | 0.4 | n |  | TRUE
131 | bus_LV_1203-4_0_6_node_122 | 0.4 | n |  | TRUE
132 | bus_LV_1203-4_0_6_node_123 | 0.4 | n |  | TRUE
133 | bus_LV_1203-4_0_6_node_138 | 0.4 | n |  | TRUE
134 | bus_LV_1203-4_0_6_node_128 | 0.4 | n |  | TRUE
135 | bus_LV_1203-4_0_6_node_136 | 0.4 | n |  | TRUE
136 | bus_LV_1203-4_0_6_node_137 | 0.4 | n |  | TRUE
137 | bus_LV_1203-4_0_6_node_139 | 0.4 | n |  | TRUE
138 | bus_LV_1203-4_0_6_node_140 | 0.4 | n |  | TRUE
139 | bus_MV_11_0_node_170 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1203-4_0_6_load_0 | 0 | 0.00096 | 0.0002406 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1203-4_0_6_load_1 | 1 | 0.00039347 | 9.8613e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1203-4_0_6_load_3 | 3 | 0.00017365 | 4.352e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1203-4_0_6_load_5 | 5 | 0.00030077 | 7.5381e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1203-4_0_6_load_95 | 7 | 0.00092999 | 0.00023308 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1203-4_0_6_load_106 | 9 | 0.00020709 | 5.1902e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1203-4_0_6_load_105 | 10 | 0.00028 | 7.0174e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1203-4_0_6_load_108 | 11 | 0.00020039 | 5.0223e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1203-4_0_6_load_76 | 15 | 0.0016067 | 0.00040269 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1203-4_0_6_load_77 | 16 | 0.0016961 | 0.00042508 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1203-4_0_6_load_44 | 17 | 0.0012676 | 0.00031769 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1203-4_0_6_load_6 | 18 | 0.0093886 | 0.002353 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1203-4_0_6_load_20 | 19 | 0.0012054 | 0.0003021 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1203-4_0_6_load_21 | 20 | 0.00087267 | 0.00021871 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1203-4_0_6_load_90 | 23 | 0.037971 | 0.0095163 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1203-4_0_6_load_9 | 24 | 0.0078337 | 0.0019633 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1203-4_0_6_load_10 | 25 | 0.0035574 | 0.00089156 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1203-4_0_6_load_13 | 28 | 0.008201 | 0.0020554 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1203-4_0_6_load_14 | 29 | 0.0049367 | 0.0012373 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1203-4_0_6_load_64 | 31 | 0.0044396 | 0.0011127 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1203-4_0_6_load_30 | 32 | 0.0037284 | 0.00093442 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1203-4_0_6_load_33 | 33 | 0.0059793 | 0.0014985 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1203-4_0_6_load_41 | 35 | 0.0034854 | 0.00087353 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1203-4_0_6_load_65 | 36 | 0.0052346 | 0.0013119 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1203-4_0_6_load_31 | 37 | 0.00060424 | 0.00015144 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1203-4_0_6_load_32 | 38 | 0.004636 | 0.0011619 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1203-4_0_6_load_15 | 39 | 0.0048476 | 0.0012149 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1203-4_0_6_load_16 | 40 | 0.0048677 | 0.00122 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1203-4_0_6_load_17 | 41 | 0.003679 | 0.00092206 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1203-4_0_6_load_18 | 42 | 0.0041929 | 0.0010508 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1203-4_0_6_load_74 | 44 | 0.0026513 | 0.00066449 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1203-4_0_6_load_37 | 45 | 0.0059198 | 0.0014837 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1203-4_0_6_load_75 | 46 | 0.0090929 | 0.0022789 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1203-4_0_6_load_38 | 47 | 0.0026937 | 0.0006751 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1203-4_0_6_load_24 | 50 | 0.0075601 | 0.0018947 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1203-4_0_6_load_55 | 51 | 0.018956 | 0.0047507 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1203-4_0_6_load_51 | 52 | 0.053503 | 0.013409 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1203-4_0_6_load_103 | 53 | 0.0058722 | 0.0014717 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1203-4_0_6_load_98 | 54 | 0.00049089 | 0.00012303 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1203-4_0_6_load_102 | 55 | 0.00051026 | 0.00012788 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1203-4_0_6_load_25 | 56 | 0.004522 | 0.0011333 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1203-4_0_6_load_26 | 57 | 0.0055739 | 0.001397 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1203-4_0_6_load_27 | 58 | 0.0059105 | 0.0014813 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1203-4_0_6_load_28 | 59 | 0.0047986 | 0.0012026 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1203-4_0_6_load_29 | 60 | 0.0029196 | 0.00073173 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1203-4_0_6_load_56 | 61 | 0.0060633 | 0.0015196 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1203-4_0_6_load_70 | 62 | 0.0021392 | 0.00053613 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1203-4_0_6_load_35 | 63 | 0.0053803 | 0.0013484 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1203-4_0_6_load_58 | 65 | 0.003261 | 0.00081729 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1203-4_0_6_load_49 | 66 | 0.00088878 | 0.00022275 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1203-4_0_6_load_36 | 68 | 0.0065028 | 0.0016297 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1203-4_0_6_load_39 | 69 | 0.004473 | 0.0011211 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1203-4_0_6_load_40 | 70 | 0.0033267 | 0.00083374 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1203-4_0_6_load_42 | 71 | 0.011567 | 0.002899 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1203-4_0_6_load_83 | 72 | 0.0031696 | 0.00079438 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1203-4_0_6_load_81 | 73 | 0.0020465 | 0.0005129 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1203-4_0_6_load_50 | 75 | 0.0014283 | 0.00035797 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1203-4_0_6_load_84 | 76 | 0.0034647 | 0.00086833 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1203-4_0_6_load_47 | 78 | 0.0011174 | 0.00028005 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1203-4_0_6_load_142 | 80 | 0.0012751 | 0.00031958 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1203-4_0_6_load_89 | 82 | 0.0012167 | 0.00030494 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1203-4_0_6_load_87 | 83 | 0.00080387 | 0.00020147 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1203-4_0_6_load_92 | 84 | 0.0008657 | 0.00021697 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1203-4_0_6_load_94 | 86 | 0.0005481 | 0.00013737 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1203-4_0_6_load_104 | 87 | 0.00083967 | 0.00021044 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1203-4_0_6_load_54 | 90 | 0.012578 | 0.0031525 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1203-4_0_6_load_85 | 92 | 0.0067748 | 0.0016979 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1203-4_0_6_load_69 | 93 | 0.011448 | 0.002869 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1203-4_0_6_load_59 | 95 | 0.030475 | 0.0076378 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1203-4_0_6_load_86 | 96 | 0.013027 | 0.0032649 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1203-4_0_6_load_67 | 97 | 0.045812 | 0.011482 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1203-4_0_6_load_72 | 98 | 0.0025213 | 0.00063189 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1203-4_0_6_load_71 | 99 | 0.0010993 | 0.00027552 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1203-4_0_6_load_60 | 100 | 0.010621 | 0.0026618 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1203-4_0_6_load_62 | 101 | 0.012355 | 0.0030965 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1203-4_0_6_load_66 | 102 | 0.0042591 | 0.0010674 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1203-4_0_6_load_73 | 103 | 0.0064618 | 0.0016195 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1203-4_0_6_load_111 | 106 | 0.00042806 | 0.00010728 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1203-4_0_6_load_112 | 107 | 0.00016526 | 4.1419e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1203-4_0_6_load_131 | 108 | 0.00083069 | 0.00020819 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1203-4_0_6_load_130 | 109 | 0.00027313 | 6.8452e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1203-4_0_6_load_79 | 110 | 0.0033827 | 0.00084778 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1203-4_0_6_load_135 | 111 | 0.00097978 | 0.00024556 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1203-4_0_6_load_134 | 112 | 0.00051807 | 0.00012984 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1203-4_0_6_load_132 | 113 | 0.00016845 | 4.2217e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1203-4_0_6_load_133 | 114 | 0.00036631 | 9.1806e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1203-4_0_6_load_99 | 115 | 0.0013513 | 0.00033867 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1203-4_0_6_load_100 | 116 | 0.0023558 | 0.00059043 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1203-4_0_6_load_101 | 117 | 0.00088 | 0.00022055 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1203-4_0_6_load_141 | 119 | 0.00063763 | 0.0001598 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1203-4_0_6_load_113 | 120 | 0.00015662 | 3.9252e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1203-4_0_6_load_115 | 121 | 0.00026417 | 6.6208e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1203-4_0_6_load_125 | 122 | 0.00019983 | 5.0082e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1203-4_0_6_load_127 | 125 | 0.00035399 | 8.8717e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1203-4_0_6_load_124 | 126 | 0.00023633 | 5.923e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1203-4_0_6_load_116 | 127 | 0.00039692 | 9.9477e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1203-4_0_6_load_117 | 128 | 0.00025638 | 6.4256e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1203-4_0_6_load_118 | 129 | 0.00070478 | 0.00017663 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1203-4_0_6_load_122 | 131 | 0.00039661 | 9.9399e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1203-4_0_6_load_123 | 132 | 0.00037566 | 9.415e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1203-4_0_6_load_138 | 133 | 0.00064608 | 0.00016192 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1203-4_0_6_load_128 | 134 | 0.00029897 | 7.4928e-05 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1203-4_0_6_load_136 | 135 | 0.0005169 | 0.00012955 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1203-4_0_6_load_137 | 136 | 0.0003194 | 8.0048e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1203-4_0_6_load_140 | 138 | 0.00054915 | 0.00013763 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1203-4_0_6_line_0 |  | 0 | 1 | 0.0042266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1203-4_0_6_line_1 |  | 0 | 2 | 0.022974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1203-4_0_6_line_2 |  | 1 | 3 | 0.00085821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1203-4_0_6_line_3 |  | 2 | 4 | 0.045274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1203-4_0_6_line_4 |  | 2 | 5 | 0.081024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1203-4_0_6_line_5 |  | 3 | 9 | 0.088028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1203-4_0_6_line_6 |  | 4 | 10 | 0.051089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1203-4_0_6_line_7 |  | 5 | 11 | 0.01045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1203-4_0_6_line_8 |  | 6 | 7 | 0.037189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1203-4_0_6_line_9 |  | 6 | 8 | 0.018562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1203-4_0_6_line_10 |  | 7 | 13 | 0.050632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1203-4_0_6_line_11 |  | 8 | 110 | 0.041802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1203-4_0_6_line_12 |  | 9 | 12 | 0.02364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1203-4_0_6_line_13 |  | 10 | 13 | 0.13457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1203-4_0_6_line_14 |  | 11 | 14 | 0.031964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1203-4_0_6_line_15 |  | 12 | 104 | 0.11266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1203-4_0_6_line_16 |  | 14 | 105 | 0.07443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1203-4_0_6_line_17 |  | 14 | 106 | 0.034858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1203-4_0_6_line_18 |  | 15 | 16 | 0.029466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1203-4_0_6_line_19 |  | 15 | 17 | 0.11026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1203-4_0_6_line_20 |  | 16 | 78 | 0.094597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1203-4_0_6_line_21 |  | 17 | 74 | 0.029581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1203-4_0_6_line_22 |  | 18 | 19 | 0.1148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1203-4_0_6_line_23 |  | 19 | 20 | 0.0049897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1203-4_0_6_line_24 |  | 20 | 21 | 0.10363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1203-4_0_6_line_25 |  | 21 | 22 | 0.026039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1203-4_0_6_line_26 |  | 22 | 23 | 0.029424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1203-4_0_6_line_27 |  | 23 | 94 | 0.023502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1203-4_0_6_line_28 |  | 24 | 25 | 0.035043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1203-4_0_6_line_29 |  | 24 | 26 | 0.04766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1203-4_0_6_line_30 |  | 25 | 27 | 0.0004702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1203-4_0_6_line_31 |  | 26 | 28 | 0.049143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1203-4_0_6_line_32 |  | 26 | 29 | 0.023135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_1203-4_0_6_line_33 |  | 27 | 30 | 0.049762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1203-4_0_6_line_34 |  | 27 | 31 | 0.026304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1203-4_0_6_line_35 |  | 28 | 32 | 0.0641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1203-4_0_6_line_36 |  | 29 | 33 | 0.027065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_1203-4_0_6_line_37 |  | 30 | 34 | 0.038516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1203-4_0_6_line_38 |  | 30 | 35 | 0.023709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1203-4_0_6_line_39 |  | 31 | 36 | 0.0031868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1203-4_0_6_line_40 |  | 32 | 37 | 0.061163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1203-4_0_6_line_41 |  | 33 | 38 | 0.028209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_1203-4_0_6_line_42 |  | 34 | 72 | 0.030676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1203-4_0_6_line_43 |  | 34 | 73 | 0.07348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1203-4_0_6_line_44 |  | 35 | 70 | 0.0099227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1203-4_0_6_line_45 |  | 36 | 102 | 0.031681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1203-4_0_6_line_46 |  | 37 | 64 | 0.062983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1203-4_0_6_line_47 |  | 38 | 67 | 0.0038692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_1203-4_0_6_line_48 |  | 39 | 40 | 0.010895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_1203-4_0_6_line_49 |  | 39 | 41 | 0.023248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_1203-4_0_6_line_50 |  | 40 | 42 | 0.017549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_1203-4_0_6_line_51 |  | 41 | 43 | 0.045491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_1203-4_0_6_line_52 |  | 42 | 44 | 0.015651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_1203-4_0_6_line_53 |  | 43 | 45 | 0.064961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_1203-4_0_6_line_54 |  | 44 | 46 | 0.006779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_1203-4_0_6_line_55 |  | 45 | 47 | 0.004994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_1203-4_0_6_line_56 |  | 46 | 94 | 0.013233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_1203-4_0_6_line_57 |  | 47 | 69 | 0.013795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_1203-4_0_6_line_58 |  | 48 | 49 | 0.033016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_1203-4_0_6_line_59 |  | 48 | 50 | 0.052135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_1203-4_0_6_line_60 |  | 49 | 51 | 0.025341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_1203-4_0_6_line_61 |  | 49 | 52 | 0.011256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1203-4_0_6_line_62 |  | 50 | 53 | 0.054576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_1203-4_0_6_line_63 |  | 51 | 54 | 0.011635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_1203-4_0_6_line_64 |  | 53 | 55 | 0.11976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_1203-4_0_6_line_65 |  | 54 | 97 | 0.027687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_1203-4_0_6_line_66 |  | 55 | 117 | 0.025027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_1203-4_0_6_line_67 |  | 56 | 57 | 0.021824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1203-4_0_6_line_68 |  | 56 | 58 | 0.0034382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1203-4_0_6_line_69 |  | 57 | 59 | 0.017803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1203-4_0_6_line_70 |  | 58 | 60 | 0.019692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1203-4_0_6_line_71 |  | 59 | 61 | 0.024955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1203-4_0_6_line_72 |  | 60 | 62 | 0.026869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1203-4_0_6_line_73 |  | 61 | 63 | 0.010436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1203-4_0_6_line_74 |  | 63 | 67 | 0.024153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1203-4_0_6_line_75 |  | 64 | 65 | 0.036036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1203-4_0_6_line_76 |  | 64 | 66 | 0.0056221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1203-4_0_6_line_77 |  | 65 | 98 | 0.0099694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1203-4_0_6_line_78 |  | 66 | 74 | 0.027701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1203-4_0_6_line_79 |  | 67 | 68 | 0.019856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_1203-4_0_6_line_80 |  | 68 | 69 | 0.0063181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_1203-4_0_6_line_81 |  | 70 | 71 | 0.0084605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1203-4_0_6_line_82 |  | 73 | 110 | 0.071873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1203-4_0_6_line_83 |  | 74 | 75 | 0.083239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1203-4_0_6_line_84 |  | 75 | 76 | 0.011372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1203-4_0_6_line_85 |  | 77 | 78 | 0.033222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1203-4_0_6_line_86 |  | 77 | 79 | 0.023889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1203-4_0_6_line_87 |  | 79 | 80 | 0.021696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1203-4_0_6_line_88 |  | 81 | 82 | 0.10577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1203-4_0_6_line_89 |  | 81 | 83 | 0.090426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1203-4_0_6_line_90 |  | 82 | 84 | 0.078346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1203-4_0_6_line_91 |  | 83 | 111 | 0.11139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1203-4_0_6_line_92 |  | 84 | 85 | 0.051722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1203-4_0_6_line_93 |  | 85 | 86 | 0.030308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1203-4_0_6_line_94 |  | 86 | 87 | 0.13131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1203-4_0_6_line_95 |  | 88 | 89 | 0.022148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1203-4_0_6_line_96 |  | 88 | 90 | 0.016333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1203-4_0_6_line_97 |  | 89 | 91 | 0.013029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1203-4_0_6_line_98 |  | 89 | 92 | 0.0078313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1203-4_0_6_line_99 |  | 90 | 93 | 0.0031587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1203-4_0_6_line_100 |  | 91 | 94 | 0.00635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_1203-4_0_6_line_101 |  | 91 | 95 | 0.026352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_1203-4_0_6_line_102 |  | 92 | 96 | 0.026729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1203-4_0_6_line_103 |  | 95 | 100 | 0.013631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_1203-4_0_6_line_104 |  | 97 | 101 | 0.013606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_1203-4_0_6_line_105 |  | 98 | 99 | 0.0081571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1203-4_0_6_line_106 |  | 99 | 103 | 0.01192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1203-4_0_6_line_107 |  | 100 | 101 | 0.0026988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_1203-4_0_6_line_108 |  | 104 | 118 | 0.040982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1203-4_0_6_line_109 |  | 104 | 108 | 0.086439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1203-4_0_6_line_110 |  | 105 | 119 | 0.033253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1203-4_0_6_line_111 |  | 106 | 107 | 0.033303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1203-4_0_6_line_112 |  | 108 | 109 | 0.030687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1203-4_0_6_line_113 |  | 109 | 134 | 0.010986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1203-4_0_6_line_114 |  | 111 | 112 | 0.042627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1203-4_0_6_line_115 |  | 112 | 133 | 0.13083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1203-4_0_6_line_116 |  | 112 | 130 | 0.12902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1203-4_0_6_line_117 |  | 113 | 114 | 0.1522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1203-4_0_6_line_118 |  | 114 | 123 | 0.041161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1203-4_0_6_line_119 |  | 115 | 116 | 0.027649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1203-4_0_6_line_120 |  | 115 | 117 | 0.015549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1203-4_0_6_line_121 |  | 118 | 131 | 0.028627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1203-4_0_6_line_122 |  | 118 | 128 | 0.0098605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1203-4_0_6_line_123 |  | 120 | 121 | 0.0086179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1203-4_0_6_line_124 |  | 121 | 122 | 0.087351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1203-4_0_6_line_125 |  | 122 | 125 | 0.019718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1203-4_0_6_line_126 |  | 122 | 126 | 0.0099935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1203-4_0_6_line_127 |  | 123 | 124 | 0.078107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1203-4_0_6_line_128 |  | 124 | 134 | 0.084499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1203-4_0_6_line_129 |  | 124 | 126 | 0.0080266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1203-4_0_6_line_130 |  | 127 | 128 | 0.1217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1203-4_0_6_line_131 |  | 127 | 129 | 0.047244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1203-4_0_6_line_132 |  | 129 | 130 | 0.015312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1203-4_0_6_line_133 |  | 131 | 132 | 0.020284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1203-4_0_6_line_134 |  | 133 | 136 | 0.034717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1203-4_0_6_line_135 |  | 135 | 136 | 0.031508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1203-4_0_6_line_136 |  | 135 | 137 | 0.082032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1203-4_0_6_line_137 |  | 137 | 138 | 0.077491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1203-4_0_6_trafo_11 | 0.63 MVA 20/0.4 kV | 139 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2690308.6082 | 1190227.0817 | 2690308.6835 | 1190222.8558
1 | 2690308.199 | 1190250.0525 | 2690308.6082 | 1190227.0817
2 | 2690308.6987 | 1190221.9978 | 2690308.6835 | 1190222.8558
3 | 2690306.7475 | 1190292.6576 | 2690301.7367 | 1190282.5534 | 2690300.0662 | 1190274.9901 | 2690302.3409 | 1190266.2744 | 2690308.199 | 1190250.0525
4 | 2690308.199 | 1190250.0525 | 2690327.2813 | 1190248.5283 | 2690334.7472 | 1190246.0504 | 2690369.1229 | 1190218.6629 | 2690374.8598 | 1190210.3955
5 | 2690308.6987 | 1190221.9978 | 2690301.64 | 1190207.6044 | 2690273.1732 | 1190194.1888 | 2690264.9431 | 1190169.9715 | 2690253.13 | 1190160.8099
6 | 2690306.7475 | 1190292.6576 | 2690331.0328 | 1190337.6054
7 | 2690374.8598 | 1190210.3955 | 2690379.4455 | 1190203.7871 | 2690380.5575 | 1190201.6527
8 | 2690464.3808 | 1190397.2928 | 2690453.9813 | 1190406.6638 | 2690444.6312 | 1190414.2274 | 2690436.8198 | 1190422.204
9 | 2690474.8963 | 1190412.528 | 2690468.3111 | 1190404.1788 | 2690464.3808 | 1190397.2928
10 | 2690398.1144 | 1190454.2614 | 2690416.3812 | 1190443.0746 | 2690436.8198 | 1190422.204
11 | 2690474.8963 | 1190412.528 | 2690481.1384 | 1190419.3489 | 2690487.104 | 1190423.2749 | 2690499.2665 | 1190425.4157 | 2690509.1483 | 1190423.5417 | 2690511.9056 | 1190422.3411
12 | 2690249.665 | 1190139.2217 | 2690246.6491 | 1190148.0374 | 2690253.13 | 1190160.8099
13 | 2690398.1144 | 1190454.2614 | 2690331.0328 | 1190337.6054
14 | 2690405.4749 | 1190185.6797 | 2690395.0458 | 1190186.9008 | 2690388.657 | 1190189.7617 | 2690383.4513 | 1190196.0982 | 2690380.5575 | 1190201.6527
15 | 2690249.665 | 1190139.2217 | 2690278.7284 | 1190059.0312 | 2690288.0557 | 1190033.2889
16 | 2690405.4749 | 1190185.6797 | 2690401.0461 | 1190169.8694 | 2690402.1248 | 1190157.0331 | 2690411.8239 | 1190133.4646 | 2690414.6389 | 1190123.3229 | 2690415.4473 | 1190114.2405
17 | 2690405.4749 | 1190185.6797 | 2690432.5921 | 1190163.7764
18 | 2690555.8937 | 1190260.6339 | 2690555.3256 | 1190268.4414 | 2690549.3992 | 1190281.5712 | 2690544.7013 | 1190287.0701
19 | 2690644.2128 | 1190334.5618 | 2690544.7013 | 1190287.0701
20 | 2690616.6258 | 1190188.1067 | 2690555.8937 | 1190260.6339
21 | 2690664.3081 | 1190356.2688 | 2690644.2128 | 1190334.5618
22 | 2690945.4555 | 1190524.6816 | 2691040.6156 | 1190460.468
23 | 2690942.3044 | 1190528.5504 | 2690945.4555 | 1190524.6816
24 | 2690916.4848 | 1190620.6614 | 2690920.7831 | 1190582.7136 | 2690927.3885 | 1190576.6323 | 2690941.9693 | 1190565.6468 | 2690945.2659 | 1190557.992 | 2690941.4338 | 1190539.6665 | 2690942.3044 | 1190528.5504
25 | 2690891.6131 | 1190613.279 | 2690910.5212 | 1190619.648 | 2690913.8553 | 1190620.5547 | 2690916.4848 | 1190620.6614
26 | 2690891.6131 | 1190613.279 | 2690872.5258 | 1190604.6504 | 2690865.4915 | 1190599.9192
27 | 2690845.9903 | 1190586.803 | 2690865.4915 | 1190599.9192
28 | 2690724.843 | 1190505.4797 | 2690696.5206 | 1190526.1156
29 | 2690766.4545 | 1190508.4134 | 2690763.4632 | 1190503.4982 | 2690749.3252 | 1190497.3689 | 2690732.555 | 1190499.8607 | 2690724.843 | 1190505.4797
30 | 2690696.1406 | 1190526.3925 | 2690696.5206 | 1190526.1156
31 | 2690766.4545 | 1190508.4134 | 2690766.7369 | 1190492.8188 | 2690764.1263 | 1190474.3675 | 2690763.6344 | 1190459.5395 | 2690763.6538 | 1190459.4675
32 | 2690766.4545 | 1190508.4134 | 2690768.8952 | 1190512.4196 | 2690772.5311 | 1190528.1292 | 2690772.6343 | 1190530.446
33 | 2690696.1406 | 1190526.3925 | 2690686.6882 | 1190522.5802 | 2690670.5387 | 1190511.7954 | 2690655.8089 | 1190497.908
34 | 2690696.1406 | 1190526.3925 | 2690676.211 | 1190543.5597
35 | 2690771.7738 | 1190398.5583 | 2690774.4652 | 1190402.1561 | 2690777.0783 | 1190410.3899 | 2690775.4822 | 1190420.5833 | 2690766.3818 | 1190449.3636 | 2690763.6538 | 1190459.4675
36 | 2690772.6343 | 1190530.446 | 2690773.7313 | 1190555.0867 | 2690773.4981 | 1190557.4756
37 | 2690655.8089 | 1190497.908 | 2690629.3197 | 1190469.878
38 | 2690655.8089 | 1190497.908 | 2690644.7639 | 1190497.5294 | 2690641.741 | 1190499.2291 | 2690638.4011 | 1190507.7899
39 | 2690676.211 | 1190543.5597 | 2690673.7965 | 1190545.6395
40 | 2690771.7738 | 1190398.5583 | 2690740.9322 | 1190357.3304 | 2690732.3435 | 1190352.8751
41 | 2690773.4981 | 1190557.4756 | 2690770.7572 | 1190585.5513
42 | 2690641.7865 | 1190441.86 | 2690633.8635 | 1190458.4061 | 2690629.3197 | 1190469.878
43 | 2690629.3197 | 1190469.878 | 2690594.7621 | 1190445.3282 | 2690577.1128 | 1190419.7338
44 | 2690634.7947 | 1190517.034 | 2690638.4011 | 1190507.7899
45 | 2690673.7965 | 1190545.6395 | 2690649.7931 | 1190566.3157
46 | 2690682.3727 | 1190383.6376 | 2690692.7535 | 1190384.0729 | 2690699.8904 | 1190380.1563 | 2690716.9607 | 1190358.4011 | 2690723.3798 | 1190354.04 | 2690732.3435 | 1190352.8751
47 | 2690770.3813 | 1190589.4022 | 2690770.7572 | 1190585.5513
48 | 2690809.1799 | 1190636.7789 | 2690812.6036 | 1190630.9134 | 2690814.5385 | 1190627.2953
49 | 2690797.4599 | 1190656.857 | 2690809.1799 | 1190636.7789
50 | 2690814.5385 | 1190627.2953 | 2690821.0493 | 1190615.1204 | 2690822.4327 | 1190611.6434
51 | 2690774.5272 | 1190696.1442 | 2690797.4599 | 1190656.857
52 | 2690829.7214 | 1190598.0557 | 2690826.4488 | 1190601.5492 | 2690822.4327 | 1190611.6434
53 | 2690774.5272 | 1190696.1442 | 2690761.0184 | 1190656.1139 | 2690761.1189 | 1190633.4009
54 | 2690829.7214 | 1190598.0557 | 2690834.3559 | 1190593.1083 | 2690834.3559 | 1190593.1083
55 | 2690762.1477 | 1190628.514 | 2690761.1189 | 1190633.4009
56 | 2690845.9903 | 1190586.803 | 2690834.3559 | 1190593.1083
57 | 2690762.1477 | 1190628.514 | 2690764.9894 | 1190615.015
58 | 2690869.3845 | 1190501.6705 | 2690880.2159 | 1190478.4535 | 2690882.0788 | 1190471.2883
59 | 2690882.0788 | 1190471.2883 | 2690885.7886 | 1190457.0133 | 2690885.5279 | 1190428.4912 | 2690885.6169 | 1190419.6289
60 | 2690869.3845 | 1190501.6705 | 2690886.6956 | 1190512.2734 | 2690889.929 | 1190516.1405
61 | 2690869.3845 | 1190501.6705 | 2690862.3952 | 1190510.4942
62 | 2690884.8093 | 1190366.024 | 2690881.387 | 1190392.3164 | 2690885.7664 | 1190404.7575 | 2690885.6169 | 1190419.6289
63 | 2690889.929 | 1190516.1405 | 2690897.3919 | 1190525.0661
64 | 2690881.3862 | 1190250.7819 | 2690873.3241 | 1190270.9057 | 2690874.676 | 1190279.8096 | 2690883.1919 | 1190295.0819 | 2690883.9058 | 1190313.36 | 2690886.7171 | 1190324.0984 | 2690888.1066 | 1190341.0747 | 2690884.9357 | 1190365.0529 | 2690884.8093 | 1190366.024
65 | 2690897.3919 | 1190525.0661 | 2690897.3919 | 1190525.0661 | 2690898.963 | 1190538.6097 | 2690890.734 | 1190550.001
66 | 2690881.3862 | 1190250.7819 | 2690881.3862 | 1190250.7819 | 2690880.8524 | 1190225.7608
67 | 2690710.4604 | 1190570.2332 | 2690697.4045 | 1190587.7207
68 | 2690695.3476 | 1190590.4758 | 2690697.4045 | 1190587.7207
69 | 2690710.4604 | 1190570.2332 | 2690721.111 | 1190555.9675 | 2690721.111 | 1190555.9675
70 | 2690683.5668 | 1190606.2553 | 2690695.3476 | 1190590.4758
71 | 2690721.111 | 1190555.9675 | 2690741.7601 | 1190569.9799
72 | 2690683.5668 | 1190606.2553 | 2690677.0434 | 1190614.9929 | 2690671.5936 | 1190615.7998 | 2690664.1057 | 1190608.5018
73 | 2690750.3959 | 1190575.8401 | 2690741.7601 | 1190569.9799
74 | 2690770.3813 | 1190589.4022 | 2690750.3959 | 1190575.8401
75 | 2690682.3727 | 1190383.6376 | 2690678.9149 | 1190393.3914 | 2690670.9162 | 1190403.8547 | 2690664.5063 | 1190404.5914 | 2690658.871 | 1190402.3493
76 | 2690682.3727 | 1190383.6376 | 2690680.195 | 1190378.4544
77 | 2690658.871 | 1190402.3493 | 2690649.6078 | 1190398.6637
78 | 2690664.3081 | 1190356.2688 | 2690676.1673 | 1190368.8675 | 2690680.195 | 1190378.4544
79 | 2690770.3813 | 1190589.4022 | 2690766.2909 | 1190608.8324
80 | 2690766.2909 | 1190608.8324 | 2690764.9894 | 1190615.015
81 | 2690631.7196 | 1190524.916 | 2690634.7947 | 1190517.034
82 | 2690577.1128 | 1190419.7338 | 2690561.2012 | 1190408.3191 | 2690547.172 | 1190407.5731 | 2690535.0587 | 1190412.2596 | 2690511.9056 | 1190422.3411
83 | 2690664.3081 | 1190356.2688 | 2690669.9543 | 1190347.0485 | 2690673.4829 | 1190333.1264 | 2690678.2684 | 1190315.7767 | 2690683.283 | 1190302.9445 | 2690691.1731 | 1190289.0885 | 2690698.3238 | 1190281.6126
84 | 2690706.184 | 1190273.3949 | 2690698.3238 | 1190281.6126
85 | 2690638.1745 | 1190163.2504 | 2690630.4871 | 1190168.7598 | 2690616.6258 | 1190188.1067
86 | 2690630.6965 | 1190140.8341 | 2690632.1344 | 1190150.6398 | 2690638.1745 | 1190163.2504
87 | 2690610.2307 | 1190133.4641 | 2690630.6965 | 1190140.8341
88 | 2690770.5848 | 1189791.7202 | 2690770.8676 | 1189811.2925 | 2690771.8236 | 1189824.6933 | 2690770.4986 | 1189835.6135 | 2690758.3727 | 1189845.069 | 2690738.7553 | 1189854.1219 | 2690727.0814 | 1189862.4392 | 2690720.9399 | 1189870.8842
89 | 2690770.5848 | 1189791.7202 | 2690763.9041 | 1189789.651 | 2690752.0189 | 1189792.7839 | 2690744.1164 | 1189799.8575 | 2690737.055 | 1189808.8118 | 2690726.3345 | 1189811.0952 | 2690716.5792 | 1189807.0671 | 2690711.2054 | 1189799.7921 | 2690710.0966 | 1189787.4008 | 2690711.9478 | 1189781.5563
90 | 2690706.5368 | 1189945.676 | 2690706.7394 | 1189899.6768 | 2690710.2265 | 1189888.5115 | 2690718.0844 | 1189874.8107 | 2690720.9399 | 1189870.8842
91 | 2690711.9478 | 1189781.5563 | 2690601.1803 | 1189793.2777
92 | 2690706.9895 | 1189997.3872 | 2690706.3863 | 1189979.8224 | 2690706.5368 | 1189945.676
93 | 2690713.743 | 1189968.4822 | 2690712.2692 | 1189987.7166 | 2690706.9895 | 1189997.3872
94 | 2690713.743 | 1189968.4822 | 2690840.6906 | 1190002.0324
95 | 2690841.0778 | 1190545.6912 | 2690842.9468 | 1190567.7558
96 | 2690841.0778 | 1190545.6912 | 2690837.1501 | 1190541.6735 | 2690827.636 | 1190536.7462
97 | 2690844.1454 | 1190580.7267 | 2690842.9468 | 1190567.7558
98 | 2690842.9468 | 1190567.7558 | 2690836.3322 | 1190563.5635
99 | 2690824.8312 | 1190535.2936 | 2690827.636 | 1190536.7462
100 | 2690844.1454 | 1190580.7267 | 2690845.9903 | 1190586.803
101 | 2690844.1454 | 1190580.7267 | 2690862.9247 | 1190569.9715 | 2690866.9414 | 1190567.5104
102 | 2690812.2735 | 1190557.7063 | 2690819.4686 | 1190555.4695 | 2690823.6622 | 1190555.5332 | 2690836.3322 | 1190563.5635
103 | 2690866.9414 | 1190567.5104 | 2690878.5643 | 1190560.3888
104 | 2690880.8655 | 1190558.9788 | 2690886.9349 | 1190555.2599 | 2690890.734 | 1190550.001
105 | 2690642.0286 | 1190395.6482 | 2690649.6078 | 1190398.6637
106 | 2690630.9533 | 1190391.2416 | 2690642.0286 | 1190395.6482
107 | 2690878.5643 | 1190560.3888 | 2690880.8655 | 1190558.9788
108 | 2690307.6895 | 1189997.2955 | 2690288.0557 | 1190033.2889
109 | 2690288.0557 | 1190033.2889 | 2690281.9633 | 1190031.1623 | 2690270.7115 | 1190030.7813 | 2690264.5599 | 1190038.6491 | 2690260.51 | 1190051.7853 | 2690252.2472 | 1190068.1489 | 2690244.4793 | 1190076.4815 | 2690235.6673 | 1190074.6475 | 2690230.543 | 1190071.0347 | 2690230.543 | 1190071.0347
110 | 2690415.4473 | 1190114.2405 | 2690431.3443 | 1190106.509 | 2690443.7225 | 1190096.9454
111 | 2690463.325 | 1190152.866 | 2690447.9506 | 1190155.2908 | 2690438.336 | 1190159.1369 | 2690432.5921 | 1190163.7764
112 | 2690221.5048 | 1190041.7132 | 2690226.5093 | 1190058.8328 | 2690230.543 | 1190071.0347
113 | 2690213.3111 | 1190034.3947 | 2690221.5048 | 1190041.7132 | 2690221.5048 | 1190041.7132
114 | 2690601.1803 | 1189793.2777 | 2690572.2988 | 1189808.1724 | 2690563.9059 | 1189813.8461
115 | 2690563.9059 | 1189813.8461 | 2690472.5831 | 1189720.1559
116 | 2690457.3889 | 1189886.6406 | 2690563.9059 | 1189813.8461
117 | 2690102.9578 | 1189985.3456 | 2690003.7797 | 1190100.7959
118 | 2690127.0048 | 1189963.8072 | 2690120.1316 | 1189965.4048 | 2690112.5657 | 1189968.9376 | 2690113.0129 | 1189975.7041 | 2690113.6166 | 1189980.6942 | 2690111.1035 | 1189985.5038 | 2690105.3447 | 1189986.54 | 2690102.9578 | 1189985.3456
119 | 2690880.5209 | 1190210.215 | 2690880.4239 | 1190205.6719 | 2690877.0338 | 1190190.3552 | 2690877.4312 | 1190182.9484
120 | 2690880.5209 | 1190210.215 | 2690880.8524 | 1190225.7608
121 | 2690307.6895 | 1189997.2955 | 2690302.136 | 1189970.5725 | 2690301.3207 | 1189969.5174
122 | 2690307.6895 | 1189997.2955 | 2690313.7041 | 1189989.4818
123 | 2690173.553 | 1189883.3459 | 2690167.7111 | 1189881.7903 | 2690165.5863 | 1189880.3404
124 | 2690215.4015 | 1189960.02 | 2690173.553 | 1189883.3459
125 | 2690232.9551 | 1189951.0394 | 2690215.4015 | 1189960.02
126 | 2690206.5389 | 1189964.637 | 2690210.0726 | 1189962.7464 | 2690215.4015 | 1189960.02
127 | 2690199.4616 | 1189968.4235 | 2690184.087 | 1189961.7321 | 2690172.0767 | 1189962.5851 | 2690162.6909 | 1189959.842 | 2690152.5331 | 1189953.6629 | 2690136.2969 | 1189961.6346 | 2690127.0048 | 1189963.8072
128 | 2690199.4616 | 1189968.4235 | 2690199.1511 | 1189978.9032 | 2690197.0021 | 1189984.341 | 2690184.9671 | 1189997.9683 | 2690183.4034 | 1190006.5836 | 2690190.2416 | 1190016.415 | 2690211.3376 | 1190032.632 | 2690213.3111 | 1190034.3947
129 | 2690199.4616 | 1189968.4235 | 2690206.5389 | 1189964.637
130 | 2690397.0306 | 1189903.0617 | 2690382.3119 | 1189923.6414 | 2690370.6123 | 1189941.7874 | 2690341.1222 | 1189967.2808 | 2690321.5217 | 1189979.326 | 2690313.7041 | 1189989.4818
131 | 2690442.5799 | 1189890.5322 | 2690419.9813 | 1189896.4707 | 2690397.0306 | 1189903.0617 | 2690397.0306 | 1189903.0617
132 | 2690457.3889 | 1189886.6406 | 2690442.5799 | 1189890.5322
133 | 2690301.3207 | 1189969.5174 | 2690292.1563 | 1189957.6583 | 2690289.7552 | 1189952.9376
134 | 2690472.5831 | 1189720.1559 | 2690463.6058 | 1189705.4751 | 2690461.3818 | 1189688.1083
135 | 2690488.0582 | 1189686.7184 | 2690480.3755 | 1189680.9685 | 2690467.9457 | 1189681.2698 | 2690461.3818 | 1189688.1083 | 2690461.3818 | 1189688.1083
136 | 2690488.0582 | 1189686.7184 | 2690540.855 | 1189623.9354
137 | 2690540.855 | 1189623.9354 | 2690545.1628 | 1189615.9844 | 2690556.6744 | 1189612.8565 | 2690566.9722 | 1189610.2995 | 2690573.4245 | 1189602.2809 | 2690586.5962 | 1189569.1036

## bus_geodata
| x | y | coords
0 | 2690308.6082 | 1190227.0817
1 | 2690308.6835 | 1190222.8558
2 | 2690308.199 | 1190250.0525
3 | 2690308.6987 | 1190221.9978
4 | 2690306.7475 | 1190292.6576
5 | 2690374.8598 | 1190210.3955
6 | 2690464.3808 | 1190397.2928
7 | 2690436.8198 | 1190422.204
8 | 2690474.8963 | 1190412.528
9 | 2690253.13 | 1190160.8099
10 | 2690331.0328 | 1190337.6054
11 | 2690380.5575 | 1190201.6527
12 | 2690249.665 | 1190139.2217
13 | 2690398.1144 | 1190454.2614
14 | 2690405.4749 | 1190185.6797
15 | 2690544.7013 | 1190287.0701
16 | 2690555.8937 | 1190260.6339
17 | 2690644.2128 | 1190334.5618
18 | 2691040.6156 | 1190460.468
19 | 2690945.4555 | 1190524.6816
20 | 2690942.3044 | 1190528.5504
21 | 2690916.4848 | 1190620.6614
22 | 2690891.6131 | 1190613.279
23 | 2690865.4915 | 1190599.9192
24 | 2690724.843 | 1190505.4797
25 | 2690696.5206 | 1190526.1156
26 | 2690766.4545 | 1190508.4134
27 | 2690696.1406 | 1190526.3925
28 | 2690763.6538 | 1190459.4675
29 | 2690772.6343 | 1190530.446
30 | 2690655.8089 | 1190497.908
31 | 2690676.211 | 1190543.5597
32 | 2690771.7738 | 1190398.5583
33 | 2690773.4981 | 1190557.4756
34 | 2690629.3197 | 1190469.878
35 | 2690638.4011 | 1190507.7899
36 | 2690673.7965 | 1190545.6395
37 | 2690732.3435 | 1190352.8751
38 | 2690770.7572 | 1190585.5513
39 | 2690809.1799 | 1190636.7789
40 | 2690814.5385 | 1190627.2953
41 | 2690797.4599 | 1190656.857
42 | 2690822.4327 | 1190611.6434
43 | 2690774.5272 | 1190696.1442
44 | 2690829.7214 | 1190598.0557
45 | 2690761.1189 | 1190633.4009
46 | 2690834.3559 | 1190593.1083
47 | 2690762.1477 | 1190628.514
48 | 2690882.0788 | 1190471.2883
49 | 2690869.3845 | 1190501.6705
50 | 2690885.6169 | 1190419.6289
51 | 2690889.929 | 1190516.1405
52 | 2690862.3952 | 1190510.4942
53 | 2690884.8093 | 1190366.024
54 | 2690897.3919 | 1190525.0661
55 | 2690881.3862 | 1190250.7819
56 | 2690697.4045 | 1190587.7207
57 | 2690710.4604 | 1190570.2332
58 | 2690695.3476 | 1190590.4758
59 | 2690721.111 | 1190555.9675
60 | 2690683.5668 | 1190606.2553
61 | 2690741.7601 | 1190569.9799
62 | 2690664.1057 | 1190608.5018
63 | 2690750.3959 | 1190575.8401
64 | 2690682.3727 | 1190383.6376
65 | 2690658.871 | 1190402.3493
66 | 2690680.195 | 1190378.4544
67 | 2690770.3813 | 1190589.4022
68 | 2690766.2909 | 1190608.8324
69 | 2690764.9894 | 1190615.015
70 | 2690634.7947 | 1190517.034
71 | 2690631.7196 | 1190524.916
72 | 2690641.7865 | 1190441.86
73 | 2690577.1128 | 1190419.7338
74 | 2690664.3081 | 1190356.2688
75 | 2690698.3238 | 1190281.6126
76 | 2690706.184 | 1190273.3949
77 | 2690638.1745 | 1190163.2504
78 | 2690616.6258 | 1190188.1067
79 | 2690630.6965 | 1190140.8341
80 | 2690610.2307 | 1190133.4641
81 | 2690770.5848 | 1189791.7202
82 | 2690720.9399 | 1189870.8842
83 | 2690711.9478 | 1189781.5563
84 | 2690706.5368 | 1189945.676
85 | 2690706.9895 | 1189997.3872
86 | 2690713.743 | 1189968.4822
87 | 2690840.6906 | 1190002.0324
88 | 2690841.0778 | 1190545.6912
89 | 2690842.9468 | 1190567.7558
90 | 2690827.636 | 1190536.7462
91 | 2690844.1454 | 1190580.7267
92 | 2690836.3322 | 1190563.5635
93 | 2690824.8312 | 1190535.2936
94 | 2690845.9903 | 1190586.803
95 | 2690866.9414 | 1190567.5104
96 | 2690812.2735 | 1190557.7063
97 | 2690890.734 | 1190550.001
98 | 2690649.6078 | 1190398.6637
99 | 2690642.0286 | 1190395.6482
100 | 2690878.5643 | 1190560.3888
101 | 2690880.8655 | 1190558.9788
102 | 2690649.7931 | 1190566.3157
103 | 2690630.9533 | 1190391.2416
104 | 2690288.0557 | 1190033.2889
105 | 2690415.4473 | 1190114.2405
106 | 2690432.5921 | 1190163.7764
107 | 2690463.325 | 1190152.866
108 | 2690230.543 | 1190071.0347
109 | 2690221.5048 | 1190041.7132
110 | 2690511.9056 | 1190422.3411
111 | 2690601.1803 | 1189793.2777
112 | 2690563.9059 | 1189813.8461
113 | 2690003.7797 | 1190100.7959
114 | 2690102.9578 | 1189985.3456
115 | 2690880.5209 | 1190210.215
116 | 2690877.4312 | 1190182.9484
117 | 2690880.8524 | 1190225.7608
118 | 2690307.6895 | 1189997.2955
119 | 2690443.7225 | 1190096.9454
120 | 2690165.5863 | 1189880.3404
121 | 2690173.553 | 1189883.3459
122 | 2690215.4015 | 1189960.02
123 | 2690127.0048 | 1189963.8072
124 | 2690199.4616 | 1189968.4235
125 | 2690232.9551 | 1189951.0394
126 | 2690206.5389 | 1189964.637
127 | 2690397.0306 | 1189903.0617
128 | 2690313.7041 | 1189989.4818
129 | 2690442.5799 | 1189890.5322
130 | 2690457.3889 | 1189886.6406
131 | 2690301.3207 | 1189969.5174
132 | 2690289.7552 | 1189952.9376
133 | 2690472.5831 | 1189720.1559
134 | 2690213.3111 | 1190034.3947
135 | 2690488.0582 | 1189686.7184
136 | 2690461.3818 | 1189688.1083
137 | 2690540.855 | 1189623.9354
138 | 2690586.5962 | 1189569.1036
139 | 2690770.3813 | 1190589.4022

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98267 | -0.33458 | 0.00096 | 0.0002406
1 | 0.98262 | -0.33564 | 0.00039347 | 9.8613e-05
2 | 0.98299 | -0.32841 | 0 | 0
3 | 0.9826 | -0.33585 | 0.00017365 | 4.352e-05
4 | 0.98368 | -0.31484 | 0 | 0
5 | 0.98286 | -0.33095 | 0.00030077 | 7.5381e-05
6 | 0.98796 | -0.23149 | 0 | 0
7 | 0.98735 | -0.24336 | 0.00092999 | 0.00023308
8 | 0.98827 | -0.22558 | 0 | 0
9 | 0.98152 | -0.35711 | 0.00020709 | 5.1902e-05
10 | 0.98446 | -0.29954 | 0.00028 | 7.0174e-05
11 | 0.98284 | -0.33122 | 0.00020039 | 5.0223e-05
12 | 0.98123 | -0.36273 | 0 | 0
13 | 0.98656 | -0.25869 | 0 | 0
14 | 0.98281 | -0.33194 | 0 | 0
15 | 0.99237 | -0.14691 | 0.0016067 | 0.00040269
16 | 0.99226 | -0.14905 | 0.0016961 | 0.00042508
17 | 0.99294 | -0.13579 | 0.0012676 | 0.00031769
18 | 0.97129 | -0.55276 | 0.0093886 | 0.002353
19 | 0.9723 | -0.53287 | 0.0012054 | 0.0003021
20 | 0.97235 | -0.53189 | 0.00087267 | 0.00021871
21 | 0.97346 | -0.51 | 0 | 0
22 | 0.97373 | -0.50451 | 0 | 0
23 | 0.97405 | -0.4983 | 0.037971 | 0.0095163
24 | 0.99694 | -0.058468 | 0.0078337 | 0.0019633
25 | 0.99494 | -0.096852 | 0.0035574 | 0.00089156
26 | 1 | 0 | -0.50548 | -0.12982
27 | 0.99491 | -0.097339 | 0 | 0
28 | 0.99827 | -0.03316 | 0.008201 | 0.0020554
29 | 0.99792 | -0.038983 | 0.0049367 | 0.0012373
30 | 0.99287 | -0.13671 | 0 | 0
31 | 0.99458 | -0.1038 | 0.0044396 | 0.0011127
32 | 0.99649 | -0.067351 | 0.0037284 | 0.00093442
33 | 0.99552 | -0.084206 | 0.0059793 | 0.0014985
34 | 0.99193 | -0.15475 | 0 | 0
35 | 0.99247 | -0.14442 | 0.0034854 | 0.00087353
36 | 0.99455 | -0.10433 | 0.0052346 | 0.0013119
37 | 0.995 | -0.096072 | 0.00060424 | 0.00015144
38 | 0.99306 | -0.13083 | 0.004636 | 0.0011619
39 | 0.97955 | -0.39047 | 0.0048476 | 0.0012149
40 | 0.97878 | -0.40557 | 0.0048677 | 0.00122
41 | 0.98123 | -0.35783 | 0.003679 | 0.00092206
42 | 0.97755 | -0.42955 | 0.0041929 | 0.0010508
43 | 0.98455 | -0.29352 | 0 | 0
44 | 0.97647 | -0.45068 | 0.0026513 | 0.00066449
45 | 0.9893 | -0.20244 | 0.0059198 | 0.0014837
46 | 0.97601 | -0.45977 | 0.0090929 | 0.0022789
47 | 0.98967 | -0.19534 | 0.0026937 | 0.0006751
48 | 0.97116 | -0.55523 | 0 | 0
49 | 0.97131 | -0.5524 | 0 | 0
50 | 0.97094 | -0.5597 | 0.0075601 | 0.0018947
51 | 0.97173 | -0.54397 | 0.018956 | 0.0047507
52 | 0.97074 | -0.56353 | 0.053503 | 0.013409
53 | 0.9708 | -0.56248 | 0.0058722 | 0.0014717
54 | 0.97198 | -0.53908 | 0.00049089 | 0.00012303
55 | 0.97066 | -0.56531 | 0.00051026 | 0.00012788
56 | 0.99036 | -0.18313 | 0.004522 | 0.0011333
57 | 0.99067 | -0.17713 | 0.0055739 | 0.001397
58 | 0.99032 | -0.1838 | 0.0059105 | 0.0014813
59 | 0.99101 | -0.17047 | 0.0047986 | 0.0012026
60 | 0.99023 | -0.18557 | 0.0029196 | 0.00073173
61 | 0.9916 | -0.15902 | 0.0060633 | 0.0015196
62 | 0.99018 | -0.1866 | 0.0021392 | 0.00053613
63 | 0.99191 | -0.15311 | 0.0053803 | 0.0013484
64 | 0.9935 | -0.12506 | 0 | 0
65 | 0.99306 | -0.13356 | 0.003261 | 0.00081729
66 | 0.99343 | -0.12633 | 0.00088878 | 0.00022275
67 | 0.99273 | -0.13716 | 0 | 0
68 | 0.99119 | -0.16644 | 0.0065028 | 0.0016297
69 | 0.99071 | -0.1756 | 0.004473 | 0.0011211
70 | 0.99233 | -0.14703 | 0.0033267 | 0.00083374
71 | 0.99225 | -0.14877 | 0.011567 | 0.002899
72 | 0.99184 | -0.15647 | 0.0031696 | 0.00079438
73 | 0.99036 | -0.18511 | 0.0020465 | 0.0005129
74 | 0.99313 | -0.13214 | 0 | 0
75 | 0.99276 | -0.13934 | 0.0014283 | 0.00035797
76 | 0.99272 | -0.14004 | 0.0034647 | 0.00086833
77 | 0.99201 | -0.15381 | 0 | 0
78 | 0.99205 | -0.15306 | 0.0011174 | 0.00028005
79 | 0.99199 | -0.15435 | 0 | 0
80 | 0.99196 | -0.15484 | 0.0012751 | 0.00031958
81 | 0.97604 | -0.46506 | 0 | 0
82 | 0.9757 | -0.4718 | 0.0012167 | 0.00030494
83 | 0.97633 | -0.4593 | 0.00080387 | 0.00020147
84 | 0.97554 | -0.47504 | 0.0008657 | 0.00021697
85 | 0.97547 | -0.47636 | 0 | 0
86 | 0.97543 | -0.47714 | 0.0005481 | 0.00013737
87 | 0.97533 | -0.47916 | 0.00083967 | 0.00021044
88 | 0.97376 | -0.50407 | 0 | 0
89 | 0.97425 | -0.49429 | 0 | 0
90 | 0.97339 | -0.51128 | 0.012578 | 0.0031525
91 | 0.97478 | -0.48381 | 0 | 0
92 | 0.97411 | -0.49714 | 0.0067748 | 0.0016979
93 | 0.97336 | -0.51195 | 0.011448 | 0.002869
94 | 0.97513 | -0.47698 | 0 | 0
95 | 0.97361 | -0.50689 | 0.030475 | 0.0076378
96 | 0.97378 | -0.50354 | 0.013027 | 0.0032649
97 | 0.97257 | -0.5274 | 0.045812 | 0.011482
98 | 0.99297 | -0.13534 | 0.0025213 | 0.00063189
99 | 0.99291 | -0.13643 | 0.0010993 | 0.00027552
100 | 0.9731 | -0.51694 | 0.010621 | 0.0026618
101 | 0.97301 | -0.5188 | 0.012355 | 0.0030965
102 | 0.99443 | -0.10671 | 0.0042591 | 0.0010674
103 | 0.99284 | -0.13779 | 0.0064618 | 0.0016195
104 | 0.97987 | -0.38959 | 0 | 0
105 | 0.98276 | -0.3328 | 0 | 0
106 | 0.98279 | -0.33231 | 0.00042806 | 0.00010728
107 | 0.98278 | -0.33241 | 0.00016526 | 4.1419e-05
108 | 0.97962 | -0.39456 | 0.00083069 | 0.00020819
109 | 0.97955 | -0.39586 | 0.00027313 | 6.8452e-05
110 | 0.98895 | -0.21227 | 0.0033827 | 0.00084778
111 | 0.97677 | -0.45056 | 0.00097978 | 0.00024556
112 | 0.97698 | -0.44645 | 0.00051807 | 0.00012984
113 | 0.97931 | -0.40062 | 0.00016845 | 4.2217e-05
114 | 0.97933 | -0.40015 | 0.00036631 | 9.1806e-05
115 | 0.97055 | -0.56744 | 0.0013513 | 0.00033867
116 | 0.97049 | -0.56864 | 0.0023558 | 0.00059043
117 | 0.9706 | -0.56637 | 0.00088 | 0.00022055
118 | 0.97949 | -0.39702 | 0 | 0
119 | 0.98274 | -0.33318 | 0.00063763 | 0.0001598
120 | 0.97934 | -0.40003 | 0.00015662 | 3.9252e-05
121 | 0.97934 | -0.4 | 0.00026417 | 6.6208e-05
122 | 0.97938 | -0.39933 | 0.00019983 | 5.0082e-05
123 | 0.97935 | -0.39975 | 0 | 0
124 | 0.97939 | -0.39898 | 0 | 0
125 | 0.97937 | -0.39946 | 0.00035399 | 8.8717e-05
126 | 0.97938 | -0.39915 | 0.00023633 | 5.923e-05
127 | 0.9784 | -0.41847 | 0.00039692 | 9.9477e-05
128 | 0.97941 | -0.39867 | 0.00025638 | 6.4256e-05
129 | 0.97803 | -0.42582 | 0.00070478 | 0.00017663
130 | 0.97792 | -0.42801 | 0 | 0
131 | 0.97947 | -0.39742 | 0.00039661 | 9.9399e-05
132 | 0.97946 | -0.39756 | 0.00037566 | 9.415e-05
133 | 0.97674 | -0.45133 | 0.00064608 | 0.00016192
134 | 0.97953 | -0.39627 | 0.00029897 | 7.4928e-05
135 | 0.97666 | -0.45283 | 0.0005169 | 0.00012955
136 | 0.97669 | -0.45221 | 0.0003194 | 8.0048e-05
137 | 0.97662 | -0.45366 | 0 | 0
138 | 0.97658 | -0.45444 | 0.00054915 | 0.00013763
139 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.013922 | 0.0034861 | -0.013921 | -0.0034857 | 7.0429e-07 | 3.9721e-07 | 0.02108 | 0.02108 | 0.02108 | 0.98267 | -0.33458 | 0.98262 | -0.33564 | 5.7912
1 | -0.014882 | -0.0037267 | 0.014886 | 0.0037292 | 4.3745e-06 | 2.5086e-06 | 0.022534 | 0.022533 | 0.022534 | 0.98267 | -0.33458 | 0.98299 | -0.32841 | 6.1905
2 | 0.013527 | 0.0033871 | -0.013527 | -0.003387 | 1.3504e-07 | 7.5553e-08 | 0.020484 | 0.020484 | 0.020484 | 0.98262 | -0.33564 | 0.9826 | -0.33585 | 5.6275
3 | -0.016618 | -0.0041597 | 0.016629 | 0.004166 | 1.0743e-05 | 6.301e-06 | 0.025155 | 0.025154 | 0.025155 | 0.98299 | -0.32841 | 0.98368 | -0.31484 | 6.9106
4 | 0.0017324 | 0.00043052 | -0.0017322 | -0.00043141 | 2.0879e-07 | -8.9335e-07 | 0.0026212 | 0.0026216 | 0.0026216 | 0.98299 | -0.32841 | 0.98286 | -0.33095 | 0.72021
5 | 0.013354 | 0.0033435 | -0.01334 | -0.003336 | 1.3498e-05 | 7.5249e-06 | 0.020221 | 0.020221 | 0.020221 | 0.9826 | -0.33585 | 0.98152 | -0.35711 | 5.5553
6 | -0.016629 | -0.004166 | 0.016641 | 0.0041731 | 1.2122e-05 | 7.1092e-06 | 0.025154 | 0.025154 | 0.025154 | 0.98368 | -0.31484 | 0.98446 | -0.29954 | 6.9106
7 | 0.0014314 | 0.00035603 | -0.0014314 | -0.00035615 | 1.8389e-08 | -1.2067e-07 | 0.0021662 | 0.0021663 | 0.0021663 | 0.98286 | -0.33095 | 0.98284 | -0.33122 | 0.59512
8 | 0.017907 | 0.0045091 | -0.017897 | -0.0045031 | 1.015e-05 | 6.0202e-06 | 0.026978 | 0.026978 | 0.026978 | 0.98796 | -0.23149 | 0.98735 | -0.24336 | 7.4116
9 | -0.017907 | -0.0045091 | 0.017912 | 0.0045121 | 5.0662e-06 | 3.0046e-06 | 0.026978 | 0.026978 | 0.026978 | 0.98796 | -0.23149 | 0.98827 | -0.22558 | 7.4115
10 | 0.016967 | 0.00427 | -0.016954 | -0.0042627 | 1.2421e-05 | 7.3021e-06 | 0.025577 | 0.025577 | 0.025577 | 0.98735 | -0.24336 | 0.98656 | -0.25869 | 7.0266
11 | -0.017912 | -0.0045121 | 0.017923 | 0.0045189 | 1.1409e-05 | 6.7657e-06 | 0.026978 | 0.026978 | 0.026978 | 0.98827 | -0.22558 | 0.98895 | -0.21227 | 7.4115
12 | 0.013133 | 0.0032841 | -0.01313 | -0.0032821 | 3.5133e-06 | 1.9498e-06 | 0.019907 | 0.019908 | 0.019908 | 0.98152 | -0.35711 | 0.98123 | -0.36273 | 5.4691
13 | -0.016921 | -0.0042433 | 0.016954 | 0.0042627 | 3.3012e-05 | 1.9413e-05 | 0.025577 | 0.025577 | 0.025577 | 0.98446 | -0.29954 | 0.98656 | -0.25869 | 7.0268
14 | 0.001231 | 0.00030593 | -0.001231 | -0.00030631 | 4.16e-08 | -3.7844e-07 | 0.0018629 | 0.001863 | 0.001863 | 0.98284 | -0.33122 | 0.98281 | -0.33194 | 0.51181
15 | 0.01313 | 0.0032821 | -0.013113 | -0.0032728 | 1.6744e-05 | 9.2951e-06 | 0.019908 | 0.019908 | 0.019908 | 0.98123 | -0.36273 | 0.97987 | -0.38959 | 5.4693
16 | 0.00063767 | 0.00015846 | -0.00063764 | -0.00015939 | 2.6e-08 | -9.265e-07 | 0.00096498 | 0.00096531 | 0.00096531 | 0.98281 | -0.33194 | 0.98276 | -0.3328 | 0.2652
17 | 0.00059333 | 0.00014784 | -0.00059332 | -0.00014828 | 1.0544e-08 | -4.3497e-07 | 0.00089803 | 0.00089818 | 0.00089818 | 0.98281 | -0.33194 | 0.98279 | -0.33231 | 0.24675
18 | 0.0040896 | 0.0010227 | -0.0040892 | -0.0010228 | 4.1542e-07 | -1.1479e-07 | 0.0061314 | 0.0061315 | 0.0061315 | 0.99237 | -0.14691 | 0.99226 | -0.14905 | 1.6845
19 | -0.0056963 | -0.0014254 | 0.0056994 | 0.0014259 | 3.0159e-06 | 5.0477e-07 | 0.0085406 | 0.0085401 | 0.0085406 | 0.99237 | -0.14691 | 0.99294 | -0.13579 | 2.3463
20 | 0.0023931 | 0.00059775 | -0.0023927 | -0.00059868 | 4.5675e-07 | -9.2933e-07 | 0.0035881 | 0.0035885 | 0.0035885 | 0.99226 | -0.14905 | 0.99205 | -0.15306 | 0.98585
21 | -0.006967 | -0.0017436 | 0.0069682 | 0.001744 | 1.209e-06 | 3.9105e-07 | 0.01044 | 0.01044 | 0.01044 | 0.99294 | -0.13579 | 0.99313 | -0.13214 | 2.8681
22 | -0.0093886 | -0.002353 | 0.0093976 | 0.0023573 | 8.9059e-06 | 4.2774e-06 | 0.014383 | 0.014383 | 0.014383 | 0.97129 | -0.55276 | 0.9723 | -0.53287 | 3.9515
23 | -0.010603 | -0.0026594 | 0.010603 | 0.0026597 | 4.9274e-07 | 2.5347e-07 | 0.016228 | 0.016228 | 0.016228 | 0.9723 | -0.53287 | 0.97235 | -0.53189 | 4.4581
24 | -0.011476 | -0.0028784 | 0.011488 | 0.0028847 | 1.1987e-05 | 6.3849e-06 | 0.017563 | 0.017563 | 0.017563 | 0.97235 | -0.53189 | 0.97346 | -0.51 | 4.825
25 | -0.011488 | -0.0028847 | 0.011491 | 0.0028864 | 3.0118e-06 | 1.6038e-06 | 0.017563 | 0.017563 | 0.017563 | 0.97346 | -0.51 | 0.97373 | -0.50451 | 4.8249
26 | -0.011491 | -0.0028864 | 0.011495 | 0.0028882 | 3.4034e-06 | 1.812e-06 | 0.017563 | 0.017562 | 0.017563 | 0.97373 | -0.50451 | 0.97405 | -0.4983 | 4.8249
27 | -0.049465 | -0.012404 | 0.049515 | 0.012436 | 5.0328e-05 | 3.1917e-05 | 0.075568 | 0.075568 | 0.075568 | 0.97405 | -0.4983 | 0.97513 | -0.47698 | 20.7606
28 | 0.062693 | 0.015851 | -0.062578 | -0.015778 | 0.00011519 | 7.3264e-05 | 0.093624 | 0.093624 | 0.093624 | 0.99694 | -0.058468 | 0.99494 | -0.096852 | 25.7208
29 | -0.070527 | -0.017815 | 0.070725 | 0.017941 | 0.00019823 | 0.00012624 | 0.10532 | 0.10532 | 0.10532 | 0.99694 | -0.058468 | 1 | 0 | 28.933
30 | 0.05902 | 0.014886 | -0.059019 | -0.014886 | 1.3749e-06 | 8.7383e-07 | 0.088304 | 0.088304 | 0.088304 | 0.99494 | -0.096852 | 0.99491 | -0.097339 | 24.2592
31 | 0.038824 | 0.009799 | -0.038763 | -0.0097603 | 6.1557e-05 | 3.8753e-05 | 0.057795 | 0.057795 | 0.057795 | 1 | 0 | 0.99827 | -0.03316 | 15.8779
32 | 0.39429 | 0.10208 | -0.39354 | -0.1016 | 0.00074955 | 0.0004785 | 0.58787 | 0.58787 | 0.58787 | 1 | 0 | 0.99792 | -0.038983 | 40.3755
33 | 0.045081 | 0.011391 | -0.044996 | -0.011337 | 8.4914e-05 | 5.37e-05 | 0.067457 | 0.067457 | 0.067457 | 0.99491 | -0.097339 | 0.99287 | -0.13671 | 18.5321
34 | 0.013938 | 0.0034944 | -0.013934 | -0.003492 | 4.2868e-06 | 2.4021e-06 | 0.020847 | 0.020847 | 0.020847 | 0.99491 | -0.097339 | 0.99458 | -0.1038 | 5.7272
35 | 0.030562 | 0.0077049 | -0.030512 | -0.0076738 | 4.9919e-05 | 3.1112e-05 | 0.045571 | 0.045571 | 0.045571 | 0.99827 | -0.03316 | 0.99649 | -0.067351 | 12.5196
36 | 0.3886 | 0.10037 | -0.38774 | -0.099821 | 0.00085507 | 0.00054583 | 0.58051 | 0.58051 | 0.58051 | 0.99792 | -0.038983 | 0.99552 | -0.084206 | 39.87
37 | 0.026607 | 0.0067256 | -0.026584 | -0.0067114 | 2.299e-05 | 1.4216e-05 | 0.039896 | 0.039897 | 0.039897 | 0.99287 | -0.13671 | 0.99193 | -0.15475 | 10.9606
38 | 0.018389 | 0.0046119 | -0.018382 | -0.0046078 | 6.7533e-06 | 4.0156e-06 | 0.027561 | 0.027561 | 0.027561 | 0.99287 | -0.13671 | 0.99247 | -0.14442 | 7.5716
39 | 0.0094944 | 0.0023793 | -0.0094942 | -0.0023792 | 2.4113e-07 | 1.1297e-07 | 0.014205 | 0.014205 | 0.014205 | 0.99458 | -0.1038 | 0.99455 | -0.10433 | 3.9024
40 | 0.026783 | 0.0067394 | -0.026747 | -0.0067167 | 3.6705e-05 | 2.2696e-05 | 0.040004 | 0.040004 | 0.040004 | 0.99649 | -0.067351 | 0.995 | -0.096072 | 10.9902
41 | 0.38177 | 0.098322 | -0.3809 | -0.097771 | 0.00086397 | 0.00055148 | 0.57157 | 0.57157 | 0.57157 | 0.99552 | -0.084206 | 0.99306 | -0.13083 | 39.2562
42 | 0.0031699 | 0.00079415 | -0.0031696 | -0.00079438 | 2.6011e-07 | -2.2947e-07 | 0.0047551 | 0.0047552 | 0.0047552 | 0.99193 | -0.15475 | 0.99184 | -0.15647 | 1.3064
43 | 0.023414 | 0.0059172 | -0.02338 | -0.0058964 | 3.4029e-05 | 2.0831e-05 | 0.035142 | 0.035142 | 0.035142 | 0.99193 | -0.15475 | 0.99036 | -0.18511 | 9.6544
44 | 0.014897 | 0.0037343 | -0.014895 | -0.0037332 | 1.8562e-06 | 1.0598e-06 | 0.022335 | 0.022335 | 0.022335 | 0.99247 | -0.14442 | 0.99233 | -0.14703 | 6.136
45 | 0.0042596 | 0.0010673 | -0.0042591 | -0.0010674 | 4.8252e-07 | -1.0225e-07 | 0.0063729 | 0.0063731 | 0.0063731 | 0.99455 | -0.10433 | 0.99443 | -0.10671 | 1.7508
46 | 0.026142 | 0.0065653 | -0.026106 | -0.006543 | 3.611e-05 | 2.2294e-05 | 0.039101 | 0.039101 | 0.039101 | 0.995 | -0.096072 | 0.9935 | -0.12506 | 10.742
47 | 0.37627 | 0.096609 | -0.37615 | -0.096535 | 0.00011564 | 7.3811e-05 | 0.56462 | 0.56462 | 0.56462 | 0.99306 | -0.13083 | 0.99273 | -0.13716 | 38.7791
48 | 0.30674 | 0.0776 | -0.30652 | -0.077458 | 0.00022201 | 0.00014154 | 0.46623 | 0.46623 | 0.46623 | 0.97955 | -0.39047 | 0.97878 | -0.40557 | 32.0211
49 | -0.31159 | -0.078815 | 0.31208 | 0.079127 | 0.00048885 | 0.00031169 | 0.47359 | 0.47359 | 0.47359 | 0.97955 | -0.39047 | 0.98123 | -0.35783 | 32.5268
50 | 0.30165 | 0.076238 | -0.30131 | -0.076018 | 0.00034635 | 0.00022078 | 0.45883 | 0.45883 | 0.45883 | 0.97878 | -0.40557 | 0.97755 | -0.42955 | 31.5128
51 | -0.31576 | -0.080049 | 0.31674 | 0.080673 | 0.0009792 | 0.00062438 | 0.47917 | 0.47917 | 0.47917 | 0.98123 | -0.35783 | 0.98455 | -0.29352 | 32.91
52 | 0.29711 | 0.074967 | -0.29681 | -0.074775 | 0.00030036 | 0.00019144 | 0.45244 | 0.45244 | 0.45244 | 0.97755 | -0.42955 | 0.97647 | -0.45068 | 31.0745
53 | -0.31674 | -0.080673 | 0.31814 | 0.081565 | 0.0013983 | 0.0008916 | 0.47917 | 0.47917 | 0.47917 | 0.98455 | -0.29352 | 0.9893 | -0.20244 | 32.9099
54 | 0.29416 | 0.074111 | -0.29403 | -0.074029 | 0.00012779 | 8.1443e-05 | 0.4484 | 0.4484 | 0.4484 | 0.97647 | -0.45068 | 0.97601 | -0.45977 | 30.797
55 | -0.32406 | -0.083048 | 0.32417 | 0.083119 | 0.00011153 | 7.1122e-05 | 0.48807 | 0.48807 | 0.48807 | 0.9893 | -0.20244 | 0.98967 | -0.19534 | 33.5214
56 | 0.28494 | 0.071751 | -0.28471 | -0.071601 | 0.00023426 | 0.00014927 | 0.43454 | 0.43454 | 0.43454 | 0.97601 | -0.45977 | 0.97513 | -0.47698 | 29.8449
57 | -0.32686 | -0.083794 | 0.32717 | 0.083994 | 0.00031321 | 0.00019974 | 0.49212 | 0.49212 | 0.49212 | 0.98967 | -0.19534 | 0.99071 | -0.1756 | 33.7995
58 | -0.018536 | -0.0046359 | 0.018539 | 0.0046358 | 2.4961e-06 | -3.6867e-08 | 0.028398 | 0.028397 | 0.028398 | 0.97116 | -0.55523 | 0.97131 | -0.5524 | 1.9504
59 | 0.018536 | 0.0046359 | -0.018532 | -0.0046359 | 3.9417e-06 | -5.7103e-08 | 0.028398 | 0.028399 | 0.028399 | 0.97116 | -0.55523 | 0.97094 | -0.5597 | 1.9505
60 | -0.07207 | -0.018063 | 0.072099 | 0.01808 | 2.896e-05 | 1.7279e-05 | 0.11041 | 0.11041 | 0.11041 | 0.97131 | -0.5524 | 0.97173 | -0.54397 | 7.5831
61 | 0.053531 | 0.013427 | -0.053503 | -0.013409 | 2.8392e-05 | 1.8031e-05 | 0.082012 | 0.082012 | 0.082012 | 0.97131 | -0.5524 | 0.97074 | -0.56353 | 22.5309
62 | 0.010972 | 0.0027412 | -0.010971 | -0.0027429 | 1.4463e-06 | -1.7739e-06 | 0.016812 | 0.016813 | 0.016813 | 0.97094 | -0.5597 | 0.9708 | -0.56248 | 1.1548
63 | -0.091055 | -0.022831 | 0.091076 | 0.022844 | 2.1206e-05 | 1.2995e-05 | 0.13944 | 0.13944 | 0.13944 | 0.97173 | -0.54397 | 0.97198 | -0.53908 | 9.5766
64 | 0.0050986 | 0.0012712 | -0.0050979 | -0.0012767 | 6.855e-07 | -5.4835e-06 | 0.0078127 | 0.0078148 | 0.0078148 | 0.9708 | -0.56248 | 0.97066 | -0.56531 | 0.53673
65 | -0.091567 | -0.022967 | 0.091618 | 0.022998 | 5.1011e-05 | 3.1274e-05 | 0.14019 | 0.14019 | 0.14019 | 0.97198 | -0.53908 | 0.97257 | -0.5274 | 9.6282
66 | 0.0045877 | 0.0011488 | -0.0045874 | -0.0011493 | 2.3209e-07 | -4.7013e-07 | 0.0070326 | 0.0070328 | 0.0070328 | 0.97066 | -0.56531 | 0.9706 | -0.56637 | 0.96604
67 | -0.015492 | -0.0038824 | 0.015497 | 0.003885 | 4.4342e-06 | 2.557e-06 | 0.023277 | 0.023277 | 0.023277 | 0.99036 | -0.18313 | 0.99067 | -0.17713 | 6.3948
68 | 0.01097 | 0.0027491 | -0.01097 | -0.0027489 | 3.5029e-07 | 1.7994e-07 | 0.016483 | 0.016483 | 0.016483 | 0.99036 | -0.18313 | 0.99032 | -0.1838 | 4.5282
69 | -0.021071 | -0.0052819 | 0.021077 | 0.005286 | 6.6873e-06 | 4.0506e-06 | 0.031649 | 0.031649 | 0.031649 | 0.99067 | -0.17713 | 0.99101 | -0.17047 | 8.6948
70 | 0.0050593 | 0.0012676 | -0.0050589 | -0.0012676 | 4.2674e-07 | 1.9765e-08 | 0.0076018 | 0.0076019 | 0.0076019 | 0.99032 | -0.1838 | 0.99023 | -0.18557 | 2.0884
71 | -0.025876 | -0.0064886 | 0.02589 | 0.0064974 | 1.4127e-05 | 8.7197e-06 | 0.038854 | 0.038854 | 0.038854 | 0.99101 | -0.17047 | 0.9916 | -0.15902 | 10.6743
72 | 0.0021393 | 0.00053585 | -0.0021392 | -0.00053613 | 1.0412e-07 | -2.79e-07 | 0.0032146 | 0.0032147 | 0.0032147 | 0.99023 | -0.18557 | 0.99018 | -0.1866 | 0.88316
73 | -0.031953 | -0.008017 | 0.031962 | 0.0080226 | 8.9994e-06 | 5.6249e-06 | 0.047953 | 0.047953 | 0.047953 | 0.9916 | -0.15902 | 0.99191 | -0.15311 | 13.1739
74 | -0.037343 | -0.009371 | 0.037371 | 0.0093889 | 2.8428e-05 | 1.7882e-05 | 0.056024 | 0.056024 | 0.056024 | 0.99191 | -0.15311 | 0.99273 | -0.13716 | 15.3912
75 | 0.013351 | 0.0033479 | -0.013345 | -0.0033449 | 5.4035e-06 | 2.9918e-06 | 0.019996 | 0.019997 | 0.019997 | 0.9935 | -0.12506 | 0.99306 | -0.13356 | 5.4936
76 | 0.012756 | 0.0031951 | -0.012755 | -0.0031947 | 7.6948e-07 | 4.1967e-07 | 0.019104 | 0.019104 | 0.019104 | 0.9935 | -0.12506 | 0.99343 | -0.12633 | 5.2485
77 | 0.010084 | 0.0025276 | -0.010083 | -0.0025271 | 8.5358e-07 | 4.1732e-07 | 0.01511 | 0.01511 | 0.01511 | 0.99306 | -0.13356 | 0.99297 | -0.13534 | 4.1512
78 | 0.011866 | 0.0029719 | -0.011863 | -0.0029702 | 3.2814e-06 | 1.7415e-06 | 0.017773 | 0.017773 | 0.017773 | 0.99343 | -0.12633 | 0.99313 | -0.13214 | 4.8828
79 | 0.33878 | 0.087146 | -0.3383 | -0.086839 | 0.00048152 | 0.00030715 | 0.5086 | 0.5086 | 0.5086 | 0.99273 | -0.13716 | 0.99119 | -0.16644 | 34.9314
80 | 0.33179 | 0.085209 | -0.33165 | -0.085115 | 0.00014739 | 9.4006e-05 | 0.49884 | 0.49884 | 0.49884 | 0.99119 | -0.16644 | 0.99071 | -0.1756 | 34.2609
81 | 0.011568 | 0.0028995 | -0.011567 | -0.002899 | 9.5468e-07 | 5.0171e-07 | 0.017347 | 0.017347 | 0.017347 | 0.99233 | -0.14703 | 0.99225 | -0.14877 | 4.7656
82 | 0.021334 | 0.0053835 | -0.021306 | -0.0053667 | 2.7715e-05 | 1.6814e-05 | 0.032067 | 0.032067 | 0.032067 | 0.99036 | -0.18511 | 0.98895 | -0.21227 | 8.8097
83 | 0.0048948 | 0.0012262 | -0.0048931 | -0.0012262 | 1.6789e-06 | -2.1876e-09 | 0.0073337 | 0.0073341 | 0.0073341 | 0.99313 | -0.13214 | 0.99276 | -0.13934 | 2.0149
84 | 0.0034648 | 0.00086826 | -0.0034647 | -0.00086833 | 1.1501e-07 | -7.3425e-08 | 0.0051932 | 0.0051933 | 0.0051933 | 0.99276 | -0.13934 | 0.99272 | -0.14004 | 1.4267
85 | -0.0012752 | -0.00031903 | 0.0012752 | 0.00031863 | 4.5568e-08 | -3.9977e-07 | 0.0019126 | 0.0019124 | 0.0019126 | 0.99201 | -0.15381 | 0.99205 | -0.15306 | 0.52543
86 | 0.0012752 | 0.00031903 | -0.0012752 | -0.00031931 | 3.2771e-08 | -2.8744e-07 | 0.0019126 | 0.0019127 | 0.0019127 | 0.99201 | -0.15381 | 0.99199 | -0.15435 | 0.52546
87 | 0.0012752 | 0.00031931 | -0.0012751 | -0.00031958 | 2.9766e-08 | -2.6104e-07 | 0.0019127 | 0.0019128 | 0.0019128 | 0.99199 | -0.15435 | 0.99196 | -0.15484 | 0.52549
88 | 0.0034719 | 0.00086583 | -0.0034708 | -0.00086644 | 1.1106e-06 | -6.1062e-07 | 0.0052915 | 0.005292 | 0.005292 | 0.97604 | -0.46506 | 0.9757 | -0.4718 | 1.4538
89 | -0.0034719 | -0.00086583 | 0.0034728 | 0.0008653 | 9.4939e-07 | -5.2288e-07 | 0.0052915 | 0.0052911 | 0.0052915 | 0.97604 | -0.46506 | 0.97633 | -0.4593 | 1.4537
90 | 0.002254 | 0.0005615 | -0.0022537 | -0.00056225 | 3.4697e-07 | -7.5628e-07 | 0.0034364 | 0.0034367 | 0.0034367 | 0.9757 | -0.4718 | 0.97554 | -0.47504 | 0.94415
91 | -0.0042767 | -0.0010668 | 0.0042785 | 0.0010665 | 1.7735e-06 | -2.5857e-07 | 0.0065162 | 0.0065157 | 0.0065162 | 0.97633 | -0.4593 | 0.97677 | -0.45056 | 1.7902
92 | 0.001388 | 0.00034529 | -0.0013879 | -0.00034588 | 8.6871e-08 | -5.9012e-07 | 0.0021162 | 0.0021165 | 0.0021165 | 0.97554 | -0.47504 | 0.97547 | -0.47636 | 0.58144
93 | 0.0013879 | 0.00034588 | -0.0013879 | -0.00034622 | 5.0914e-08 | -3.4575e-07 | 0.0021165 | 0.0021166 | 0.0021166 | 0.97547 | -0.47636 | 0.97543 | -0.47714 | 0.58148
94 | 0.00083975 | 0.00020885 | -0.00083967 | -0.00021044 | 8.077e-08 | -1.5872e-06 | 0.0012805 | 0.0012811 | 0.0012811 | 0.97543 | -0.47714 | 0.97533 | -0.47916 | 0.35194
95 | -0.024035 | -0.0060268 | 0.024046 | 0.0060337 | 1.1204e-05 | 6.895e-06 | 0.036729 | 0.036729 | 0.036729 | 0.97376 | -0.50407 | 0.97425 | -0.49429 | 10.0904
96 | 0.024035 | 0.0060268 | -0.024026 | -0.0060217 | 8.2625e-06 | 5.0849e-06 | 0.036729 | 0.036729 | 0.036729 | 0.97376 | -0.50407 | 0.97339 | -0.51128 | 10.0904
97 | -0.043854 | -0.011 | 0.043876 | 0.011014 | 2.1922e-05 | 1.3868e-05 | 0.066984 | 0.066984 | 0.066984 | 0.97425 | -0.49429 | 0.97478 | -0.48381 | 18.4022
98 | 0.019808 | 0.0049666 | -0.019806 | -0.004965 | 2.6882e-06 | 1.6229e-06 | 0.030255 | 0.030255 | 0.030255 | 0.97425 | -0.49429 | 0.97411 | -0.49714 | 8.3118
99 | 0.011448 | 0.0028692 | -0.011448 | -0.002869 | 3.6277e-07 | 1.9291e-07 | 0.0175 | 0.0175 | 0.0175 | 0.97339 | -0.51128 | 0.97336 | -0.51195 | 4.8078
100 | -0.23511 | -0.059116 | 0.23519 | 0.059165 | 7.6713e-05 | 4.878e-05 | 0.35897 | 0.35897 | 0.35897 | 0.97478 | -0.48381 | 0.97513 | -0.47698 | 24.6548
101 | 0.19124 | 0.048102 | -0.19103 | -0.047968 | 0.00021063 | 0.00013349 | 0.29199 | 0.29199 | 0.29199 | 0.97478 | -0.48381 | 0.97361 | -0.50689 | 20.0543
102 | 0.013031 | 0.0032671 | -0.013027 | -0.0032649 | 3.9718e-06 | 2.2093e-06 | 0.019906 | 0.019906 | 0.019906 | 0.97411 | -0.49714 | 0.97378 | -0.50354 | 5.4687
103 | 0.16055 | 0.040331 | -0.16048 | -0.040282 | 7.6967e-05 | 4.8581e-05 | 0.24541 | 0.24541 | 0.24541 | 0.97361 | -0.50689 | 0.9731 | -0.51694 | 16.8553
104 | -0.13743 | -0.03448 | 0.13749 | 0.034515 | 5.6401e-05 | 3.5421e-05 | 0.21028 | 0.21028 | 0.21028 | 0.97257 | -0.5274 | 0.97301 | -0.5188 | 14.4422
105 | 0.0075619 | 0.0018953 | -0.0075615 | -0.0018951 | 3.9281e-07 | 1.4589e-07 | 0.011332 | 0.011332 | 0.011332 | 0.99297 | -0.13534 | 0.99291 | -0.13643 | 3.1132
106 | 0.0064622 | 0.0016196 | -0.0064618 | -0.0016195 | 4.1923e-07 | 1.1415e-07 | 0.0096845 | 0.0096846 | 0.0096846 | 0.99291 | -0.13643 | 0.99284 | -0.13779 | 2.6606
107 | 0.14985 | 0.03762 | -0.14984 | -0.037612 | 1.3288e-05 | 8.3705e-06 | 0.22917 | 0.22917 | 0.22917 | 0.9731 | -0.51694 | 0.97301 | -0.5188 | 15.7399
108 | 0.0099631 | 0.0024907 | -0.0099596 | -0.002489 | 3.517e-06 | 1.7349e-06 | 0.015128 | 0.015128 | 0.015128 | 0.97987 | -0.38959 | 0.97949 | -0.39702 | 4.156
109 | 0.0031497 | 0.00078208 | -0.0031489 | -0.0007827 | 7.4083e-07 | -6.144e-07 | 0.0047805 | 0.0047809 | 0.0047809 | 0.97987 | -0.38959 | 0.97962 | -0.39456 | 1.3134
110 | 0.00063764 | 0.00015939 | -0.00063763 | -0.0001598 | 1.1622e-08 | -4.139e-07 | 0.00096531 | 0.00096546 | 0.00096546 | 0.98276 | -0.3328 | 0.98274 | -0.33318 | 0.26524
111 | 0.00016526 | 4.0997e-05 | -0.00016526 | -4.1419e-05 | 7.8146e-10 | -4.215e-07 | 0.00025007 | 0.00025022 | 0.00025022 | 0.98279 | -0.33231 | 0.98278 | -0.33241 | 0.068742
112 | 0.0023183 | 0.00057451 | -0.0023181 | -0.0005748 | 1.4252e-07 | -2.9512e-07 | 0.0035191 | 0.0035192 | 0.0035192 | 0.97962 | -0.39456 | 0.97955 | -0.39586 | 0.96681
113 | 0.002045 | 0.00050635 | -0.002045 | -0.00050646 | 3.9702e-08 | -1.1288e-07 | 0.0031043 | 0.0031044 | 0.0031044 | 0.97955 | -0.39586 | 0.97953 | -0.39627 | 0.85285
114 | -0.0052583 | -0.0013121 | 0.0052593 | 0.0013122 | 1.0252e-06 | 1.2243e-07 | 0.0080083 | 0.0080081 | 0.0080083 | 0.97677 | -0.45056 | 0.97698 | -0.44645 | 2.2001
115 | 0.0020321 | 0.00050507 | -0.0020317 | -0.00050641 | 4.6963e-07 | -1.3374e-06 | 0.0030936 | 0.0030942 | 0.0030942 | 0.97698 | -0.44645 | 0.97674 | -0.45133 | 0.85004
116 | -0.0078095 | -0.0019471 | 0.0078163 | 0.0019499 | 6.8402e-06 | 2.7606e-06 | 0.011891 | 0.01189 | 0.011891 | 0.97698 | -0.44645 | 0.97792 | -0.42801 | 3.2667
117 | -0.00016845 | -4.2217e-05 | 0.00016845 | 4.0305e-05 | 3.7291e-09 | -1.9127e-06 | 0.00025595 | 0.00025528 | 0.00025595 | 0.97931 | -0.40062 | 0.97933 | -0.40015 | 0.070316
118 | -0.00053476 | -0.00013211 | 0.00053477 | 0.0001316 | 1.0171e-08 | -5.1142e-07 | 0.00081185 | 0.00081167 | 0.00081185 | 0.97933 | -0.40015 | 0.97935 | -0.39975 | 0.22304
119 | 0.002356 | 0.00059017 | -0.0023558 | -0.00059043 | 1.3528e-07 | -2.5509e-07 | 0.003612 | 0.0036121 | 0.0036121 | 0.97055 | -0.56744 | 0.97049 | -0.56864 | 0.99234
120 | -0.0037073 | -0.00092884 | 0.0037074 | 0.00092877 | 1.8837e-07 | -7.1613e-08 | 0.0056837 | 0.0056837 | 0.0056837 | 0.97055 | -0.56744 | 0.9706 | -0.56637 | 1.5615
121 | 0.00077229 | 0.00019294 | -0.00077227 | -0.0001933 | 1.4773e-08 | -3.5086e-07 | 0.001173 | 0.0011732 | 0.0011732 | 0.97949 | -0.39702 | 0.97947 | -0.39742 | 0.32229
122 | 0.0091873 | 0.0022961 | -0.0091866 | -0.0022957 | 7.2007e-07 | 3.3675e-07 | 0.013955 | 0.013955 | 0.013955 | 0.97949 | -0.39702 | 0.97941 | -0.39867 | 3.8337
123 | -0.00015662 | -3.9252e-05 | 0.00015662 | 3.9144e-05 | 1.8298e-10 | -1.0832e-07 | 0.00023797 | 0.00023793 | 0.00023797 | 0.97934 | -0.40003 | 0.97934 | -0.4 | 0.065376
124 | -0.00042079 | -0.00010535 | 0.00042081 | 0.00010426 | 1.338e-08 | -1.0906e-06 | 0.00063931 | 0.00063892 | 0.00063931 | 0.97934 | -0.4 | 0.97938 | -0.39933 | 0.17564
125 | 0.00035399 | 8.847e-05 | -0.00035399 | -8.8717e-05 | 2.1385e-09 | -2.4675e-07 | 0.00053774 | 0.00053783 | 0.00053783 | 0.97938 | -0.39933 | 0.97937 | -0.39946 | 0.14776
126 | -0.00097462 | -0.00024281 | 0.00097463 | 0.00024269 | 8.2115e-09 | -1.205e-07 | 0.0014803 | 0.0014802 | 0.0014803 | 0.97938 | -0.39933 | 0.97938 | -0.39915 | 0.40667
127 | -0.00053477 | -0.0001316 | 0.00053479 | 0.00013063 | 1.9288e-08 | -9.7052e-07 | 0.00081167 | 0.00081132 | 0.00081167 | 0.97935 | -0.39975 | 0.97939 | -0.39898 | 0.22299
128 | -0.0017458 | -0.00043246 | 0.001746 | 0.00043154 | 2.2259e-07 | -9.2104e-07 | 0.0026506 | 0.0026502 | 0.0026506 | 0.97939 | -0.39898 | 0.97953 | -0.39627 | 0.72818
129 | 0.001211 | 0.00030183 | -0.001211 | -0.00030192 | 1.0183e-08 | -9.449e-08 | 0.0018393 | 0.0018393 | 0.0018393 | 0.97939 | -0.39898 | 0.97938 | -0.39915 | 0.5053
130 | -0.0089218 | -0.0022276 | 0.0089302 | 0.0022315 | 8.3982e-06 | 3.8449e-06 | 0.013566 | 0.013565 | 0.013566 | 0.9784 | -0.41847 | 0.97941 | -0.39867 | 3.7269
131 | 0.0085249 | 0.0021281 | -0.0085219 | -0.0021268 | 2.9768e-06 | 1.312e-06 | 0.012962 | 0.012962 | 0.012962 | 0.9784 | -0.41847 | 0.97803 | -0.42582 | 3.5611
132 | 0.0078171 | 0.0019502 | -0.0078163 | -0.0019499 | 8.1177e-07 | 3.2741e-07 | 0.01189 | 0.01189 | 0.01189 | 0.97803 | -0.42582 | 0.97792 | -0.42801 | 3.2665
133 | 0.00037566 | 9.3896e-05 | -0.00037566 | -9.415e-05 | 2.4771e-09 | -2.5371e-07 | 0.00057062 | 0.00057071 | 0.00057071 | 0.97947 | -0.39742 | 0.97946 | -0.39756 | 0.15679
134 | 0.0013856 | 0.00034449 | -0.0013855 | -0.00034488 | 5.7959e-08 | -3.974e-07 | 0.0021099 | 0.00211 | 0.00211 | 0.97674 | -0.45133 | 0.97669 | -0.45221 | 0.57968
135 | -0.0010661 | -0.00026521 | 0.0010661 | 0.00026483 | 3.1143e-08 | -3.7438e-07 | 0.0016236 | 0.0016234 | 0.0016236 | 0.97666 | -0.45283 | 0.97669 | -0.45221 | 0.44604
136 | 0.0005492 | 0.00013566 | -0.00054917 | -0.00013667 | 2.1511e-08 | -1.0127e-06 | 0.00083604 | 0.0008364 | 0.0008364 | 0.97666 | -0.45283 | 0.97662 | -0.45366 | 0.22978
137 | 0.00054917 | 0.00013667 | -0.00054915 | -0.00013763 | 2.0337e-08 | -9.5659e-07 | 0.0008364 | 0.00083675 | 0.00083675 | 0.97662 | -0.45366 | 0.97658 | -0.45444 | 0.22988

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50548 | 0.12982

## res_load
| p_mw | q_mvar
0 | 0.00096 | 0.0002406
1 | 0.00039347 | 9.8613e-05
2 | 0.00017365 | 4.352e-05
3 | 0.00030077 | 7.5381e-05
4 | 0.00092999 | 0.00023308
5 | 0.00020709 | 5.1902e-05
6 | 0.00028 | 7.0174e-05
7 | 0.00020039 | 5.0223e-05
8 | 0.0016067 | 0.00040269
9 | 0.0016961 | 0.00042508
10 | 0.0012676 | 0.00031769
11 | 0.0093886 | 0.002353
12 | 0.0012054 | 0.0003021
13 | 0.00087267 | 0.00021871
14 | 0.037971 | 0.0095163
15 | 0.0078337 | 0.0019633
16 | 0.0035574 | 0.00089156
17 | 0.008201 | 0.0020554
18 | 0.0049367 | 0.0012373
19 | 0.0044396 | 0.0011127
20 | 0.0037284 | 0.00093442
21 | 0.0059793 | 0.0014985
22 | 0.0034854 | 0.00087353
23 | 0.0052346 | 0.0013119
24 | 0.00060424 | 0.00015144
25 | 0.004636 | 0.0011619
26 | 0.0048476 | 0.0012149
27 | 0.0048677 | 0.00122
28 | 0.003679 | 0.00092206
29 | 0.0041929 | 0.0010508
30 | 0.0026513 | 0.00066449
31 | 0.0059198 | 0.0014837
32 | 0.0090929 | 0.0022789
33 | 0.0026937 | 0.0006751
34 | 0.0075601 | 0.0018947
35 | 0.018956 | 0.0047507
36 | 0.053503 | 0.013409
37 | 0.0058722 | 0.0014717
38 | 0.00049089 | 0.00012303
39 | 0.00051026 | 0.00012788
40 | 0.004522 | 0.0011333
41 | 0.0055739 | 0.001397
42 | 0.0059105 | 0.0014813
43 | 0.0047986 | 0.0012026
44 | 0.0029196 | 0.00073173
45 | 0.0060633 | 0.0015196
46 | 0.0021392 | 0.00053613
47 | 0.0053803 | 0.0013484
48 | 0.003261 | 0.00081729
49 | 0.00088878 | 0.00022275
50 | 0.0065028 | 0.0016297
51 | 0.004473 | 0.0011211
52 | 0.0033267 | 0.00083374
53 | 0.011567 | 0.002899
54 | 0.0031696 | 0.00079438
55 | 0.0020465 | 0.0005129
56 | 0.0014283 | 0.00035797
57 | 0.0034647 | 0.00086833
58 | 0.0011174 | 0.00028005
59 | 0.0012751 | 0.00031958
60 | 0.0012167 | 0.00030494
61 | 0.00080387 | 0.00020147
62 | 0.0008657 | 0.00021697
63 | 0.0005481 | 0.00013737
64 | 0.00083967 | 0.00021044
65 | 0.012578 | 0.0031525
66 | 0.0067748 | 0.0016979
67 | 0.011448 | 0.002869
68 | 0.030475 | 0.0076378
69 | 0.013027 | 0.0032649
70 | 0.045812 | 0.011482
71 | 0.0025213 | 0.00063189
72 | 0.0010993 | 0.00027552
73 | 0.010621 | 0.0026618
74 | 0.012355 | 0.0030965
75 | 0.0042591 | 0.0010674
76 | 0.0064618 | 0.0016195
77 | 0.00042806 | 0.00010728
78 | 0.00016526 | 4.1419e-05
79 | 0.00083069 | 0.00020819
80 | 0.00027313 | 6.8452e-05
81 | 0.0033827 | 0.00084778
82 | 0.00097978 | 0.00024556
83 | 0.00051807 | 0.00012984
84 | 0.00016845 | 4.2217e-05
85 | 0.00036631 | 9.1806e-05
86 | 0.0013513 | 0.00033867
87 | 0.0023558 | 0.00059043
88 | 0.00088 | 0.00022055
89 | 0.00063763 | 0.0001598
90 | 0.00015662 | 3.9252e-05
91 | 0.00026417 | 6.6208e-05
92 | 0.00019983 | 5.0082e-05
93 | 0.00035399 | 8.8717e-05
94 | 0.00023633 | 5.923e-05
95 | 0.00039692 | 9.9477e-05
96 | 0.00025638 | 6.4256e-05
97 | 0.00070478 | 0.00017663
98 | 0.00039661 | 9.9399e-05
99 | 0.00037566 | 9.415e-05
100 | 0.00064608 | 0.00016192
101 | 0.00029897 | 7.4928e-05
102 | 0.0005169 | 0.00012955
103 | 0.0003194 | 8.0048e-05
104 | 0.00054915 | 0.00013763

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1