## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1205-13_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1205-13_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1205-13_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1205-13_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1205-13_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1205-13_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1205-13_0_4_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_1205-13_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1205-13_0_4_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_1205-13_0_4_node_64 | 0.4 | n |  | TRUE
10 | bus_LV_1205-13_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1205-13_0_4_node_26 | 0.4 | n |  | TRUE
12 | bus_LV_1205-13_0_4_node_65 | 0.4 | n |  | TRUE
13 | bus_LV_1205-13_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1205-13_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1205-13_0_4_node_25 | 0.4 | n |  | TRUE
16 | bus_LV_1205-13_0_4_node_82 | 0.4 | n |  | TRUE
17 | bus_LV_1205-13_0_4_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_1205-13_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1205-13_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1205-13_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1205-13_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1205-13_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1205-13_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1205-13_0_4_node_62 | 0.4 | n |  | TRUE
25 | bus_LV_1205-13_0_4_node_74 | 0.4 | n |  | TRUE
26 | bus_LV_1205-13_0_4_node_79 | 0.4 | n |  | TRUE
27 | bus_LV_1205-13_0_4_node_63 | 0.4 | n |  | TRUE
28 | bus_LV_1205-13_0_4_node_75 | 0.4 | n |  | TRUE
29 | bus_LV_1205-13_0_4_node_80 | 0.4 | n |  | TRUE
30 | bus_LV_1205-13_0_4_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_1205-13_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_1205-13_0_4_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_1205-13_0_4_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_1205-13_0_4_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_1205-13_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1205-13_0_4_node_83 | 0.4 | n |  | TRUE
37 | bus_LV_1205-13_0_4_node_40 | 0.4 | n |  | TRUE
38 | bus_LV_1205-13_0_4_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_1205-13_0_4_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_1205-13_0_4_node_68 | 0.4 | n |  | TRUE
41 | bus_LV_1205-13_0_4_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_1205-13_0_4_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_1205-13_0_4_node_47 | 0.4 | n |  | TRUE
44 | bus_LV_1205-13_0_4_node_28 | 0.4 | n |  | TRUE
45 | bus_LV_1205-13_0_4_node_29 | 0.4 | n |  | TRUE
46 | bus_LV_1205-13_0_4_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_1205-13_0_4_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_1205-13_0_4_node_77 | 0.4 | n |  | TRUE
49 | bus_LV_1205-13_0_4_node_78 | 0.4 | n |  | TRUE
50 | bus_LV_1205-13_0_4_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_1205-13_0_4_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_1205-13_0_4_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_1205-13_0_4_node_36 | 0.4 | n |  | TRUE
54 | bus_LV_1205-13_0_4_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_1205-13_0_4_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_1205-13_0_4_node_42 | 0.4 | n |  | TRUE
57 | bus_LV_1205-13_0_4_node_67 | 0.4 | n |  | TRUE
58 | bus_LV_1205-13_0_4_node_69 | 0.4 | n |  | TRUE
59 | bus_LV_1205-13_0_4_node_48 | 0.4 | n |  | TRUE
60 | bus_LV_1205-13_0_4_node_57 | 0.4 | n |  | TRUE
61 | bus_LV_1205-13_0_4_node_43 | 0.4 | n |  | TRUE
62 | bus_LV_1205-13_0_4_node_44 | 0.4 | n |  | TRUE
63 | bus_LV_1205-13_0_4_node_45 | 0.4 | n |  | TRUE
64 | bus_LV_1205-13_0_4_node_73 | 0.4 | n |  | TRUE
65 | bus_LV_1205-13_0_4_node_71 | 0.4 | n |  | TRUE
66 | bus_LV_1205-13_0_4_node_59 | 0.4 | n |  | TRUE
67 | bus_LV_1205-13_0_4_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_1205-13_0_4_node_70 | 0.4 | n |  | TRUE
69 | bus_LV_1205-13_0_4_node_72 | 0.4 | n |  | TRUE
70 | bus_LV_1205-13_0_4_node_46 | 0.4 | n |  | TRUE
71 | bus_LV_1205-13_0_4_node_49 | 0.4 | n |  | TRUE
72 | bus_LV_1205-13_0_4_node_50 | 0.4 | n |  | TRUE
73 | bus_LV_1205-13_0_4_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_1205-13_0_4_node_61 | 0.4 | n |  | TRUE
75 | bus_LV_1205-13_0_4_node_76 | 0.4 | n |  | TRUE
76 | bus_LV_1205-13_0_4_node_56 | 0.4 | n |  | TRUE
77 | bus_LV_1205-13_0_4_node_53 | 0.4 | n |  | TRUE
78 | bus_LV_1205-13_0_4_node_54 | 0.4 | n |  | TRUE
79 | bus_LV_1205-13_0_4_node_55 | 0.4 | n |  | TRUE
80 | bus_LV_1205-13_0_4_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_1205-13_0_4_node_60 | 0.4 | n |  | TRUE
82 | bus_LV_1205-13_0_4_node_81 | 0.4 | n |  | TRUE
83 | bus_MV_14_0_node_91 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1205-13_0_4_load_0 | 0 | 0.0042311 | 0.0010604 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1205-13_0_4_load_1 | 1 | 0.0036508 | 0.00091496 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1205-13_0_4_load_4 | 4 | 0.0025999 | 0.0006516 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1205-13_0_4_load_5 | 5 | 0.0028567 | 0.00071595 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1205-13_0_4_load_10 | 6 | 0.0048188 | 0.0012077 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1205-13_0_4_load_7 | 7 | 0.0038663 | 0.00096897 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1205-13_0_4_load_27 | 8 | 0.0033444 | 0.00083819 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1205-13_0_4_load_64 | 9 | 0.0024619 | 0.000617 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1205-13_0_4_load_6 | 10 | 0.0041471 | 0.0010394 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1205-13_0_4_load_26 | 11 | 0.0068318 | 0.0017122 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1205-13_0_4_load_65 | 12 | 0.0029018 | 0.00072726 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1205-13_0_4_load_8 | 13 | 0.004473 | 0.001121 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1205-13_0_4_load_9 | 14 | 0.0043178 | 0.0010821 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1205-13_0_4_load_25 | 15 | 0.0055741 | 0.001397 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1205-13_0_4_load_82 | 16 | 0.0048458 | 0.0012145 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1205-13_0_4_load_24 | 17 | 0.003424 | 0.00085814 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1205-13_0_4_load_11 | 18 | 0.0041502 | 0.0010401 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1205-13_0_4_load_12 | 19 | 0.0046821 | 0.0011735 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1205-13_0_4_load_15 | 22 | 0.005946 | 0.0014902 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1205-13_0_4_load_16 | 23 | 0.0044247 | 0.0011089 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1205-13_0_4_load_62 | 24 | 0.0058668 | 0.0014704 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1205-13_0_4_load_74 | 25 | 0.0038722 | 0.00097045 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1205-13_0_4_load_79 | 26 | 0.0039265 | 0.00098408 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1205-13_0_4_load_63 | 27 | 0.0060145 | 0.0015074 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1205-13_0_4_load_75 | 28 | 0.0039264 | 0.00098405 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1205-13_0_4_load_80 | 29 | 0.01581 | 0.0039623 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1205-13_0_4_load_17 | 30 | 0.006051 | 0.0015165 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1205-13_0_4_load_18 | 31 | 0.0042015 | 0.001053 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1205-13_0_4_load_20 | 33 | 0.0040516 | 0.0010154 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1205-13_0_4_load_21 | 34 | 0.0060655 | 0.0015202 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1205-13_0_4_load_22 | 35 | 0.0050886 | 0.0012753 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1205-13_0_4_load_83 | 36 | 0.071564 | 0.017936 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1205-13_0_4_load_40 | 37 | 0.0041406 | 0.0010377 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1205-13_0_4_load_32 | 38 | 0.0038747 | 0.0009711 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1205-13_0_4_load_23 | 39 | 0.0051504 | 0.0012908 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1205-13_0_4_load_68 | 40 | 0.0057816 | 0.001449 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1205-13_0_4_load_41 | 41 | 0.0030024 | 0.00075248 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1205-13_0_4_load_28 | 44 | 0.0030152 | 0.00075568 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1205-13_0_4_load_29 | 45 | 0.0063148 | 0.0015826 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1205-13_0_4_load_31 | 46 | 0.003394 | 0.00085062 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1205-13_0_4_load_33 | 47 | 0.0031059 | 0.00077841 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1205-13_0_4_load_77 | 48 | 0.003683 | 0.00092306 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1205-13_0_4_load_78 | 49 | 0.0023045 | 0.00057756 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1205-13_0_4_load_34 | 50 | 0.0066745 | 0.0016728 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1205-13_0_4_load_35 | 51 | 0.0019836 | 0.00049713 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1205-13_0_4_load_38 | 54 | 0.0036374 | 0.00091161 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1205-13_0_4_load_39 | 55 | 0.0021935 | 0.00054974 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1205-13_0_4_load_42 | 56 | 0.0030748 | 0.00077062 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1205-13_0_4_load_67 | 57 | 0.0037261 | 0.00093384 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1205-13_0_4_load_69 | 58 | 0.0021302 | 0.00053388 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1205-13_0_4_load_48 | 59 | 0.0023186 | 0.00058109 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1205-13_0_4_load_57 | 60 | 0.0023346 | 0.00058511 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1205-13_0_4_load_43 | 61 | 0.0055484 | 0.0013906 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1205-13_0_4_load_44 | 62 | 0.0068652 | 0.0017206 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1205-13_0_4_load_45 | 63 | 0.0037214 | 0.00093267 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1205-13_0_4_load_73 | 64 | 0.0097082 | 0.0024331 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1205-13_0_4_load_71 | 65 | 0.0053557 | 0.0013423 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1205-13_0_4_load_59 | 66 | 0.0037137 | 0.00093075 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1205-13_0_4_load_52 | 67 | 0.0036822 | 0.00092284 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1205-13_0_4_load_70 | 68 | 0.0041137 | 0.001031 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1205-13_0_4_load_72 | 69 | 0.0037754 | 0.0009462 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1205-13_0_4_load_49 | 71 | 0.0036728 | 0.00092048 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1205-13_0_4_load_50 | 72 | 0.0038504 | 0.00096499 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1205-13_0_4_load_51 | 73 | 0.0032921 | 0.00082507 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1205-13_0_4_load_61 | 74 | 0.005354 | 0.0013418 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1205-13_0_4_load_76 | 75 | 0.0064884 | 0.0016262 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1205-13_0_4_load_53 | 77 | 0.0047175 | 0.0011823 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1205-13_0_4_load_54 | 78 | 0.0061583 | 0.0015434 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1205-13_0_4_load_58 | 80 | 0.0026219 | 0.0006571 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1205-13_0_4_load_60 | 81 | 0.0037144 | 0.00093091 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1205-13_0_4_load_81 | 82 | 0.0024641 | 0.00061757 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 47 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1205-13_0_4_line_0 |  | 0 | 1 | 0.025796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1205-13_0_4_line_1 |  | 0 | 2 | 0.027307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1205-13_0_4_line_2 |  | 1 | 3 | 0.0034775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1205-13_0_4_line_3 |  | 2 | 4 | 0.015648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1205-13_0_4_line_4 |  | 2 | 5 | 0.0064837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1205-13_0_4_line_5 |  | 3 | 6 | 0.018868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1205-13_0_4_line_6 |  | 3 | 7 | 0.014523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1205-13_0_4_line_7 |  | 4 | 8 | 0.0033642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1205-13_0_4_line_8 |  | 5 | 9 | 0.010651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1205-13_0_4_line_9 |  | 7 | 10 | 0.00032237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1205-13_0_4_line_10 |  | 8 | 11 | 0.026021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1205-13_0_4_line_11 |  | 9 | 12 | 0.0053317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1205-13_0_4_line_12 |  | 11 | 17 | 0.027539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1205-13_0_4_line_13 |  | 12 | 82 | 0.00027724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1205-13_0_4_line_14 |  | 13 | 14 | 0.0025434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1205-13_0_4_line_15 |  | 13 | 15 | 0.048505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1205-13_0_4_line_16 |  | 14 | 16 | 0.0076963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1205-13_0_4_line_17 |  | 15 | 17 | 0.0008958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1205-13_0_4_line_18 |  | 18 | 19 | 0.019574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1205-13_0_4_line_19 |  | 18 | 20 | 0.019434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1205-13_0_4_line_20 |  | 19 | 21 | 0.021475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1205-13_0_4_line_21 |  | 20 | 22 | 0.0010985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1205-13_0_4_line_22 |  | 20 | 23 | 0.011332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1205-13_0_4_line_23 |  | 21 | 24 | 0.020508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1205-13_0_4_line_24 |  | 22 | 25 | 0.013879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1205-13_0_4_line_25 |  | 23 | 26 | 0.0093324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1205-13_0_4_line_26 |  | 24 | 27 | 0.015823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1205-13_0_4_line_27 |  | 25 | 28 | 0.0082315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1205-13_0_4_line_28 |  | 26 | 29 | 0.010008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1205-13_0_4_line_29 |  | 28 | 75 | 0.011723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1205-13_0_4_line_30 |  | 30 | 31 | 0.01167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1205-13_0_4_line_31 |  | 30 | 32 | 0.0080995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1205-13_0_4_line_32 |  | 31 | 33 | 0.01359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1205-13_0_4_line_33 |  | 32 | 34 | 0.011778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1205-13_0_4_line_34 |  | 32 | 35 | 0.029039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1205-13_0_4_line_35 |  | 32 | 36 | 0.17222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1205-13_0_4_line_36 |  | 34 | 37 | 0.026886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1205-13_0_4_line_37 |  | 35 | 38 | 0.0065829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1205-13_0_4_line_38 |  | 37 | 41 | 0.0012214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1205-13_0_4_line_39 |  | 38 | 42 | 0.015538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1205-13_0_4_line_40 |  | 39 | 40 | 0.031287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1205-13_0_4_line_41 |  | 40 | 43 | 0.025014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1205-13_0_4_line_42 |  | 41 | 56 | 0.01022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1205-13_0_4_line_43 |  | 42 | 47 | 0.023411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_1205-13_0_4_line_44 |  | 42 | 44 | 0.011829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1205-13_0_4_line_45 |  | 43 | 70 | 0.009827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1205-13_0_4_line_46 |  | 44 | 45 | 0.009725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1205-13_0_4_line_47 |  | 45 | 46 | 0.033061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1205-13_0_4_line_48 |  | 47 | 48 | 0.019534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_1205-13_0_4_line_49 |  | 48 | 49 | 0.0051877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_1205-13_0_4_line_50 |  | 49 | 54 | 0.0022464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_1205-13_0_4_line_51 |  | 50 | 51 | 0.00061241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1205-13_0_4_line_52 |  | 51 | 52 | 0.0097946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1205-13_0_4_line_53 |  | 52 | 56 | 0.015978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1205-13_0_4_line_54 |  | 52 | 57 | 0.0095242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1205-13_0_4_line_55 |  | 53 | 54 | 0.017534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_1205-13_0_4_line_56 |  | 53 | 55 | 0.02052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_1205-13_0_4_line_57 |  | 55 | 58 | 0.0057408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_1205-13_0_4_line_58 |  | 57 | 59 | 0.0090456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1205-13_0_4_line_59 |  | 58 | 60 | 0.015024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_1205-13_0_4_line_60 |  | 59 | 70 | 0.027285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1205-13_0_4_line_61 |  | 60 | 79 | 0.0095268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_1205-13_0_4_line_62 |  | 61 | 62 | 0.025404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1205-13_0_4_line_63 |  | 62 | 63 | 0.020836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1205-13_0_4_line_64 |  | 62 | 64 | 0.041184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1205-13_0_4_line_65 |  | 63 | 66 | 0.009464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1205-13_0_4_line_66 |  | 64 | 65 | 0.0020458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1205-13_0_4_line_67 |  | 65 | 68 | 0.0068623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1205-13_0_4_line_68 |  | 66 | 67 | 0.01606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1205-13_0_4_line_69 |  | 67 | 72 | 0.0078904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1205-13_0_4_line_70 |  | 68 | 69 | 0.012626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1205-13_0_4_line_71 |  | 69 | 81 | 0.0080469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1205-13_0_4_line_72 |  | 71 | 72 | 0.019069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1205-13_0_4_line_73 |  | 71 | 73 | 0.0053969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1205-13_0_4_line_74 |  | 74 | 75 | 0.018748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1205-13_0_4_line_75 |  | 74 | 76 | 0.017297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1205-13_0_4_line_76 |  | 76 | 81 | 0.012863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1205-13_0_4_line_77 |  | 76 | 78 | 0.0023018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1205-13_0_4_line_78 |  | 77 | 78 | 0.012054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1205-13_0_4_line_79 |  | 77 | 79 | 0.021269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
80 | LV_1205-13_0_4_line_80 |  | 79 | 80 | 0.0056792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1205-13_0_4_line_81 |  | 80 | 82 | 0.0057748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1205-13_0_4_trafo_33 | 0.63 MVA 20/0.4 kV | 83 | 47 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2692139.6601 | 1191796.1888 | 2692126.8229 | 1191792.7491 | 2692114.3517 | 1191793.6792
1 | 2692165.1508 | 1191805.7697 | 2692158.1262 | 1191803.9271 | 2692141.8353 | 1191796.7717 | 2692139.6601 | 1191796.1888
2 | 2692110.8839 | 1191793.9379 | 2692114.3517 | 1191793.6792
3 | 2692165.1508 | 1191805.7697 | 2692162.2419 | 1191821.1452
4 | 2692165.1508 | 1191805.7697 | 2692169.2606 | 1191805.7664 | 2692171.6344 | 1191805.767
5 | 2692110.8839 | 1191793.9379 | 2692099.8351 | 1191796.4361 | 2692092.2988 | 1191796.1946
6 | 2692110.8839 | 1191793.9379 | 2692110.9947 | 1191808.4602
7 | 2692162.2419 | 1191821.1452 | 2692161.6166 | 1191824.4508
8 | 2692171.6344 | 1191805.767 | 2692182.2853 | 1191805.7697
9 | 2692110.9972 | 1191808.7826 | 2692110.9947 | 1191808.4602
10 | 2692156.7797 | 1191850.0178 | 2692161.6166 | 1191824.4508
11 | 2692187.617 | 1191805.7711 | 2692182.2853 | 1191805.7697
12 | 2692156.7797 | 1191850.0178 | 2692156.2855 | 1191852.63 | 2692148.0811 | 1191876.1191
13 | 2692187.617 | 1191805.7711 | 2692187.8943 | 1191805.7712
14 | 2692099.5551 | 1191870.4247 | 2692100.1266 | 1191867.9463
15 | 2692147.7857 | 1191876.9648 | 2692100.1266 | 1191867.9463
16 | 2692097.8256 | 1191877.9242 | 2692099.5551 | 1191870.4247
17 | 2692148.0811 | 1191876.1191 | 2692147.7857 | 1191876.9648
18 | 2692116.8817 | 1191738.4424 | 2692136.2073 | 1191741.5502
19 | 2692155.395 | 1191744.6358 | 2692136.2073 | 1191741.5502
20 | 2692095.6795 | 1191735.0328 | 2692116.8817 | 1191738.4424
21 | 2692155.395 | 1191744.6358 | 2692156.4709 | 1191744.8572
22 | 2692155.395 | 1191744.6358 | 2692159.1375 | 1191733.9394
23 | 2692095.6795 | 1191735.0328 | 2692105.0336 | 1191716.7819
24 | 2692170.065 | 1191747.6539 | 2692156.4709 | 1191744.8572
25 | 2692159.1375 | 1191733.9394 | 2692162.2196 | 1191725.1307
26 | 2692112.2507 | 1191702.7004 | 2692105.0336 | 1191716.7819
27 | 2692170.065 | 1191747.6539 | 2692178.1276 | 1191749.3126
28 | 2692165.5247 | 1191715.6844 | 2692162.2196 | 1191725.1307
29 | 2692178.1276 | 1191749.3126 | 2692189.6105 | 1191751.675
30 | 2692283.327 | 1191892.9032 | 2692294.7256 | 1191895.4035
31 | 2692275.4155 | 1191891.1679 | 2692283.327 | 1191892.9032
32 | 2692294.7256 | 1191895.4035 | 2692308.0003 | 1191898.3152
33 | 2692275.4155 | 1191891.1679 | 2692279.1943 | 1191880.0129
34 | 2692275.4155 | 1191891.1679 | 2692247.1164 | 1191884.6541
35 | 2692275.4155 | 1191891.1679 | 2692236.5724 | 1192058.9547
36 | 2692287.9118 | 1191854.5804 | 2692286.4797 | 1191858.5064 | 2692279.1943 | 1191880.0129
37 | 2692240.7013 | 1191883.1775 | 2692247.1164 | 1191884.6541
38 | 2692287.9118 | 1191854.5804 | 2692288.3303 | 1191853.4329
39 | 2692225.5589 | 1191879.6921 | 2692240.7013 | 1191883.1775
40 | 2692332.3584 | 1191870.5811 | 2692341.943 | 1191840.7982
41 | 2692349.606 | 1191816.9867 | 2692341.943 | 1191840.7982
42 | 2692288.3303 | 1191853.4329 | 2692291.8325 | 1191843.8314
43 | 2692225.5589 | 1191879.6921 | 2692233.2856 | 1191857.5931
44 | 2692225.5589 | 1191879.6921 | 2692213.9866 | 1191877.2427
45 | 2692340.4355 | 1191813.3874 | 2692349.606 | 1191816.9867
46 | 2692213.9866 | 1191877.2427 | 2692204.4723 | 1191875.2288
47 | 2692204.4723 | 1191875.2288 | 2692172.1284 | 1191868.3827
48 | 2692239.7326 | 1191839.154 | 2692233.2856 | 1191857.5931
49 | 2692239.7326 | 1191839.154 | 2692241.4448 | 1191834.2569
50 | 2692242.1862 | 1191832.1364 | 2692241.4448 | 1191834.2569
51 | 2692287.1105 | 1191826.7408 | 2692287.7105 | 1191826.8633
52 | 2692297.3075 | 1191828.821 | 2692287.7105 | 1191826.8633
53 | 2692297.3075 | 1191828.821 | 2692291.8325 | 1191843.8314
54 | 2692297.3075 | 1191828.821 | 2692306.2119 | 1191825.4412
55 | 2692247.9731 | 1191815.5853 | 2692242.1862 | 1191832.1364
56 | 2692247.9731 | 1191815.5853 | 2692228.8451 | 1191808.1574
57 | 2692228.8451 | 1191808.1574 | 2692223.4936 | 1191806.0793
58 | 2692314.6688 | 1191822.2314 | 2692306.2119 | 1191825.4412
59 | 2692208.8453 | 1191805.0228 | 2692218.7543 | 1191804.2388 | 2692223.4936 | 1191806.0793
60 | 2692340.4355 | 1191813.3874 | 2692333.9 | 1191814.932 | 2692314.6688 | 1191822.2314
61 | 2692199.3482 | 1191805.7742 | 2692208.8453 | 1191805.0228
62 | 2692289.4731 | 1191771.0017 | 2692286.5741 | 1191768.3722 | 2692271.0761 | 1191753.4853
63 | 2692271.0761 | 1191753.4853 | 2692256.0494 | 1191739.0511
64 | 2692250.0923 | 1191788.923 | 2692271.0761 | 1191753.4853
65 | 2692248.7662 | 1191733.0154 | 2692254.9419 | 1191737.9873 | 2692256.0494 | 1191739.0511
66 | 2692250.0923 | 1191788.923 | 2692248.2131 | 1191788.1143
67 | 2692241.9097 | 1191785.4016 | 2692248.2131 | 1191788.1143
68 | 2692248.7662 | 1191733.0154 | 2692236.2566 | 1191722.9443
69 | 2692236.2566 | 1191722.9443 | 2692230.1105 | 1191717.9962
70 | 2692241.9097 | 1191785.4016 | 2692230.3124 | 1191780.4106
71 | 2692222.9209 | 1191777.2296 | 2692230.3124 | 1191780.4106
72 | 2692214.0528 | 1191707.7882 | 2692226.247 | 1191714.8858 | 2692230.1105 | 1191717.9962
73 | 2692214.0528 | 1191707.7882 | 2692209.7649 | 1191705.2924 | 2692209.414 | 1191705.0345
74 | 2692207.4549 | 1191756.6584 | 2692206.0643 | 1191755.412 | 2692200.9619 | 1191754.0103 | 2692189.6105 | 1191751.675
75 | 2692211.1057 | 1191772.1448 | 2692212.7056 | 1191765.7988 | 2692209.712 | 1191758.6814 | 2692207.4549 | 1191756.6584
76 | 2692211.1057 | 1191772.1448 | 2692222.9209 | 1191777.2296
77 | 2692211.1057 | 1191772.1448 | 2692210.346 | 1191774.3177
78 | 2692206.3678 | 1191785.6964 | 2692210.346 | 1191774.3177
79 | 2692199.3482 | 1191805.7742 | 2692206.3678 | 1191785.6964
80 | 2692199.3482 | 1191805.7742 | 2692193.669 | 1191805.7727
81 | 2692193.669 | 1191805.7727 | 2692187.8943 | 1191805.7712

## bus_geodata
| x | y | coords
0 | 2692139.6601 | 1191796.1888
1 | 2692114.3517 | 1191793.6792
2 | 2692165.1508 | 1191805.7697
3 | 2692110.8839 | 1191793.9379
4 | 2692162.2419 | 1191821.1452
5 | 2692171.6345 | 1191805.767
6 | 2692092.2988 | 1191796.1946
7 | 2692110.9947 | 1191808.4602
8 | 2692161.6166 | 1191824.4508
9 | 2692182.2853 | 1191805.7697
10 | 2692110.9972 | 1191808.7826
11 | 2692156.7797 | 1191850.0178
12 | 2692187.617 | 1191805.7711
13 | 2692100.1266 | 1191867.9463
14 | 2692099.5551 | 1191870.4247
15 | 2692147.7857 | 1191876.9648
16 | 2692097.8256 | 1191877.9242
17 | 2692148.0811 | 1191876.1191
18 | 2692136.2073 | 1191741.5502
19 | 2692116.8817 | 1191738.4424
20 | 2692155.395 | 1191744.6358
21 | 2692095.6795 | 1191735.0328
22 | 2692156.4709 | 1191744.8572
23 | 2692159.1375 | 1191733.9394
24 | 2692105.0336 | 1191716.7819
25 | 2692170.065 | 1191747.6539
26 | 2692162.2196 | 1191725.1307
27 | 2692112.2507 | 1191702.7004
28 | 2692178.1276 | 1191749.3126
29 | 2692165.5247 | 1191715.6844
30 | 2692283.327 | 1191892.9032
31 | 2692294.7256 | 1191895.4035
32 | 2692275.4155 | 1191891.1679
33 | 2692308.0003 | 1191898.3152
34 | 2692279.1943 | 1191880.0129
35 | 2692247.1164 | 1191884.6541
36 | 2692236.5724 | 1192058.9547
37 | 2692287.9118 | 1191854.5804
38 | 2692240.7013 | 1191883.1775
39 | 2692332.3584 | 1191870.5811
40 | 2692341.943 | 1191840.7982
41 | 2692288.3303 | 1191853.4329
42 | 2692225.5589 | 1191879.6921
43 | 2692349.606 | 1191816.9867
44 | 2692213.9866 | 1191877.2427
45 | 2692204.4723 | 1191875.2288
46 | 2692172.1284 | 1191868.3827
47 | 2692233.2856 | 1191857.5931
48 | 2692239.7326 | 1191839.154
49 | 2692241.4448 | 1191834.2569
50 | 2692287.1105 | 1191826.7408
51 | 2692287.7105 | 1191826.8633
52 | 2692297.3075 | 1191828.821
53 | 2692247.9731 | 1191815.5853
54 | 2692242.1862 | 1191832.1364
55 | 2692228.8451 | 1191808.1574
56 | 2692291.8325 | 1191843.8314
57 | 2692306.2119 | 1191825.4412
58 | 2692223.4936 | 1191806.0793
59 | 2692314.6688 | 1191822.2314
60 | 2692208.8453 | 1191805.0228
61 | 2692289.4731 | 1191771.0017
62 | 2692271.0761 | 1191753.4853
63 | 2692256.0494 | 1191739.0511
64 | 2692250.0923 | 1191788.923
65 | 2692248.2131 | 1191788.1143
66 | 2692248.7662 | 1191733.0154
67 | 2692236.2566 | 1191722.9443
68 | 2692241.9097 | 1191785.4016
69 | 2692230.3124 | 1191780.4106
70 | 2692340.4355 | 1191813.3874
71 | 2692214.0528 | 1191707.7882
72 | 2692230.1105 | 1191717.9962
73 | 2692209.414 | 1191705.0345
74 | 2692207.4549 | 1191756.6584
75 | 2692189.6105 | 1191751.675
76 | 2692211.1057 | 1191772.1448
77 | 2692206.3678 | 1191785.6964
78 | 2692210.346 | 1191774.3177
79 | 2692199.3482 | 1191805.7742
80 | 2692193.669 | 1191805.7727
81 | 2692222.9209 | 1191777.2296
82 | 2692187.8943 | 1191805.7712
83 | 2692225.5589 | 1191879.6921

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98791 | -0.23179 | 0.0042311 | 0.0010604
1 | 0.98752 | -0.23939 | 0.0036508 | 0.00091496
2 | 0.98843 | -0.22169 | 0 | 0
3 | 0.98748 | -0.24019 | 0 | 0
4 | 0.98792 | -0.23158 | 0.0025999 | 0.0006516
5 | 0.98876 | -0.2152 | 0.0028567 | 0.00071595
6 | 0.98739 | -0.24181 | 0.0048188 | 0.0012077
7 | 0.98737 | -0.24227 | 0.0038663 | 0.00096897
8 | 0.98782 | -0.23356 | 0.0033444 | 0.00083819
9 | 0.98934 | -0.20401 | 0.0024619 | 0.000617
10 | 0.98737 | -0.24229 | 0.0041471 | 0.0010394
11 | 0.98711 | -0.24726 | 0.0068318 | 0.0017122
12 | 0.98964 | -0.19818 | 0.0029018 | 0.00072726
13 | 0.98592 | -0.27058 | 0.004473 | 0.001121
14 | 0.98589 | -0.271 | 0.0043178 | 0.0010821
15 | 0.98652 | -0.25873 | 0.0055741 | 0.001397
16 | 0.98586 | -0.27167 | 0.0048458 | 0.0012145
17 | 0.98654 | -0.25842 | 0.003424 | 0.00085814
18 | 0.9828 | -0.331 | 0.0041502 | 0.0010401
19 | 0.9825 | -0.33686 | 0.0046821 | 0.0011735
20 | 0.98317 | -0.32374 | 0 | 0
21 | 0.98227 | -0.34146 | 0 | 0
22 | 0.98322 | -0.32285 | 0.005946 | 0.0014902
23 | 0.98292 | -0.32868 | 0.0044247 | 0.0011089
24 | 0.98204 | -0.34587 | 0.0058668 | 0.0014704
25 | 0.98387 | -0.31014 | 0.0038722 | 0.00097045
26 | 0.98275 | -0.332 | 0.0039265 | 0.00098408
27 | 0.98195 | -0.34759 | 0.0060145 | 0.0015074
28 | 0.98428 | -0.30204 | 0.0039264 | 0.00098405
29 | 0.9826 | -0.33486 | 0.01581 | 0.0039623
30 | 0.9921 | -0.15068 | 0.006051 | 0.0015165
31 | 0.99202 | -0.15238 | 0.0042015 | 0.001053
32 | 0.99221 | -0.14863 | 0 | 0
33 | 0.99197 | -0.15336 | 0.0040516 | 0.0010154
34 | 0.99176 | -0.15737 | 0.0060655 | 0.0015202
35 | 0.99563 | -0.083148 | 0.0050886 | 0.0012753
36 | 0.98081 | -0.36938 | 0.071564 | 0.017936
37 | 0.99088 | -0.17447 | 0.0041406 | 0.0010377
38 | 0.99643 | -0.06778 | 0.0038747 | 0.0009711
39 | 0.98917 | -0.20762 | 0.0051504 | 0.0012908
40 | 0.98932 | -0.20475 | 0.0057816 | 0.001449
41 | 0.99084 | -0.17516 | 0.0030024 | 0.00075248
42 | 0.99839 | -0.030548 | 0 | 0
43 | 0.98957 | -0.19988 | 0 | 0
44 | 0.99825 | -0.033181 | 0.0030152 | 0.00075568
45 | 0.99817 | -0.034832 | 0.0063148 | 0.0015826
46 | 0.99807 | -0.036796 | 0.003394 | 0.00085062
47 | 1 | 0 | -0.384 | -0.097682
48 | 0.99795 | -0.038908 | 0.003683 | 0.00092306
49 | 0.99741 | -0.049101 | 0.0023045 | 0.00057756
50 | 0.99011 | -0.18923 | 0.0066745 | 0.0016728
51 | 0.99012 | -0.18916 | 0.0019836 | 0.00049713
52 | 0.9902 | -0.18765 | 0 | 0
53 | 0.99542 | -0.087103 | 0 | 0
54 | 0.99718 | -0.053473 | 0.0036374 | 0.00091161
55 | 0.99335 | -0.12661 | 0.0021935 | 0.00054974
56 | 0.99057 | -0.18037 | 0.0030748 | 0.00077062
57 | 0.99005 | -0.19052 | 0.0037261 | 0.00093384
58 | 0.99278 | -0.13758 | 0.0021302 | 0.00053388
59 | 0.98994 | -0.19266 | 0.0023186 | 0.00058109
60 | 0.9913 | -0.16607 | 0.0023346 | 0.00058511
61 | 0.98357 | -0.31608 | 0.0055484 | 0.0013906
62 | 0.9837 | -0.31354 | 0.0068652 | 0.0017206
63 | 0.98328 | -0.32178 | 0.0037214 | 0.00093267
64 | 0.985 | -0.28809 | 0.0097082 | 0.0024331
65 | 0.98509 | -0.28647 | 0.0053557 | 0.0013423
66 | 0.98312 | -0.32488 | 0.0037137 | 0.00093075
67 | 0.9829 | -0.32908 | 0.0036822 | 0.00092284
68 | 0.9854 | -0.28038 | 0.0041137 | 0.001031
69 | 0.98602 | -0.26826 | 0.0037754 | 0.0009462
70 | 0.98966 | -0.19796 | 0 | 0
71 | 0.9827 | -0.33302 | 0.0036728 | 0.00092048
72 | 0.98282 | -0.33062 | 0.0038504 | 0.00096499
73 | 0.98269 | -0.33334 | 0.0032921 | 0.00082507
74 | 0.98604 | -0.26777 | 0.005354 | 0.0013418
75 | 0.98492 | -0.28968 | 0.0064884 | 0.0016262
76 | 0.98717 | -0.24595 | 0 | 0
77 | 0.98898 | -0.21093 | 0.0047175 | 0.0011823
78 | 0.98745 | -0.24054 | 0.0061583 | 0.0015434
79 | 0.99037 | -0.18398 | 0 | 0
80 | 0.99001 | -0.19099 | 0.0026219 | 0.0006571
81 | 0.98645 | -0.26 | 0.0037144 | 0.00093091
82 | 0.98966 | -0.19786 | 0.0024641 | 0.00061757
83 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.016491 | 0.0041351 | -0.016485 | -0.0041316 | 5.9684e-06 | 3.4896e-06 | 0.024839 | 0.024839 | 0.024839 | 0.98791 | -0.23179 | 0.98752 | -0.23939 | 6.824
1 | -0.020722 | -0.0051955 | 0.020732 | 0.0052015 | 9.9761e-06 | 6.0349e-06 | 0.031212 | 0.031212 | 0.031212 | 0.98791 | -0.23179 | 0.98843 | -0.22169 | 8.5748
2 | 0.012834 | 0.0032166 | -0.012833 | -0.0032164 | 4.8768e-07 | 2.6763e-07 | 0.019338 | 0.019338 | 0.019338 | 0.98752 | -0.23939 | 0.98748 | -0.24019 | 5.3127
3 | 0.03547 | 0.0089112 | -0.035454 | -0.0089007 | 1.6737e-05 | 1.0511e-05 | 0.053406 | 0.053406 | 0.053406 | 0.98843 | -0.22169 | 0.98792 | -0.23158 | 14.672
4 | -0.056202 | -0.014113 | 0.056219 | 0.014124 | 1.7409e-05 | 1.1059e-05 | 0.084618 | 0.084618 | 0.084618 | 0.98843 | -0.22169 | 0.98876 | -0.2152 | 23.2468
5 | 0.0048192 | 0.0012077 | -0.0048188 | -0.0012077 | 3.7313e-07 | -2.55e-09 | 0.0072619 | 0.007262 | 0.007262 | 0.98748 | -0.24019 | 0.98739 | -0.24181 | 1.995
6 | 0.0080142 | 0.0020087 | -0.0080134 | -0.0020083 | 7.9426e-07 | 3.2256e-07 | 0.012076 | 0.012077 | 0.012077 | 0.98748 | -0.24019 | 0.98737 | -0.24227 | 3.3177
7 | 0.032854 | 0.0082491 | -0.032851 | -0.0082471 | 3.0899e-06 | 1.9345e-06 | 0.04949 | 0.04949 | 0.04949 | 0.98792 | -0.23158 | 0.98782 | -0.23356 | 13.5962
8 | -0.059076 | -0.01484 | 0.059108 | 0.01486 | 3.1578e-05 | 2.0073e-05 | 0.088917 | 0.088917 | 0.088917 | 0.98876 | -0.2152 | 0.98934 | -0.20401 | 24.4278
9 | 0.0041471 | 0.0010394 | -0.0041471 | -0.0010394 | 4.7221e-09 | -1.1011e-09 | 0.0062499 | 0.0062499 | 0.0062499 | 0.98737 | -0.24227 | 0.98737 | -0.24229 | 1.717
10 | 0.029506 | 0.0074089 | -0.029487 | -0.0073969 | 1.9281e-05 | 1.2007e-05 | 0.044452 | 0.044452 | 0.044452 | 0.98782 | -0.23356 | 0.98711 | -0.24726 | 12.2122
11 | -0.06157 | -0.015477 | 0.061587 | 0.015488 | 1.7152e-05 | 1.0909e-05 | 0.09262 | 0.09262 | 0.09262 | 0.98934 | -0.20401 | 0.98964 | -0.19818 | 25.4451
12 | 0.022655 | 0.0056847 | -0.022643 | -0.0056774 | 1.2046e-05 | 7.3579e-06 | 0.034154 | 0.034154 | 0.034154 | 0.98711 | -0.24726 | 0.98654 | -0.25842 | 9.3829
13 | -0.064488 | -0.016215 | 0.064489 | 0.016216 | 9.7785e-07 | 6.2226e-07 | 0.096983 | 0.096983 | 0.096983 | 0.98964 | -0.19818 | 0.98966 | -0.19786 | 26.6437
14 | 0.0091639 | 0.0022967 | -0.0091637 | -0.0022966 | 1.8245e-07 | 8.4335e-08 | 0.013831 | 0.013831 | 0.013831 | 0.98592 | -0.27058 | 0.98589 | -0.271 | 3.7997
15 | -0.013637 | -0.0034177 | 0.013645 | 0.0034221 | 7.7052e-06 | 4.3124e-06 | 0.020582 | 0.020582 | 0.020582 | 0.98592 | -0.27058 | 0.98652 | -0.25873 | 5.6544
16 | 0.0048459 | 0.0012145 | -0.0048458 | -0.0012145 | 1.5439e-07 | 6.7219e-10 | 0.007314 | 0.007314 | 0.007314 | 0.98589 | -0.271 | 0.98586 | -0.27167 | 2.0093
17 | -0.019219 | -0.0048191 | 0.019219 | 0.0048192 | 2.823e-07 | 1.6924e-07 | 0.028989 | 0.028989 | 0.028989 | 0.98652 | -0.25873 | 0.98654 | -0.25842 | 7.9641
18 | 0.016574 | 0.0041568 | -0.016569 | -0.004154 | 4.6224e-06 | 2.7104e-06 | 0.025095 | 0.025095 | 0.025095 | 0.9828 | -0.331 | 0.9825 | -0.33686 | 6.8941
19 | -0.020724 | -0.0051969 | 0.020731 | 0.0052012 | 7.1755e-06 | 4.346e-06 | 0.031378 | 0.031378 | 0.031378 | 0.9828 | -0.331 | 0.98317 | -0.32374 | 8.6204
20 | 0.011887 | 0.0029806 | -0.011884 | -0.0029792 | 2.6102e-06 | 1.3986e-06 | 0.018003 | 0.018004 | 0.018004 | 0.9825 | -0.33686 | 0.98227 | -0.34146 | 4.946
21 | -0.044903 | -0.011263 | 0.044905 | 0.011264 | 1.9027e-06 | 1.2038e-06 | 0.067963 | 0.067963 | 0.067963 | 0.98317 | -0.32374 | 0.98322 | -0.32285 | 18.6712
22 | 0.024172 | 0.0060619 | -0.024166 | -0.0060584 | 5.6879e-06 | 3.4966e-06 | 0.036585 | 0.036585 | 0.036585 | 0.98317 | -0.32374 | 0.98292 | -0.32868 | 10.0508
23 | 0.011884 | 0.0029792 | -0.011882 | -0.0029778 | 2.4928e-06 | 1.3358e-06 | 0.018004 | 0.018004 | 0.018004 | 0.98227 | -0.34146 | 0.98204 | -0.34587 | 4.946
24 | -0.050851 | -0.012755 | 0.050882 | 0.012774 | 3.0827e-05 | 1.9553e-05 | 0.076962 | 0.076962 | 0.076962 | 0.98322 | -0.32285 | 0.98387 | -0.31014 | 21.1433
25 | 0.019741 | 0.0049495 | -0.019738 | -0.0049476 | 3.1259e-06 | 1.8823e-06 | 0.029887 | 0.029887 | 0.029887 | 0.98292 | -0.32868 | 0.98275 | -0.332 | 8.2106
26 | 0.006015 | 0.0015075 | -0.0060145 | -0.0015074 | 4.9289e-07 | 1.1527e-07 | 0.009114 | 0.0091141 | 0.0091141 | 0.98204 | -0.34587 | 0.98195 | -0.34759 | 2.5039
27 | -0.054754 | -0.013745 | 0.054775 | 0.013758 | 2.1172e-05 | 1.3445e-05 | 0.082818 | 0.082818 | 0.082818 | 0.98387 | -0.31014 | 0.98428 | -0.30204 | 22.7522
28 | 0.015812 | 0.0039635 | -0.01581 | -0.0039623 | 2.1511e-06 | 1.2499e-06 | 0.023941 | 0.023941 | 0.023941 | 0.98275 | -0.332 | 0.9826 | -0.33486 | 6.5773
29 | -0.058701 | -0.014742 | 0.058736 | 0.014764 | 3.463e-05 | 2.2014e-05 | 0.088754 | 0.088754 | 0.088754 | 0.98428 | -0.30204 | 0.98492 | -0.28968 | 24.3829
30 | 0.008254 | 0.0020686 | -0.0082533 | -0.0020684 | 6.7068e-07 | 2.7856e-07 | 0.01238 | 0.01238 | 0.01238 | 0.9921 | -0.15068 | 0.99202 | -0.15238 | 3.401
31 | -0.014305 | -0.0035852 | 0.014306 | 0.003586 | 1.3982e-06 | 7.9023e-07 | 0.021455 | 0.021455 | 0.021455 | 0.9921 | -0.15068 | 0.99221 | -0.14863 | 5.8943
32 | 0.0040518 | 0.0010154 | -0.0040516 | -0.0010154 | 1.8825e-07 | -5.4972e-08 | 0.0060776 | 0.0060777 | 0.0060777 | 0.99202 | -0.15238 | 0.99197 | -0.15336 | 1.6697
33 | 0.041993 | 0.010551 | -0.041976 | -0.01054 | 1.7522e-05 | 1.1062e-05 | 0.062987 | 0.062987 | 0.062987 | 0.99221 | -0.14863 | 0.99176 | -0.15737 | 17.304
34 | -0.12863 | -0.032558 | 0.12903 | 0.032817 | 0.00040568 | 0.00025926 | 0.19301 | 0.19301 | 0.19301 | 0.99221 | -0.14863 | 0.99563 | -0.083148 | 53.0255
35 | 0.072325 | 0.018421 | -0.071564 | -0.017936 | 0.0007613 | 0.00048504 | 0.10857 | 0.10857 | 0.10857 | 0.99221 | -0.14863 | 0.98081 | -0.36938 | 29.8275
36 | 0.03591 | 0.0090201 | -0.035881 | -0.0090017 | 2.9276e-05 | 1.839e-05 | 0.053886 | 0.053886 | 0.053886 | 0.99176 | -0.15737 | 0.99088 | -0.17447 | 14.8039
37 | -0.13412 | -0.034093 | 0.13422 | 0.034156 | 9.9355e-05 | 6.3501e-05 | 0.20062 | 0.20062 | 0.20062 | 0.99563 | -0.083148 | 0.99643 | -0.06778 | 55.1148
38 | 0.03174 | 0.007964 | -0.031739 | -0.0079634 | 1.0408e-06 | 6.5038e-07 | 0.047668 | 0.047668 | 0.047668 | 0.99088 | -0.17447 | 0.99084 | -0.17516 | 13.0957
39 | -0.13809 | -0.035127 | 0.13834 | 0.035286 | 0.00024824 | 0.00015867 | 0.2064 | 0.2064 | 0.2064 | 0.99643 | -0.06778 | 0.99839 | -0.030548 | 56.7044
40 | -0.0051504 | -0.0012908 | 0.0051511 | 0.0012909 | 7.0429e-07 | 4.9062e-08 | 0.0077478 | 0.0077477 | 0.0077478 | 0.98917 | -0.20762 | 0.98932 | -0.20475 | 2.1285
41 | -0.010933 | -0.0027399 | 0.010935 | 0.0027412 | 2.5364e-06 | 1.302e-06 | 0.016444 | 0.016444 | 0.016444 | 0.98932 | -0.20475 | 0.98957 | -0.19988 | 4.5175
42 | 0.028737 | 0.0072109 | -0.02873 | -0.0072065 | 7.1391e-06 | 4.4374e-06 | 0.043159 | 0.043159 | 0.043159 | 0.99084 | -0.17516 | 0.99057 | -0.18037 | 11.857
43 | -0.15107 | -0.038476 | 0.15129 | 0.038618 | 0.00022296 | 0.00014208 | 0.22537 | 0.22537 | 0.22537 | 0.99839 | -0.030548 | 1 | 0 | 30.9577
44 | 0.012727 | 0.0031899 | -0.012725 | -0.0031891 | 1.5959e-06 | 8.6674e-07 | 0.018968 | 0.018968 | 0.018968 | 0.99839 | -0.030548 | 0.99825 | -0.033181 | 5.211
45 | -0.010935 | -0.0027412 | 0.010936 | 0.0027417 | 9.9642e-07 | 5.1145e-07 | 0.016444 | 0.016444 | 0.016444 | 0.98957 | -0.19988 | 0.98966 | -0.19796 | 4.5175
46 | 0.0097099 | 0.0024334 | -0.0097091 | -0.002433 | 7.6398e-07 | 3.6182e-07 | 0.014474 | 0.014474 | 0.014474 | 0.99825 | -0.033181 | 0.99817 | -0.034832 | 3.9763
47 | 0.0033943 | 0.00085039 | -0.003394 | -0.00085062 | 3.1743e-07 | -2.2894e-07 | 0.00506 | 0.0050601 | 0.0050601 | 0.99817 | -0.034832 | 0.99807 | -0.036796 | 1.3901
48 | 0.23106 | 0.059064 | -0.23063 | -0.058787 | 0.000434 | 0.00027725 | 0.34423 | 0.34423 | 0.34423 | 1 | 0 | 0.99795 | -0.038908 | 47.2845
49 | 0.22694 | 0.057864 | -0.22683 | -0.057793 | 0.00011161 | 7.1296e-05 | 0.33874 | 0.33874 | 0.33874 | 0.99795 | -0.038908 | 0.99741 | -0.049101 | 46.5302
50 | 0.22453 | 0.057215 | -0.22448 | -0.057185 | 4.7355e-05 | 3.0249e-05 | 0.3353 | 0.3353 | 0.3353 | 0.99741 | -0.049101 | 0.99718 | -0.053473 | 46.0579
51 | -0.0066745 | -0.0016728 | 0.0066746 | 0.0016728 | 2.3108e-08 | 6.9127e-09 | 0.010031 | 0.010031 | 0.010031 | 0.99011 | -0.18923 | 0.99012 | -0.18916 | 2.7558
52 | -0.0086581 | -0.0021699 | 0.0086588 | 0.0021702 | 6.2188e-07 | 2.7202e-07 | 0.013012 | 0.013012 | 0.013012 | 0.99012 | -0.18916 | 0.9902 | -0.18765 | 3.5747
53 | -0.025646 | -0.0064304 | 0.025655 | 0.0064358 | 8.8999e-06 | 5.4903e-06 | 0.038541 | 0.038541 | 0.038541 | 0.9902 | -0.18765 | 0.99057 | -0.18037 | 10.5881
54 | 0.016987 | 0.0042601 | -0.016985 | -0.0042588 | 2.3277e-06 | 1.3672e-06 | 0.025529 | 0.025529 | 0.025529 | 0.9902 | -0.18765 | 0.99005 | -0.19052 | 7.0134
55 | -0.22049 | -0.056045 | 0.22084 | 0.056273 | 0.00035774 | 0.0002285 | 0.32987 | 0.32987 | 0.32987 | 0.99542 | -0.087103 | 0.99718 | -0.053473 | 45.3124
56 | 0.22049 | 0.056045 | -0.22007 | -0.055777 | 0.00041867 | 0.00026741 | 0.32987 | 0.32987 | 0.32987 | 0.99542 | -0.087103 | 0.99335 | -0.12661 | 45.3124
57 | 0.21787 | 0.055228 | -0.21776 | -0.055154 | 0.00011481 | 7.3329e-05 | 0.32659 | 0.32659 | 0.32659 | 0.99335 | -0.12661 | 0.99278 | -0.13758 | 44.8611
58 | 0.013259 | 0.0033249 | -0.013258 | -0.0033242 | 1.3472e-06 | 7.4587e-07 | 0.019929 | 0.019929 | 0.019929 | 0.99005 | -0.19052 | 0.98994 | -0.19266 | 5.4749
59 | 0.21563 | 0.05462 | -0.21533 | -0.054432 | 0.00029462 | 0.00018817 | 0.3234 | 0.3234 | 0.3234 | 0.99278 | -0.13758 | 0.9913 | -0.16607 | 44.4225
60 | 0.010939 | 0.0027431 | -0.010936 | -0.0027417 | 2.7666e-06 | 1.4199e-06 | 0.016443 | 0.016444 | 0.016444 | 0.98994 | -0.19266 | 0.98966 | -0.19796 | 4.5175
61 | 0.213 | 0.053847 | -0.21282 | -0.05373 | 0.00018279 | 0.00011674 | 0.31989 | 0.31989 | 0.31989 | 0.9913 | -0.16607 | 0.99037 | -0.18398 | 43.9412
62 | -0.0055484 | -0.0013906 | 0.005549 | 0.0013907 | 6.7121e-07 | 1.0712e-07 | 0.008394 | 0.0083939 | 0.008394 | 0.98357 | -0.31608 | 0.9837 | -0.31354 | 2.306
63 | 0.021948 | 0.005506 | -0.02194 | -0.0055007 | 8.6138e-06 | 5.2484e-06 | 0.033203 | 0.033203 | 0.033203 | 0.9837 | -0.31354 | 0.98328 | -0.32178 | 9.1216
64 | -0.034363 | -0.0086172 | 0.034404 | 0.0086434 | 4.1731e-05 | 2.6184e-05 | 0.051981 | 0.051981 | 0.051981 | 0.9837 | -0.31354 | 0.985 | -0.28809 | 14.2806
65 | 0.018218 | 0.004568 | -0.018216 | -0.0045664 | 2.6978e-06 | 1.6066e-06 | 0.027571 | 0.027571 | 0.027571 | 0.98328 | -0.32178 | 0.98312 | -0.32488 | 7.5745
66 | -0.044113 | -0.011076 | 0.044116 | 0.011079 | 3.4077e-06 | 2.1549e-06 | 0.066647 | 0.066647 | 0.066647 | 0.985 | -0.28809 | 0.98509 | -0.28647 | 18.3096
67 | -0.049472 | -0.012421 | 0.049486 | 0.01243 | 1.4374e-05 | 9.1118e-06 | 0.074737 | 0.074737 | 0.074737 | 0.98509 | -0.28647 | 0.9854 | -0.28038 | 20.5322
68 | 0.014502 | 0.0036357 | -0.014499 | -0.003634 | 2.9016e-06 | 1.6535e-06 | 0.02195 | 0.02195 | 0.02195 | 0.98312 | -0.32488 | 0.9829 | -0.32908 | 6.0303
69 | 0.010817 | 0.0027112 | -0.010816 | -0.0027108 | 7.9347e-07 | 4.0782e-07 | 0.016376 | 0.016376 | 0.016376 | 0.9829 | -0.32908 | 0.98282 | -0.33062 | 4.4988
70 | -0.0536 | -0.013461 | 0.053631 | 0.013481 | 3.1025e-05 | 1.9695e-05 | 0.080949 | 0.080949 | 0.080949 | 0.9854 | -0.28038 | 0.98602 | -0.26826 | 22.2387
71 | -0.057406 | -0.014427 | 0.057429 | 0.014441 | 2.2655e-05 | 1.4396e-05 | 0.086646 | 0.086646 | 0.086646 | 0.98602 | -0.26826 | 0.98645 | -0.26 | 23.804
72 | -0.0069649 | -0.0017455 | 0.0069657 | 0.0017458 | 7.9536e-07 | 2.674e-07 | 0.010546 | 0.010546 | 0.010546 | 0.9827 | -0.33302 | 0.98282 | -0.33062 | 2.8973
73 | 0.0032921 | 0.00082503 | -0.0032921 | -0.00082507 | 5.0291e-08 | -3.6187e-08 | 0.0049849 | 0.004985 | 0.004985 | 0.9827 | -0.33302 | 0.98269 | -0.33334 | 1.3695
74 | 0.065293 | 0.016434 | -0.065224 | -0.01639 | 6.829e-05 | 4.3467e-05 | 0.098556 | 0.098556 | 0.098556 | 0.98604 | -0.26777 | 0.98492 | -0.28968 | 27.0759
75 | -0.070647 | -0.017776 | 0.07072 | 0.017822 | 7.3758e-05 | 4.6984e-05 | 0.10664 | 0.10664 | 0.10664 | 0.98604 | -0.26777 | 0.98717 | -0.24595 | 29.2956
76 | 0.061184 | 0.015398 | -0.061143 | -0.015372 | 4.1048e-05 | 2.6107e-05 | 0.092249 | 0.092249 | 0.092249 | 0.98717 | -0.24595 | 0.98645 | -0.26 | 25.3432
77 | -0.1319 | -0.033221 | 0.13194 | 0.033243 | 3.4143e-05 | 2.1822e-05 | 0.19889 | 0.19889 | 0.19889 | 0.98717 | -0.24595 | 0.98745 | -0.24054 | 54.6388
78 | 0.13829 | 0.034911 | -0.1381 | -0.034786 | 0.00019588 | 0.00012521 | 0.20817 | 0.20817 | 0.20817 | 0.98898 | -0.21093 | 0.98745 | -0.24054 | 57.1882
79 | -0.14301 | -0.036094 | 0.1432 | 0.036211 | 0.0001848 | 0.00011772 | 0.21526 | 0.21526 | 0.21526 | 0.98898 | -0.21093 | 0.99037 | -0.18398 | 29.5691
80 | 0.069621 | 0.017519 | -0.069597 | -0.017504 | 2.3314e-05 | 1.4848e-05 | 0.10463 | 0.10463 | 0.10463 | 0.99037 | -0.18398 | 0.99001 | -0.19099 | 28.7442
81 | 0.066976 | 0.016847 | -0.066954 | -0.016833 | 2.1954e-05 | 1.3977e-05 | 0.10069 | 0.10069 | 0.10069 | 0.99001 | -0.19099 | 0.98966 | -0.19786 | 27.6616

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38711 | 0.098461

## res_load
| p_mw | q_mvar
0 | 0.0042311 | 0.0010604
1 | 0.0036508 | 0.00091496
2 | 0.0025999 | 0.0006516
3 | 0.0028567 | 0.00071595
4 | 0.0048188 | 0.0012077
5 | 0.0038663 | 0.00096897
6 | 0.0033444 | 0.00083819
7 | 0.0024619 | 0.000617
8 | 0.0041471 | 0.0010394
9 | 0.0068318 | 0.0017122
10 | 0.0029018 | 0.00072726
11 | 0.004473 | 0.001121
12 | 0.0043178 | 0.0010821
13 | 0.0055741 | 0.001397
14 | 0.0048458 | 0.0012145
15 | 0.003424 | 0.00085814
16 | 0.0041502 | 0.0010401
17 | 0.0046821 | 0.0011735
18 | 0.005946 | 0.0014902
19 | 0.0044247 | 0.0011089
20 | 0.0058668 | 0.0014704
21 | 0.0038722 | 0.00097045
22 | 0.0039265 | 0.00098408
23 | 0.0060145 | 0.0015074
24 | 0.0039264 | 0.00098405
25 | 0.01581 | 0.0039623
26 | 0.006051 | 0.0015165
27 | 0.0042015 | 0.001053
28 | 0.0040516 | 0.0010154
29 | 0.0060655 | 0.0015202
30 | 0.0050886 | 0.0012753
31 | 0.071564 | 0.017936
32 | 0.0041406 | 0.0010377
33 | 0.0038747 | 0.0009711
34 | 0.0051504 | 0.0012908
35 | 0.0057816 | 0.001449
36 | 0.0030024 | 0.00075248
37 | 0.0030152 | 0.00075568
38 | 0.0063148 | 0.0015826
39 | 0.003394 | 0.00085062
40 | 0.0031059 | 0.00077841
41 | 0.003683 | 0.00092306
42 | 0.0023045 | 0.00057756
43 | 0.0066745 | 0.0016728
44 | 0.0019836 | 0.00049713
45 | 0.0036374 | 0.00091161
46 | 0.0021935 | 0.00054974
47 | 0.0030748 | 0.00077062
48 | 0.0037261 | 0.00093384
49 | 0.0021302 | 0.00053388
50 | 0.0023186 | 0.00058109
51 | 0.0023346 | 0.00058511
52 | 0.0055484 | 0.0013906
53 | 0.0068652 | 0.0017206
54 | 0.0037214 | 0.00093267
55 | 0.0097082 | 0.0024331
56 | 0.0053557 | 0.0013423
57 | 0.0037137 | 0.00093075
58 | 0.0036822 | 0.00092284
59 | 0.0041137 | 0.001031
60 | 0.0037754 | 0.0009462
61 | 0.0036728 | 0.00092048
62 | 0.0038504 | 0.00096499
63 | 0.0032921 | 0.00082507
64 | 0.005354 | 0.0013418
65 | 0.0064884 | 0.0016262
66 | 0.0047175 | 0.0011823
67 | 0.0061583 | 0.0015434
68 | 0.0026219 | 0.0006571
69 | 0.0037144 | 0.00093091
70 | 0.0024641 | 0.00061757

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1