## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1205-14_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1205-14_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1205-14_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1205-14_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1205-14_0_6_node_16 | 0.4 | n |  | TRUE
5 | bus_LV_1205-14_0_6_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_1205-14_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1205-14_0_6_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_1205-14_0_6_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1205-14_0_6_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_1205-14_0_6_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_1205-14_0_6_node_23 | 0.4 | n |  | TRUE
12 | bus_LV_1205-14_0_6_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_1205-14_0_6_node_28 | 0.4 | n |  | TRUE
14 | bus_LV_1205-14_0_6_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_1205-14_0_6_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1205-14_0_6_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1205-14_0_6_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1205-14_0_6_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1205-14_0_6_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1205-14_0_6_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1205-14_0_6_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_1205-14_0_6_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_1205-14_0_6_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1205-14_0_6_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1205-14_0_6_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_1205-14_0_6_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_1205-14_0_6_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_1205-14_0_6_node_32 | 0.4 | n |  | TRUE
29 | bus_LV_1205-14_0_6_node_33 | 0.4 | n |  | TRUE
30 | bus_MV_14_0_node_92 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1205-14_0_6_load_0 | 0 | 0.021489 | 0.0053855 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1205-14_0_6_load_4 | 3 | 0.0020831 | 0.00052206 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1205-14_0_6_load_25 | 5 | 0.001955 | 0.00048997 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1205-14_0_6_load_10 | 7 | 0.00077541 | 0.00019433 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1205-14_0_6_load_7 | 8 | 0.091072 | 0.022825 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1205-14_0_6_load_15 | 9 | 0.078498 | 0.019673 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1205-14_0_6_load_22 | 10 | 0.083723 | 0.020983 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1205-14_0_6_load_26 | 12 | 0.0051008 | 0.0012784 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1205-14_0_6_load_28 | 13 | 0.00082054 | 0.00020565 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1205-14_0_6_load_13 | 15 | 0.069644 | 0.017454 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1205-14_0_6_load_8 | 16 | 0.082208 | 0.020603 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1205-14_0_6_load_9 | 17 | 0.072834 | 0.018254 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1205-14_0_6_load_11 | 19 | 0.00097381 | 0.00024406 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1205-14_0_6_load_17 | 20 | 0.0015067 | 0.00037761 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1205-14_0_6_load_20 | 22 | 0.0025351 | 0.00063535 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1205-14_0_6_load_24 | 24 | 0.002185 | 0.00054761 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1205-14_0_6_load_29 | 27 | 0.065399 | 0.01639 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1205-14_0_6_load_33 | 29 | 0.0041189 | 0.0010323 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1205-14_0_6_line_0 |  | 0 | 1 | 0.012625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1205-14_0_6_line_1 |  | 1 | 2 | 0.011134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_1205-14_0_6_line_2 |  | 1 | 3 | 0.022002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_1205-14_0_6_line_3 |  | 2 | 4 | 0.012437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_1205-14_0_6_line_4 |  | 3 | 5 | 0.012534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_1205-14_0_6_line_5 |  | 4 | 9 | 0.016021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_1205-14_0_6_line_6 |  | 5 | 12 | 0.014163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_1205-14_0_6_line_7 |  | 6 | 7 | 0.0094325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1205-14_0_6_line_8 |  | 6 | 8 | 0.0016894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1205-14_0_6_line_9 |  | 7 | 15 | 0.0082139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1205-14_0_6_line_10 |  | 8 | 16 | 0.027698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1205-14_0_6_line_11 |  | 9 | 17 | 0.022143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_1205-14_0_6_line_12 |  | 10 | 11 | 0.0023143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1205-14_0_6_line_13 |  | 11 | 24 | 0.007646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1205-14_0_6_line_14 |  | 11 | 22 | 0.015976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_1205-14_0_6_line_15 |  | 12 | 23 | 0.0089112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1205-14_0_6_line_16 |  | 13 | 14 | 0.025572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1205-14_0_6_line_17 |  | 14 | 18 | 0.010793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1205-14_0_6_line_18 |  | 15 | 18 | 0.033007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1205-14_0_6_line_19 |  | 16 | 17 | 0.016448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1205-14_0_6_line_20 |  | 18 | 19 | 0.019574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1205-14_0_6_line_21 |  | 20 | 21 | 0.030321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1205-14_0_6_line_22 |  | 21 | 22 | 0.023438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_1205-14_0_6_line_23 |  | 21 | 23 | 0.017107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_1205-14_0_6_line_24 |  | 24 | 25 | 0.012301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1205-14_0_6_line_25 |  | 25 | 26 | 0.028665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1205-14_0_6_line_26 |  | 25 | 27 | 0.011716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1205-14_0_6_line_27 |  | 26 | 28 | 0.041754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1205-14_0_6_line_28 |  | 28 | 29 | 0.014957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1205-14_0_6_trafo_15 | 0.63 MVA 20/0.4 kV | 30 | 9 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2693319.1755 | 1192299.4028 | 2693309.4572 | 1192302.6534 | 2693307.5664 | 1192304.0948
1 | 2693319.1755 | 1192299.4028 | 2693321.5564 | 1192304.1541 | 2693326.9501 | 1192306.3841
2 | 2693319.1755 | 1192299.4028 | 2693319.4817 | 1192295.4161 | 2693323.7314 | 1192282.0293 | 2693324.7714 | 1192278.2104
3 | 2693322.8176 | 1192318.1161 | 2693326.9501 | 1192306.3841
4 | 2693331.3496 | 1192267.7611 | 2693331.3496 | 1192267.7611 | 2693325.6158 | 1192275.1097 | 2693324.7714 | 1192278.2104
5 | 2693322.8176 | 1192318.1161 | 2693317.8195 | 1192333.3377
6 | 2693342.2956 | 1192258.7735 | 2693331.3496 | 1192267.7611
7 | 2693332.3147 | 1192391.0891 | 2693340.3185 | 1192396.0801
8 | 2693332.3147 | 1192391.0891 | 2693330.94 | 1192390.107
9 | 2693347.2883 | 1192400.4264 | 2693340.3185 | 1192396.0801
10 | 2693330.94 | 1192390.107 | 2693326.6823 | 1192387.0653 | 2693317.735 | 1192380.4882 | 2693313.8198 | 1192374.8791 | 2693312.2099 | 1192370.6555
11 | 2693317.8195 | 1192333.3377 | 2693313.1161 | 1192347.6617 | 2693311.6073 | 1192354.5657
12 | 2693365.8461 | 1192295.8284 | 2693364.0323 | 1192294.391
13 | 2693369.9847 | 1192302.2637 | 2693365.8461 | 1192295.8284
14 | 2693365.8461 | 1192295.8284 | 2693365.66 | 1192279.8535
15 | 2693349.1827 | 1192253.1186 | 2693342.2956 | 1192258.7735
16 | 2693373.9928 | 1192433.7779 | 2693349.526 | 1192431.895 | 2693348.5173 | 1192431.6732
17 | 2693373.9928 | 1192433.7779 | 2693370.3853 | 1192423.6039
18 | 2693370.3853 | 1192423.6039 | 2693364.7435 | 1192415.2994 | 2693349.651 | 1192401.8998 | 2693347.2883 | 1192400.4264
19 | 2693312.2099 | 1192370.6555 | 2693311.0146 | 1192367.5195 | 2693310.4888 | 1192359.684 | 2693311.6073 | 1192354.5657
20 | 2693370.3853 | 1192423.6039 | 2693383.7311 | 1192421.911 | 2693389.8136 | 1192422.603
21 | 2693365.371 | 1192256.4177 | 2693395.6834 | 1192257.136
22 | 2693365.371 | 1192256.4177 | 2693365.4421 | 1192261.1441 | 2693365.66 | 1192279.8535
23 | 2693349.1827 | 1192253.1186 | 2693355.8041 | 1192256.8021 | 2693365.371 | 1192256.4177
24 | 2693369.9847 | 1192302.2637 | 2693368.7111 | 1192314.4962
25 | 2693368.7111 | 1192314.4962 | 2693371.6827 | 1192320.969 | 2693375.1264 | 1192328.4498 | 2693387.548 | 1192333.2244
26 | 2693368.7111 | 1192314.4962 | 2693357.0482 | 1192313.3802
27 | 2693387.548 | 1192333.2244 | 2693398.6051 | 1192344.8156 | 2693405.3284 | 1192332.2012 | 2693411.3208 | 1192322.4551
28 | 2693416.0484 | 1192308.2642 | 2693411.3208 | 1192322.4551

## bus_geodata
| x | y | coords
0 | 2693307.5664 | 1192304.0948
1 | 2693319.1755 | 1192299.4028
2 | 2693326.9501 | 1192306.3841
3 | 2693324.7714 | 1192278.2104
4 | 2693322.8176 | 1192318.1161
5 | 2693331.3496 | 1192267.7611
6 | 2693332.3147 | 1192391.0891
7 | 2693340.3185 | 1192396.0801
8 | 2693330.94 | 1192390.107
9 | 2693317.8195 | 1192333.3377
10 | 2693364.0323 | 1192294.391
11 | 2693365.8461 | 1192295.8284
12 | 2693342.2956 | 1192258.7735
13 | 2693348.5173 | 1192431.6732
14 | 2693373.9928 | 1192433.7779
15 | 2693347.2883 | 1192400.4264
16 | 2693312.2099 | 1192370.6555
17 | 2693311.6073 | 1192354.5657
18 | 2693370.3853 | 1192423.6039
19 | 2693389.8136 | 1192422.603
20 | 2693395.6834 | 1192257.136
21 | 2693365.371 | 1192256.4177
22 | 2693365.66 | 1192279.8535
23 | 2693349.1827 | 1192253.1186
24 | 2693369.9847 | 1192302.2637
25 | 2693368.7111 | 1192314.4962
26 | 2693387.548 | 1192333.2244
27 | 2693357.0482 | 1192313.3802
28 | 2693411.3208 | 1192322.4551
29 | 2693416.0484 | 1192308.2642
30 | 2693321.247 | 1192322.8992

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99746 | -0.048582 | 0.021489 | 0.0053855
1 | 0.9977 | -0.043831 | 0 | 0
2 | 0.99835 | -0.031485 | 0 | 0
3 | 0.99657 | -0.065508 | 0.0020831 | 0.00052206
4 | 0.99907 | -0.017712 | 0 | 0
5 | 0.99594 | -0.077727 | 0.001955 | 0.00048997
6 | 0.99446 | -0.10654 | 0 | 0
7 | 0.99384 | -0.11856 | 0.00077541 | 0.00019433
8 | 0.99457 | -0.10439 | 0.091072 | 0.022825
9 | 1 | 0 | -0.51282 | -0.12917
10 | 0.99152 | -0.16297 | 0.083723 | 0.020983
11 | 0.99169 | -0.15954 | 0 | 0
12 | 0.99523 | -0.09139 | 0.0051008 | 0.0012784
13 | 0.99322 | -0.13049 | 0.00082054 | 0.00020565
14 | 0.99324 | -0.13012 | 0 | 0
15 | 0.9933 | -0.12892 | 0.069644 | 0.017454
16 | 0.99663 | -0.064631 | 0.082208 | 0.020603
17 | 0.99786 | -0.041041 | 0.072834 | 0.018254
18 | 0.99325 | -0.12997 | 0 | 0
19 | 0.99323 | -0.1303 | 0.00097381 | 0.00024406
20 | 0.99392 | -0.11657 | 0.0015067 | 0.00037761
21 | 0.99396 | -0.11576 | 0 | 0
22 | 0.99283 | -0.13756 | 0.0025351 | 0.00063535
23 | 0.99479 | -0.09973 | 0 | 0
24 | 0.99119 | -0.16926 | 0.002185 | 0.00054761
25 | 0.99041 | -0.18444 | 0 | 0
26 | 0.9903 | -0.18654 | 0 | 0
27 | 0.98971 | -0.19806 | 0.065399 | 0.01639
28 | 0.99014 | -0.1896 | 0 | 0
29 | 0.99009 | -0.19069 | 0.0041189 | 0.0010323
30 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.021489 | -0.0053855 | 0.021493 | 0.0053885 | 4.8652e-06 | 2.9489e-06 | 0.032057 | 0.032057 | 0.032057 | 0.99746 | -0.048582 | 0.9977 | -0.043831 | 8.8068
1 | -0.19114 | -0.048303 | 0.19125 | 0.048375 | 0.00011321 | 7.2019e-05 | 0.28521 | 0.28521 | 0.28521 | 0.9977 | -0.043831 | 0.99835 | -0.031485 | 26.1182
2 | 0.16964 | 0.042915 | -0.16947 | -0.042803 | 0.00017625 | 0.00011194 | 0.25315 | 0.25315 | 0.25315 | 0.9977 | -0.043831 | 0.99657 | -0.065508 | 23.1827
3 | -0.19125 | -0.048375 | 0.19138 | 0.048456 | 0.00012646 | 8.0447e-05 | 0.28521 | 0.28521 | 0.28521 | 0.99835 | -0.031485 | 0.99907 | -0.017712 | 26.1182
4 | 0.16738 | 0.042281 | -0.16729 | -0.042219 | 9.796e-05 | 6.2205e-05 | 0.25004 | 0.25004 | 0.25004 | 0.99657 | -0.065508 | 0.99594 | -0.077727 | 22.8978
5 | -0.19138 | -0.048456 | 0.19154 | 0.048559 | 0.00016291 | 0.00010363 | 0.28521 | 0.28521 | 0.28521 | 0.99907 | -0.017712 | 1 | 0 | 26.1182
6 | 0.16533 | 0.041729 | -0.16522 | -0.04166 | 0.00010812 | 6.8642e-05 | 0.24712 | 0.24712 | 0.24712 | 0.99594 | -0.077727 | 0.99523 | -0.09139 | 22.6304
7 | 0.07229 | 0.018146 | -0.072249 | -0.01812 | 4.1394e-05 | 2.637e-05 | 0.10818 | 0.10818 | 0.10818 | 0.99446 | -0.10654 | 0.99384 | -0.11856 | 29.7193
8 | -0.07229 | -0.018146 | 0.072298 | 0.018151 | 7.414e-06 | 4.723e-06 | 0.10818 | 0.10818 | 0.10818 | 0.99446 | -0.10654 | 0.99457 | -0.10439 | 29.7193
9 | 0.071473 | 0.017925 | -0.071438 | -0.017903 | 3.5277e-05 | 2.2471e-05 | 0.10702 | 0.10702 | 0.10702 | 0.99384 | -0.11856 | 0.9933 | -0.12892 | 29.4004
10 | -0.16337 | -0.040976 | 0.16368 | 0.041174 | 0.00031029 | 0.00019787 | 0.24443 | 0.24443 | 0.24443 | 0.99457 | -0.10439 | 0.99663 | -0.064631 | 33.5762
11 | 0.31963 | 0.080608 | -0.319 | -0.080207 | 0.00062658 | 0.00040014 | 0.47578 | 0.47578 | 0.47578 | 1 | 0 | 0.99786 | -0.041041 | 43.57
12 | -0.083723 | -0.020983 | 0.083736 | 0.020992 | 1.3701e-05 | 8.7387e-06 | 0.12565 | 0.12565 | 0.12565 | 0.99152 | -0.16297 | 0.99169 | -0.15954 | 34.5184
13 | 0.07183 | 0.01805 | -0.071796 | -0.018029 | 3.3318e-05 | 2.1225e-05 | 0.1078 | 0.1078 | 0.1078 | 0.99169 | -0.15954 | 0.99119 | -0.16926 | 29.6144
14 | -0.15557 | -0.039042 | 0.15573 | 0.039146 | 0.00016324 | 0.00010406 | 0.23344 | 0.23344 | 0.23344 | 0.99169 | -0.15954 | 0.99283 | -0.13756 | 32.0664
15 | 0.16012 | 0.040382 | -0.16006 | -0.040341 | 6.3892e-05 | 4.0544e-05 | 0.2395 | 0.2395 | 0.2395 | 0.99523 | -0.09139 | 0.99479 | -0.09973 | 21.932
16 | -0.00082054 | -0.00020565 | 0.00082056 | 0.00020533 | 1.449e-08 | -3.2168e-07 | 0.0012293 | 0.0012292 | 0.0012293 | 0.99322 | -0.13049 | 0.99324 | -0.13012 | 0.33772
17 | -0.00082056 | -0.00020533 | 0.00082056 | 0.00020519 | 6.115e-09 | -1.3578e-07 | 0.0012292 | 0.0012291 | 0.0012292 | 0.99324 | -0.13012 | 0.99325 | -0.12997 | 0.33769
18 | 0.0017945 | 0.00044864 | -0.0017944 | -0.00044901 | 8.9425e-08 | -3.6999e-07 | 0.0026878 | 0.002688 | 0.002688 | 0.9933 | -0.12892 | 0.99325 | -0.12997 | 0.73846
19 | -0.24589 | -0.061777 | 0.24617 | 0.061954 | 0.00027719 | 0.00017676 | 0.36717 | 0.36717 | 0.36717 | 0.99663 | -0.064631 | 0.99786 | -0.041041 | 33.624
20 | 0.00097383 | 0.00024382 | -0.00097381 | -0.00024406 | 1.5623e-08 | -2.4334e-07 | 0.0014588 | 0.0014589 | 0.0014589 | 0.99325 | -0.12997 | 0.99323 | -0.1303 | 0.4008
21 | -0.0015067 | -0.00037761 | 0.0015067 | 0.00037725 | 5.785e-08 | -3.5596e-07 | 0.0022557 | 0.0022556 | 0.0022557 | 0.99392 | -0.11657 | 0.99396 | -0.11576 | 0.6197
22 | 0.15843 | 0.039886 | -0.15826 | -0.039781 | 0.00016489 | 0.00010462 | 0.23724 | 0.23724 | 0.23724 | 0.99396 | -0.11576 | 0.99283 | -0.13756 | 21.7255
23 | -0.15994 | -0.040263 | 0.16006 | 0.040341 | 0.00012266 | 7.7834e-05 | 0.2395 | 0.2395 | 0.2395 | 0.99396 | -0.11576 | 0.99479 | -0.09973 | 21.932
24 | 0.069612 | 0.017482 | -0.069561 | -0.017449 | 5.0389e-05 | 3.2091e-05 | 0.10452 | 0.10452 | 0.10452 | 0.99119 | -0.16926 | 0.99041 | -0.18444 | 28.7132
25 | 0.0041201 | 0.001032 | -0.0041197 | -0.0010321 | 4.1188e-07 | -1.0524e-07 | 0.00619 | 0.0061901 | 0.0061901 | 0.99041 | -0.18444 | 0.9903 | -0.18654 | 1.7006
26 | 0.065441 | 0.016417 | -0.065399 | -0.01639 | 4.2477e-05 | 2.7035e-05 | 0.098326 | 0.098326 | 0.098326 | 0.99041 | -0.18444 | 0.98971 | -0.19806 | 27.0127
27 | 0.0041197 | 0.0010321 | -0.0041191 | -0.0010322 | 5.9999e-07 | -1.5314e-07 | 0.0061901 | 0.0061903 | 0.0061903 | 0.9903 | -0.18654 | 0.99014 | -0.1896 | 1.7006
28 | 0.0041191 | 0.0010322 | -0.0041189 | -0.0010323 | 2.1493e-07 | -5.4808e-08 | 0.0061903 | 0.0061904 | 0.0061904 | 0.99014 | -0.1896 | 0.99009 | -0.19069 | 1.7006

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.59131 | 0.14884

## res_load
| p_mw | q_mvar
0 | 0.021489 | 0.0053855
1 | 0.0020831 | 0.00052206
2 | 0.001955 | 0.00048997
3 | 0.00077541 | 0.00019433
4 | 0.091072 | 0.022825
5 | 0.078498 | 0.019673
6 | 0.083723 | 0.020983
7 | 0.0051008 | 0.0012784
8 | 0.00082054 | 0.00020565
9 | 0.069644 | 0.017454
10 | 0.082208 | 0.020603
11 | 0.072834 | 0.018254
12 | 0.00097381 | 0.00024406
13 | 0.0015067 | 0.00037761
14 | 0.0025351 | 0.00063535
15 | 0.002185 | 0.00054761
16 | 0.065399 | 0.01639
17 | 0.0041189 | 0.0010323

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1