## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1213-12_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1213-12_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1213-12_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1213-12_0_5_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1213-12_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1213-12_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1213-12_0_5_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_1213-12_0_5_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_1213-12_0_5_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1213-12_0_5_node_33 | 0.4 | n |  | TRUE
10 | bus_LV_1213-12_0_5_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1213-12_0_5_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1213-12_0_5_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1213-12_0_5_node_30 | 0.4 | n |  | TRUE
14 | bus_LV_1213-12_0_5_node_34 | 0.4 | n |  | TRUE
15 | bus_LV_1213-12_0_5_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_1213-12_0_5_node_35 | 0.4 | n |  | TRUE
17 | bus_LV_1213-12_0_5_node_36 | 0.4 | n |  | TRUE
18 | bus_LV_1213-12_0_5_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1213-12_0_5_node_31 | 0.4 | n |  | TRUE
20 | bus_LV_1213-12_0_5_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_1213-12_0_5_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1213-12_0_5_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1213-12_0_5_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1213-12_0_5_node_123 | 0.4 | n |  | TRUE
25 | bus_LV_1213-12_0_5_node_115 | 0.4 | n |  | TRUE
26 | bus_LV_1213-12_0_5_node_56 | 0.4 | n |  | TRUE
27 | bus_LV_1213-12_0_5_node_122 | 0.4 | n |  | TRUE
28 | bus_LV_1213-12_0_5_node_121 | 0.4 | n |  | TRUE
29 | bus_LV_1213-12_0_5_node_55 | 0.4 | n |  | TRUE
30 | bus_LV_1213-12_0_5_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_1213-12_0_5_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_1213-12_0_5_node_132 | 0.4 | n |  | TRUE
33 | bus_LV_1213-12_0_5_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_1213-12_0_5_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_1213-12_0_5_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_1213-12_0_5_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_1213-12_0_5_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_1213-12_0_5_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_1213-12_0_5_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_1213-12_0_5_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_1213-12_0_5_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_1213-12_0_5_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_1213-12_0_5_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_1213-12_0_5_node_38 | 0.4 | n |  | TRUE
45 | bus_LV_1213-12_0_5_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_1213-12_0_5_node_78 | 0.4 | n |  | TRUE
47 | bus_LV_1213-12_0_5_node_41 | 0.4 | n |  | TRUE
48 | bus_LV_1213-12_0_5_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_1213-12_0_5_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_1213-12_0_5_node_77 | 0.4 | n |  | TRUE
51 | bus_LV_1213-12_0_5_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_1213-12_0_5_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_1213-12_0_5_node_76 | 0.4 | n |  | TRUE
54 | bus_LV_1213-12_0_5_node_44 | 0.4 | n |  | TRUE
55 | bus_LV_1213-12_0_5_node_45 | 0.4 | n |  | TRUE
56 | bus_LV_1213-12_0_5_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_1213-12_0_5_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_1213-12_0_5_node_72 | 0.4 | n |  | TRUE
59 | bus_LV_1213-12_0_5_node_49 | 0.4 | n |  | TRUE
60 | bus_LV_1213-12_0_5_node_50 | 0.4 | n |  | TRUE
61 | bus_LV_1213-12_0_5_node_51 | 0.4 | n |  | TRUE
62 | bus_LV_1213-12_0_5_node_73 | 0.4 | n |  | TRUE
63 | bus_LV_1213-12_0_5_node_84 | 0.4 | n |  | TRUE
64 | bus_LV_1213-12_0_5_node_85 | 0.4 | n |  | TRUE
65 | bus_LV_1213-12_0_5_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_1213-12_0_5_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_1213-12_0_5_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_1213-12_0_5_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_1213-12_0_5_node_67 | 0.4 | n |  | TRUE
70 | bus_LV_1213-12_0_5_node_69 | 0.4 | n |  | TRUE
71 | bus_LV_1213-12_0_5_node_65 | 0.4 | n |  | TRUE
72 | bus_LV_1213-12_0_5_node_75 | 0.4 | n |  | TRUE
73 | bus_LV_1213-12_0_5_node_74 | 0.4 | n |  | TRUE
74 | bus_LV_1213-12_0_5_node_60 | 0.4 | n |  | TRUE
75 | bus_LV_1213-12_0_5_node_61 | 0.4 | n |  | TRUE
76 | bus_LV_1213-12_0_5_node_62 | 0.4 | n |  | TRUE
77 | bus_LV_1213-12_0_5_node_63 | 0.4 | n |  | TRUE
78 | bus_LV_1213-12_0_5_node_64 | 0.4 | n |  | TRUE
79 | bus_LV_1213-12_0_5_node_70 | 0.4 | n |  | TRUE
80 | bus_LV_1213-12_0_5_node_68 | 0.4 | n |  | TRUE
81 | bus_LV_1213-12_0_5_node_71 | 0.4 | n |  | TRUE
82 | bus_LV_1213-12_0_5_node_66 | 0.4 | n |  | TRUE
83 | bus_LV_1213-12_0_5_node_125 | 0.4 | n |  | TRUE
84 | bus_LV_1213-12_0_5_node_124 | 0.4 | n |  | TRUE
85 | bus_LV_1213-12_0_5_node_79 | 0.4 | n |  | TRUE
86 | bus_LV_1213-12_0_5_node_80 | 0.4 | n |  | TRUE
87 | bus_LV_1213-12_0_5_node_81 | 0.4 | n |  | TRUE
88 | bus_LV_1213-12_0_5_node_82 | 0.4 | n |  | TRUE
89 | bus_LV_1213-12_0_5_node_83 | 0.4 | n |  | TRUE
90 | bus_LV_1213-12_0_5_node_87 | 0.4 | n |  | TRUE
91 | bus_LV_1213-12_0_5_node_86 | 0.4 | n |  | TRUE
92 | bus_LV_1213-12_0_5_node_88 | 0.4 | n |  | TRUE
93 | bus_LV_1213-12_0_5_node_92 | 0.4 | n |  | TRUE
94 | bus_LV_1213-12_0_5_node_89 | 0.4 | n |  | TRUE
95 | bus_LV_1213-12_0_5_node_96 | 0.4 | n |  | TRUE
96 | bus_LV_1213-12_0_5_node_90 | 0.4 | n |  | TRUE
97 | bus_LV_1213-12_0_5_node_91 | 0.4 | n |  | TRUE
98 | bus_LV_1213-12_0_5_node_93 | 0.4 | n |  | TRUE
99 | bus_LV_1213-12_0_5_node_94 | 0.4 | n |  | TRUE
100 | bus_LV_1213-12_0_5_node_95 | 0.4 | n |  | TRUE
101 | bus_LV_1213-12_0_5_node_99 | 0.4 | n |  | TRUE
102 | bus_LV_1213-12_0_5_node_102 | 0.4 | n |  | TRUE
103 | bus_LV_1213-12_0_5_node_130 | 0.4 | n |  | TRUE
104 | bus_LV_1213-12_0_5_node_97 | 0.4 | n |  | TRUE
105 | bus_LV_1213-12_0_5_node_100 | 0.4 | n |  | TRUE
106 | bus_LV_1213-12_0_5_node_103 | 0.4 | n |  | TRUE
107 | bus_LV_1213-12_0_5_node_128 | 0.4 | n |  | TRUE
108 | bus_LV_1213-12_0_5_node_98 | 0.4 | n |  | TRUE
109 | bus_LV_1213-12_0_5_node_101 | 0.4 | n |  | TRUE
110 | bus_LV_1213-12_0_5_node_108 | 0.4 | n |  | TRUE
111 | bus_LV_1213-12_0_5_node_104 | 0.4 | n |  | TRUE
112 | bus_LV_1213-12_0_5_node_105 | 0.4 | n |  | TRUE
113 | bus_LV_1213-12_0_5_node_106 | 0.4 | n |  | TRUE
114 | bus_LV_1213-12_0_5_node_107 | 0.4 | n |  | TRUE
115 | bus_LV_1213-12_0_5_node_109 | 0.4 | n |  | TRUE
116 | bus_LV_1213-12_0_5_node_110 | 0.4 | n |  | TRUE
117 | bus_LV_1213-12_0_5_node_111 | 0.4 | n |  | TRUE
118 | bus_LV_1213-12_0_5_node_118 | 0.4 | n |  | TRUE
119 | bus_LV_1213-12_0_5_node_117 | 0.4 | n |  | TRUE
120 | bus_LV_1213-12_0_5_node_112 | 0.4 | n |  | TRUE
121 | bus_LV_1213-12_0_5_node_113 | 0.4 | n |  | TRUE
122 | bus_LV_1213-12_0_5_node_114 | 0.4 | n |  | TRUE
123 | bus_LV_1213-12_0_5_node_116 | 0.4 | n |  | TRUE
124 | bus_LV_1213-12_0_5_node_119 | 0.4 | n |  | TRUE
125 | bus_LV_1213-12_0_5_node_120 | 0.4 | n |  | TRUE
126 | bus_LV_1213-12_0_5_node_126 | 0.4 | n |  | TRUE
127 | bus_LV_1213-12_0_5_node_127 | 0.4 | n |  | TRUE
128 | bus_LV_1213-12_0_5_node_129 | 0.4 | n |  | TRUE
129 | bus_LV_1213-12_0_5_node_131 | 0.4 | n |  | TRUE
130 | bus_MV_14_0_node_114 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1213-12_0_5_load_0 | 0 | 0.0094872 | 0.0023777 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1213-12_0_5_load_1 | 1 | 0.0033703 | 0.00084467 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1213-12_0_5_load_3 | 2 | 0.0035795 | 0.0008971 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1213-12_0_5_load_4 | 4 | 0.0028081 | 0.00070377 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1213-12_0_5_load_5 | 5 | 0.0081531 | 0.0020434 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1213-12_0_5_load_9 | 6 | 0.002549 | 0.00063884 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1213-12_0_5_load_32 | 7 | 0.0027698 | 0.00069419 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1213-12_0_5_load_6 | 10 | 0.0082113 | 0.002058 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1213-12_0_5_load_8 | 11 | 0.0058652 | 0.00147 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1213-12_0_5_load_10 | 12 | 0.0042225 | 0.0010583 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1213-12_0_5_load_30 | 13 | 0.0048595 | 0.0012179 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1213-12_0_5_load_29 | 15 | 0.0061106 | 0.0015315 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1213-12_0_5_load_35 | 16 | 0.0040506 | 0.0010152 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1213-12_0_5_load_36 | 17 | 0.0041458 | 0.001039 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1213-12_0_5_load_11 | 18 | 0.0081251 | 0.0020363 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1213-12_0_5_load_31 | 19 | 0.0078256 | 0.0019613 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1213-12_0_5_load_28 | 20 | 0.0079157 | 0.0019839 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1213-12_0_5_load_12 | 21 | 0.010856 | 0.0027208 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1213-12_0_5_load_123 | 24 | 0.011338 | 0.0028416 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1213-12_0_5_load_115 | 25 | 0.0036286 | 0.00090941 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1213-12_0_5_load_56 | 26 | 0.0043701 | 0.0010953 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1213-12_0_5_load_122 | 27 | 0.0055472 | 0.0013903 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1213-12_0_5_load_121 | 28 | 0.0058636 | 0.0014696 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1213-12_0_5_load_15 | 30 | 0.0034774 | 0.00087151 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1213-12_0_5_load_16 | 31 | 0.00224 | 0.0005614 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1213-12_0_5_load_132 | 32 | 0.0020517 | 0.0005142 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1213-12_0_5_load_18 | 33 | 0.003604 | 0.00090325 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1213-12_0_5_load_19 | 34 | 0.002908 | 0.00072881 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1213-12_0_5_load_20 | 35 | 0.0039583 | 0.00099204 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1213-12_0_5_load_21 | 36 | 0.0020814 | 0.00052164 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1213-12_0_5_load_22 | 37 | 0.0025643 | 0.00064266 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1213-12_0_5_load_23 | 38 | 0.0017079 | 0.00042804 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1213-12_0_5_load_25 | 40 | 0.0026971 | 0.00067595 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1213-12_0_5_load_26 | 41 | 0.010329 | 0.0025887 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1213-12_0_5_load_27 | 42 | 0.0060171 | 0.001508 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1213-12_0_5_load_37 | 43 | 0.0048895 | 0.0012254 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1213-12_0_5_load_38 | 44 | 0.0031389 | 0.00078668 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1213-12_0_5_load_78 | 46 | 0.0026205 | 0.00065675 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1213-12_0_5_load_41 | 47 | 0.004904 | 0.001229 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1213-12_0_5_load_42 | 49 | 0.018375 | 0.0046052 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1213-12_0_5_load_77 | 50 | 0.0027868 | 0.00069844 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1213-12_0_5_load_46 | 51 | 0.0028531 | 0.00071505 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1213-12_0_5_load_43 | 52 | 0.0055246 | 0.0013846 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1213-12_0_5_load_76 | 53 | 0.014832 | 0.0037172 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1213-12_0_5_load_44 | 54 | 0.0038691 | 0.0009697 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1213-12_0_5_load_45 | 55 | 0.0032401 | 0.00081205 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1213-12_0_5_load_47 | 56 | 0.0045031 | 0.0011286 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1213-12_0_5_load_48 | 57 | 0.0031873 | 0.00079881 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1213-12_0_5_load_50 | 60 | 0.0046749 | 0.0011716 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1213-12_0_5_load_51 | 61 | 0.0029685 | 0.00074398 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1213-12_0_5_load_73 | 62 | 0.0034811 | 0.00087244 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1213-12_0_5_load_84 | 63 | 0.0049107 | 0.0012307 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1213-12_0_5_load_85 | 64 | 0.0023484 | 0.00058856 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1213-12_0_5_load_52 | 65 | 0.0083979 | 0.0021047 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1213-12_0_5_load_53 | 66 | 0.0061002 | 0.0015288 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1213-12_0_5_load_54 | 67 | 0.0055611 | 0.0013937 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1213-12_0_5_load_57 | 68 | 0.0057235 | 0.0014344 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1213-12_0_5_load_69 | 70 | 0.0036203 | 0.00090733 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1213-12_0_5_load_65 | 71 | 0.0042027 | 0.0010533 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1213-12_0_5_load_75 | 72 | 0.0026434 | 0.00066249 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1213-12_0_5_load_74 | 73 | 0.0034673 | 0.00086898 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1213-12_0_5_load_60 | 74 | 0.0050501 | 0.0012657 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1213-12_0_5_load_61 | 75 | 0.0031752 | 0.00079577 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1213-12_0_5_load_62 | 76 | 0.0035873 | 0.00089907 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1213-12_0_5_load_63 | 77 | 0.0042069 | 0.0010543 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1213-12_0_5_load_64 | 78 | 0.0033403 | 0.00083716 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1213-12_0_5_load_70 | 79 | 0.0017345 | 0.00043471 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1213-12_0_5_load_68 | 80 | 0.0053118 | 0.0013313 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1213-12_0_5_load_66 | 82 | 0.00426 | 0.0010677 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1213-12_0_5_load_125 | 83 | 0.0038344 | 0.00096099 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1213-12_0_5_load_124 | 84 | 0.0033998 | 0.00085207 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1213-12_0_5_load_79 | 85 | 0.0049287 | 0.0012352 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1213-12_0_5_load_80 | 86 | 0.0054249 | 0.0013596 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1213-12_0_5_load_81 | 87 | 0.0035212 | 0.0008825 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1213-12_0_5_load_82 | 88 | 0.0047887 | 0.0012002 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1213-12_0_5_load_83 | 89 | 0.01406 | 0.0035237 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1213-12_0_5_load_87 | 90 | 0.005565 | 0.0013947 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1213-12_0_5_load_86 | 91 | 0.0016295 | 0.00040839 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1213-12_0_5_load_92 | 93 | 0.0030355 | 0.00076077 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1213-12_0_5_load_89 | 94 | 0.0015787 | 0.00039565 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1213-12_0_5_load_96 | 95 | 0.0028556 | 0.00071569 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1213-12_0_5_load_90 | 96 | 0.0018935 | 0.00047457 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1213-12_0_5_load_93 | 98 | 0.0035378 | 0.00088666 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1213-12_0_5_load_94 | 99 | 0.0031873 | 0.0007988 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1213-12_0_5_load_95 | 100 | 0.0015408 | 0.00038616 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1213-12_0_5_load_99 | 101 | 0.0059987 | 0.0015034 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1213-12_0_5_load_97 | 104 | 0.0041181 | 0.0010321 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1213-12_0_5_load_100 | 105 | 0.0049128 | 0.0012313 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1213-12_0_5_load_103 | 106 | 0.0026137 | 0.00065504 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1213-12_0_5_load_128 | 107 | 0.0013989 | 0.0003506 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1213-12_0_5_load_98 | 108 | 0.0081747 | 0.0020488 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1213-12_0_5_load_101 | 109 | 0.0021232 | 0.00053214 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1213-12_0_5_load_108 | 110 | 0.0087274 | 0.0021873 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1213-12_0_5_load_105 | 112 | 0.004434 | 0.0011113 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1213-12_0_5_load_106 | 113 | 0.005292 | 0.0013263 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1213-12_0_5_load_107 | 114 | 0.0038581 | 0.00096693 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1213-12_0_5_load_109 | 115 | 0.0068863 | 0.0017259 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1213-12_0_5_load_110 | 116 | 0.0046928 | 0.0011761 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1213-12_0_5_load_111 | 117 | 0.0057992 | 0.0014534 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1213-12_0_5_load_118 | 118 | 0.0069416 | 0.0017397 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1213-12_0_5_load_117 | 119 | 0.0041363 | 0.0010366 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1213-12_0_5_load_112 | 120 | 0.0034524 | 0.00086525 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1213-12_0_5_load_113 | 121 | 0.0037417 | 0.00093776 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1213-12_0_5_load_114 | 122 | 0.0031364 | 0.00078605 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1213-12_0_5_load_116 | 123 | 0.0010318 | 0.00025859 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1213-12_0_5_load_119 | 124 | 0.0061463 | 0.0015404 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1213-12_0_5_load_120 | 125 | 0.011932 | 0.0029905 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1213-12_0_5_load_126 | 126 | 0.002788 | 0.00069874 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1213-12_0_5_load_127 | 127 | 0.0027398 | 0.00068667 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1213-12_0_5_load_129 | 128 | 0.0028385 | 0.0007114 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1213-12_0_5_load_131 | 129 | 0.0024934 | 0.00062491 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 60 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1213-12_0_5_line_0 |  | 0 | 1 | 0.0147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1213-12_0_5_line_1 |  | 1 | 2 | 0.010395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1213-12_0_5_line_2 |  | 2 | 6 | 0.0063585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1213-12_0_5_line_3 |  | 3 | 4 | 0.041712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1213-12_0_5_line_4 |  | 3 | 5 | 0.049312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1213-12_0_5_line_5 |  | 4 | 7 | 0.030598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1213-12_0_5_line_6 |  | 6 | 8 | 0.020301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1213-12_0_5_line_7 |  | 7 | 9 | 0.0092535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1213-12_0_5_line_8 |  | 8 | 11 | 0.047337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1213-12_0_5_line_9 |  | 8 | 12 | 0.015078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1213-12_0_5_line_10 |  | 8 | 10 | 0.019834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1213-12_0_5_line_11 |  | 9 | 43 | 0.013666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1213-12_0_5_line_12 |  | 9 | 44 | 0.016353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1213-12_0_5_line_13 |  | 11 | 13 | 0.04457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1213-12_0_5_line_14 |  | 12 | 14 | 0.026342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1213-12_0_5_line_15 |  | 13 | 15 | 0.012165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1213-12_0_5_line_16 |  | 14 | 16 | 0.02085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_1213-12_0_5_line_17 |  | 14 | 17 | 0.013964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1213-12_0_5_line_18 |  | 15 | 41 | 0.0047256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1213-12_0_5_line_19 |  | 16 | 45 | 0.018085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_1213-12_0_5_line_20 |  | 17 | 47 | 0.01297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1213-12_0_5_line_21 |  | 18 | 19 | 0.077412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1213-12_0_5_line_22 |  | 19 | 20 | 0.019184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1213-12_0_5_line_23 |  | 20 | 42 | 0.024783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1213-12_0_5_line_24 |  | 21 | 22 | 0.011727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1213-12_0_5_line_25 |  | 22 | 23 | 0.045431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1213-12_0_5_line_26 |  | 23 | 26 | 0.10751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1213-12_0_5_line_27 |  | 24 | 25 | 0.0013823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1213-12_0_5_line_28 |  | 25 | 121 | 0.0022267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1213-12_0_5_line_29 |  | 26 | 29 | 0.0072539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1213-12_0_5_line_30 |  | 27 | 28 | 0.0079054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1213-12_0_5_line_31 |  | 28 | 125 | 0.020996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1213-12_0_5_line_32 |  | 29 | 68 | 0.019814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1213-12_0_5_line_33 |  | 29 | 66 | 0.011873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1213-12_0_5_line_34 |  | 30 | 31 | 0.0047045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1213-12_0_5_line_35 |  | 30 | 32 | 0.044958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1213-12_0_5_line_36 |  | 31 | 33 | 0.034371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1213-12_0_5_line_37 |  | 33 | 34 | 0.020174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1213-12_0_5_line_38 |  | 34 | 35 | 0.018014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1213-12_0_5_line_39 |  | 35 | 36 | 0.0049287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1213-12_0_5_line_40 |  | 36 | 37 | 0.0096281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1213-12_0_5_line_41 |  | 37 | 38 | 0.00088965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1213-12_0_5_line_42 |  | 38 | 39 | 0.026375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1213-12_0_5_line_43 |  | 39 | 40 | 0.011464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1213-12_0_5_line_44 |  | 39 | 41 | 0.014302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1213-12_0_5_line_45 |  | 40 | 42 | 0.039533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1213-12_0_5_line_46 |  | 43 | 45 | 0.021108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1213-12_0_5_line_47 |  | 44 | 46 | 0.021377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1213-12_0_5_line_48 |  | 45 | 48 | 0.008522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_1213-12_0_5_line_49 |  | 46 | 50 | 0.019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1213-12_0_5_line_50 |  | 47 | 49 | 0.0045543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1213-12_0_5_line_51 |  | 48 | 51 | 0.0093688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1213-12_0_5_line_52 |  | 48 | 52 | 0.01909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_1213-12_0_5_line_53 |  | 51 | 53 | 0.029493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1213-12_0_5_line_54 |  | 52 | 54 | 0.017572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_1213-12_0_5_line_55 |  | 53 | 58 | 0.02282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1213-12_0_5_line_56 |  | 54 | 55 | 0.0032413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_1213-12_0_5_line_57 |  | 55 | 56 | 0.0032895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_1213-12_0_5_line_58 |  | 56 | 57 | 0.020237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_1213-12_0_5_line_59 |  | 57 | 59 | 0.011707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_1213-12_0_5_line_60 |  | 58 | 73 | 0.038179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1213-12_0_5_line_61 |  | 58 | 81 | 0.00977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1213-12_0_5_line_62 |  | 59 | 60 | 0.02068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_1213-12_0_5_line_63 |  | 59 | 61 | 0.0093194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_1213-12_0_5_line_64 |  | 60 | 62 | 0.0089958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1213-12_0_5_line_65 |  | 61 | 63 | 0.0097325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_1213-12_0_5_line_66 |  | 63 | 64 | 0.0010066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_1213-12_0_5_line_67 |  | 64 | 91 | 0.027588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_1213-12_0_5_line_68 |  | 65 | 66 | 0.017172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1213-12_0_5_line_69 |  | 65 | 67 | 0.014755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1213-12_0_5_line_70 |  | 68 | 69 | 0.014438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1213-12_0_5_line_71 |  | 69 | 70 | 0.0162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1213-12_0_5_line_72 |  | 69 | 71 | 0.0029264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1213-12_0_5_line_73 |  | 70 | 83 | 0.018107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1213-12_0_5_line_74 |  | 71 | 82 | 0.0014427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1213-12_0_5_line_75 |  | 72 | 73 | 0.030209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1213-12_0_5_line_76 |  | 74 | 75 | 0.0013784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1213-12_0_5_line_77 |  | 74 | 76 | 0.0068754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1213-12_0_5_line_78 |  | 75 | 77 | 0.0060027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1213-12_0_5_line_79 |  | 76 | 78 | 0.0041442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1213-12_0_5_line_80 |  | 77 | 79 | 0.010442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1213-12_0_5_line_81 |  | 78 | 80 | 0.0047031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1213-12_0_5_line_82 |  | 79 | 81 | 0.01839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1213-12_0_5_line_83 |  | 80 | 82 | 0.010426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1213-12_0_5_line_84 |  | 83 | 84 | 0.0054028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1213-12_0_5_line_85 |  | 84 | 123 | 0.017325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1213-12_0_5_line_86 |  | 85 | 86 | 0.013944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1213-12_0_5_line_87 |  | 85 | 87 | 0.018208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1213-12_0_5_line_88 |  | 86 | 88 | 0.019864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1213-12_0_5_line_89 |  | 87 | 89 | 0.0086308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1213-12_0_5_line_90 |  | 88 | 90 | 0.00019317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1213-12_0_5_line_91 |  | 90 | 91 | 0.019369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1213-12_0_5_line_92 |  | 91 | 92 | 0.022079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1213-12_0_5_line_93 |  | 92 | 93 | 0.023057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1213-12_0_5_line_94 |  | 92 | 94 | 0.0025028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1213-12_0_5_line_95 |  | 93 | 95 | 0.022182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1213-12_0_5_line_96 |  | 94 | 96 | 0.024718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1213-12_0_5_line_97 |  | 95 | 104 | 0.02133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1213-12_0_5_line_98 |  | 96 | 97 | 0.013393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1213-12_0_5_line_99 |  | 97 | 98 | 0.032729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1213-12_0_5_line_100 |  | 97 | 99 | 0.02141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1213-12_0_5_line_101 |  | 97 | 100 | 0.039366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1213-12_0_5_line_102 |  | 98 | 101 | 8.3243e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1213-12_0_5_line_103 |  | 99 | 102 | 0.032534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1213-12_0_5_line_104 |  | 100 | 103 | 0.021705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1213-12_0_5_line_105 |  | 101 | 105 | 0.018341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1213-12_0_5_line_106 |  | 102 | 106 | 0.05076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1213-12_0_5_line_107 |  | 103 | 107 | 0.012515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1213-12_0_5_line_108 |  | 104 | 108 | 0.010987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1213-12_0_5_line_109 |  | 105 | 109 | 0.00053552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1213-12_0_5_line_110 |  | 106 | 111 | 0.0035097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1213-12_0_5_line_111 |  | 107 | 126 | 0.022208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1213-12_0_5_line_112 |  | 109 | 110 | 0.01555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1213-12_0_5_line_113 |  | 111 | 112 | 0.021904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1213-12_0_5_line_114 |  | 112 | 113 | 0.024789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1213-12_0_5_line_115 |  | 113 | 114 | 0.0025074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1213-12_0_5_line_116 |  | 114 | 115 | 0.019403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1213-12_0_5_line_117 |  | 115 | 116 | 0.0025573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1213-12_0_5_line_118 |  | 116 | 117 | 0.025251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1213-12_0_5_line_119 |  | 117 | 118 | 0.00011071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1213-12_0_5_line_120 |  | 118 | 119 | 0.00072454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1213-12_0_5_line_121 |  | 119 | 124 | 0.022398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1213-12_0_5_line_122 |  | 120 | 121 | 0.019773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1213-12_0_5_line_123 |  | 120 | 122 | 0.00078872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1213-12_0_5_line_124 |  | 122 | 123 | 0.00035176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1213-12_0_5_line_125 |  | 124 | 125 | 0.0052032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1213-12_0_5_line_126 |  | 126 | 127 | 0.0069053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1213-12_0_5_line_127 |  | 127 | 128 | 0.018342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1213-12_0_5_line_128 |  | 128 | 129 | 0.0071496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1213-12_0_5_trafo_50 | 0.63 MVA 20/0.4 kV | 130 | 60 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2692443.648 | 1191668.9584 | 2692440.8808 | 1191655.7922 | 2692440.6243 | 1191654.5731
1 | 2692438.4844 | 1191644.401 | 2692440.6243 | 1191654.5731
2 | 2692437.1754 | 1191638.1787 | 2692438.4844 | 1191644.401
3 | 2692450.243 | 1191715.5752 | 2692462.8919 | 1191695.4132 | 2692472.4698 | 1191680.2784
4 | 2692450.243 | 1191715.5752 | 2692440.5897 | 1191715.5816 | 2692428.8906 | 1191710.3087 | 2692417.9814 | 1191696.8427 | 2692409.4302 | 1191692.7149
5 | 2692472.4698 | 1191680.2784 | 2692488.8323 | 1191654.4228
6 | 2692432.9961 | 1191618.313 | 2692437.1754 | 1191638.1787
7 | 2692493.7807 | 1191646.6035 | 2692488.8323 | 1191654.4228
8 | 2692432.9961 | 1191618.313 | 2692424.8218 | 1191571.6868
9 | 2692432.9961 | 1191618.313 | 2692448.0328 | 1191617.2017
10 | 2692432.9961 | 1191618.313 | 2692426.6311 | 1191616.2134 | 2692413.5513 | 1191617.3822
11 | 2692493.7807 | 1191646.6035 | 2692501.2809 | 1191635.1802
12 | 2692493.7807 | 1191646.6035 | 2692507.0188 | 1191656.2039
13 | 2692417.3471 | 1191527.7493 | 2692419.2055 | 1191539.6384 | 2692422.6881 | 1191559.5161 | 2692424.8218 | 1191571.6868
14 | 2692474.3028 | 1191615.2602 | 2692448.0328 | 1191617.2017
15 | 2692417.3471 | 1191527.7493 | 2692415.4684 | 1191515.73
16 | 2692474.3028 | 1191615.2602 | 2692495.1519 | 1191615.0821
17 | 2692474.3028 | 1191615.2602 | 2692474.6082 | 1191604.3801 | 2692473.7571 | 1191601.4209
18 | 2692414.7386 | 1191511.0611 | 2692415.4684 | 1191515.73
19 | 2692512.8659 | 1191617.5353 | 2692504.4107 | 1191615.003 | 2692495.1519 | 1191615.0821
20 | 2692473.7571 | 1191601.4209 | 2692470.1722 | 1191588.9563
21 | 2692387.7295 | 1191569.2048 | 2692314.4187 | 1191594.0675
22 | 2692387.7295 | 1191569.2048 | 2692384.4069 | 1191550.3111
23 | 2692380.1146 | 1191525.9022 | 2692384.4069 | 1191550.3111
24 | 2692795.2194 | 1191662.068 | 2692785.8329 | 1191655.0386
25 | 2692767.9587 | 1191697.5349 | 2692770.3888 | 1191697.1946 | 2692795.2194 | 1191662.068
26 | 2692669.577 | 1191654.1909 | 2692767.9587 | 1191697.5349
27 | 2692709.0031 | 1191571.029 | 2692707.9114 | 1191571.8768
28 | 2692706.1527 | 1191573.2426 | 2692707.9114 | 1191571.8768
29 | 2692665.0946 | 1191648.4878 | 2692669.577 | 1191654.1909
30 | 2692763.128 | 1191534.6267 | 2692768.8561 | 1191540.075
31 | 2692763.128 | 1191534.6267 | 2692747.9145 | 1191520.1566
32 | 2692665.0946 | 1191648.4878 | 2692653.2323 | 1191632.6172
33 | 2692665.0946 | 1191648.4878 | 2692659.6371 | 1191659.0326
34 | 2692396.518 | 1191378.9376 | 2692397.1074 | 1191383.605
35 | 2692396.518 | 1191378.9376 | 2692351.6445 | 1191381.6943
36 | 2692397.1074 | 1191383.605 | 2692401.4141 | 1191417.705
37 | 2692401.4141 | 1191417.705 | 2692403.9419 | 1191437.7202
38 | 2692406.199 | 1191455.5921 | 2692403.9419 | 1191437.7202
39 | 2692406.199 | 1191455.5921 | 2692406.7832 | 1191460.2179 | 2692406.8244 | 1191460.4809
40 | 2692408.3133 | 1191469.9932 | 2692406.8244 | 1191460.4809
41 | 2692408.3133 | 1191469.9932 | 2692408.4509 | 1191470.8721
42 | 2692412.5298 | 1191496.9302 | 2692408.4509 | 1191470.8721
43 | 2692412.5298 | 1191496.9302 | 2692402.1833 | 1191501.8661
44 | 2692412.5298 | 1191496.9302 | 2692414.7386 | 1191511.0611
45 | 2692402.1833 | 1191501.8661 | 2692377.923 | 1191513.4399 | 2692380.1146 | 1191525.9022
46 | 2692512.8659 | 1191617.5353 | 2692501.2809 | 1191635.1802
47 | 2692507.0188 | 1191656.2039 | 2692524.3238 | 1191668.7535
48 | 2692516.7501 | 1191609.946 | 2692512.8659 | 1191617.5353
49 | 2692539.7045 | 1191679.9077 | 2692524.3238 | 1191668.7535
50 | 2692468.9134 | 1191584.5794 | 2692470.1722 | 1191588.9563
51 | 2692516.7501 | 1191609.946 | 2692522.4811 | 1191611.6246 | 2692525.7409 | 1191612.5806
52 | 2692516.7501 | 1191609.946 | 2692525.8961 | 1191593.1901
53 | 2692555.0804 | 1191614.9405 | 2692528.2045 | 1191613.303 | 2692525.7409 | 1191612.5806
54 | 2692525.8961 | 1191593.1901 | 2692534.315 | 1191577.7661
55 | 2692577.8582 | 1191616.3283 | 2692555.0804 | 1191614.9405
56 | 2692535.8679 | 1191574.921 | 2692534.315 | 1191577.7661
57 | 2692535.8679 | 1191574.921 | 2692537.444 | 1191572.0336
58 | 2692547.1393 | 1191554.27 | 2692545.1425 | 1191557.9293 | 2692537.444 | 1191572.0336
59 | 2692552.747 | 1191543.9935 | 2692547.1393 | 1191554.27
60 | 2692577.8582 | 1191616.3283 | 2692573.3128 | 1191648.9012 | 2692574.4538 | 1191654.0676
61 | 2692581.9984 | 1191607.4756 | 2692577.8582 | 1191616.3283
62 | 2692552.747 | 1191543.9935 | 2692564.6664 | 1191549.826 | 2692569.3355 | 1191555.5797
63 | 2692552.747 | 1191543.9935 | 2692556.9394 | 1191535.6704
64 | 2692569.3355 | 1191555.5797 | 2692569.3355 | 1191555.5797 | 2692570.7638 | 1191564.4614
65 | 2692561.3183 | 1191526.9786 | 2692557.9706 | 1191533.6232 | 2692556.9394 | 1191535.6704
66 | 2692561.3183 | 1191526.9786 | 2692561.7712 | 1191526.0796
67 | 2692574.1842 | 1191501.4421 | 2692561.7712 | 1191526.0796
68 | 2692651.7443 | 1191674.2829 | 2692659.6371 | 1191659.0326
69 | 2692651.7443 | 1191674.2829 | 2692650.498 | 1191676.6911 | 2692643.4761 | 1191686.4754
70 | 2692644.5886 | 1191621.0527 | 2692653.2323 | 1191632.6172
71 | 2692644.5886 | 1191621.0527 | 2692657.3839 | 1191611.1161
72 | 2692644.5886 | 1191621.0527 | 2692642.3848 | 1191619.1274
73 | 2692671.6846 | 1191600.0103 | 2692657.3839 | 1191611.1161
74 | 2692642.3848 | 1191619.1274 | 2692641.2984 | 1191618.1782
75 | 2692574.4538 | 1191654.0676 | 2692575.0301 | 1191656.6772 | 2692578.5512 | 1191667.1272 | 2692581.6067 | 1191683.3516
76 | 2692617.7252 | 1191611.1141 | 2692616.3469 | 1191611.0961
77 | 2692617.7252 | 1191611.1141 | 2692624.6 | 1191611.2034
78 | 2692610.3447 | 1191611.0181 | 2692616.3469 | 1191611.0961
79 | 2692624.6 | 1191611.2034 | 2692628.7439 | 1191611.2573
80 | 2692599.9034 | 1191610.8824 | 2692610.3447 | 1191611.0181
81 | 2692633.4466 | 1191611.3185 | 2692628.7439 | 1191611.2573
82 | 2692581.9984 | 1191607.4756 | 2692593.1254 | 1191610.7942 | 2692599.9034 | 1191610.8824
83 | 2692633.4466 | 1191611.3185 | 2692633.4466 | 1191611.3185 | 2692641.2984 | 1191618.1782
84 | 2692675.9517 | 1191596.6964 | 2692671.6846 | 1191600.0103
85 | 2692689.6349 | 1191586.0702 | 2692675.9517 | 1191596.6964
86 | 2692623.9309 | 1191520.7679 | 2692610.8955 | 1191515.8176
87 | 2692623.9309 | 1191520.7679 | 2692640.9529 | 1191527.2322
88 | 2692592.3989 | 1191508.5761 | 2692610.6558 | 1191515.7266 | 2692610.8955 | 1191515.8176
89 | 2692649.0215 | 1191530.2963 | 2692640.9529 | 1191527.2322
90 | 2692592.3989 | 1191508.5761 | 2692592.219 | 1191508.5057
91 | 2692574.1842 | 1191501.4421 | 2692592.219 | 1191508.5057
92 | 2692583.0906 | 1191481.2336 | 2692574.1842 | 1191501.4421
93 | 2692583.0906 | 1191481.2336 | 2692603.3599 | 1191492.2227
94 | 2692583.0906 | 1191481.2336 | 2692584.244 | 1191479.0123
95 | 2692603.3599 | 1191492.2227 | 2692610.9559 | 1191496.341 | 2692623.4735 | 1191501.5053
96 | 2692584.244 | 1191479.0123 | 2692592.1449 | 1191463.7957 | 2692595.1254 | 1191456.834
97 | 2692623.4735 | 1191501.5053 | 2692643.1915 | 1191509.6402
98 | 2692600.3964 | 1191444.5221 | 2692595.1254 | 1191456.834
99 | 2692600.3964 | 1191444.5221 | 2692628.4788 | 1191461.3315
100 | 2692600.3964 | 1191444.5221 | 2692608.821 | 1191424.8396
101 | 2692600.3964 | 1191444.5221 | 2692573.2183 | 1191416.0436
102 | 2692628.5502 | 1191461.3743 | 2692628.4788 | 1191461.3315
103 | 2692621.6231 | 1191394.9298 | 2692608.821 | 1191424.8396
104 | 2692558.2333 | 1191400.3416 | 2692573.2183 | 1191416.0436
105 | 2692628.5502 | 1191461.3743 | 2692633.3073 | 1191464.2218 | 2692635.195 | 1191469.3654 | 2692638.308 | 1191475.9874
106 | 2692621.6231 | 1191394.9298 | 2692642.7972 | 1191407.3432 | 2692658.5522 | 1191428.2965
107 | 2692558.2333 | 1191400.3416 | 2692551.9976 | 1191411.1924
108 | 2692653.3484 | 1191513.8305 | 2692643.1915 | 1191509.6402
109 | 2692638.5359 | 1191476.472 | 2692638.308 | 1191475.9874
110 | 2692660.6614 | 1191431.1017 | 2692658.5522 | 1191428.2965
111 | 2692540.9319 | 1191430.4477 | 2692551.9976 | 1191411.1924
112 | 2692648.3161 | 1191488.2028 | 2692640.8866 | 1191481.4724 | 2692638.5359 | 1191476.472
113 | 2692660.6614 | 1191431.1017 | 2692674.7112 | 1191447.9067
114 | 2692674.7112 | 1191447.9067 | 2692685.4197 | 1191460.7151 | 2692691.2846 | 1191466.2935
115 | 2692693.1015 | 1191468.0216 | 2692691.2846 | 1191466.2935
116 | 2692693.1015 | 1191468.0216 | 2692707.1605 | 1191481.3938
117 | 2692709.0136 | 1191483.1563 | 2692707.1605 | 1191481.3938
118 | 2692709.0136 | 1191483.1563 | 2692727.3101 | 1191500.5589
119 | 2692727.3904 | 1191500.6352 | 2692727.3101 | 1191500.5589
120 | 2692727.9153 | 1191501.1345 | 2692727.3904 | 1191500.6352
121 | 2692744.1444 | 1191516.5706 | 2692727.9153 | 1191501.1345
122 | 2692690.5356 | 1191585.3707 | 2692706.1527 | 1191573.2426
123 | 2692689.9127 | 1191585.8545 | 2692690.5356 | 1191585.3707
124 | 2692689.6349 | 1191586.0702 | 2692689.9127 | 1191585.8545
125 | 2692744.1444 | 1191516.5706 | 2692747.9145 | 1191520.1566
126 | 2692540.9319 | 1191430.4477 | 2692537.4912 | 1191436.4348
127 | 2692528.3519 | 1191452.3381 | 2692537.4912 | 1191436.4348
128 | 2692528.3519 | 1191452.3381 | 2692524.7895 | 1191458.537

## bus_geodata
| x | y | coords
0 | 2692443.648 | 1191668.9584
1 | 2692440.6243 | 1191654.5731
2 | 2692438.4844 | 1191644.401
3 | 2692450.243 | 1191715.5752
4 | 2692472.4698 | 1191680.2784
5 | 2692409.4302 | 1191692.7149
6 | 2692437.1754 | 1191638.1787
7 | 2692488.8323 | 1191654.4228
8 | 2692432.9961 | 1191618.313
9 | 2692493.7807 | 1191646.6035
10 | 2692413.5513 | 1191617.3822
11 | 2692424.8218 | 1191571.6868
12 | 2692448.0328 | 1191617.2017
13 | 2692417.3471 | 1191527.7493
14 | 2692474.3028 | 1191615.2602
15 | 2692415.4684 | 1191515.73
16 | 2692495.1519 | 1191615.0821
17 | 2692473.7571 | 1191601.4209
18 | 2692314.4187 | 1191594.0675
19 | 2692387.7295 | 1191569.2048
20 | 2692384.4069 | 1191550.3111
21 | 2692785.8329 | 1191655.0386
22 | 2692795.2194 | 1191662.068
23 | 2692767.9587 | 1191697.5349
24 | 2692709.0031 | 1191571.029
25 | 2692707.9114 | 1191571.8768
26 | 2692669.577 | 1191654.1909
27 | 2692768.8561 | 1191540.075
28 | 2692763.128 | 1191534.6267
29 | 2692665.0946 | 1191648.4878
30 | 2692396.518 | 1191378.9376
31 | 2692397.1074 | 1191383.605
32 | 2692351.6445 | 1191381.6943
33 | 2692401.4141 | 1191417.705
34 | 2692403.9419 | 1191437.7202
35 | 2692406.199 | 1191455.5921
36 | 2692406.8244 | 1191460.4809
37 | 2692408.3133 | 1191469.9932
38 | 2692408.4509 | 1191470.8721
39 | 2692412.5298 | 1191496.9302
40 | 2692402.1833 | 1191501.8661
41 | 2692414.7386 | 1191511.0611
42 | 2692380.1146 | 1191525.9022
43 | 2692501.2809 | 1191635.1802
44 | 2692507.0188 | 1191656.2039
45 | 2692512.8659 | 1191617.5353
46 | 2692524.3238 | 1191668.7535
47 | 2692470.1722 | 1191588.9563
48 | 2692516.7501 | 1191609.946
49 | 2692468.9134 | 1191584.5794
50 | 2692539.7045 | 1191679.9077
51 | 2692525.7409 | 1191612.5806
52 | 2692525.8961 | 1191593.1901
53 | 2692555.0804 | 1191614.9405
54 | 2692534.315 | 1191577.7661
55 | 2692535.8679 | 1191574.921
56 | 2692537.444 | 1191572.0336
57 | 2692547.1393 | 1191554.27
58 | 2692577.8582 | 1191616.3283
59 | 2692552.747 | 1191543.9935
60 | 2692569.3355 | 1191555.5797
61 | 2692556.9394 | 1191535.6704
62 | 2692570.7638 | 1191564.4614
63 | 2692561.3183 | 1191526.9786
64 | 2692561.7712 | 1191526.0796
65 | 2692651.7443 | 1191674.2829
66 | 2692659.6371 | 1191659.0326
67 | 2692643.4761 | 1191686.4754
68 | 2692653.2323 | 1191632.6172
69 | 2692644.5886 | 1191621.0527
70 | 2692657.3839 | 1191611.1161
71 | 2692642.3848 | 1191619.1274
72 | 2692581.6067 | 1191683.3516
73 | 2692574.4538 | 1191654.0676
74 | 2692617.7252 | 1191611.1141
75 | 2692616.3469 | 1191611.0961
76 | 2692624.6 | 1191611.2034
77 | 2692610.3447 | 1191611.0181
78 | 2692628.7439 | 1191611.2573
79 | 2692599.9034 | 1191610.8824
80 | 2692633.4466 | 1191611.3185
81 | 2692581.9984 | 1191607.4756
82 | 2692641.2984 | 1191618.1782
83 | 2692671.6846 | 1191600.0103
84 | 2692675.9517 | 1191596.6964
85 | 2692623.9309 | 1191520.7679
86 | 2692610.8955 | 1191515.8176
87 | 2692640.9529 | 1191527.2322
88 | 2692592.3989 | 1191508.5761
89 | 2692649.0215 | 1191530.2963
90 | 2692592.219 | 1191508.5057
91 | 2692574.1842 | 1191501.4421
92 | 2692583.0906 | 1191481.2336
93 | 2692603.3599 | 1191492.2227
94 | 2692584.244 | 1191479.0123
95 | 2692623.4735 | 1191501.5053
96 | 2692595.1254 | 1191456.834
97 | 2692600.3964 | 1191444.5221
98 | 2692628.4788 | 1191461.3315
99 | 2692608.821 | 1191424.8396
100 | 2692573.2183 | 1191416.0436
101 | 2692628.5502 | 1191461.3743
102 | 2692621.6231 | 1191394.9298
103 | 2692558.2333 | 1191400.3416
104 | 2692643.1915 | 1191509.6402
105 | 2692638.308 | 1191475.9874
106 | 2692658.5522 | 1191428.2965
107 | 2692551.9976 | 1191411.1924
108 | 2692653.3484 | 1191513.8305
109 | 2692638.5359 | 1191476.472
110 | 2692648.3161 | 1191488.2028
111 | 2692660.6614 | 1191431.1017
112 | 2692674.7112 | 1191447.9067
113 | 2692691.2846 | 1191466.2935
114 | 2692693.1015 | 1191468.0216
115 | 2692707.1605 | 1191481.3938
116 | 2692709.0136 | 1191483.1563
117 | 2692727.3101 | 1191500.5589
118 | 2692727.3904 | 1191500.6352
119 | 2692727.9153 | 1191501.1345
120 | 2692690.5356 | 1191585.3707
121 | 2692706.1527 | 1191573.2426
122 | 2692689.9127 | 1191585.8545
123 | 2692689.6349 | 1191586.0702
124 | 2692744.1444 | 1191516.5706
125 | 2692747.9145 | 1191520.1566
126 | 2692540.9319 | 1191430.4477
127 | 2692537.4912 | 1191436.4348
128 | 2692528.3519 | 1191452.3381
129 | 2692524.7895 | 1191458.537
130 | 2692552.747 | 1191543.9935

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9845 | -0.29652 | 0.0094872 | 0.0023777
1 | 0.98462 | -0.29401 | 0.0033703 | 0.00084467
2 | 0.98475 | -0.29161 | 0.0035795 | 0.0008971
3 | 0.99005 | -0.18972 | 0 | 0
4 | 0.99036 | -0.18367 | 0.0028081 | 0.00070377
5 | 0.98968 | -0.19687 | 0.0081531 | 0.0020434
6 | 0.98484 | -0.28973 | 0.002549 | 0.00063884
7 | 0.99067 | -0.17771 | 0.0027698 | 0.00069419
8 | 0.9852 | -0.28281 | 0 | 0
9 | 0.99078 | -0.17545 | 0 | 0
10 | 0.98505 | -0.28573 | 0.0082113 | 0.002058
11 | 0.98149 | -0.35478 | 0.0058652 | 0.00147
12 | 0.98676 | -0.25265 | 0.0042225 | 0.0010583
13 | 0.97823 | -0.41828 | 0.0048595 | 0.0012179
14 | 0.98959 | -0.19822 | 0 | 0
15 | 0.9774 | -0.43461 | 0.0061106 | 0.0015315
16 | 0.99097 | -0.17169 | 0.0040506 | 0.0010152
17 | 0.98924 | -0.20504 | 0.0041458 | 0.001039
18 | 0.97348 | -0.51189 | 0.0081251 | 0.0020363
19 | 0.97406 | -0.50033 | 0.0078256 | 0.0019613
20 | 0.97435 | -0.49471 | 0.0079157 | 0.0019839
21 | 0.97425 | -0.49663 | 0.010856 | 0.0027208
22 | 0.97437 | -0.49429 | 0 | 0
23 | 0.97483 | -0.48524 | 0 | 0
24 | 0.9751 | -0.47979 | 0.011338 | 0.0028416
25 | 0.97512 | -0.47951 | 0.0036286 | 0.00090941
26 | 0.97591 | -0.46385 | 0.0043701 | 0.0010953
27 | 0.97318 | -0.51758 | 0.0055472 | 0.0013903
28 | 0.97322 | -0.51678 | 0.0058636 | 0.0014696
29 | 0.97601 | -0.46183 | 0 | 0
30 | 0.97473 | -0.48715 | 0.0034774 | 0.00087151
31 | 0.97476 | -0.48667 | 0.00224 | 0.0005614
32 | 0.97465 | -0.48884 | 0.0020517 | 0.0005142
33 | 0.975 | -0.48177 | 0.003604 | 0.00090325
34 | 0.97522 | -0.47756 | 0.002908 | 0.00072881
35 | 0.97546 | -0.47285 | 0.0039583 | 0.00099204
36 | 0.97554 | -0.4712 | 0.0020814 | 0.00052164
37 | 0.97572 | -0.46762 | 0.0025643 | 0.00064266
38 | 0.97574 | -0.46725 | 0.0017079 | 0.00042804
39 | 0.97634 | -0.45538 | 0 | 0
40 | 0.976 | -0.46221 | 0.0026971 | 0.00067595
41 | 0.97711 | -0.44043 | 0.010329 | 0.0025887
42 | 0.9749 | -0.48385 | 0.0060171 | 0.001508
43 | 0.99106 | -0.17005 | 0.0048895 | 0.0012254
44 | 0.99065 | -0.17794 | 0.0031389 | 0.00078668
45 | 0.99159 | -0.15988 | 0 | 0
46 | 0.99055 | -0.17999 | 0.0026205 | 0.00065675
47 | 0.98896 | -0.21042 | 0.004904 | 0.001229
48 | 0.99193 | -0.15329 | 0 | 0
49 | 0.98888 | -0.21191 | 0.018375 | 0.0046052
50 | 0.9905 | -0.18093 | 0.0027868 | 0.00069844
51 | 0.99074 | -0.17603 | 0.0028531 | 0.00071505
52 | 0.9933 | -0.12701 | 0.0055246 | 0.0013846
53 | 0.98707 | -0.24648 | 0.014832 | 0.0037172
54 | 0.99459 | -0.10245 | 0.0038691 | 0.0009697
55 | 0.99483 | -0.097876 | 0.0032401 | 0.00081205
56 | 0.99508 | -0.093186 | 0.0045031 | 0.0011286
57 | 0.99662 | -0.063981 | 0.0031873 | 0.00079881
58 | 0.98455 | -0.29526 | 0 | 0
59 | 0.99752 | -0.046964 | 0 | 0
60 | 1 | 0 | -0.53349 | -0.13659
61 | 0.99711 | -0.05465 | 0.0029685 | 0.00074398
62 | 0.99997 | -0.00054584 | 0.0034811 | 0.00087244
63 | 0.99669 | -0.062557 | 0.0049107 | 0.0012307
64 | 0.99665 | -0.063353 | 0.0023484 | 0.00058856
65 | 0.97557 | -0.47058 | 0.0083979 | 0.0021047
66 | 0.97579 | -0.46619 | 0.0061002 | 0.0015288
67 | 0.97549 | -0.47208 | 0.0055611 | 0.0013937
68 | 0.97666 | -0.44905 | 0.0057235 | 0.0014344
69 | 0.97721 | -0.43823 | 0 | 0
70 | 0.97665 | -0.44923 | 0.0036203 | 0.00090733
71 | 0.97743 | -0.43406 | 0.0042027 | 0.0010533
72 | 0.98426 | -0.30089 | 0.0026434 | 0.00066249
73 | 0.98433 | -0.29946 | 0.0034673 | 0.00086898
74 | 0.97978 | -0.38801 | 0.0050501 | 0.0012657
75 | 0.97991 | -0.38541 | 0.0031752 | 0.00079577
76 | 0.97915 | -0.40036 | 0.0035873 | 0.00089907
77 | 0.98051 | -0.37374 | 0.0042069 | 0.0010543
78 | 0.97878 | -0.40755 | 0.0033403 | 0.00083716
79 | 0.98159 | -0.35269 | 0.0017345 | 0.00043471
80 | 0.97838 | -0.41542 | 0.0053118 | 0.0013313
81 | 0.98352 | -0.31515 | 0 | 0
82 | 0.97754 | -0.43189 | 0.00426 | 0.0010677
83 | 0.97609 | -0.46034 | 0.0038344 | 0.00096099
84 | 0.97594 | -0.46328 | 0.0033998 | 0.00085207
85 | 0.99291 | -0.13508 | 0.0049287 | 0.0012352
86 | 0.9932 | -0.12953 | 0.0054249 | 0.0013596
87 | 0.99262 | -0.14074 | 0.0035212 | 0.0008825
88 | 0.9937 | -0.11973 | 0.0047887 | 0.0012002
89 | 0.99251 | -0.14289 | 0.01406 | 0.0035237
90 | 0.99371 | -0.11962 | 0.005565 | 0.0013947
91 | 0.99439 | -0.10654 | 0.0016295 | 0.00040839
92 | 0.99156 | -0.16044 | 0 | 0
93 | 0.99118 | -0.16788 | 0.0030355 | 0.00076077
94 | 0.99129 | -0.16576 | 0.0015787 | 0.00039565
95 | 0.99087 | -0.17384 | 0.0028556 | 0.00071569
96 | 0.98857 | -0.21779 | 0.0018935 | 0.00047457
97 | 0.98713 | -0.24564 | 0 | 0
98 | 0.98637 | -0.26047 | 0.0035378 | 0.00088666
99 | 0.98559 | -0.27531 | 0.0031873 | 0.0007988
100 | 0.98663 | -0.25537 | 0.0015408 | 0.00038616
101 | 0.98637 | -0.2605 | 0.0059987 | 0.0015034
102 | 0.98334 | -0.31869 | 0 | 0
103 | 0.98638 | -0.26013 | 0 | 0
104 | 0.99063 | -0.1785 | 0.0041181 | 0.0010321
105 | 0.9861 | -0.26568 | 0.0049128 | 0.0012313
106 | 0.97984 | -0.38678 | 0.0026137 | 0.00065504
107 | 0.98624 | -0.26288 | 0.0013989 | 0.0003506
108 | 0.99055 | -0.18009 | 0.0081747 | 0.0020488
109 | 0.98609 | -0.26578 | 0.0021232 | 0.00053214
110 | 0.98597 | -0.26822 | 0.0087274 | 0.0021873
111 | 0.97961 | -0.39134 | 0 | 0
112 | 0.97815 | -0.41984 | 0.004434 | 0.0011113
113 | 0.9766 | -0.45019 | 0.005292 | 0.0013263
114 | 0.97646 | -0.45302 | 0.0038581 | 0.00096693
115 | 0.97541 | -0.47359 | 0.0068863 | 0.0017259
116 | 0.97529 | -0.47599 | 0.0046928 | 0.0011761
117 | 0.9742 | -0.49747 | 0.0057992 | 0.0014534
118 | 0.97419 | -0.49755 | 0.0069416 | 0.0017397
119 | 0.97417 | -0.498 | 0.0041363 | 0.0010366
120 | 0.97549 | -0.47212 | 0.0034524 | 0.00086525
121 | 0.97515 | -0.4789 | 0.0037417 | 0.00093776
122 | 0.97551 | -0.4718 | 0.0031364 | 0.00078605
123 | 0.97552 | -0.47163 | 0.0010318 | 0.00025859
124 | 0.97355 | -0.51013 | 0.0061463 | 0.0015404
125 | 0.97344 | -0.51237 | 0.011932 | 0.0029905
126 | 0.98602 | -0.26721 | 0.002788 | 0.00069874
127 | 0.98597 | -0.26821 | 0.0027398 | 0.00068667
128 | 0.98588 | -0.26996 | 0.0028385 | 0.0007114
129 | 0.98586 | -0.27028 | 0.0024934 | 0.00062491
130 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0094872 | -0.0023777 | 0.0094883 | 0.0023782 | 1.1334e-06 | 5.3846e-07 | 0.014339 | 0.014339 | 0.014339 | 0.9845 | -0.29652 | 0.98462 | -0.29401 | 3.9394
1 | -0.012859 | -0.0032229 | 0.01286 | 0.0032237 | 1.472e-06 | 8.0985e-07 | 0.019433 | 0.019433 | 0.019433 | 0.98462 | -0.29401 | 0.98475 | -0.29161 | 5.3386
2 | -0.016439 | -0.0041208 | 0.016441 | 0.0041217 | 1.4714e-06 | 8.6081e-07 | 0.024841 | 0.024841 | 0.024841 | 0.98475 | -0.29161 | 0.98484 | -0.28973 | 6.8246
3 | -0.0081559 | -0.0020445 | 0.0081582 | 0.0020455 | 2.3504e-06 | 9.677e-07 | 0.012258 | 0.012258 | 0.012258 | 0.99005 | -0.18972 | 0.99036 | -0.18367 | 3.3676
4 | 0.0081559 | 0.0020445 | -0.0081531 | -0.0020434 | 2.7787e-06 | 1.1445e-06 | 0.012258 | 0.012258 | 0.012258 | 0.99005 | -0.18972 | 0.98968 | -0.19687 | 3.3677
5 | -0.010966 | -0.0027492 | 0.010969 | 0.0027508 | 3.1152e-06 | 1.5999e-06 | 0.016477 | 0.016477 | 0.016477 | 0.99036 | -0.18367 | 0.99067 | -0.17771 | 4.5267
6 | -0.01899 | -0.0047605 | 0.018996 | 0.0047643 | 6.2673e-06 | 3.7526e-06 | 0.028693 | 0.028693 | 0.028693 | 0.98484 | -0.28973 | 0.9852 | -0.28281 | 7.8826
7 | -0.013739 | -0.003445 | 0.013741 | 0.0034459 | 1.4779e-06 | 8.267e-07 | 0.020637 | 0.020637 | 0.020637 | 0.99067 | -0.17771 | 0.99078 | -0.17545 | 5.6696
8 | 0.085077 | 0.021605 | -0.084784 | -0.021417 | 0.00029357 | 0.00018729 | 0.1286 | 0.1286 | 0.1286 | 0.9852 | -0.28281 | 0.98149 | -0.35478 | 35.3296
9 | -0.11229 | -0.028427 | 0.11245 | 0.028531 | 0.00016282 | 0.00010401 | 0.1697 | 0.1697 | 0.1697 | 0.9852 | -0.28281 | 0.98676 | -0.25265 | 46.6198
10 | 0.0082125 | 0.0020584 | -0.0082113 | -0.002058 | 1.1444e-06 | 4.7988e-07 | 0.012404 | 0.012404 | 0.012404 | 0.9852 | -0.28281 | 0.98505 | -0.28573 | 3.4077
11 | -0.022289 | -0.0055881 | 0.022294 | 0.0055916 | 5.7425e-06 | 3.4991e-06 | 0.033475 | 0.033475 | 0.033475 | 0.99078 | -0.17545 | 0.99106 | -0.17005 | 9.1964
12 | 0.0085478 | 0.0021422 | -0.0085468 | -0.0021418 | 1.0106e-06 | 4.3624e-07 | 0.012838 | 0.012838 | 0.012838 | 0.99078 | -0.17545 | 0.99065 | -0.17794 | 3.5268
13 | 0.078919 | 0.019947 | -0.078679 | -0.019795 | 0.00023951 | 0.00015272 | 0.11971 | 0.11971 | 0.11971 | 0.98149 | -0.35478 | 0.97823 | -0.41828 | 32.8868
14 | -0.11667 | -0.02959 | 0.11698 | 0.029785 | 0.0003062 | 0.00019563 | 0.17606 | 0.17606 | 0.17606 | 0.98676 | -0.25265 | 0.98959 | -0.19822 | 48.3691
15 | 0.07382 | 0.018577 | -0.073762 | -0.01854 | 5.7549e-05 | 3.6679e-05 | 0.11232 | 0.11232 | 0.11232 | 0.97823 | -0.41828 | 0.9774 | -0.43461 | 30.8561
16 | -0.14442 | -0.036669 | 0.1446 | 0.036786 | 0.00018464 | 0.00011763 | 0.21733 | 0.21733 | 0.21733 | 0.98959 | -0.19822 | 0.99097 | -0.17169 | 29.8526
17 | 0.027441 | 0.0068832 | -0.027432 | -0.0068777 | 8.916e-06 | 5.5269e-06 | 0.041264 | 0.041264 | 0.041264 | 0.98959 | -0.19822 | 0.98924 | -0.20504 | 11.3363
18 | 0.067652 | 0.017009 | -0.067633 | -0.016997 | 1.8805e-05 | 1.1976e-05 | 0.10301 | 0.10301 | 0.10301 | 0.9774 | -0.43461 | 0.97711 | -0.44043 | 28.3003
19 | -0.14865 | -0.037801 | 0.14874 | 0.037855 | 8.4625e-05 | 5.3228e-05 | 0.22341 | 0.22341 | 0.22341 | 0.99097 | -0.17169 | 0.99159 | -0.15988 | 15.344
20 | 0.023286 | 0.0058387 | -0.02328 | -0.005835 | 5.9676e-06 | 3.6528e-06 | 0.035028 | 0.035028 | 0.035028 | 0.98924 | -0.20504 | 0.98896 | -0.21042 | 9.6231
21 | -0.0081251 | -0.0020363 | 0.0081296 | 0.0020382 | 4.4776e-06 | 1.9027e-06 | 0.01242 | 0.012419 | 0.01242 | 0.97348 | -0.51189 | 0.97406 | -0.50033 | 3.412
22 | -0.015955 | -0.0039995 | 0.015959 | 0.004002 | 4.2738e-06 | 2.4964e-06 | 0.024374 | 0.024374 | 0.024374 | 0.97406 | -0.50033 | 0.97435 | -0.49471 | 6.6962
23 | -0.023875 | -0.0059859 | 0.023888 | 0.0059935 | 1.2356e-05 | 7.5992e-06 | 0.036463 | 0.036463 | 0.036463 | 0.97435 | -0.49471 | 0.9749 | -0.48385 | 10.0173
24 | -0.010856 | -0.0027208 | 0.010857 | 0.0027214 | 1.209e-06 | 6.2771e-07 | 0.016581 | 0.016581 | 0.016581 | 0.97425 | -0.49663 | 0.97437 | -0.49429 | 4.5552
25 | -0.010857 | -0.0027214 | 0.010862 | 0.0027238 | 4.6837e-06 | 2.4314e-06 | 0.016581 | 0.016581 | 0.016581 | 0.97437 | -0.49429 | 0.97483 | -0.48524 | 4.5551
26 | -0.010862 | -0.0027238 | 0.010873 | 0.0027296 | 1.1083e-05 | 5.7512e-06 | 0.016581 | 0.01658 | 0.016581 | 0.97483 | -0.48524 | 0.97591 | -0.46385 | 4.5551
27 | -0.011338 | -0.0028416 | 0.011338 | 0.0028417 | 1.5517e-07 | 8.2067e-08 | 0.017302 | 0.017302 | 0.017302 | 0.9751 | -0.47979 | 0.97512 | -0.47951 | 4.7533
28 | -0.014967 | -0.0037511 | 0.014967 | 0.0037513 | 4.3557e-07 | 2.5098e-07 | 0.022839 | 0.022839 | 0.022839 | 0.97512 | -0.47951 | 0.97515 | -0.4789 | 6.2745
29 | -0.015243 | -0.0038248 | 0.015244 | 0.0038257 | 1.4696e-06 | 8.4989e-07 | 0.023243 | 0.023243 | 0.023243 | 0.97591 | -0.46385 | 0.97601 | -0.46183 | 6.3855
30 | -0.0055472 | -0.0013903 | 0.0055474 | 0.0013903 | 2.1327e-07 | 3.8266e-08 | 0.0084819 | 0.0084818 | 0.0084819 | 0.97318 | -0.51758 | 0.97322 | -0.51678 | 2.3302
31 | -0.011411 | -0.0028599 | 0.011413 | 0.0028611 | 2.3967e-06 | 1.2729e-06 | 0.017447 | 0.017447 | 0.017447 | 0.97322 | -0.51678 | 0.97344 | -0.51237 | 4.7932
32 | -0.035311 | -0.0088572 | 0.035333 | 0.0088707 | 2.1536e-05 | 1.3535e-05 | 0.053837 | 0.053837 | 0.053837 | 0.97601 | -0.46183 | 0.97666 | -0.44905 | 14.7905
33 | 0.020067 | 0.0050315 | -0.020062 | -0.005029 | 4.1676e-06 | 2.5189e-06 | 0.030594 | 0.030594 | 0.030594 | 0.97601 | -0.46183 | 0.97579 | -0.46619 | 8.405
34 | -0.0055292 | -0.0013853 | 0.0055293 | 0.0013853 | 1.2569e-07 | 2.1799e-08 | 0.0084407 | 0.0084406 | 0.0084407 | 0.97473 | -0.48715 | 0.97476 | -0.48667 | 2.3189
35 | 0.0020518 | 0.00051375 | -0.0020517 | -0.0005142 | 1.6541e-07 | -4.5448e-07 | 0.0031321 | 0.0031323 | 0.0031323 | 0.97473 | -0.48715 | 0.97465 | -0.48884 | 0.86054
36 | -0.0077694 | -0.0019467 | 0.0077712 | 0.0019474 | 1.813e-06 | 7.3176e-07 | 0.01186 | 0.01186 | 0.01186 | 0.97476 | -0.48667 | 0.975 | -0.48177 | 3.2583
37 | -0.011375 | -0.0028507 | 0.011377 | 0.0028519 | 2.28e-06 | 1.2076e-06 | 0.01736 | 0.01736 | 0.01736 | 0.975 | -0.48177 | 0.97522 | -0.47756 | 4.7693
38 | -0.014285 | -0.0035807 | 0.014289 | 0.0035825 | 3.2095e-06 | 1.8293e-06 | 0.021797 | 0.021797 | 0.021797 | 0.97522 | -0.47756 | 0.97546 | -0.47285 | 5.9883
39 | -0.018247 | -0.0045745 | 0.018248 | 0.0045754 | 1.432e-06 | 8.5497e-07 | 0.027835 | 0.027835 | 0.027835 | 0.97546 | -0.47285 | 0.97554 | -0.4712 | 7.6471
40 | -0.02033 | -0.005097 | 0.020333 | 0.0050991 | 3.472e-06 | 2.1018e-06 | 0.03101 | 0.03101 | 0.03101 | 0.97554 | -0.4712 | 0.97572 | -0.46762 | 8.5193
41 | -0.022897 | -0.0057418 | 0.022898 | 0.005742 | 4.0683e-07 | 2.4926e-07 | 0.034921 | 0.034921 | 0.034921 | 0.97572 | -0.46762 | 0.97574 | -0.46725 | 9.5936
42 | -0.024606 | -0.0061701 | 0.02462 | 0.0061787 | 1.3928e-05 | 8.584e-06 | 0.037525 | 0.037525 | 0.037525 | 0.97574 | -0.46725 | 0.97634 | -0.45538 | 10.3091
43 | 0.032643 | 0.0082034 | -0.032633 | -0.0081967 | 1.0644e-05 | 6.6686e-06 | 0.049759 | 0.049759 | 0.049759 | 0.97634 | -0.45538 | 0.976 | -0.46221 | 13.6699
44 | -0.057263 | -0.014382 | 0.057304 | 0.014408 | 4.0861e-05 | 2.5972e-05 | 0.087284 | 0.087284 | 0.087284 | 0.97634 | -0.45538 | 0.97711 | -0.44043 | 23.979
45 | 0.029936 | 0.0075208 | -0.029905 | -0.0075015 | 3.089e-05 | 1.9276e-05 | 0.045647 | 0.045647 | 0.045647 | 0.976 | -0.46221 | 0.9749 | -0.48385 | 12.5403
46 | -0.027184 | -0.006817 | 0.027197 | 0.0068251 | 1.3187e-05 | 8.1675e-06 | 0.040816 | 0.040816 | 0.040816 | 0.99106 | -0.17005 | 0.99159 | -0.15988 | 11.2132
47 | 0.005408 | 0.0013551 | -0.0054074 | -0.001355 | 5.2893e-07 | 6.3319e-08 | 0.0081229 | 0.008123 | 0.008123 | 0.99065 | -0.17794 | 0.99055 | -0.17999 | 2.2316
48 | -0.17594 | -0.04468 | 0.17599 | 0.044715 | 5.5778e-05 | 3.5258e-05 | 0.26422 | 0.26422 | 0.26422 | 0.99159 | -0.15988 | 0.99193 | -0.15329 | 18.1473
49 | 0.0027869 | 0.00069828 | -0.0027868 | -0.00069844 | 1.2488e-07 | -1.6464e-07 | 0.0041865 | 0.0041866 | 0.0041866 | 0.99055 | -0.17999 | 0.9905 | -0.18093 | 1.1502
50 | 0.018376 | 0.004606 | -0.018375 | -0.0046052 | 1.3057e-06 | 7.7719e-07 | 0.02765 | 0.02765 | 0.02765 | 0.98896 | -0.21042 | 0.98888 | -0.21191 | 7.596
51 | 0.1386 | 0.035407 | -0.13844 | -0.035309 | 0.00015222 | 9.7301e-05 | 0.20815 | 0.20815 | 0.20815 | 0.99193 | -0.15329 | 0.99074 | -0.17603 | 57.1846
52 | -0.31459 | -0.080122 | 0.31499 | 0.080376 | 0.00039934 | 0.00025459 | 0.47238 | 0.47238 | 0.47238 | 0.99193 | -0.15329 | 0.9933 | -0.12701 | 32.4434
53 | 0.13559 | 0.034594 | -0.13513 | -0.0343 | 0.00045967 | 0.00029381 | 0.20387 | 0.20387 | 0.20387 | 0.99074 | -0.17603 | 0.98707 | -0.24648 | 56.0074
54 | -0.32051 | -0.081761 | 0.32089 | 0.082003 | 0.00038059 | 0.00024266 | 0.48065 | 0.48065 | 0.48065 | 0.9933 | -0.12701 | 0.99459 | -0.10245 | 33.0118
55 | 0.1203 | 0.030583 | -0.12002 | -0.030403 | 0.00028193 | 0.00018014 | 0.18151 | 0.18151 | 0.18151 | 0.98707 | -0.24648 | 0.98455 | -0.29526 | 49.8649
56 | -0.32476 | -0.082973 | 0.32483 | 0.083019 | 7.1904e-05 | 4.585e-05 | 0.48644 | 0.48644 | 0.48644 | 0.99459 | -0.10245 | 0.99483 | -0.097876 | 33.4094
57 | -0.32807 | -0.083831 | 0.32815 | 0.083879 | 7.4435e-05 | 4.7467e-05 | 0.49129 | 0.49129 | 0.49129 | 0.99483 | -0.097876 | 0.99508 | -0.093186 | 33.7422
58 | -0.33265 | -0.085007 | 0.33312 | 0.085307 | 0.00047056 | 0.00030011 | 0.49802 | 0.49802 | 0.49802 | 0.99508 | -0.093186 | 0.99662 | -0.063981 | 34.2047
59 | -0.33631 | -0.086106 | 0.33659 | 0.086283 | 0.00027744 | 0.00017695 | 0.50278 | 0.50278 | 0.50278 | 0.99662 | -0.063981 | 0.99752 | -0.046964 | 34.5315
60 | 0.006112 | 0.0015315 | -0.0061108 | -0.0015312 | 1.2217e-06 | 2.9648e-07 | 0.0092374 | 0.0092376 | 0.0092376 | 0.98455 | -0.29526 | 0.98433 | -0.29946 | 2.5378
61 | 0.11391 | 0.028872 | -0.1138 | -0.028802 | 0.00010873 | 6.9463e-05 | 0.17227 | 0.17227 | 0.17227 | 0.98455 | -0.29526 | 0.98352 | -0.31515 | 47.3272
62 | -0.52716 | -0.13495 | 0.52836 | 0.13571 | 0.0012019 | 0.00076816 | 0.78738 | 0.78738 | 0.78738 | 0.99752 | -0.046964 | 1 | 0 | 54.0783
63 | 0.19057 | 0.048663 | -0.1905 | -0.048619 | 7.0768e-05 | 4.4805e-05 | 0.2846 | 0.2846 | 0.2846 | 0.99752 | -0.046964 | 0.99711 | -0.05465 | 19.5468
64 | 0.0034812 | 0.00087238 | -0.0034811 | -0.00087244 | 9.0518e-08 | -6.0084e-08 | 0.00518 | 0.00518 | 0.00518 | 1 | 0 | 0.99997 | -0.00054584 | 1.4231
65 | 0.18753 | 0.047875 | -0.18746 | -0.047829 | 7.1622e-05 | 4.5331e-05 | 0.28017 | 0.28017 | 0.28017 | 0.99711 | -0.05465 | 0.99669 | -0.062557 | 19.2426
66 | 0.18255 | 0.046599 | -0.18254 | -0.046594 | 7.0253e-06 | 4.4437e-06 | 0.27284 | 0.27284 | 0.27284 | 0.99669 | -0.062557 | 0.99665 | -0.063353 | 18.7391
67 | 0.1802 | 0.046006 | -0.17982 | -0.045766 | 0.00037524 | 0.00023943 | 0.26933 | 0.26934 | 0.26934 | 0.99665 | -0.063353 | 0.99439 | -0.10654 | 36.9966
68 | -0.013959 | -0.0034985 | 0.013962 | 0.0035002 | 2.9193e-06 | 1.6539e-06 | 0.021292 | 0.021292 | 0.021292 | 0.97557 | -0.47058 | 0.97579 | -0.46619 | 5.8494
69 | 0.0055615 | 0.0013938 | -0.0055611 | -0.0013937 | 3.9816e-07 | 7.0604e-08 | 0.0084829 | 0.0084829 | 0.0084829 | 0.97557 | -0.47058 | 0.97549 | -0.47208 | 2.3305
70 | -0.041056 | -0.010305 | 0.041077 | 0.010319 | 2.1188e-05 | 1.338e-05 | 0.062558 | 0.062557 | 0.062558 | 0.97666 | -0.44905 | 0.97721 | -0.43823 | 17.1861
71 | 0.037242 | 0.0093559 | -0.037223 | -0.0093436 | 1.9543e-05 | 1.2305e-05 | 0.056718 | 0.056718 | 0.056718 | 0.97721 | -0.43823 | 0.97665 | -0.44923 | 15.5818
72 | -0.07832 | -0.019674 | 0.078335 | 0.019684 | 1.5612e-05 | 9.9551e-06 | 0.11927 | 0.11927 | 0.11927 | 0.97721 | -0.43823 | 0.97743 | -0.43406 | 32.7678
73 | 0.033603 | 0.0084362 | -0.033585 | -0.0084251 | 1.7801e-05 | 1.1166e-05 | 0.051202 | 0.051202 | 0.051202 | 0.97665 | -0.44923 | 0.97609 | -0.46034 | 14.0664
74 | -0.082538 | -0.020738 | 0.082547 | 0.020743 | 8.5444e-06 | 5.4503e-06 | 0.12567 | 0.12567 | 0.12567 | 0.97743 | -0.43406 | 0.97754 | -0.43189 | 34.5255
75 | -0.0026434 | -0.00066249 | 0.0026435 | 0.00066222 | 1.8091e-07 | -2.6819e-07 | 0.0039963 | 0.0039961 | 0.0039963 | 0.98426 | -0.30089 | 0.98433 | -0.29946 | 1.0979
76 | -0.10429 | -0.026268 | 0.1043 | 0.026276 | 1.2976e-05 | 8.287e-06 | 0.15844 | 0.15844 | 0.15844 | 0.97978 | -0.38801 | 0.97991 | -0.38541 | 43.5263
77 | 0.09924 | 0.025002 | -0.099182 | -0.024965 | 5.8605e-05 | 3.7421e-05 | 0.15077 | 0.15077 | 0.15077 | 0.97978 | -0.38801 | 0.97915 | -0.40036 | 41.4193
78 | -0.10748 | -0.027072 | 0.10754 | 0.02711 | 5.9996e-05 | 3.8322e-05 | 0.16326 | 0.16326 | 0.16326 | 0.97991 | -0.38541 | 0.98051 | -0.37374 | 44.8509
79 | 0.095595 | 0.024066 | -0.095562 | -0.024045 | 3.2817e-05 | 2.0951e-05 | 0.14531 | 0.14531 | 0.14531 | 0.97915 | -0.40036 | 0.97878 | -0.40755 | 39.9216
80 | -0.11175 | -0.028165 | 0.11186 | 0.028237 | 0.00011269 | 7.199e-05 | 0.16964 | 0.16964 | 0.16964 | 0.98051 | -0.37374 | 0.98159 | -0.35269 | 46.6049
81 | 0.092221 | 0.023208 | -0.092187 | -0.023186 | 3.4684e-05 | 2.2139e-05 | 0.14024 | 0.14024 | 0.14024 | 0.97878 | -0.40755 | 0.97838 | -0.41542 | 38.5265
82 | -0.11359 | -0.028671 | 0.1138 | 0.028802 | 0.00020466 | 0.00013075 | 0.17227 | 0.17227 | 0.17227 | 0.98159 | -0.35269 | 0.98352 | -0.31515 | 47.3272
83 | 0.086875 | 0.021854 | -0.086807 | -0.021811 | 6.8288e-05 | 4.3573e-05 | 0.13216 | 0.13216 | 0.13216 | 0.97838 | -0.41542 | 0.97754 | -0.43189 | 36.307
84 | 0.02975 | 0.0074641 | -0.029746 | -0.0074615 | 4.168e-06 | 2.6e-06 | 0.045356 | 0.045356 | 0.045356 | 0.97609 | -0.46034 | 0.97594 | -0.46328 | 12.4606
85 | 0.026346 | 0.0066094 | -0.026336 | -0.0066029 | 1.0485e-05 | 6.4939e-06 | 0.040173 | 0.040173 | 0.040173 | 0.97594 | -0.46328 | 0.97552 | -0.47163 | 11.0365
86 | -0.022516 | -0.0056451 | 0.022522 | 0.0056487 | 5.9539e-06 | 3.6301e-06 | 0.033744 | 0.033744 | 0.033744 | 0.99291 | -0.13508 | 0.9932 | -0.12953 | 9.2703
87 | 0.017587 | 0.0044098 | -0.017583 | -0.004407 | 4.7437e-06 | 2.8005e-06 | 0.026358 | 0.026358 | 0.026358 | 0.99291 | -0.13508 | 0.99262 | -0.14074 | 7.2412
88 | -0.027947 | -0.0070083 | 0.02796 | 0.0070164 | 1.306e-05 | 8.1009e-06 | 0.041872 | 0.041871 | 0.041872 | 0.9932 | -0.12953 | 0.9937 | -0.11973 | 11.5032
89 | 0.014061 | 0.0035245 | -0.01406 | -0.0035237 | 1.4381e-06 | 8.0884e-07 | 0.021079 | 0.021079 | 0.021079 | 0.99262 | -0.14074 | 0.99251 | -0.14289 | 5.791
90 | -0.032749 | -0.0082166 | 0.032749 | 0.0082167 | 1.7423e-07 | 1.09e-07 | 0.049042 | 0.049042 | 0.049042 | 0.9937 | -0.11973 | 0.99371 | -0.11962 | 13.4732
91 | -0.038314 | -0.0096114 | 0.038338 | 0.0096265 | 2.391e-05 | 1.5052e-05 | 0.057376 | 0.057376 | 0.057376 | 0.99371 | -0.11962 | 0.99439 | -0.10654 | 15.7625
92 | 0.13985 | 0.035731 | -0.13949 | -0.035499 | 0.00036347 | 0.00023234 | 0.20952 | 0.20952 | 0.20952 | 0.99439 | -0.10654 | 0.99156 | -0.16044 | 57.5609
93 | 0.018198 | 0.0045654 | -0.018192 | -0.0045615 | 6.4491e-06 | 3.8302e-06 | 0.027311 | 0.027311 | 0.027311 | 0.99156 | -0.16044 | 0.99118 | -0.16788 | 7.503
94 | 0.12129 | 0.030934 | -0.12126 | -0.030914 | 3.1161e-05 | 1.9911e-05 | 0.18221 | 0.18221 | 0.18221 | 0.99156 | -0.16044 | 0.99129 | -0.16576 | 50.058
95 | 0.015156 | 0.0038008 | -0.015152 | -0.0037983 | 4.3067e-06 | 2.4705e-06 | 0.022754 | 0.022754 | 0.022754 | 0.99118 | -0.16788 | 0.99087 | -0.17384 | 6.2511
96 | 0.11968 | 0.030518 | -0.11938 | -0.030327 | 0.0002998 | 0.00019155 | 0.17984 | 0.17984 | 0.17984 | 0.99129 | -0.16576 | 0.98857 | -0.21779 | 49.407
97 | 0.012296 | 0.0030826 | -0.012293 | -0.0030811 | 2.7275e-06 | 1.4709e-06 | 0.018466 | 0.018466 | 0.018466 | 0.99087 | -0.17384 | 0.99063 | -0.1785 | 5.073
98 | 0.11749 | 0.029852 | -0.11733 | -0.029751 | 0.00015733 | 0.00010052 | 0.17699 | 0.17699 | 0.17699 | 0.98857 | -0.21779 | 0.98713 | -0.24564 | 48.624
99 | 0.025323 | 0.0063545 | -0.025305 | -0.0063435 | 1.7886e-05 | 1.1029e-05 | 0.038175 | 0.038175 | 0.038175 | 0.98713 | -0.24564 | 0.98637 | -0.26047 | 10.4876
100 | 0.078195 | 0.019931 | -0.078084 | -0.01986 | 0.00011178 | 7.1264e-05 | 0.11799 | 0.11799 | 0.11799 | 0.98713 | -0.24564 | 0.98559 | -0.27531 | 32.4156
101 | 0.013813 | 0.0034657 | -0.013807 | -0.0034621 | 6.4015e-06 | 3.5939e-06 | 0.020824 | 0.020824 | 0.020824 | 0.98713 | -0.24564 | 0.98663 | -0.25537 | 5.7209
102 | 0.021767 | 0.0054568 | -0.021767 | -0.0054568 | 3.366e-08 | 2.0481e-08 | 0.032838 | 0.032838 | 0.032838 | 0.98637 | -0.26047 | 0.98637 | -0.2605 | 9.0214
103 | 0.074896 | 0.019061 | -0.07474 | -0.018961 | 0.00015629 | 9.961e-05 | 0.11318 | 0.11318 | 0.11318 | 0.98559 | -0.27531 | 0.98334 | -0.31869 | 31.0937
104 | 0.012266 | 0.003076 | -0.012263 | -0.0030745 | 2.7858e-06 | 1.5058e-06 | 0.0185 | 0.0185 | 0.0185 | 0.98663 | -0.25537 | 0.98638 | -0.26013 | 5.0825
105 | 0.015768 | 0.0039534 | -0.015764 | -0.0039512 | 3.892e-06 | 2.2569e-06 | 0.023788 | 0.023789 | 0.023789 | 0.98637 | -0.2605 | 0.9861 | -0.26568 | 6.5353
106 | 0.07474 | 0.018961 | -0.074496 | -0.018806 | 0.00024384 | 0.00015542 | 0.11318 | 0.11318 | 0.11318 | 0.98334 | -0.31869 | 0.97984 | -0.38678 | 31.0937
107 | 0.012263 | 0.0030745 | -0.012262 | -0.0030736 | 1.6063e-06 | 8.6829e-07 | 0.0185 | 0.0185 | 0.0185 | 0.98638 | -0.26013 | 0.98624 | -0.26288 | 5.0825
108 | 0.0081753 | 0.002049 | -0.0081747 | -0.0020488 | 6.2133e-07 | 2.5621e-07 | 0.01228 | 0.01228 | 0.01228 | 0.99063 | -0.1785 | 0.99055 | -0.18009 | 3.3737
109 | 0.010852 | 0.0027199 | -0.010852 | -0.0027199 | 5.385e-08 | 2.7632e-08 | 0.016375 | 0.016375 | 0.016375 | 0.9861 | -0.26568 | 0.98609 | -0.26578 | 4.4987
110 | 0.071883 | 0.018151 | -0.071867 | -0.018141 | 1.5698e-05 | 1.0002e-05 | 0.10921 | 0.10921 | 0.10921 | 0.97984 | -0.38678 | 0.97961 | -0.39134 | 30.0033
111 | 0.010863 | 0.002723 | -0.010861 | -0.0027219 | 2.2372e-06 | 1.1485e-06 | 0.01639 | 0.01639 | 0.01639 | 0.98624 | -0.26288 | 0.98602 | -0.26721 | 4.5027
112 | 0.0087284 | 0.0021877 | -0.0087274 | -0.0021873 | 1.0116e-06 | 4.491e-07 | 0.013171 | 0.013171 | 0.013171 | 0.98609 | -0.26578 | 0.98597 | -0.26822 | 3.6185
113 | 0.071867 | 0.018141 | -0.071769 | -0.018079 | 9.7973e-05 | 6.2427e-05 | 0.10921 | 0.10921 | 0.10921 | 0.97961 | -0.39134 | 0.97815 | -0.41984 | 30.0033
114 | 0.067335 | 0.016967 | -0.067237 | -0.016905 | 9.7603e-05 | 6.2155e-05 | 0.10247 | 0.10247 | 0.10247 | 0.97815 | -0.41984 | 0.9766 | -0.45019 | 28.1503
115 | 0.061945 | 0.015579 | -0.061937 | -0.015574 | 8.3799e-06 | 5.3317e-06 | 0.094404 | 0.094404 | 0.094404 | 0.9766 | -0.45019 | 0.97646 | -0.45302 | 25.9351
116 | 0.058079 | 0.014607 | -0.058022 | -0.01457 | 5.702e-05 | 3.625e-05 | 0.088524 | 0.088525 | 0.088525 | 0.97646 | -0.45302 | 0.97541 | -0.47359 | 24.3199
117 | 0.051136 | 0.012844 | -0.05113 | -0.012841 | 5.8375e-06 | 3.7041e-06 | 0.078019 | 0.078019 | 0.078019 | 0.97541 | -0.47359 | 0.97529 | -0.47599 | 21.4339
118 | 0.046437 | 0.011665 | -0.046389 | -0.011635 | 4.7545e-05 | 3.0114e-05 | 0.070859 | 0.070859 | 0.070859 | 0.97529 | -0.47599 | 0.9742 | -0.49747 | 19.4669
119 | 0.04059 | 0.010181 | -0.04059 | -0.010181 | 1.596e-07 | 1.0077e-07 | 0.062002 | 0.062002 | 0.062002 | 0.9742 | -0.49747 | 0.97419 | -0.49755 | 17.0334
120 | 0.033648 | 0.0084413 | -0.033648 | -0.0084408 | 7.1779e-07 | 4.5037e-07 | 0.051399 | 0.051399 | 0.051399 | 0.97419 | -0.49755 | 0.97417 | -0.498 | 14.1205
121 | 0.029511 | 0.0074042 | -0.029494 | -0.0073935 | 1.7069e-05 | 1.0646e-05 | 0.045081 | 0.045081 | 0.045081 | 0.97417 | -0.498 | 0.97355 | -0.51013 | 12.3848
122 | 0.018715 | 0.0046927 | -0.018709 | -0.0046891 | 6.0434e-06 | 3.621e-06 | 0.028549 | 0.028549 | 0.028549 | 0.97549 | -0.47212 | 0.97515 | -0.4789 | 7.843
123 | -0.022167 | -0.0055579 | 0.022168 | 0.0055582 | 3.382e-07 | 2.066e-07 | 0.033815 | 0.033815 | 0.033815 | 0.97549 | -0.47212 | 0.97551 | -0.4718 | 9.2898
124 | -0.025304 | -0.0063442 | 0.025304 | 0.0063443 | 1.9653e-07 | 1.2139e-07 | 0.038599 | 0.038599 | 0.038599 | 0.97551 | -0.4718 | 0.97552 | -0.47163 | 10.6041
125 | 0.023348 | 0.0058531 | -0.023346 | -0.0058516 | 2.4849e-06 | 1.5256e-06 | 0.035687 | 0.035687 | 0.035687 | 0.97355 | -0.51013 | 0.97344 | -0.51237 | 9.804
126 | 0.0080726 | 0.0020231 | -0.0080722 | -0.002023 | 3.8432e-07 | 1.5789e-07 | 0.012182 | 0.012182 | 0.012182 | 0.98602 | -0.26721 | 0.98597 | -0.26821 | 3.3468
127 | 0.0053324 | 0.0013363 | -0.005332 | -0.0013362 | 4.4547e-07 | 5.1189e-08 | 0.0080476 | 0.0080476 | 0.0080476 | 0.98597 | -0.26821 | 0.98588 | -0.26996 | 2.2109
128 | 0.0024934 | 0.00062484 | -0.0024934 | -0.00062491 | 3.7973e-08 | -6.6864e-08 | 0.0037634 | 0.0037634 | 0.0037634 | 0.98588 | -0.26996 | 0.98586 | -0.27028 | 1.0339

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53817 | 0.13776

## res_load
| p_mw | q_mvar
0 | 0.0094872 | 0.0023777
1 | 0.0033703 | 0.00084467
2 | 0.0035795 | 0.0008971
3 | 0.0028081 | 0.00070377
4 | 0.0081531 | 0.0020434
5 | 0.002549 | 0.00063884
6 | 0.0027698 | 0.00069419
7 | 0.0082113 | 0.002058
8 | 0.0058652 | 0.00147
9 | 0.0042225 | 0.0010583
10 | 0.0048595 | 0.0012179
11 | 0.0061106 | 0.0015315
12 | 0.0040506 | 0.0010152
13 | 0.0041458 | 0.001039
14 | 0.0081251 | 0.0020363
15 | 0.0078256 | 0.0019613
16 | 0.0079157 | 0.0019839
17 | 0.010856 | 0.0027208
18 | 0.011338 | 0.0028416
19 | 0.0036286 | 0.00090941
20 | 0.0043701 | 0.0010953
21 | 0.0055472 | 0.0013903
22 | 0.0058636 | 0.0014696
23 | 0.0034774 | 0.00087151
24 | 0.00224 | 0.0005614
25 | 0.0020517 | 0.0005142
26 | 0.003604 | 0.00090325
27 | 0.002908 | 0.00072881
28 | 0.0039583 | 0.00099204
29 | 0.0020814 | 0.00052164
30 | 0.0025643 | 0.00064266
31 | 0.0017079 | 0.00042804
32 | 0.0026971 | 0.00067595
33 | 0.010329 | 0.0025887
34 | 0.0060171 | 0.001508
35 | 0.0048895 | 0.0012254
36 | 0.0031389 | 0.00078668
37 | 0.0026205 | 0.00065675
38 | 0.004904 | 0.001229
39 | 0.018375 | 0.0046052
40 | 0.0027868 | 0.00069844
41 | 0.0028531 | 0.00071505
42 | 0.0055246 | 0.0013846
43 | 0.014832 | 0.0037172
44 | 0.0038691 | 0.0009697
45 | 0.0032401 | 0.00081205
46 | 0.0045031 | 0.0011286
47 | 0.0031873 | 0.00079881
48 | 0.0046749 | 0.0011716
49 | 0.0029685 | 0.00074398
50 | 0.0034811 | 0.00087244
51 | 0.0049107 | 0.0012307
52 | 0.0023484 | 0.00058856
53 | 0.0083979 | 0.0021047
54 | 0.0061002 | 0.0015288
55 | 0.0055611 | 0.0013937
56 | 0.0057235 | 0.0014344
57 | 0.0036203 | 0.00090733
58 | 0.0042027 | 0.0010533
59 | 0.0026434 | 0.00066249
60 | 0.0034673 | 0.00086898
61 | 0.0050501 | 0.0012657
62 | 0.0031752 | 0.00079577
63 | 0.0035873 | 0.00089907
64 | 0.0042069 | 0.0010543
65 | 0.0033403 | 0.00083716
66 | 0.0017345 | 0.00043471
67 | 0.0053118 | 0.0013313
68 | 0.00426 | 0.0010677
69 | 0.0038344 | 0.00096099
70 | 0.0033998 | 0.00085207
71 | 0.0049287 | 0.0012352
72 | 0.0054249 | 0.0013596
73 | 0.0035212 | 0.0008825
74 | 0.0047887 | 0.0012002
75 | 0.01406 | 0.0035237
76 | 0.005565 | 0.0013947
77 | 0.0016295 | 0.00040839
78 | 0.0030355 | 0.00076077
79 | 0.0015787 | 0.00039565
80 | 0.0028556 | 0.00071569
81 | 0.0018935 | 0.00047457
82 | 0.0035378 | 0.00088666
83 | 0.0031873 | 0.0007988
84 | 0.0015408 | 0.00038616
85 | 0.0059987 | 0.0015034
86 | 0.0041181 | 0.0010321
87 | 0.0049128 | 0.0012313
88 | 0.0026137 | 0.00065504
89 | 0.0013989 | 0.0003506
90 | 0.0081747 | 0.0020488
91 | 0.0021232 | 0.00053214
92 | 0.0087274 | 0.0021873
93 | 0.004434 | 0.0011113
94 | 0.005292 | 0.0013263
95 | 0.0038581 | 0.00096693
96 | 0.0068863 | 0.0017259
97 | 0.0046928 | 0.0011761
98 | 0.0057992 | 0.0014534
99 | 0.0069416 | 0.0017397
100 | 0.0041363 | 0.0010366
101 | 0.0034524 | 0.00086525
102 | 0.0037417 | 0.00093776
103 | 0.0031364 | 0.00078605
104 | 0.0010318 | 0.00025859
105 | 0.0061463 | 0.0015404
106 | 0.011932 | 0.0029905
107 | 0.002788 | 0.00069874
108 | 0.0027398 | 0.00068667
109 | 0.0028385 | 0.0007114
110 | 0.0024934 | 0.00062491

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1