## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1213-15_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1213-15_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1213-15_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1213-15_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1213-15_0_8_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1213-15_0_8_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1213-15_0_8_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1213-15_0_8_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_1213-15_0_8_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1213-15_0_8_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_1213-15_0_8_node_132 | 0.4 | n |  | TRUE
11 | bus_LV_1213-15_0_8_node_133 | 0.4 | n |  | TRUE
12 | bus_LV_1213-15_0_8_node_136 | 0.4 | n |  | TRUE
13 | bus_LV_1213-15_0_8_node_134 | 0.4 | n |  | TRUE
14 | bus_LV_1213-15_0_8_node_135 | 0.4 | n |  | TRUE
15 | bus_LV_1213-15_0_8_node_124 | 0.4 | n |  | TRUE
16 | bus_LV_1213-15_0_8_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1213-15_0_8_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1213-15_0_8_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1213-15_0_8_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1213-15_0_8_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1213-15_0_8_node_72 | 0.4 | n |  | TRUE
22 | bus_LV_1213-15_0_8_node_70 | 0.4 | n |  | TRUE
23 | bus_LV_1213-15_0_8_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1213-15_0_8_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1213-15_0_8_node_79 | 0.4 | n |  | TRUE
26 | bus_LV_1213-15_0_8_node_80 | 0.4 | n |  | TRUE
27 | bus_LV_1213-15_0_8_node_116 | 0.4 | n |  | TRUE
28 | bus_LV_1213-15_0_8_node_117 | 0.4 | n |  | TRUE
29 | bus_LV_1213-15_0_8_node_115 | 0.4 | n |  | TRUE
30 | bus_LV_1213-15_0_8_node_123 | 0.4 | n |  | TRUE
31 | bus_LV_1213-15_0_8_node_125 | 0.4 | n |  | TRUE
32 | bus_LV_1213-15_0_8_node_121 | 0.4 | n |  | TRUE
33 | bus_LV_1213-15_0_8_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_1213-15_0_8_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_1213-15_0_8_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_1213-15_0_8_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_1213-15_0_8_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_1213-15_0_8_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_1213-15_0_8_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_1213-15_0_8_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_1213-15_0_8_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_1213-15_0_8_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_1213-15_0_8_node_27 | 0.4 | n |  | TRUE
44 | bus_LV_1213-15_0_8_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_1213-15_0_8_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_1213-15_0_8_node_119 | 0.4 | n |  | TRUE
47 | bus_LV_1213-15_0_8_node_128 | 0.4 | n |  | TRUE
48 | bus_LV_1213-15_0_8_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_1213-15_0_8_node_23 | 0.4 | n |  | TRUE
50 | bus_LV_1213-15_0_8_node_25 | 0.4 | n |  | TRUE
51 | bus_LV_1213-15_0_8_node_69 | 0.4 | n |  | TRUE
52 | bus_LV_1213-15_0_8_node_24 | 0.4 | n |  | TRUE
53 | bus_LV_1213-15_0_8_node_71 | 0.4 | n |  | TRUE
54 | bus_LV_1213-15_0_8_node_68 | 0.4 | n |  | TRUE
55 | bus_LV_1213-15_0_8_node_73 | 0.4 | n |  | TRUE
56 | bus_LV_1213-15_0_8_node_62 | 0.4 | n |  | TRUE
57 | bus_LV_1213-15_0_8_node_66 | 0.4 | n |  | TRUE
58 | bus_LV_1213-15_0_8_node_75 | 0.4 | n |  | TRUE
59 | bus_LV_1213-15_0_8_node_74 | 0.4 | n |  | TRUE
60 | bus_LV_1213-15_0_8_node_28 | 0.4 | n |  | TRUE
61 | bus_LV_1213-15_0_8_node_34 | 0.4 | n |  | TRUE
62 | bus_LV_1213-15_0_8_node_76 | 0.4 | n |  | TRUE
63 | bus_LV_1213-15_0_8_node_35 | 0.4 | n |  | TRUE
64 | bus_LV_1213-15_0_8_node_77 | 0.4 | n |  | TRUE
65 | bus_LV_1213-15_0_8_node_127 | 0.4 | n |  | TRUE
66 | bus_LV_1213-15_0_8_node_126 | 0.4 | n |  | TRUE
67 | bus_LV_1213-15_0_8_node_37 | 0.4 | n |  | TRUE
68 | bus_LV_1213-15_0_8_node_38 | 0.4 | n |  | TRUE
69 | bus_LV_1213-15_0_8_node_53 | 0.4 | n |  | TRUE
70 | bus_LV_1213-15_0_8_node_40 | 0.4 | n |  | TRUE
71 | bus_LV_1213-15_0_8_node_49 | 0.4 | n |  | TRUE
72 | bus_LV_1213-15_0_8_node_44 | 0.4 | n |  | TRUE
73 | bus_LV_1213-15_0_8_node_41 | 0.4 | n |  | TRUE
74 | bus_LV_1213-15_0_8_node_42 | 0.4 | n |  | TRUE
75 | bus_LV_1213-15_0_8_node_43 | 0.4 | n |  | TRUE
76 | bus_LV_1213-15_0_8_node_47 | 0.4 | n |  | TRUE
77 | bus_LV_1213-15_0_8_node_45 | 0.4 | n |  | TRUE
78 | bus_LV_1213-15_0_8_node_46 | 0.4 | n |  | TRUE
79 | bus_LV_1213-15_0_8_node_48 | 0.4 | n |  | TRUE
80 | bus_LV_1213-15_0_8_node_50 | 0.4 | n |  | TRUE
81 | bus_LV_1213-15_0_8_node_51 | 0.4 | n |  | TRUE
82 | bus_LV_1213-15_0_8_node_52 | 0.4 | n |  | TRUE
83 | bus_LV_1213-15_0_8_node_54 | 0.4 | n |  | TRUE
84 | bus_LV_1213-15_0_8_node_55 | 0.4 | n |  | TRUE
85 | bus_LV_1213-15_0_8_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_1213-15_0_8_node_58 | 0.4 | n |  | TRUE
87 | bus_LV_1213-15_0_8_node_57 | 0.4 | n |  | TRUE
88 | bus_LV_1213-15_0_8_node_59 | 0.4 | n |  | TRUE
89 | bus_LV_1213-15_0_8_node_60 | 0.4 | n |  | TRUE
90 | bus_LV_1213-15_0_8_node_61 | 0.4 | n |  | TRUE
91 | bus_LV_1213-15_0_8_node_64 | 0.4 | n |  | TRUE
92 | bus_LV_1213-15_0_8_node_63 | 0.4 | n |  | TRUE
93 | bus_LV_1213-15_0_8_node_65 | 0.4 | n |  | TRUE
94 | bus_LV_1213-15_0_8_node_67 | 0.4 | n |  | TRUE
95 | bus_LV_1213-15_0_8_node_78 | 0.4 | n |  | TRUE
96 | bus_LV_1213-15_0_8_node_130 | 0.4 | n |  | TRUE
97 | bus_LV_1213-15_0_8_node_129 | 0.4 | n |  | TRUE
98 | bus_LV_1213-15_0_8_node_81 | 0.4 | n |  | TRUE
99 | bus_LV_1213-15_0_8_node_82 | 0.4 | n |  | TRUE
100 | bus_LV_1213-15_0_8_node_83 | 0.4 | n |  | TRUE
101 | bus_LV_1213-15_0_8_node_84 | 0.4 | n |  | TRUE
102 | bus_LV_1213-15_0_8_node_92 | 0.4 | n |  | TRUE
103 | bus_LV_1213-15_0_8_node_93 | 0.4 | n |  | TRUE
104 | bus_LV_1213-15_0_8_node_94 | 0.4 | n |  | TRUE
105 | bus_LV_1213-15_0_8_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_1213-15_0_8_node_85 | 0.4 | n |  | TRUE
107 | bus_LV_1213-15_0_8_node_86 | 0.4 | n |  | TRUE
108 | bus_LV_1213-15_0_8_node_87 | 0.4 | n |  | TRUE
109 | bus_LV_1213-15_0_8_node_88 | 0.4 | n |  | TRUE
110 | bus_LV_1213-15_0_8_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_1213-15_0_8_node_91 | 0.4 | n |  | TRUE
112 | bus_LV_1213-15_0_8_node_95 | 0.4 | n |  | TRUE
113 | bus_LV_1213-15_0_8_node_96 | 0.4 | n |  | TRUE
114 | bus_LV_1213-15_0_8_node_100 | 0.4 | n |  | TRUE
115 | bus_LV_1213-15_0_8_node_113 | 0.4 | n |  | TRUE
116 | bus_LV_1213-15_0_8_node_101 | 0.4 | n |  | TRUE
117 | bus_LV_1213-15_0_8_node_112 | 0.4 | n |  | TRUE
118 | bus_LV_1213-15_0_8_node_97 | 0.4 | n |  | TRUE
119 | bus_LV_1213-15_0_8_node_99 | 0.4 | n |  | TRUE
120 | bus_LV_1213-15_0_8_node_138 | 0.4 | n |  | TRUE
121 | bus_LV_1213-15_0_8_node_102 | 0.4 | n |  | TRUE
122 | bus_LV_1213-15_0_8_node_103 | 0.4 | n |  | TRUE
123 | bus_LV_1213-15_0_8_node_104 | 0.4 | n |  | TRUE
124 | bus_LV_1213-15_0_8_node_106 | 0.4 | n |  | TRUE
125 | bus_LV_1213-15_0_8_node_107 | 0.4 | n |  | TRUE
126 | bus_LV_1213-15_0_8_node_108 | 0.4 | n |  | TRUE
127 | bus_LV_1213-15_0_8_node_109 | 0.4 | n |  | TRUE
128 | bus_LV_1213-15_0_8_node_110 | 0.4 | n |  | TRUE
129 | bus_LV_1213-15_0_8_node_111 | 0.4 | n |  | TRUE
130 | bus_LV_1213-15_0_8_node_114 | 0.4 | n |  | TRUE
131 | bus_LV_1213-15_0_8_node_122 | 0.4 | n |  | TRUE
132 | bus_LV_1213-15_0_8_node_118 | 0.4 | n |  | TRUE
133 | bus_LV_1213-15_0_8_node_120 | 0.4 | n |  | TRUE
134 | bus_MV_11_0_node_91 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1213-15_0_8_load_0 | 0 | 0.0084155 | 0.0021091 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1213-15_0_8_load_1 | 1 | 0.0053467 | 0.00134 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1213-15_0_8_load_3 | 3 | 0.0037959 | 0.00095135 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1213-15_0_8_load_4 | 4 | 0.0031437 | 0.0007879 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1213-15_0_8_load_5 | 5 | 0.0066861 | 0.0016757 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1213-15_0_8_load_6 | 6 | 0.0046767 | 0.0011721 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1213-15_0_8_load_14 | 7 | 0.0018829 | 0.0004719 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1213-15_0_8_load_7 | 8 | 0.0033909 | 0.00084985 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1213-15_0_8_load_132 | 10 | 0.0050615 | 0.0012685 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1213-15_0_8_load_134 | 13 | 0.0077672 | 0.0019466 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1213-15_0_8_load_135 | 14 | 0.0037336 | 0.00093572 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1213-15_0_8_load_8 | 16 | 0.0014735 | 0.0003693 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1213-15_0_8_load_9 | 17 | 0.0012373 | 0.00031011 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1213-15_0_8_load_10 | 18 | 0.0038957 | 0.00097635 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1213-15_0_8_load_11 | 19 | 0.0014623 | 0.00036647 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1213-15_0_8_load_12 | 20 | 0.0012172 | 0.00030505 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1213-15_0_8_load_72 | 21 | 0.0056242 | 0.0014096 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1213-15_0_8_load_70 | 22 | 0.002906 | 0.00072832 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1213-15_0_8_load_15 | 23 | 0.0019539 | 0.0004897 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1213-15_0_8_load_19 | 24 | 0.0034195 | 0.00085701 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1213-15_0_8_load_79 | 25 | 0.015571 | 0.0039026 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1213-15_0_8_load_80 | 26 | 0.0040569 | 0.0010168 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1213-15_0_8_load_116 | 27 | 0.0032731 | 0.00082033 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1213-15_0_8_load_117 | 28 | 0.0030723 | 0.00076998 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1213-15_0_8_load_115 | 29 | 0.0083308 | 0.0020879 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1213-15_0_8_load_121 | 32 | 0.0029351 | 0.0007356 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1213-15_0_8_load_17 | 33 | 0.0024069 | 0.00060323 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1213-15_0_8_load_16 | 34 | 0.0038136 | 0.00095579 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1213-15_0_8_load_18 | 35 | 0.003817 | 0.00095662 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1213-15_0_8_load_30 | 37 | 0.0052591 | 0.0013181 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1213-15_0_8_load_22 | 38 | 0.0052363 | 0.0013123 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1213-15_0_8_load_21 | 39 | 0.005657 | 0.0014178 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1213-15_0_8_load_29 | 40 | 0.0051968 | 0.0013024 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1213-15_0_8_load_31 | 41 | 0.0030661 | 0.00076844 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1213-15_0_8_load_26 | 42 | 0.0040091 | 0.0010048 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1213-15_0_8_load_27 | 43 | 0.0030267 | 0.00075856 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1213-15_0_8_load_32 | 44 | 0.0035226 | 0.00088285 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1213-15_0_8_load_33 | 45 | 0.0034661 | 0.0008687 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1213-15_0_8_load_119 | 46 | 0.0034396 | 0.00086205 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1213-15_0_8_load_128 | 47 | 0.012116 | 0.0030367 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1213-15_0_8_load_25 | 50 | 0.0038072 | 0.00095416 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1213-15_0_8_load_69 | 51 | 0.0063021 | 0.0015794 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1213-15_0_8_load_24 | 52 | 0.0040872 | 0.0010244 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1213-15_0_8_load_71 | 53 | 0.0038109 | 0.0009551 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1213-15_0_8_load_68 | 54 | 0.0046027 | 0.0011535 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1213-15_0_8_load_73 | 55 | 0.0056942 | 0.0014271 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1213-15_0_8_load_62 | 56 | 0.0059377 | 0.0014881 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1213-15_0_8_load_66 | 57 | 0.0044284 | 0.0011099 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1213-15_0_8_load_75 | 58 | 0.0072842 | 0.0018256 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1213-15_0_8_load_74 | 59 | 0.0053029 | 0.001329 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1213-15_0_8_load_28 | 60 | 0.0034996 | 0.00087709 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1213-15_0_8_load_34 | 61 | 0.0027405 | 0.00068683 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1213-15_0_8_load_76 | 62 | 0.0039896 | 0.0009999 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1213-15_0_8_load_35 | 63 | 0.0061555 | 0.0015427 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1213-15_0_8_load_77 | 64 | 0.0034914 | 0.00087502 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1213-15_0_8_load_127 | 65 | 0.0040483 | 0.0010146 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1213-15_0_8_load_37 | 67 | 0.0037329 | 0.00093555 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1213-15_0_8_load_38 | 68 | 0.0043861 | 0.0010993 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1213-15_0_8_load_53 | 69 | 0.0032084 | 0.0008041 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1213-15_0_8_load_40 | 70 | 0.013986 | 0.0035052 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1213-15_0_8_load_49 | 71 | 0.0034038 | 0.00085307 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1213-15_0_8_load_44 | 72 | 0.0045733 | 0.0011462 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1213-15_0_8_load_41 | 73 | 0.0015101 | 0.00037846 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1213-15_0_8_load_42 | 74 | 0.0037959 | 0.00095135 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1213-15_0_8_load_43 | 75 | 0.0014839 | 0.0003719 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1213-15_0_8_load_47 | 76 | 0.0030916 | 0.00077484 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1213-15_0_8_load_45 | 77 | 0.001978 | 0.00049573 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1213-15_0_8_load_46 | 78 | 0.003139 | 0.00078671 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1213-15_0_8_load_48 | 79 | 0.002391 | 0.00059924 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1213-15_0_8_load_50 | 80 | 0.0036674 | 0.00091913 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1213-15_0_8_load_51 | 81 | 0.0068114 | 0.0017071 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1213-15_0_8_load_52 | 82 | 0.0030175 | 0.00075627 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1213-15_0_8_load_56 | 85 | 0.0025237 | 0.00063249 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1213-15_0_8_load_58 | 86 | 0.0042365 | 0.0010618 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1213-15_0_8_load_57 | 87 | 0.0038765 | 0.00097155 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1213-15_0_8_load_59 | 88 | 0.0029743 | 0.00074544 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1213-15_0_8_load_61 | 90 | 0.0048349 | 0.0012117 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1213-15_0_8_load_64 | 91 | 0.0049241 | 0.0012341 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1213-15_0_8_load_63 | 92 | 0.0043189 | 0.0010824 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1213-15_0_8_load_65 | 93 | 0.0048973 | 0.0012274 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1213-15_0_8_load_67 | 94 | 0.0032841 | 0.00082308 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1213-15_0_8_load_78 | 95 | 0.0019948 | 0.00049995 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1213-15_0_8_load_130 | 96 | 0.0015573 | 0.00039031 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1213-15_0_8_load_129 | 97 | 0.0031427 | 0.00078763 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1213-15_0_8_load_81 | 98 | 0.012511 | 0.0031355 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1213-15_0_8_load_83 | 100 | 0.020156 | 0.0050517 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1213-15_0_8_load_84 | 101 | 0.0034504 | 0.00086474 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1213-15_0_8_load_93 | 103 | 0.0085404 | 0.0021404 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1213-15_0_8_load_94 | 104 | 0.0099936 | 0.0025046 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1213-15_0_8_load_90 | 105 | 0.0071199 | 0.0017844 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1213-15_0_8_load_85 | 106 | 0.0074934 | 0.001878 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1213-15_0_8_load_86 | 107 | 0.00619 | 0.0015514 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1213-15_0_8_load_87 | 108 | 0.0089729 | 0.0022488 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1213-15_0_8_load_88 | 109 | 0.010233 | 0.0025648 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1213-15_0_8_load_91 | 111 | 0.0057198 | 0.0014335 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1213-15_0_8_load_95 | 112 | 0.005115 | 0.0012819 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1213-15_0_8_load_96 | 113 | 0.0070464 | 0.001766 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1213-15_0_8_load_100 | 114 | 0.0084831 | 0.0021261 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1213-15_0_8_load_113 | 115 | 0.007462 | 0.0018702 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1213-15_0_8_load_101 | 116 | 0.0050559 | 0.0012671 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1213-15_0_8_load_112 | 117 | 0.006775 | 0.001698 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1213-15_0_8_load_138 | 120 | 0.006427 | 0.0016108 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1213-15_0_8_load_102 | 121 | 0.014932 | 0.0037424 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1213-15_0_8_load_103 | 122 | 0.0099242 | 0.0024872 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1213-15_0_8_load_104 | 123 | 0.011061 | 0.0027722 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1213-15_0_8_load_106 | 124 | 0.0092998 | 0.0023308 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1213-15_0_8_load_107 | 125 | 0.0086743 | 0.002174 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1213-15_0_8_load_108 | 126 | 0.0033479 | 0.00083906 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1213-15_0_8_load_110 | 128 | 0.0030029 | 0.0007526 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1213-15_0_8_load_111 | 129 | 0.0063716 | 0.0015969 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1213-15_0_8_load_114 | 130 | 0.0069786 | 0.001749 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1213-15_0_8_load_122 | 131 | 0.0043738 | 0.0010962 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1213-15_0_8_load_118 | 132 | 0.0079341 | 0.0019885 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1213-15_0_8_load_120 | 133 | 0.0031227 | 0.00078263 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 61 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1213-15_0_8_line_0 |  | 0 | 1 | 0.0075881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1213-15_0_8_line_1 |  | 0 | 2 | 0.013796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1213-15_0_8_line_2 |  | 1 | 3 | 0.018537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1213-15_0_8_line_3 |  | 2 | 4 | 0.086685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1213-15_0_8_line_4 |  | 2 | 5 | 0.003609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1213-15_0_8_line_5 |  | 3 | 6 | 0.0012213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1213-15_0_8_line_6 |  | 4 | 7 | 0.038361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1213-15_0_8_line_7 |  | 6 | 8 | 0.014395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1213-15_0_8_line_8 |  | 7 | 9 | 0.017832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1213-15_0_8_line_9 |  | 9 | 23 | 0.0019631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_1213-15_0_8_line_10 |  | 9 | 20 | 0.010671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1213-15_0_8_line_11 |  | 10 | 11 | 0.0069821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1213-15_0_8_line_12 |  | 10 | 12 | 0.060458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1213-15_0_8_line_13 |  | 11 | 13 | 0.016098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1213-15_0_8_line_14 |  | 12 | 14 | 0.0638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1213-15_0_8_line_15 |  | 14 | 15 | 0.0047619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1213-15_0_8_line_16 |  | 15 | 30 | 0.026644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1213-15_0_8_line_17 |  | 16 | 17 | 0.022522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_1213-15_0_8_line_18 |  | 16 | 18 | 0.020917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_1213-15_0_8_line_19 |  | 17 | 19 | 0.037323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_1213-15_0_8_line_20 |  | 18 | 20 | 0.039746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_1213-15_0_8_line_21 |  | 19 | 21 | 0.058198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_1213-15_0_8_line_22 |  | 21 | 22 | 0.052141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1213-15_0_8_line_23 |  | 22 | 53 | 0.030714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_1213-15_0_8_line_24 |  | 23 | 24 | 0.0057451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1213-15_0_8_line_25 |  | 24 | 33 | 0.013526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_1213-15_0_8_line_26 |  | 25 | 26 | 0.032666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1213-15_0_8_line_27 |  | 26 | 98 | 0.030807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1213-15_0_8_line_28 |  | 27 | 28 | 0.0077487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1213-15_0_8_line_29 |  | 27 | 29 | 0.019209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1213-15_0_8_line_30 |  | 28 | 30 | 0.023055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1213-15_0_8_line_31 |  | 29 | 101 | 0.011296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1213-15_0_8_line_32 |  | 30 | 31 | 0.014649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1213-15_0_8_line_33 |  | 31 | 32 | 0.010975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1213-15_0_8_line_34 |  | 32 | 46 | 0.022907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1213-15_0_8_line_35 |  | 33 | 34 | 0.0021088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_1213-15_0_8_line_36 |  | 34 | 35 | 0.012733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_1213-15_0_8_line_37 |  | 35 | 36 | 0.019573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1213-15_0_8_line_38 |  | 35 | 37 | 0.06422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_1213-15_0_8_line_39 |  | 36 | 38 | 0.0096395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1213-15_0_8_line_40 |  | 36 | 39 | 0.015234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1213-15_0_8_line_41 |  | 37 | 40 | 0.0062775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_1213-15_0_8_line_42 |  | 38 | 42 | 0.024414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1213-15_0_8_line_43 |  | 40 | 41 | 0.021198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_1213-15_0_8_line_44 |  | 41 | 44 | 0.0035531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_1213-15_0_8_line_45 |  | 42 | 43 | 0.026227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1213-15_0_8_line_46 |  | 43 | 60 | 0.017688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1213-15_0_8_line_47 |  | 44 | 45 | 0.017482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_1213-15_0_8_line_48 |  | 45 | 61 | 0.045076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_1213-15_0_8_line_49 |  | 46 | 132 | 0.010874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1213-15_0_8_line_50 |  | 47 | 48 | 0.058494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1213-15_0_8_line_51 |  | 48 | 65 | 0.023664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_1213-15_0_8_line_52 |  | 48 | 63 | 0.016939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_1213-15_0_8_line_53 |  | 49 | 50 | 0.015726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1213-15_0_8_line_54 |  | 49 | 51 | 0.049106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1213-15_0_8_line_55 |  | 50 | 55 | 0.028371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1213-15_0_8_line_56 |  | 51 | 54 | 0.018752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_1213-15_0_8_line_57 |  | 51 | 56 | 0.029867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_1213-15_0_8_line_58 |  | 52 | 53 | 0.029789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_1213-15_0_8_line_59 |  | 52 | 54 | 0.04638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_1213-15_0_8_line_60 |  | 54 | 57 | 0.0014053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1213-15_0_8_line_61 |  | 56 | 89 | 0.0154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_1213-15_0_8_line_62 |  | 57 | 93 | 0.02488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1213-15_0_8_line_63 |  | 58 | 59 | 0.012609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1213-15_0_8_line_64 |  | 59 | 86 | 0.04153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1213-15_0_8_line_65 |  | 60 | 62 | 0.020733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1213-15_0_8_line_66 |  | 61 | 63 | 0.039436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_1213-15_0_8_line_67 |  | 62 | 64 | 0.0047162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1213-15_0_8_line_68 |  | 64 | 95 | 0.0048052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1213-15_0_8_line_69 |  | 65 | 66 | 0.020495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_1213-15_0_8_line_70 |  | 66 | 131 | 0.021352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1213-15_0_8_line_71 |  | 66 | 129 | 0.0031569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_1213-15_0_8_line_72 |  | 67 | 68 | 0.017162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_1213-15_0_8_line_73 |  | 67 | 69 | 0.073637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_1213-15_0_8_line_74 |  | 68 | 70 | 0.019779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_1213-15_0_8_line_75 |  | 69 | 71 | 0.017038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_1213-15_0_8_line_76 |  | 70 | 72 | 0.058036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_1213-15_0_8_line_77 |  | 71 | 76 | 0.015321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_1213-15_0_8_line_78 |  | 72 | 75 | 0.01659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_1213-15_0_8_line_79 |  | 73 | 74 | 0.0064563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1213-15_0_8_line_80 |  | 74 | 75 | 0.029636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_1213-15_0_8_line_81 |  | 76 | 77 | 0.023851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_1213-15_0_8_line_82 |  | 77 | 78 | 0.0064544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_1213-15_0_8_line_83 |  | 78 | 79 | 0.010412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_1213-15_0_8_line_84 |  | 79 | 80 | 0.015671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_1213-15_0_8_line_85 |  | 80 | 81 | 0.012737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_1213-15_0_8_line_86 |  | 81 | 82 | 0.014811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_1213-15_0_8_line_87 |  | 82 | 83 | 0.015547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_1213-15_0_8_line_88 |  | 83 | 84 | 0.018538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1213-15_0_8_line_89 |  | 83 | 85 | 0.0078525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_1213-15_0_8_line_90 |  | 84 | 86 | 0.019146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1213-15_0_8_line_91 |  | 84 | 87 | 0.014369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1213-15_0_8_line_92 |  | 85 | 88 | 0.023851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_1213-15_0_8_line_93 |  | 88 | 89 | 0.017752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_1213-15_0_8_line_94 |  | 89 | 90 | 0.024773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1213-15_0_8_line_95 |  | 90 | 91 | 0.020613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1213-15_0_8_line_96 |  | 91 | 92 | 0.027054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1213-15_0_8_line_97 |  | 93 | 94 | 0.0013105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1213-15_0_8_line_98 |  | 95 | 96 | 0.0084704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1213-15_0_8_line_99 |  | 96 | 97 | 0.012382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1213-15_0_8_line_100 |  | 98 | 99 | 0.011783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1213-15_0_8_line_101 |  | 99 | 100 | 0.013656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1213-15_0_8_line_102 |  | 99 | 101 | 0.019172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1213-15_0_8_line_103 |  | 100 | 102 | 0.037402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1213-15_0_8_line_104 |  | 102 | 103 | 0.021435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1213-15_0_8_line_105 |  | 102 | 104 | 0.019043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
106 | LV_1213-15_0_8_line_106 |  | 102 | 105 | 0.015996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1213-15_0_8_line_107 |  | 103 | 114 | 0.012172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1213-15_0_8_line_108 |  | 104 | 115 | 0.029578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_1213-15_0_8_line_109 |  | 105 | 110 | 0.018887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1213-15_0_8_line_110 |  | 106 | 107 | 0.0016433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1213-15_0_8_line_111 |  | 107 | 108 | 0.023984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1213-15_0_8_line_112 |  | 108 | 109 | 0.0025017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1213-15_0_8_line_113 |  | 109 | 110 | 0.030162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1213-15_0_8_line_114 |  | 110 | 111 | 0.013746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1213-15_0_8_line_115 |  | 111 | 112 | 0.0047368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1213-15_0_8_line_116 |  | 112 | 113 | 0.011445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1213-15_0_8_line_117 |  | 113 | 118 | 0.026082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1213-15_0_8_line_118 |  | 114 | 116 | 0.035434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1213-15_0_8_line_119 |  | 115 | 117 | 0.014092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_1213-15_0_8_line_120 |  | 116 | 121 | 0.015817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1213-15_0_8_line_121 |  | 117 | 130 | 0.001027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_1213-15_0_8_line_122 |  | 118 | 119 | 0.003615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1213-15_0_8_line_123 |  | 119 | 120 | 0.067188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1213-15_0_8_line_124 |  | 122 | 123 | 0.0035416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1213-15_0_8_line_125 |  | 123 | 124 | 0.011517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1213-15_0_8_line_126 |  | 124 | 125 | 0.0099947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1213-15_0_8_line_127 |  | 125 | 126 | 0.01751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1213-15_0_8_line_128 |  | 126 | 127 | 0.018225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1213-15_0_8_line_129 |  | 127 | 128 | 0.0089356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_1213-15_0_8_line_130 |  | 127 | 129 | 0.016325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_1213-15_0_8_line_131 |  | 128 | 130 | 0.037481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_1213-15_0_8_line_132 |  | 131 | 133 | 0.009131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1213-15_0_8_trafo_34 | 0.63 MVA 20/0.4 kV | 134 | 61 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2692552.0582 | 1190512.2792 | 2692544.6856 | 1190510.4835
1 | 2692531.281 | 1190507.2187 | 2692544.6856 | 1190510.4835
2 | 2692552.0582 | 1190512.2792 | 2692570.0683 | 1190516.6658
3 | 2692531.281 | 1190507.2187 | 2692528.3034 | 1190515.3223 | 2692528.5145 | 1190517.4491 | 2692529.1201 | 1190523.6625 | 2692545.0717 | 1190537.1733 | 2692567.9712 | 1190580.2293
4 | 2692531.281 | 1190507.2187 | 2692530.9679 | 1190503.6233
5 | 2692571.2549 | 1190516.9548 | 2692570.0683 | 1190516.6658
6 | 2692599.8965 | 1190597.5415 | 2692572.403 | 1190588.5621 | 2692567.9712 | 1190580.2293
7 | 2692585.2413 | 1190520.3614 | 2692571.2549 | 1190516.9548
8 | 2692616.8462 | 1190603.081 | 2692603.0284 | 1190598.5644 | 2692599.8965 | 1190597.5415
9 | 2692616.8462 | 1190603.081 | 2692618.5381 | 1190604.0768
10 | 2692616.8462 | 1190603.081 | 2692619.8055 | 1190592.829
11 | 2692466.6247 | 1190738.5568 | 2692462.4964 | 1190744.1878
12 | 2692410.675 | 1190775.3276 | 2692462.4964 | 1190744.1878
13 | 2692466.6247 | 1190738.5568 | 2692476.1459 | 1190725.5767
14 | 2692410.675 | 1190775.3276 | 2692447.2513 | 1190803.3881 | 2692462.5704 | 1190812.2546
15 | 2692466.6918 | 1190814.64 | 2692462.5704 | 1190812.2546
16 | 2692486.782 | 1190832.206 | 2692469.9573 | 1190817.5034 | 2692466.6918 | 1190814.64
17 | 2692606.9651 | 1190534.331 | 2692605.0748 | 1190528.44 | 2692613.1892 | 1190514.263
18 | 2692606.9651 | 1190534.331 | 2692611.0626 | 1190547.1001 | 2692611.8495 | 1190554.5654
19 | 2692621.5921 | 1190480.7649 | 2692625.3922 | 1190492.9426 | 2692613.1892 | 1190514.263
20 | 2692619.8055 | 1190592.829 | 2692620.6579 | 1190589.876 | 2692613.543 | 1190570.6313 | 2692611.8495 | 1190554.5654
21 | 2692621.5921 | 1190480.7649 | 2692671.4941 | 1190510.7119
22 | 2692671.4941 | 1190510.7119 | 2692667.8211 | 1190526.7654 | 2692672.0832 | 1190546.5329 | 2692684.8486 | 1190555.2369
23 | 2692684.8486 | 1190555.2369 | 2692696.5271 | 1190563.1998 | 2692706.4394 | 1190576.4892
24 | 2692623.4893 | 1190606.9908 | 2692618.5381 | 1190604.0768
25 | 2692623.4893 | 1190606.9908 | 2692635.1465 | 1190613.8517
26 | 2692463.0045 | 1190909.0771 | 2692443.1175 | 1190908.5361 | 2692439.1291 | 1190920.6695
27 | 2692463.0045 | 1190909.0771 | 2692493.8002 | 1190909.9149
28 | 2692493.0532 | 1190862.3648 | 2692491.4757 | 1190854.7785
29 | 2692496.9638 | 1190881.1711 | 2692493.0532 | 1190862.3648
30 | 2692486.782 | 1190832.206 | 2692491.4757 | 1190854.7785
31 | 2692496.9638 | 1190881.1711 | 2692499.2635 | 1190892.2305
32 | 2692486.782 | 1190832.206 | 2692500.3061 | 1190837.9298
33 | 2692500.3061 | 1190837.9298 | 2692510.5466 | 1190841.8775
34 | 2692510.5466 | 1190841.8775 | 2692522.4803 | 1190846.4779 | 2692532.3158 | 1190848.8491
35 | 2692636.964 | 1190614.9214 | 2692635.1465 | 1190613.8517
36 | 2692636.964 | 1190614.9214 | 2692647.9376 | 1190621.3799
37 | 2692664.8062 | 1190631.308 | 2692647.9376 | 1190621.3799
38 | 2692647.9376 | 1190621.3799 | 2692616.6708 | 1190677.4747
39 | 2692664.8062 | 1190631.308 | 2692668.1969 | 1190636.4304 | 2692670.9318 | 1190638.6089
40 | 2692664.8062 | 1190631.308 | 2692666.1565 | 1190623.4016 | 2692671.7261 | 1190618.8182
41 | 2692616.2387 | 1190683.7373 | 2692616.6708 | 1190677.4747
42 | 2692670.9318 | 1190638.6089 | 2692690.0285 | 1190653.8198
43 | 2692616.2387 | 1190683.7373 | 2692614.7798 | 1190704.8849
44 | 2692614.5352 | 1190708.4295 | 2692614.7798 | 1190704.8849
45 | 2692710.5436 | 1190670.1599 | 2692701.9917 | 1190663.3487 | 2692690.0285 | 1190653.8198
46 | 2692724.3793 | 1190681.1802 | 2692722.1509 | 1190679.4045 | 2692710.5436 | 1190670.1599
47 | 2692614.5352 | 1190708.4295 | 2692614.4682 | 1190709.4013 | 2692615.8625 | 1190719.8296 | 2692621.669 | 1190721.2858
48 | 2692621.669 | 1190721.2858 | 2692633.7225 | 1190724.3088 | 2692628.4561 | 1190756.5304
49 | 2692543.018 | 1190850.1052 | 2692538.2 | 1190850.2678 | 2692532.3158 | 1190848.8491
50 | 2692610.3569 | 1190798.6172 | 2692587.8122 | 1190794.299 | 2692554.2069 | 1190782.2605
51 | 2692610.3569 | 1190798.6172 | 2692610.1973 | 1190815.3365 | 2692610.3098 | 1190822.2793
52 | 2692610.3569 | 1190798.6172 | 2692622.5057 | 1190798.1048 | 2692626.4819 | 1190795.4535
53 | 2692775.6014 | 1190608.2425 | 2692788.1539 | 1190617.7154
54 | 2692767.1617 | 1190559.8668 | 2692775.6014 | 1190608.2425
55 | 2692788.1539 | 1190617.7154 | 2692810.8002 | 1190634.8059
56 | 2692750.406 | 1190553.6592 | 2692756.2797 | 1190558.8225 | 2692767.1617 | 1190559.8668
57 | 2692767.1617 | 1190559.8668 | 2692770.5124 | 1190560.1884 | 2692785.7046 | 1190548.861 | 2692793.0484 | 1190547.1057
58 | 2692706.4394 | 1190576.4892 | 2692714.4058 | 1190587.1698 | 2692728.995 | 1190594.8009
59 | 2692750.406 | 1190553.6592 | 2692728.995 | 1190594.8009
60 | 2692749.3506 | 1190552.7313 | 2692750.406 | 1190553.6592
61 | 2692808.0262 | 1190543.5258 | 2692793.0484 | 1190547.1057
62 | 2692730.6644 | 1190536.3048 | 2692749.3506 | 1190552.7313
63 | 2692837.7647 | 1190591.9958 | 2692846.8599 | 1190600.7285
64 | 2692880.1927 | 1190575.9568 | 2692846.8599 | 1190600.7285
65 | 2692724.3793 | 1190681.1802 | 2692729.5787 | 1190685.3234 | 2692738.307 | 1190696.3783
66 | 2692626.4819 | 1190795.4535 | 2692626.4819 | 1190795.4535 | 2692626.7391 | 1190791.6439 | 2692624.6159 | 1190780.0258 | 2692628.4561 | 1190756.5304
67 | 2692740.6093 | 1190700.4142 | 2692739.9677 | 1190698.4816 | 2692738.307 | 1190696.3783
68 | 2692742.1235 | 1190704.9745 | 2692740.6093 | 1190700.4142
69 | 2692610.6419 | 1190842.7721 | 2692610.3098 | 1190822.2793
70 | 2692610.6419 | 1190842.7721 | 2692596.9823 | 1190843.8393 | 2692589.4083 | 1190844.9219
71 | 2692610.6419 | 1190842.7721 | 2692611.2849 | 1190845.8629
72 | 2692840.2851 | 1190390.484 | 2692852.7977 | 1190402.2294
73 | 2692784.1904 | 1190438.19 | 2692840.2851 | 1190390.484
74 | 2692860.5692 | 1190420.4171 | 2692852.7977 | 1190402.2294
75 | 2692784.1904 | 1190438.19 | 2692784.4055 | 1190444.7741 | 2692790.1741 | 1190453.4883
76 | 2692860.5692 | 1190420.4171 | 2692917.6146 | 1190409.7398
77 | 2692798.631 | 1190466.2634 | 2692790.1741 | 1190453.4883
78 | 2692917.6146 | 1190409.7398 | 2692922.5973 | 1190393.9153
79 | 2692916.0718 | 1190359.9213 | 2692919.2243 | 1190365.5556
80 | 2692919.2243 | 1190365.5556 | 2692921.5167 | 1190369.6524 | 2692924.8748 | 1190386.6821 | 2692922.5973 | 1190393.9153
81 | 2692811.7964 | 1190486.1514 | 2692798.631 | 1190466.2634
82 | 2692811.7964 | 1190486.1514 | 2692815.3592 | 1190491.5334
83 | 2692815.3592 | 1190491.5334 | 2692821.1064 | 1190500.2153
84 | 2692829.7568 | 1190513.2828 | 2692821.1064 | 1190500.2153
85 | 2692837.8057 | 1190523.1406 | 2692830.7789 | 1190514.8268 | 2692829.7568 | 1190513.2828
86 | 2692837.8057 | 1190523.1406 | 2692847.3665 | 1190534.4525
87 | 2692857.4024 | 1190546.3266 | 2692847.3665 | 1190534.4525
88 | 2692857.4024 | 1190546.3266 | 2692869.3847 | 1190560.4993
89 | 2692857.4024 | 1190546.3266 | 2692849.5624 | 1190545.8819
90 | 2692869.3847 | 1190560.4993 | 2692878.9856 | 1190571.8555 | 2692880.1927 | 1190575.9568
91 | 2692869.3847 | 1190560.4993 | 2692883.5279 | 1190563.0391
92 | 2692825.7497 | 1190544.5311 | 2692849.5624 | 1190545.8819
93 | 2692808.0262 | 1190543.5258 | 2692825.7497 | 1190544.5311
94 | 2692808.0262 | 1190543.5258 | 2692789.1015 | 1190527.5401
95 | 2692773.3549 | 1190514.2388 | 2692789.1015 | 1190527.5401
96 | 2692752.6873 | 1190496.7808 | 2692773.3549 | 1190514.2388
97 | 2692730.6644 | 1190536.3048 | 2692729.6801 | 1190535.4395
98 | 2692742.1235 | 1190704.9745 | 2692744.7927 | 1190713.0134
99 | 2692748.1445 | 1190724.8998 | 2692747.5598 | 1190721.3472 | 2692744.7927 | 1190713.0134
100 | 2692505.5787 | 1190910.2354 | 2692493.8002 | 1190909.9149
101 | 2692505.5787 | 1190910.2354 | 2692512.2067 | 1190922.1753
102 | 2692505.5787 | 1190910.2354 | 2692500.645 | 1190898.8741 | 2692499.2635 | 1190892.2305
103 | 2692541.6993 | 1190943.515 | 2692534.4549 | 1190938.0773 | 2692515.9064 | 1190928.8403 | 2692512.2067 | 1190922.1753
104 | 2692541.6993 | 1190943.515 | 2692552.6439 | 1190957.7267 | 2692554.857 | 1190960.4354
105 | 2692541.6993 | 1190943.515 | 2692552.6593 | 1190927.9423
106 | 2692541.6993 | 1190943.515 | 2692533.6177 | 1190957.3188
107 | 2692554.857 | 1190960.4354 | 2692562.5586 | 1190969.8617
108 | 2692569.993 | 1190903.9948 | 2692567.2436 | 1190907.22 | 2692552.6593 | 1190927.9423
109 | 2692524.0753 | 1190973.6175 | 2692533.6177 | 1190957.3188
110 | 2692465.993 | 1190969.0329 | 2692467.6276 | 1190969.202
111 | 2692467.6276 | 1190969.202 | 2692477.4419 | 1190970.2169 | 2692491.5441 | 1190970.8796
112 | 2692491.5441 | 1190970.8796 | 2692494.043 | 1190970.997
113 | 2692524.0753 | 1190973.6175 | 2692505.6526 | 1190971.5425 | 2692494.043 | 1190970.997
114 | 2692524.0753 | 1190973.6175 | 2692520.224 | 1190982.5081 | 2692519.7956 | 1190986.5427
115 | 2692519.7956 | 1190986.5427 | 2692519.2954 | 1190991.253
116 | 2692519.2954 | 1190991.253 | 2692519.1797 | 1190992.3427 | 2692519.4357 | 1191001.4303 | 2692519.667 | 1191002.6672
117 | 2692529.3642 | 1191026.5999 | 2692521.267 | 1191011.2204 | 2692519.667 | 1191002.6672
118 | 2692562.5586 | 1190969.8617 | 2692577.0798 | 1190987.6348 | 2692583.9914 | 1190990.9216 | 2692588.7865 | 1190991.5029
119 | 2692579.1349 | 1190893.2711 | 2692569.993 | 1190903.9948
120 | 2692588.7865 | 1190991.5029 | 2692602.3887 | 1190993.152 | 2692604.2977 | 1190994.0625
121 | 2692579.1349 | 1190893.2711 | 2692579.8012 | 1190892.4896
122 | 2692531.138 | 1191029.7515 | 2692529.3642 | 1191026.5999
123 | 2692531.138 | 1191029.7515 | 2692509.5609 | 1191035.4106 | 2692501.0825 | 1191037.2807 | 2692465.8786 | 1191028.0976
124 | 2692641.4033 | 1190914.8471 | 2692638.8528 | 1190912.3897
125 | 2692630.5589 | 1190904.3986 | 2692638.8528 | 1190912.3897
126 | 2692626.3094 | 1190895.6069 | 2692628.5992 | 1190902.5105 | 2692630.5589 | 1190904.3986
127 | 2692626.3094 | 1190895.6069 | 2692620.7969 | 1190878.9872
128 | 2692614.6096 | 1190861.8457 | 2692619.9216 | 1190876.3483 | 2692620.7969 | 1190878.9872
129 | 2692614.6096 | 1190861.8457 | 2692607.7432 | 1190867.5639
130 | 2692614.6096 | 1190861.8457 | 2692611.2849 | 1190845.8629
131 | 2692607.7432 | 1190867.5639 | 2692594.3066 | 1190878.7536 | 2692581.6126 | 1190890.3647 | 2692579.8012 | 1190892.4896
132 | 2692589.4083 | 1190844.9219 | 2692580.3692 | 1190846.214

## bus_geodata
| x | y | coords
0 | 2692544.6856 | 1190510.4835
1 | 2692552.0582 | 1190512.2792
2 | 2692531.281 | 1190507.2187
3 | 2692570.0683 | 1190516.6658
4 | 2692567.9712 | 1190580.2293
5 | 2692530.9679 | 1190503.6233
6 | 2692571.2549 | 1190516.9548
7 | 2692599.8965 | 1190597.5415
8 | 2692585.2413 | 1190520.3614
9 | 2692616.8462 | 1190603.081
10 | 2692462.4964 | 1190744.1878
11 | 2692466.6247 | 1190738.5568
12 | 2692410.675 | 1190775.3276
13 | 2692476.1459 | 1190725.5767
14 | 2692462.5704 | 1190812.2546
15 | 2692466.6918 | 1190814.64
16 | 2692606.9651 | 1190534.331
17 | 2692613.1892 | 1190514.263
18 | 2692611.8495 | 1190554.5654
19 | 2692621.5921 | 1190480.7649
20 | 2692619.8055 | 1190592.829
21 | 2692671.4941 | 1190510.7119
22 | 2692684.8486 | 1190555.2369
23 | 2692618.5381 | 1190604.0768
24 | 2692623.4893 | 1190606.9908
25 | 2692439.1291 | 1190920.6695
26 | 2692463.0045 | 1190909.0771
27 | 2692493.0532 | 1190862.3648
28 | 2692491.4757 | 1190854.7784
29 | 2692496.9638 | 1190881.1711
30 | 2692486.782 | 1190832.206
31 | 2692500.3061 | 1190837.9298
32 | 2692510.5466 | 1190841.8775
33 | 2692635.1465 | 1190613.8517
34 | 2692636.964 | 1190614.9214
35 | 2692647.9376 | 1190621.3799
36 | 2692664.8062 | 1190631.308
37 | 2692616.6708 | 1190677.4747
38 | 2692670.9318 | 1190638.6089
39 | 2692671.7261 | 1190618.8182
40 | 2692616.2387 | 1190683.7373
41 | 2692614.7798 | 1190704.8849
42 | 2692690.0285 | 1190653.8198
43 | 2692710.5436 | 1190670.1599
44 | 2692614.5352 | 1190708.4295
45 | 2692621.669 | 1190721.2858
46 | 2692532.3158 | 1190848.8491
47 | 2692554.2069 | 1190782.2605
48 | 2692610.3569 | 1190798.6172
49 | 2692775.6014 | 1190608.2425
50 | 2692788.1539 | 1190617.7154
51 | 2692767.1617 | 1190559.8668
52 | 2692728.995 | 1190594.8009
53 | 2692706.4394 | 1190576.4892
54 | 2692750.406 | 1190553.6592
55 | 2692810.8002 | 1190634.8059
56 | 2692793.0484 | 1190547.1057
57 | 2692749.3506 | 1190552.7313
58 | 2692837.7647 | 1190591.9958
59 | 2692846.8599 | 1190600.7285
60 | 2692724.3793 | 1190681.1802
61 | 2692628.4561 | 1190756.5304
62 | 2692738.307 | 1190696.3783
63 | 2692626.4819 | 1190795.4535
64 | 2692740.6093 | 1190700.4142
65 | 2692610.3098 | 1190822.2793
66 | 2692610.6419 | 1190842.7721
67 | 2692840.2851 | 1190390.484
68 | 2692852.7977 | 1190402.2294
69 | 2692784.1904 | 1190438.19
70 | 2692860.5692 | 1190420.4171
71 | 2692790.1741 | 1190453.4883
72 | 2692917.6146 | 1190409.7398
73 | 2692916.0718 | 1190359.9213
74 | 2692919.2243 | 1190365.5556
75 | 2692922.5973 | 1190393.9153
76 | 2692798.631 | 1190466.2634
77 | 2692811.7964 | 1190486.1514
78 | 2692815.3592 | 1190491.5334
79 | 2692821.1064 | 1190500.2153
80 | 2692829.7568 | 1190513.2828
81 | 2692837.8057 | 1190523.1406
82 | 2692847.3665 | 1190534.4525
83 | 2692857.4024 | 1190546.3266
84 | 2692869.3847 | 1190560.4993
85 | 2692849.5624 | 1190545.8819
86 | 2692880.1927 | 1190575.9568
87 | 2692883.5279 | 1190563.0391
88 | 2692825.7497 | 1190544.5311
89 | 2692808.0262 | 1190543.5258
90 | 2692789.1015 | 1190527.5401
91 | 2692773.3549 | 1190514.2388
92 | 2692752.6873 | 1190496.7808
93 | 2692730.6644 | 1190536.3048
94 | 2692729.6801 | 1190535.4395
95 | 2692742.1235 | 1190704.9745
96 | 2692744.7927 | 1190713.0134
97 | 2692748.1445 | 1190724.8998
98 | 2692493.8002 | 1190909.9149
99 | 2692505.5787 | 1190910.2354
100 | 2692512.2067 | 1190922.1753
101 | 2692499.2635 | 1190892.2305
102 | 2692541.6993 | 1190943.515
103 | 2692554.857 | 1190960.4355
104 | 2692552.6593 | 1190927.9423
105 | 2692533.6177 | 1190957.3188
106 | 2692465.993 | 1190969.0329
107 | 2692467.6276 | 1190969.202
108 | 2692491.5441 | 1190970.8796
109 | 2692494.043 | 1190970.997
110 | 2692524.0753 | 1190973.6175
111 | 2692519.7956 | 1190986.5427
112 | 2692519.2954 | 1190991.253
113 | 2692519.667 | 1191002.6672
114 | 2692562.5586 | 1190969.8617
115 | 2692569.993 | 1190903.9948
116 | 2692588.7865 | 1190991.5029
117 | 2692579.1349 | 1190893.2711
118 | 2692529.3642 | 1191026.5999
119 | 2692531.138 | 1191029.7515
120 | 2692465.8786 | 1191028.0976
121 | 2692604.2977 | 1190994.0625
122 | 2692641.4033 | 1190914.8471
123 | 2692638.8528 | 1190912.3897
124 | 2692630.5589 | 1190904.3986
125 | 2692626.3094 | 1190895.6069
126 | 2692620.7969 | 1190878.9872
127 | 2692614.6096 | 1190861.8457
128 | 2692607.7432 | 1190867.5639
129 | 2692611.2849 | 1190845.8629
130 | 2692579.8012 | 1190892.4896
131 | 2692589.4083 | 1190844.9219
132 | 2692543.018 | 1190850.1052
133 | 2692580.3692 | 1190846.214
134 | 2692610.3569 | 1190798.6172

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98366 | -0.31276 | 0.0084155 | 0.0021091
1 | 0.98354 | -0.31511 | 0.0053467 | 0.00134
2 | 0.98399 | -0.30639 | 0 | 0
3 | 0.98334 | -0.31908 | 0.0037959 | 0.00095135
4 | 0.98657 | -0.2561 | 0.0031437 | 0.0007879
5 | 0.98396 | -0.30683 | 0.0066861 | 0.0016757
6 | 0.98333 | -0.31925 | 0.0046767 | 0.0011721
7 | 0.98782 | -0.23177 | 0.0018829 | 0.0004719
8 | 0.98328 | -0.32013 | 0.0033909 | 0.00084985
9 | 0.98844 | -0.21988 | 0 | 0
10 | 0.97572 | -0.46899 | 0.0050615 | 0.0012685
11 | 0.97567 | -0.46998 | 0 | 0
12 | 0.97644 | -0.4548 | 0 | 0
13 | 0.97555 | -0.47227 | 0.0077672 | 0.0019466
14 | 0.9772 | -0.43984 | 0.0037336 | 0.00093572
15 | 0.97727 | -0.4384 | 0 | 0
16 | 0.98566 | -0.27318 | 0.0014735 | 0.0003693
17 | 0.98481 | -0.28962 | 0.0012373 | 0.00031011
18 | 0.98646 | -0.2578 | 0.0038957 | 0.00097635
19 | 0.9834 | -0.31672 | 0.0014623 | 0.00036647
20 | 0.98801 | -0.22794 | 0.0012172 | 0.00030505
21 | 0.98124 | -0.35875 | 0.0056242 | 0.0014096
22 | 0.97936 | -0.39523 | 0.002906 | 0.00072832
23 | 0.98853 | -0.21807 | 0.0019539 | 0.0004897
24 | 0.98881 | -0.21273 | 0.0034195 | 0.00085701
25 | 0.97922 | -0.40027 | 0.015571 | 0.0039026
26 | 0.97969 | -0.39103 | 0.0040569 | 0.0010168
27 | 0.97859 | -0.41259 | 0.0032731 | 0.00082033
28 | 0.97834 | -0.41738 | 0.0030723 | 0.00076998
29 | 0.97925 | -0.39958 | 0.0083308 | 0.0020879
30 | 0.97768 | -0.43035 | 0 | 0
31 | 0.97749 | -0.43417 | 0 | 0
32 | 0.97734 | -0.43704 | 0.0029351 | 0.0007356
33 | 0.98947 | -0.19997 | 0.0024069 | 0.00060323
34 | 0.98958 | -0.19795 | 0.0038136 | 0.00095579
35 | 0.99022 | -0.1856 | 0.003817 | 0.00095662
36 | 0.98958 | -0.198 | 0 | 0
37 | 0.99406 | -0.11237 | 0.0052591 | 0.0013181
38 | 0.98932 | -0.20314 | 0.0052363 | 0.0013123
39 | 0.98951 | -0.19953 | 0.005657 | 0.0014178
40 | 0.99444 | -0.10509 | 0.0051968 | 0.0013024
41 | 0.99576 | -0.080088 | 0.0030661 | 0.00076844
42 | 0.98877 | -0.21389 | 0.0040091 | 0.0010048
43 | 0.98827 | -0.22357 | 0.0030267 | 0.00075856
44 | 0.99598 | -0.075855 | 0.0035226 | 0.00088285
45 | 0.9971 | -0.054788 | 0.0034661 | 0.0008687
46 | 0.9771 | -0.44179 | 0.0034396 | 0.00086205
47 | 0.99528 | -0.089797 | 0.012116 | 0.0030367
48 | 0.99593 | -0.077333 | 0 | 0
49 | 0.97472 | -0.48622 | 0 | 0
50 | 0.97458 | -0.48896 | 0.0038072 | 0.00095416
51 | 0.97515 | -0.47766 | 0.0063021 | 0.0015794
52 | 0.97726 | -0.43641 | 0.0040872 | 0.0010244
53 | 0.97828 | -0.41638 | 0.0038109 | 0.0009551
54 | 0.97571 | -0.46682 | 0.0046027 | 0.0011535
55 | 0.97443 | -0.49193 | 0.0056942 | 0.0014271
56 | 0.97438 | -0.49279 | 0.0059377 | 0.0014881
57 | 0.97569 | -0.46715 | 0.0044284 | 0.0011099
58 | 0.97176 | -0.54456 | 0.0072842 | 0.0018256
59 | 0.97185 | -0.54287 | 0.0053029 | 0.001329
60 | 0.98798 | -0.22916 | 0.0034996 | 0.00087709
61 | 1 | 0 | -0.60479 | -0.1549
62 | 0.98771 | -0.23441 | 0.0039896 | 0.0009999
63 | 0.99713 | -0.054351 | 0.0061555 | 0.0015427
64 | 0.98767 | -0.23526 | 0.0034914 | 0.00087502
65 | 0.9943 | -0.10827 | 0.0040483 | 0.0010146
66 | 0.99292 | -0.13478 | 0 | 0
67 | 0.97091 | -0.56138 | 0.0037329 | 0.00093555
68 | 0.97079 | -0.56374 | 0.0043861 | 0.0010993
69 | 0.97149 | -0.54999 | 0.0032084 | 0.0008041
70 | 0.97068 | -0.56606 | 0.013986 | 0.0035052
71 | 0.97163 | -0.5471 | 0.0034038 | 0.00085307
72 | 0.97052 | -0.56911 | 0.0045733 | 0.0011462
73 | 0.97045 | -0.57054 | 0.0015101 | 0.00037846
74 | 0.97046 | -0.57036 | 0.0037959 | 0.00095135
75 | 0.9705 | -0.56963 | 0.0014839 | 0.0003719
76 | 0.97178 | -0.54426 | 0.0030916 | 0.00077484
77 | 0.97202 | -0.53951 | 0.001978 | 0.00049573
78 | 0.97208 | -0.53817 | 0.003139 | 0.00078671
79 | 0.9722 | -0.53585 | 0.002391 | 0.00059924
80 | 0.97239 | -0.53218 | 0.0036674 | 0.00091913
81 | 0.97255 | -0.52899 | 0.0068114 | 0.0017071
82 | 0.97276 | -0.52481 | 0.0030175 | 0.00075627
83 | 0.97299 | -0.52022 | 0 | 0
84 | 0.97264 | -0.52729 | 0 | 0
85 | 0.97315 | -0.51715 | 0.0025237 | 0.00063249
86 | 0.97233 | -0.53322 | 0.0042365 | 0.0010618
87 | 0.97258 | -0.52831 | 0.0038765 | 0.00097155
88 | 0.97364 | -0.50756 | 0.0029743 | 0.00074544
89 | 0.97401 | -0.50018 | 0 | 0
90 | 0.97368 | -0.50659 | 0.0048349 | 0.0012117
91 | 0.97351 | -0.5101 | 0.0049241 | 0.0012341
92 | 0.9734 | -0.51225 | 0.0043189 | 0.0010824
93 | 0.9755 | -0.47087 | 0.0048973 | 0.0012274
94 | 0.9755 | -0.47095 | 0.0032841 | 0.00082308
95 | 0.98764 | -0.23584 | 0.0019948 | 0.00049995
96 | 0.9876 | -0.23655 | 0.0015573 | 0.00039031
97 | 0.98757 | -0.23725 | 0.0031427 | 0.00078763
98 | 0.98025 | -0.38005 | 0.012511 | 0.0031355
99 | 0.9806 | -0.37319 | 0 | 0
100 | 0.98163 | -0.35312 | 0.020156 | 0.0050517
101 | 0.97973 | -0.39023 | 0.0034504 | 0.00086474
102 | 0.98514 | -0.28483 | 0 | 0
103 | 0.98441 | -0.29909 | 0.0085404 | 0.0021404
104 | 0.98692 | -0.25024 | 0.0099936 | 0.0025046
105 | 0.98419 | -0.30332 | 0.0071199 | 0.0017844
106 | 0.98191 | -0.34787 | 0.0074934 | 0.001878
107 | 0.98192 | -0.34764 | 0.00619 | 0.0015514
108 | 0.98222 | -0.34171 | 0.0089729 | 0.0022488
109 | 0.98228 | -0.34069 | 0.010233 | 0.0025648
110 | 0.98319 | -0.32278 | 0 | 0
111 | 0.98288 | -0.32881 | 0.0057198 | 0.0014335
112 | 0.9828 | -0.3304 | 0.005115 | 0.0012819
113 | 0.98266 | -0.33318 | 0.0070464 | 0.001766
114 | 0.98409 | -0.30532 | 0.0084831 | 0.0021261
115 | 0.98838 | -0.22214 | 0.007462 | 0.0018702
116 | 0.98343 | -0.31808 | 0.0050559 | 0.0012671
117 | 0.98909 | -0.20832 | 0.006775 | 0.001698
118 | 0.9825 | -0.33621 | 0 | 0
119 | 0.98248 | -0.33663 | 0 | 0
120 | 0.98208 | -0.34443 | 0.006427 | 0.0016108
121 | 0.98322 | -0.32234 | 0.014932 | 0.0037424
122 | 0.9898 | -0.19504 | 0.0099242 | 0.0024872
123 | 0.98983 | -0.19441 | 0.011061 | 0.0027722
124 | 0.99005 | -0.19011 | 0.0092998 | 0.0023308
125 | 0.99033 | -0.18473 | 0.0086743 | 0.002174
126 | 0.99095 | -0.17261 | 0.0033479 | 0.00083906
127 | 0.99166 | -0.15894 | 0 | 0
128 | 0.99117 | -0.16832 | 0.0030029 | 0.0007526
129 | 0.99271 | -0.13876 | 0.0063716 | 0.0015969
130 | 0.98915 | -0.20728 | 0.0069786 | 0.001749
131 | 0.99277 | -0.13761 | 0.0043738 | 0.0010962
132 | 0.97702 | -0.44337 | 0.0079341 | 0.0019885
133 | 0.99275 | -0.13811 | 0.0031227 | 0.00078263
134 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.017215 | 0.0043156 | -0.017213 | -0.0043144 | 1.9297e-06 | 1.1387e-06 | 0.026042 | 0.026042 | 0.026042 | 0.98366 | -0.31276 | 0.98354 | -0.31511 | 7.1543
1 | -0.02563 | -0.0064247 | 0.025638 | 0.0064295 | 7.7774e-06 | 4.8024e-06 | 0.038772 | 0.038772 | 0.038772 | 0.98366 | -0.31276 | 0.98399 | -0.30639 | 10.6516
2 | 0.011866 | 0.0029744 | -0.011864 | -0.0029732 | 2.2404e-06 | 1.1986e-06 | 0.017953 | 0.017953 | 0.017953 | 0.98354 | -0.31511 | 0.98334 | -0.31908 | 4.932
3 | -0.032324 | -0.0081052 | 0.032402 | 0.0081539 | 7.7676e-05 | 4.8609e-05 | 0.048883 | 0.048883 | 0.048883 | 0.98399 | -0.30639 | 0.98657 | -0.2561 | 13.4294
4 | 0.0066863 | 0.0016757 | -0.0066861 | -0.0016757 | 1.3836e-07 | 4.2711e-08 | 0.010111 | 0.010111 | 0.010111 | 0.98399 | -0.30639 | 0.98396 | -0.30683 | 2.7778
5 | 0.0080679 | 0.0020219 | -0.0080678 | -0.0020219 | 6.8262e-08 | 2.8195e-08 | 0.012209 | 0.012209 | 0.012209 | 0.98334 | -0.31908 | 0.98333 | -0.31925 | 3.354
6 | -0.035546 | -0.0089417 | 0.035587 | 0.0089677 | 4.1366e-05 | 2.5984e-05 | 0.053624 | 0.053624 | 0.053624 | 0.98657 | -0.2561 | 0.98782 | -0.23177 | 14.732
7 | 0.0033911 | 0.00084976 | -0.0033909 | -0.00084985 | 1.4215e-07 | -9.1627e-08 | 0.0051315 | 0.0051316 | 0.0051316 | 0.98333 | -0.31925 | 0.98328 | -0.32013 | 1.4098
8 | -0.03747 | -0.0094396 | 0.037491 | 0.009453 | 2.1317e-05 | 1.3414e-05 | 0.056461 | 0.05646 | 0.056461 | 0.98782 | -0.23177 | 0.98844 | -0.21988 | 15.5111
9 | -0.20889 | -0.053252 | 0.20891 | 0.053264 | 1.8237e-05 | 1.1571e-05 | 0.31479 | 0.31479 | 0.31479 | 0.98844 | -0.21988 | 0.98853 | -0.21807 | 21.6202
10 | 0.1714 | 0.043799 | -0.17133 | -0.043757 | 6.6759e-05 | 4.2179e-05 | 0.25833 | 0.25833 | 0.25833 | 0.98844 | -0.21988 | 0.98801 | -0.22794 | 17.7424
11 | 0.0077684 | 0.0019471 | -0.007768 | -0.001947 | 3.675e-07 | 1.48e-07 | 0.011847 | 0.011847 | 0.011847 | 0.97572 | -0.46899 | 0.97567 | -0.46998 | 3.2547
12 | -0.01283 | -0.0032157 | 0.012839 | 0.0032205 | 8.6795e-06 | 4.7992e-06 | 0.019566 | 0.019566 | 0.019566 | 0.97572 | -0.46899 | 0.97644 | -0.4548 | 5.3753
13 | 0.007768 | 0.001947 | -0.0077672 | -0.0019466 | 8.473e-07 | 3.4126e-07 | 0.011847 | 0.011847 | 0.011847 | 0.97567 | -0.46998 | 0.97555 | -0.47227 | 3.2548
14 | -0.012839 | -0.0032205 | 0.012848 | 0.0032255 | 9.159e-06 | 5.0631e-06 | 0.019566 | 0.019566 | 0.019566 | 0.97644 | -0.4548 | 0.9772 | -0.43984 | 5.3753
15 | -0.016581 | -0.0041612 | 0.016582 | 0.0041619 | 1.1386e-06 | 6.6904e-07 | 0.025251 | 0.025251 | 0.025251 | 0.9772 | -0.43984 | 0.97727 | -0.4384 | 6.9371
16 | -0.016582 | -0.0041619 | 0.016589 | 0.0041657 | 6.3706e-06 | 3.7432e-06 | 0.025251 | 0.025251 | 0.025251 | 0.97727 | -0.4384 | 0.97768 | -0.43035 | 6.9371
17 | 0.16438 | 0.041874 | -0.16425 | -0.041792 | 0.00013028 | 8.223e-05 | 0.2484 | 0.2484 | 0.2484 | 0.98566 | -0.27318 | 0.98481 | -0.28962 | 17.0603
18 | -0.16585 | -0.042243 | 0.16597 | 0.042321 | 0.00012317 | 7.7762e-05 | 0.25062 | 0.25062 | 0.25062 | 0.98566 | -0.27318 | 0.98646 | -0.2578 | 17.213
19 | 0.16301 | 0.041481 | -0.1628 | -0.041347 | 0.00021266 | 0.0001342 | 0.24653 | 0.24653 | 0.24653 | 0.98481 | -0.28962 | 0.9834 | -0.31672 | 16.9319
20 | -0.16987 | -0.043297 | 0.17011 | 0.043452 | 0.00024515 | 0.00015486 | 0.2565 | 0.2565 | 0.2565 | 0.98646 | -0.2578 | 0.98801 | -0.22794 | 17.6166
21 | 0.16133 | 0.040981 | -0.16101 | -0.040775 | 0.00032568 | 0.00020549 | 0.24432 | 0.24432 | 0.24432 | 0.9834 | -0.31672 | 0.98124 | -0.35875 | 16.78
22 | 0.15538 | 0.039366 | -0.15511 | -0.039194 | 0.00027176 | 0.0001713 | 0.23579 | 0.23579 | 0.23579 | 0.98124 | -0.35875 | 0.97936 | -0.39523 | 16.1943
23 | 0.15221 | 0.038466 | -0.15205 | -0.038369 | 0.00015415 | 9.711e-05 | 0.23137 | 0.23137 | 0.23137 | 0.97936 | -0.39523 | 0.97828 | -0.41638 | 15.8911
24 | -0.21086 | -0.053754 | 0.21092 | 0.053788 | 5.4374e-05 | 3.4504e-05 | 0.31773 | 0.31773 | 0.31773 | 0.98853 | -0.21807 | 0.98881 | -0.21273 | 21.8222
25 | -0.21434 | -0.054645 | 0.21447 | 0.054729 | 0.0001322 | 8.3913e-05 | 0.32288 | 0.32288 | 0.32288 | 0.98881 | -0.21273 | 0.98947 | -0.19997 | 22.1756
26 | -0.015571 | -0.0039026 | 0.015578 | 0.0039065 | 6.8587e-06 | 3.9784e-06 | 0.023662 | 0.023662 | 0.023662 | 0.97922 | -0.40027 | 0.97969 | -0.39103 | 6.5006
27 | -0.019635 | -0.0049233 | 0.019646 | 0.0049295 | 1.0276e-05 | 6.1883e-06 | 0.029824 | 0.029824 | 0.029824 | 0.97969 | -0.39103 | 0.98025 | -0.38005 | 8.1934
28 | 0.034004 | 0.0085428 | -0.033997 | -0.0085379 | 7.7708e-06 | 4.876e-06 | 0.051714 | 0.051714 | 0.051714 | 0.97859 | -0.41259 | 0.97834 | -0.41738 | 14.2071
29 | -0.037278 | -0.0093631 | 0.037301 | 0.0093777 | 2.315e-05 | 1.4574e-05 | 0.056691 | 0.056691 | 0.056691 | 0.97859 | -0.41259 | 0.97925 | -0.39958 | 15.5744
30 | 0.030924 | 0.0077679 | -0.030905 | -0.007756 | 1.9132e-05 | 1.1955e-05 | 0.047041 | 0.047041 | 0.047041 | 0.97834 | -0.41738 | 0.97768 | -0.43035 | 12.9234
31 | -0.045632 | -0.011466 | 0.045652 | 0.011478 | 2.0372e-05 | 1.2896e-05 | 0.06935 | 0.06935 | 0.06935 | 0.97925 | -0.39958 | 0.97973 | -0.39023 | 19.0521
32 | 0.014316 | 0.0035903 | -0.014314 | -0.0035888 | 2.6083e-06 | 1.4857e-06 | 0.02179 | 0.02179 | 0.02179 | 0.97768 | -0.43035 | 0.97749 | -0.43417 | 5.9863
33 | 0.014314 | 0.0035888 | -0.014312 | -0.0035877 | 1.9542e-06 | 1.1131e-06 | 0.02179 | 0.02179 | 0.02179 | 0.97749 | -0.43417 | 0.97734 | -0.43704 | 5.9864
34 | 0.011377 | 0.0028521 | -0.011374 | -0.0028508 | 2.5774e-06 | 1.3625e-06 | 0.017322 | 0.017322 | 0.017322 | 0.97734 | -0.43704 | 0.9771 | -0.44179 | 4.7587
35 | -0.21687 | -0.055332 | 0.2169 | 0.055346 | 2.1075e-05 | 1.338e-05 | 0.3265 | 0.3265 | 0.3265 | 0.98947 | -0.19997 | 0.98958 | -0.19795 | 22.4242
36 | -0.22071 | -0.056301 | 0.22084 | 0.056385 | 0.00013176 | 8.3672e-05 | 0.33223 | 0.33223 | 0.33223 | 0.98958 | -0.19795 | 0.99022 | -0.1856 | 22.818
37 | 0.035665 | 0.0089598 | -0.035644 | -0.0089465 | 2.1089e-05 | 1.3245e-05 | 0.053601 | 0.053601 | 0.053601 | 0.99022 | -0.1856 | 0.98958 | -0.198 | 14.7257
38 | -0.26032 | -0.066302 | 0.26125 | 0.066889 | 0.00092311 | 0.00058747 | 0.39157 | 0.39157 | 0.39157 | 0.99022 | -0.1856 | 0.99406 | -0.11237 | 26.8933
39 | 0.029986 | 0.0075287 | -0.029979 | -0.0075241 | 7.3508e-06 | 4.5807e-06 | 0.045095 | 0.045095 | 0.045095 | 0.98958 | -0.198 | 0.98932 | -0.20314 | 12.3886
40 | 0.0056574 | 0.0014178 | -0.005657 | -0.0014178 | 4.1342e-07 | 6.8886e-08 | 0.0085069 | 0.008507 | 0.008507 | 0.98958 | -0.198 | 0.98951 | -0.19953 | 2.3371
41 | -0.26651 | -0.068207 | 0.2666 | 0.068267 | 9.3898e-05 | 5.9769e-05 | 0.39944 | 0.39944 | 0.39944 | 0.99406 | -0.11237 | 0.99444 | -0.10509 | 27.4339
42 | 0.024743 | 0.0062118 | -0.02473 | -0.006204 | 1.2682e-05 | 7.8034e-06 | 0.037219 | 0.037219 | 0.037219 | 0.98932 | -0.20314 | 0.98877 | -0.21389 | 10.2249
43 | -0.2718 | -0.069569 | 0.27213 | 0.069779 | 0.00032954 | 0.0002098 | 0.40721 | 0.40721 | 0.40721 | 0.99444 | -0.10509 | 0.99576 | -0.080088 | 27.968
44 | -0.27519 | -0.070548 | 0.27525 | 0.070583 | 5.6486e-05 | 3.5966e-05 | 0.4118 | 0.4118 | 0.4118 | 0.99576 | -0.080088 | 0.99598 | -0.075855 | 28.2827
45 | 0.020721 | 0.0051992 | -0.020711 | -0.0051934 | 9.5651e-06 | 5.7854e-06 | 0.031185 | 0.031186 | 0.031186 | 0.98877 | -0.21389 | 0.98827 | -0.22357 | 8.5675
46 | 0.017685 | 0.0044348 | -0.01768 | -0.0044321 | 4.7033e-06 | 2.7836e-06 | 0.026628 | 0.026628 | 0.026628 | 0.98827 | -0.22357 | 0.98798 | -0.22916 | 7.3155
47 | -0.27877 | -0.071466 | 0.27906 | 0.071648 | 0.00028506 | 0.00018153 | 0.41706 | 0.41706 | 0.41706 | 0.99598 | -0.075855 | 0.9971 | -0.054788 | 28.6441
48 | -0.28252 | -0.072517 | 0.28328 | 0.072996 | 0.00075338 | 0.0004798 | 0.42223 | 0.42223 | 0.42223 | 0.9971 | -0.054788 | 1 | 0 | 28.9994
49 | 0.0079346 | 0.0019887 | -0.0079341 | -0.0019885 | 5.9539e-07 | 2.4486e-07 | 0.012084 | 0.012084 | 0.012084 | 0.9771 | -0.44179 | 0.97702 | -0.44337 | 3.3197
50 | -0.012116 | -0.0030367 | 0.012124 | 0.0030405 | 7.198e-06 | 3.846e-06 | 0.018115 | 0.018115 | 0.018115 | 0.99528 | -0.089797 | 0.99593 | -0.077333 | 4.9766
51 | 0.3004 | 0.076568 | -0.29995 | -0.076283 | 0.00044781 | 0.00028537 | 0.44928 | 0.44928 | 0.44928 | 0.99593 | -0.077333 | 0.9943 | -0.10827 | 30.8573
52 | -0.31252 | -0.079608 | 0.31287 | 0.07983 | 0.00034691 | 0.00022114 | 0.4674 | 0.4674 | 0.4674 | 0.99593 | -0.077333 | 0.99713 | -0.054351 | 32.1014
53 | 0.0095034 | 0.002382 | -0.0095021 | -0.0023814 | 1.2413e-06 | 5.9842e-07 | 0.014508 | 0.014508 | 0.014508 | 0.97472 | -0.48622 | 0.97458 | -0.48896 | 3.9857
54 | -0.0095034 | -0.002382 | 0.0095073 | 0.0023839 | 3.876e-06 | 1.8683e-06 | 0.014508 | 0.014508 | 0.014508 | 0.97472 | -0.48622 | 0.97515 | -0.47766 | 3.9857
55 | 0.005695 | 0.0014273 | -0.0056942 | -0.0014271 | 8.0442e-07 | 1.6135e-07 | 0.0086952 | 0.0086954 | 0.0086954 | 0.97458 | -0.48896 | 0.97443 | -0.49193 | 2.3888
56 | -0.12652 | -0.031813 | 0.12659 | 0.031854 | 6.5555e-05 | 4.1019e-05 | 0.1931 | 0.1931 | 0.1931 | 0.97515 | -0.47766 | 0.97571 | -0.46682 | 13.2626
57 | 0.11071 | 0.02785 | -0.11063 | -0.0278 | 7.9952e-05 | 4.968e-05 | 0.16898 | 0.16898 | 0.16898 | 0.97515 | -0.47766 | 0.97438 | -0.49279 | 11.6057
58 | -0.1481 | -0.037324 | 0.14824 | 0.037414 | 0.00014211 | 8.9455e-05 | 0.22558 | 0.22558 | 0.22558 | 0.97726 | -0.43641 | 0.97828 | -0.41638 | 15.493
59 | 0.14401 | 0.0363 | -0.1438 | -0.036169 | 0.00020922 | 0.00013158 | 0.21935 | 0.21936 | 0.21936 | 0.97726 | -0.43641 | 0.97571 | -0.46682 | 15.0656
60 | 0.012611 | 0.003161 | -0.012611 | -0.0031609 | 1.9494e-07 | 1.0721e-07 | 0.019233 | 0.019233 | 0.019233 | 0.97571 | -0.46682 | 0.97569 | -0.46715 | 5.2839
61 | 0.1047 | 0.026312 | -0.10466 | -0.026289 | 3.6918e-05 | 2.2861e-05 | 0.15991 | 0.15991 | 0.15991 | 0.97438 | -0.49279 | 0.97401 | -0.50018 | 10.983
62 | 0.0081829 | 0.0020511 | -0.0081814 | -0.0020504 | 1.4531e-06 | 6.1931e-07 | 0.01248 | 0.01248 | 0.01248 | 0.97569 | -0.46715 | 0.9755 | -0.47087 | 3.4285
63 | -0.0072842 | -0.0018256 | 0.0072848 | 0.0018258 | 5.8825e-07 | 2.2026e-07 | 0.011154 | 0.011154 | 0.011154 | 0.97176 | -0.54456 | 0.97185 | -0.54287 | 3.0643
64 | -0.012588 | -0.0031548 | 0.012593 | 0.003158 | 5.7849e-06 | 3.1875e-06 | 0.019273 | 0.019273 | 0.019273 | 0.97185 | -0.54287 | 0.97233 | -0.53322 | 5.2949
65 | 0.01418 | 0.003555 | -0.014177 | -0.003553 | 3.5466e-06 | 2.0044e-06 | 0.021358 | 0.021358 | 0.021358 | 0.98798 | -0.22916 | 0.98771 | -0.23441 | 5.8675
66 | 0.31986 | 0.081908 | -0.31902 | -0.081372 | 0.00083972 | 0.00053536 | 0.47658 | 0.47658 | 0.47658 | 1 | 0 | 0.99713 | -0.054351 | 32.7322
67 | 0.010187 | 0.0025531 | -0.010187 | -0.0025529 | 4.1657e-07 | 2.0624e-07 | 0.015347 | 0.015347 | 0.015347 | 0.98771 | -0.23441 | 0.98767 | -0.23526 | 4.2163
68 | 0.0066953 | 0.0016778 | -0.0066951 | -0.0016778 | 1.8335e-07 | 5.5848e-08 | 0.010087 | 0.010087 | 0.010087 | 0.98767 | -0.23526 | 0.98764 | -0.23584 | 2.7712
69 | 0.2959 | 0.075268 | -0.29552 | -0.075027 | 0.00037746 | 0.00024051 | 0.44322 | 0.44322 | 0.44322 | 0.9943 | -0.10827 | 0.99292 | -0.13478 | 30.4412
70 | 0.0074976 | 0.0018791 | -0.0074966 | -0.0018787 | 1.0109e-06 | 3.7085e-07 | 0.011236 | 0.011236 | 0.011236 | 0.99292 | -0.13478 | 0.99277 | -0.13761 | 3.0869
71 | 0.28803 | 0.073148 | -0.28797 | -0.073113 | 5.523e-05 | 3.5184e-05 | 0.43199 | 0.43199 | 0.43199 | 0.99292 | -0.13478 | 0.99271 | -0.13876 | 29.6695
72 | 0.029744 | 0.0074505 | -0.02974 | -0.0074493 | 3.3431e-06 | 1.2907e-06 | 0.045583 | 0.045584 | 0.045584 | 0.97091 | -0.56138 | 0.97079 | -0.56374 | 3.1307
73 | -0.033476 | -0.0083861 | 0.033495 | 0.0083941 | 1.8171e-05 | 7.9843e-06 | 0.051304 | 0.051303 | 0.051304 | 0.97091 | -0.56138 | 0.97149 | -0.54999 | 3.5237
74 | 0.025354 | 0.00635 | -0.025351 | -0.0063492 | 2.8002e-06 | 8.1408e-07 | 0.038861 | 0.038861 | 0.038861 | 0.97079 | -0.56374 | 0.97068 | -0.56606 | 2.669
75 | -0.036703 | -0.0091982 | 0.036708 | 0.0092006 | 5.0482e-06 | 2.3868e-06 | 0.056217 | 0.056217 | 0.056217 | 0.97149 | -0.54999 | 0.97163 | -0.5471 | 3.8611
76 | 0.011365 | 0.0028439 | -0.011364 | -0.0028458 | 1.6513e-06 | -1.8122e-06 | 0.017421 | 0.017422 | 0.017422 | 0.97068 | -0.56606 | 0.97052 | -0.56911 | 1.1966
77 | -0.040112 | -0.010054 | 0.040117 | 0.010056 | 5.4201e-06 | 2.7097e-06 | 0.06143 | 0.06143 | 0.06143 | 0.97163 | -0.5471 | 0.97178 | -0.54426 | 4.2191
78 | 0.0067903 | 0.0016996 | -0.0067901 | -0.0017003 | 1.6856e-07 | -7.1214e-07 | 0.01041 | 0.01041 | 0.01041 | 0.97052 | -0.56911 | 0.9705 | -0.56963 | 0.715
79 | -0.0015101 | -0.00037846 | 0.0015101 | 0.00037839 | 1.298e-08 | -7.1463e-08 | 0.0023154 | 0.0023154 | 0.0023154 | 0.97045 | -0.57054 | 0.97046 | -0.57036 | 0.63611
80 | -0.005306 | -0.0013297 | 0.0053062 | 0.0013284 | 1.8389e-07 | -1.347e-06 | 0.0081358 | 0.0081352 | 0.0081358 | 0.97046 | -0.57036 | 0.9705 | -0.56963 | 0.55877
81 | -0.043209 | -0.010831 | 0.043219 | 0.010836 | 9.7883e-06 | 5.0823e-06 | 0.066164 | 0.066163 | 0.066164 | 0.97178 | -0.54426 | 0.97202 | -0.53951 | 4.5442
82 | -0.045197 | -0.011332 | 0.0452 | 0.011334 | 2.8969e-06 | 1.534e-06 | 0.069191 | 0.069191 | 0.069191 | 0.97202 | -0.53951 | 0.97208 | -0.53817 | 4.7521
83 | -0.048339 | -0.01212 | 0.048344 | 0.012123 | 5.3446e-06 | 2.9042e-06 | 0.073996 | 0.073996 | 0.073996 | 0.97208 | -0.53817 | 0.9722 | -0.53585 | 5.0821
84 | -0.050735 | -0.012722 | 0.050744 | 0.012727 | 8.8597e-06 | 4.8927e-06 | 0.077655 | 0.077655 | 0.077655 | 0.9722 | -0.53585 | 0.97239 | -0.53218 | 5.3335
85 | -0.054411 | -0.013646 | 0.054419 | 0.013651 | 8.2793e-06 | 4.6666e-06 | 0.083267 | 0.083267 | 0.083267 | 0.97239 | -0.53218 | 0.97255 | -0.52899 | 5.7189
86 | -0.061231 | -0.015358 | 0.061243 | 0.015365 | 1.2188e-05 | 7.065e-06 | 0.093689 | 0.093688 | 0.093689 | 0.97255 | -0.52899 | 0.97276 | -0.52481 | 6.4347
87 | -0.064261 | -0.016122 | 0.064275 | 0.01613 | 1.4085e-05 | 8.2423e-06 | 0.098304 | 0.098304 | 0.098304 | 0.97276 | -0.52481 | 0.97299 | -0.52022 | 6.7517
88 | 0.020718 | 0.0051983 | -0.020711 | -0.0051941 | 6.9801e-06 | 4.2371e-06 | 0.031687 | 0.031687 | 0.031687 | 0.97299 | -0.52022 | 0.97264 | -0.52729 | 8.7053
89 | -0.084993 | -0.021328 | 0.085005 | 0.021336 | 1.244e-05 | 7.5712e-06 | 0.12999 | 0.12999 | 0.12999 | 0.97299 | -0.52022 | 0.97315 | -0.51715 | 8.928
90 | 0.016835 | 0.0042226 | -0.01683 | -0.0042198 | 4.763e-06 | 2.8108e-06 | 0.025756 | 0.025756 | 0.025756 | 0.97264 | -0.52729 | 0.97233 | -0.53322 | 7.0759
91 | 0.0038767 | 0.00097149 | -0.0038765 | -0.00097155 | 1.8954e-07 | -5.7022e-08 | 0.0059309 | 0.0059309 | 0.0059309 | 0.97264 | -0.52729 | 0.97258 | -0.52831 | 1.6294
92 | -0.087529 | -0.021968 | 0.087569 | 0.021993 | 4.006e-05 | 2.4453e-05 | 0.13385 | 0.13385 | 0.13385 | 0.97315 | -0.51715 | 0.97364 | -0.50756 | 9.193
93 | -0.090544 | -0.022738 | 0.090575 | 0.022758 | 3.1876e-05 | 1.9517e-05 | 0.1384 | 0.13839 | 0.1384 | 0.97364 | -0.50756 | 0.97401 | -0.50018 | 9.5052
94 | 0.014084 | 0.0035314 | -0.01408 | -0.0035289 | 4.3011e-06 | 2.4445e-06 | 0.021517 | 0.021517 | 0.021517 | 0.97401 | -0.50018 | 0.97368 | -0.50659 | 5.9114
95 | 0.009245 | 0.0023172 | -0.0092435 | -0.0023165 | 1.543e-06 | 7.312e-07 | 0.014129 | 0.014129 | 0.014129 | 0.97368 | -0.50659 | 0.97351 | -0.5101 | 3.8815
96 | 0.0043194 | 0.0010824 | -0.0043189 | -0.0010824 | 4.4223e-07 | -5.3312e-08 | 0.0066022 | 0.0066023 | 0.0066023 | 0.97351 | -0.5101 | 0.9734 | -0.51225 | 1.8138
97 | 0.0032842 | 0.00082308 | -0.0032841 | -0.00082308 | 1.2333e-08 | -8.4675e-09 | 0.0050096 | 0.0050096 | 0.0050096 | 0.9755 | -0.47087 | 0.9755 | -0.47095 | 1.3763
98 | 0.0047003 | 0.0011778 | -0.0047001 | -0.0011778 | 1.5929e-07 | -6.4431e-09 | 0.0070816 | 0.0070816 | 0.0070816 | 0.98764 | -0.23584 | 0.9876 | -0.23655 | 1.9455
99 | 0.0031428 | 0.00078754 | -0.0031427 | -0.00078763 | 1.0411e-07 | -9.1799e-08 | 0.0047352 | 0.0047352 | 0.0047352 | 0.9876 | -0.23655 | 0.98757 | -0.23725 | 1.3009
100 | -0.032156 | -0.008065 | 0.032167 | 0.0080716 | 1.0529e-05 | 6.5902e-06 | 0.048816 | 0.048815 | 0.048816 | 0.98025 | -0.38005 | 0.9806 | -0.37319 | 13.4109
101 | -0.081309 | -0.02044 | 0.081387 | 0.02049 | 7.7988e-05 | 4.974e-05 | 0.12341 | 0.12341 | 0.12341 | 0.9806 | -0.37319 | 0.98163 | -0.35312 | 33.9026
102 | 0.049142 | 0.012369 | -0.049102 | -0.012343 | 4e-05 | 2.5358e-05 | 0.07459 | 0.07459 | 0.07459 | 0.9806 | -0.37319 | 0.97973 | -0.39023 | 20.4918
103 | -0.10154 | -0.025542 | 0.10188 | 0.025754 | 0.00033246 | 0.0002123 | 0.15396 | 0.15396 | 0.15396 | 0.98163 | -0.35312 | 0.98514 | -0.28483 | 42.2966
104 | 0.037061 | 0.0093063 | -0.037036 | -0.0092904 | 2.5195e-05 | 1.5852e-05 | 0.055985 | 0.055985 | 0.055985 | 0.98514 | -0.28483 | 0.98441 | -0.29909 | 15.3806
105 | -0.20341 | -0.051277 | 0.20375 | 0.051493 | 0.00033729 | 0.00021538 | 0.30735 | 0.30735 | 0.30735 | 0.98514 | -0.28483 | 0.98692 | -0.25024 | 42.2188
106 | 0.064475 | 0.016217 | -0.064418 | -0.016181 | 5.6914e-05 | 3.6221e-05 | 0.097408 | 0.097408 | 0.097408 | 0.98514 | -0.28483 | 0.98419 | -0.30332 | 26.7604
107 | 0.028495 | 0.00715 | -0.028487 | -0.0071447 | 8.4699e-06 | 5.2661e-06 | 0.043076 | 0.043076 | 0.043076 | 0.98441 | -0.29909 | 0.98409 | -0.30532 | 11.8341
108 | -0.21374 | -0.053997 | 0.21403 | 0.05418 | 0.00028826 | 0.00018297 | 0.32242 | 0.32242 | 0.32242 | 0.98692 | -0.25024 | 0.98838 | -0.22214 | 22.1442
109 | 0.057298 | 0.014397 | -0.057245 | -0.014363 | 5.3168e-05 | 3.3788e-05 | 0.086643 | 0.086643 | 0.086643 | 0.98419 | -0.30332 | 0.98319 | -0.32278 | 23.8031
110 | -0.0074934 | -0.001878 | 0.0074935 | 0.0018781 | 7.9464e-08 | 3.0071e-08 | 0.011356 | 0.011356 | 0.011356 | 0.98191 | -0.34787 | 0.98192 | -0.34764 | 3.1197
111 | -0.013684 | -0.0034294 | 0.013687 | 0.0034316 | 3.8674e-06 | 2.1716e-06 | 0.020736 | 0.020736 | 0.020736 | 0.98192 | -0.34764 | 0.98222 | -0.34171 | 5.6968
112 | -0.02266 | -0.0056804 | 0.022661 | 0.0056811 | 1.1056e-06 | 6.7593e-07 | 0.03433 | 0.03433 | 0.03433 | 0.98222 | -0.34171 | 0.98228 | -0.34069 | 9.4312
113 | -0.032895 | -0.0082458 | 0.032923 | 0.0082634 | 2.8087e-05 | 1.7593e-05 | 0.049832 | 0.049832 | 0.049832 | 0.98228 | -0.34069 | 0.98319 | -0.32278 | 13.6901
114 | 0.024322 | 0.0060993 | -0.024315 | -0.006095 | 6.9852e-06 | 4.2963e-06 | 0.036811 | 0.036811 | 0.036811 | 0.98319 | -0.32278 | 0.98288 | -0.32881 | 10.113
115 | 0.018595 | 0.0046615 | -0.018594 | -0.0046607 | 1.4078e-06 | 8.4095e-07 | 0.028152 | 0.028152 | 0.028152 | 0.98288 | -0.32881 | 0.9828 | -0.3304 | 7.7341
116 | 0.013479 | 0.0033787 | -0.013477 | -0.0033777 | 1.7875e-06 | 9.9899e-07 | 0.020408 | 0.020408 | 0.020408 | 0.9828 | -0.3304 | 0.98266 | -0.33318 | 5.6065
117 | 0.0064305 | 0.0016117 | -0.0064295 | -0.0016115 | 9.2743e-07 | 2.6319e-07 | 0.0097375 | 0.0097376 | 0.0097376 | 0.98266 | -0.33318 | 0.9825 | -0.33621 | 2.6752
118 | 0.020004 | 0.0050186 | -0.019991 | -0.0050113 | 1.2158e-05 | 7.3315e-06 | 0.030249 | 0.030249 | 0.030249 | 0.98409 | -0.30532 | 0.98343 | -0.31808 | 8.3102
119 | -0.22149 | -0.056051 | 0.22164 | 0.056144 | 0.00014707 | 9.3401e-05 | 0.33365 | 0.33365 | 0.33365 | 0.98838 | -0.22214 | 0.98909 | -0.20832 | 22.9158
120 | 0.014935 | 0.0037442 | -0.014932 | -0.0037424 | 3.0292e-06 | 1.738e-06 | 0.022599 | 0.022599 | 0.022599 | 0.98343 | -0.31808 | 0.98322 | -0.32234 | 6.2085
121 | -0.22842 | -0.057842 | 0.22843 | 0.057849 | 1.1384e-05 | 7.2327e-06 | 0.34385 | 0.34385 | 0.34385 | 0.98909 | -0.20832 | 0.98915 | -0.20728 | 23.6158
122 | 0.0064295 | 0.0016115 | -0.0064294 | -0.0016114 | 1.2854e-07 | 3.6487e-08 | 0.0097376 | 0.0097377 | 0.0097377 | 0.9825 | -0.33621 | 0.98248 | -0.33663 | 2.6752
123 | 0.0064294 | 0.0016114 | -0.006427 | -0.0016108 | 2.3892e-06 | 6.7856e-07 | 0.0097377 | 0.009738 | 0.009738 | 0.98248 | -0.33663 | 0.98208 | -0.34443 | 2.6753
124 | -0.0099242 | -0.0024872 | 0.0099245 | 0.0024874 | 2.9563e-07 | 1.4368e-07 | 0.01492 | 0.01492 | 0.01492 | 0.9898 | -0.19504 | 0.98983 | -0.19441 | 4.0988
125 | -0.020986 | -0.0052596 | 0.02099 | 0.0052622 | 4.2986e-06 | 2.603e-06 | 0.031548 | 0.031548 | 0.031548 | 0.98983 | -0.19441 | 0.99005 | -0.19011 | 8.6671
126 | -0.03029 | -0.007593 | 0.030298 | 0.0075978 | 7.7679e-06 | 4.8429e-06 | 0.045525 | 0.045525 | 0.045525 | 0.99005 | -0.19011 | 0.99033 | -0.18473 | 12.507
127 | -0.038972 | -0.0097718 | 0.038995 | 0.009786 | 2.2517e-05 | 1.4185e-05 | 0.058559 | 0.058559 | 0.058559 | 0.99033 | -0.18473 | 0.99095 | -0.17261 | 16.0876
128 | -0.042342 | -0.010625 | 0.04237 | 0.010642 | 2.7633e-05 | 1.745e-05 | 0.063586 | 0.063586 | 0.063586 | 0.99095 | -0.17261 | 0.99166 | -0.15894 | 17.4687
129 | 0.23896 | 0.0607 | -0.23885 | -0.060631 | 0.00010788 | 6.858e-05 | 0.35885 | 0.35885 | 0.35885 | 0.99166 | -0.15894 | 0.99117 | -0.16832 | 24.6464
130 | -0.28133 | -0.071342 | 0.2816 | 0.071516 | 0.00027312 | 0.00017395 | 0.42244 | 0.42244 | 0.42244 | 0.99166 | -0.15894 | 0.99271 | -0.13876 | 29.0135
131 | 0.23585 | 0.059879 | -0.23541 | -0.059598 | 0.0004412 | 0.00028044 | 0.35434 | 0.35434 | 0.35434 | 0.99117 | -0.16832 | 0.98915 | -0.20728 | 24.3368
132 | 0.0031228 | 0.00078256 | -0.0031227 | -0.00078263 | 7.5016e-08 | -7.0054e-08 | 0.0046806 | 0.0046806 | 0.0046806 | 0.99277 | -0.13761 | 0.99275 | -0.13811 | 1.2859

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60753 | 0.15559

## res_load
| p_mw | q_mvar
0 | 0.0084155 | 0.0021091
1 | 0.0053467 | 0.00134
2 | 0.0037959 | 0.00095135
3 | 0.0031437 | 0.0007879
4 | 0.0066861 | 0.0016757
5 | 0.0046767 | 0.0011721
6 | 0.0018829 | 0.0004719
7 | 0.0033909 | 0.00084985
8 | 0.0050615 | 0.0012685
9 | 0.0077672 | 0.0019466
10 | 0.0037336 | 0.00093572
11 | 0.0014735 | 0.0003693
12 | 0.0012373 | 0.00031011
13 | 0.0038957 | 0.00097635
14 | 0.0014623 | 0.00036647
15 | 0.0012172 | 0.00030505
16 | 0.0056242 | 0.0014096
17 | 0.002906 | 0.00072832
18 | 0.0019539 | 0.0004897
19 | 0.0034195 | 0.00085701
20 | 0.015571 | 0.0039026
21 | 0.0040569 | 0.0010168
22 | 0.0032731 | 0.00082033
23 | 0.0030723 | 0.00076998
24 | 0.0083308 | 0.0020879
25 | 0.0029351 | 0.0007356
26 | 0.0024069 | 0.00060323
27 | 0.0038136 | 0.00095579
28 | 0.003817 | 0.00095662
29 | 0.0052591 | 0.0013181
30 | 0.0052363 | 0.0013123
31 | 0.005657 | 0.0014178
32 | 0.0051968 | 0.0013024
33 | 0.0030661 | 0.00076844
34 | 0.0040091 | 0.0010048
35 | 0.0030267 | 0.00075856
36 | 0.0035226 | 0.00088285
37 | 0.0034661 | 0.0008687
38 | 0.0034396 | 0.00086205
39 | 0.012116 | 0.0030367
40 | 0.0038072 | 0.00095416
41 | 0.0063021 | 0.0015794
42 | 0.0040872 | 0.0010244
43 | 0.0038109 | 0.0009551
44 | 0.0046027 | 0.0011535
45 | 0.0056942 | 0.0014271
46 | 0.0059377 | 0.0014881
47 | 0.0044284 | 0.0011099
48 | 0.0072842 | 0.0018256
49 | 0.0053029 | 0.001329
50 | 0.0034996 | 0.00087709
51 | 0.0027405 | 0.00068683
52 | 0.0039896 | 0.0009999
53 | 0.0061555 | 0.0015427
54 | 0.0034914 | 0.00087502
55 | 0.0040483 | 0.0010146
56 | 0.0037329 | 0.00093555
57 | 0.0043861 | 0.0010993
58 | 0.0032084 | 0.0008041
59 | 0.013986 | 0.0035052
60 | 0.0034038 | 0.00085307
61 | 0.0045733 | 0.0011462
62 | 0.0015101 | 0.00037846
63 | 0.0037959 | 0.00095135
64 | 0.0014839 | 0.0003719
65 | 0.0030916 | 0.00077484
66 | 0.001978 | 0.00049573
67 | 0.003139 | 0.00078671
68 | 0.002391 | 0.00059924
69 | 0.0036674 | 0.00091913
70 | 0.0068114 | 0.0017071
71 | 0.0030175 | 0.00075627
72 | 0.0025237 | 0.00063249
73 | 0.0042365 | 0.0010618
74 | 0.0038765 | 0.00097155
75 | 0.0029743 | 0.00074544
76 | 0.0048349 | 0.0012117
77 | 0.0049241 | 0.0012341
78 | 0.0043189 | 0.0010824
79 | 0.0048973 | 0.0012274
80 | 0.0032841 | 0.00082308
81 | 0.0019948 | 0.00049995
82 | 0.0015573 | 0.00039031
83 | 0.0031427 | 0.00078763
84 | 0.012511 | 0.0031355
85 | 0.020156 | 0.0050517
86 | 0.0034504 | 0.00086474
87 | 0.0085404 | 0.0021404
88 | 0.0099936 | 0.0025046
89 | 0.0071199 | 0.0017844
90 | 0.0074934 | 0.001878
91 | 0.00619 | 0.0015514
92 | 0.0089729 | 0.0022488
93 | 0.010233 | 0.0025648
94 | 0.0057198 | 0.0014335
95 | 0.005115 | 0.0012819
96 | 0.0070464 | 0.001766
97 | 0.0084831 | 0.0021261
98 | 0.007462 | 0.0018702
99 | 0.0050559 | 0.0012671
100 | 0.006775 | 0.001698
101 | 0.006427 | 0.0016108
102 | 0.014932 | 0.0037424
103 | 0.0099242 | 0.0024872
104 | 0.011061 | 0.0027722
105 | 0.0092998 | 0.0023308
106 | 0.0086743 | 0.002174
107 | 0.0033479 | 0.00083906
108 | 0.0030029 | 0.0007526
109 | 0.0063716 | 0.0015969
110 | 0.0069786 | 0.001749
111 | 0.0043738 | 0.0010962
112 | 0.0079341 | 0.0019885
113 | 0.0031227 | 0.00078263

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1