## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1213-2_1_3_node_17 | 0.4 | n |  | TRUE
1 | bus_LV_1213-2_1_3_node_18 | 0.4 | n |  | TRUE
2 | bus_LV_1213-2_1_3_node_19 | 0.4 | n |  | TRUE
3 | bus_LV_1213-2_1_3_node_20 | 0.4 | n |  | TRUE
4 | bus_LV_1213-2_1_3_node_21 | 0.4 | n |  | TRUE
5 | bus_LV_1213-2_1_3_node_22 | 0.4 | n |  | TRUE
6 | bus_LV_1213-2_1_3_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_1213-2_1_3_node_40 | 0.4 | n |  | TRUE
8 | bus_LV_1213-2_1_3_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_1213-2_1_3_node_25 | 0.4 | n |  | TRUE
10 | bus_LV_1213-2_1_3_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_1213-2_1_3_node_94 | 0.4 | n |  | TRUE
12 | bus_LV_1213-2_1_3_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_1213-2_1_3_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_1213-2_1_3_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_1213-2_1_3_node_31 | 0.4 | n |  | TRUE
16 | bus_LV_1213-2_1_3_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_1213-2_1_3_node_33 | 0.4 | n |  | TRUE
18 | bus_LV_1213-2_1_3_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_1213-2_1_3_node_47 | 0.4 | n |  | TRUE
20 | bus_LV_1213-2_1_3_node_35 | 0.4 | n |  | TRUE
21 | bus_LV_1213-2_1_3_node_36 | 0.4 | n |  | TRUE
22 | bus_LV_1213-2_1_3_node_37 | 0.4 | n |  | TRUE
23 | bus_LV_1213-2_1_3_node_43 | 0.4 | n |  | TRUE
24 | bus_LV_1213-2_1_3_node_46 | 0.4 | n |  | TRUE
25 | bus_LV_1213-2_1_3_node_55 | 0.4 | n |  | TRUE
26 | bus_LV_1213-2_1_3_node_51 | 0.4 | n |  | TRUE
27 | bus_LV_1213-2_1_3_node_48 | 0.4 | n |  | TRUE
28 | bus_LV_1213-2_1_3_node_49 | 0.4 | n |  | TRUE
29 | bus_LV_1213-2_1_3_node_50 | 0.4 | n |  | TRUE
30 | bus_LV_1213-2_1_3_node_52 | 0.4 | n |  | TRUE
31 | bus_LV_1213-2_1_3_node_53 | 0.4 | n |  | TRUE
32 | bus_LV_1213-2_1_3_node_54 | 0.4 | n |  | TRUE
33 | bus_LV_1213-2_1_3_node_65 | 0.4 | n |  | TRUE
34 | bus_LV_1213-2_1_3_node_56 | 0.4 | n |  | TRUE
35 | bus_LV_1213-2_1_3_node_64 | 0.4 | n |  | TRUE
36 | bus_LV_1213-2_1_3_node_63 | 0.4 | n |  | TRUE
37 | bus_LV_1213-2_1_3_node_66 | 0.4 | n |  | TRUE
38 | bus_LV_1213-2_1_3_node_67 | 0.4 | n |  | TRUE
39 | bus_LV_1213-2_1_3_node_68 | 0.4 | n |  | TRUE
40 | bus_MV_11_0_node_165 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1213-2_1_3_load_17 | 0 | 0.0024077 | 0.00060343 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1213-2_1_3_load_18 | 1 | 0.0045844 | 0.0011489 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1213-2_1_3_load_19 | 2 | 0.00016127 | 4.0417e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1213-2_1_3_load_20 | 3 | 0.00012016 | 3.0116e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1213-2_1_3_load_21 | 4 | 0.00080426 | 0.00020157 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1213-2_1_3_load_22 | 5 | 0.00030465 | 7.6354e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1213-2_1_3_load_26 | 6 | 0.00013164 | 3.2993e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1213-2_1_3_load_24 | 8 | 0.0002173 | 5.446e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1213-2_1_3_load_25 | 9 | 0.00020829 | 5.2203e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1213-2_1_3_load_27 | 10 | 0.00047802 | 0.0001198 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1213-2_1_3_load_94 | 11 | 0.00053255 | 0.00013347 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1213-2_1_3_load_28 | 12 | 0.0010573 | 0.00026499 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1213-2_1_3_load_30 | 14 | 0.00045035 | 0.00011287 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1213-2_1_3_load_32 | 16 | 0.00048689 | 0.00012203 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1213-2_1_3_load_33 | 17 | 0.0011203 | 0.00028078 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1213-2_1_3_load_34 | 18 | 0.00044887 | 0.0001125 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1213-2_1_3_load_47 | 19 | 0.0025508 | 0.00063929 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1213-2_1_3_load_35 | 20 | 0.00033626 | 8.4274e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1213-2_1_3_load_37 | 22 | 0.0014739 | 0.00036939 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1213-2_1_3_load_43 | 23 | 0.00044453 | 0.00011141 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1213-2_1_3_load_55 | 25 | 0.010875 | 0.0027255 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1213-2_1_3_load_51 | 26 | 0.010873 | 0.0027251 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1213-2_1_3_load_48 | 27 | 0.0016068 | 0.0004027 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1213-2_1_3_load_50 | 29 | 0.0095956 | 0.0024049 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1213-2_1_3_load_54 | 32 | 0.0058748 | 0.0014724 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1213-2_1_3_load_56 | 34 | 0.0103 | 0.0025813 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1213-2_1_3_load_64 | 35 | 0.004086 | 0.0010241 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1213-2_1_3_load_63 | 36 | 0.015873 | 0.0039782 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1213-2_1_3_load_67 | 38 | 0.019506 | 0.0048886 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1213-2_1_3_load_68 | 39 | 0.013932 | 0.0034918 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1213-2_1_3_line_0 |  | 0 | 1 | 0.044187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1213-2_1_3_line_1 |  | 0 | 2 | 0.016783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1213-2_1_3_line_2 |  | 1 | 3 | 0.075748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1213-2_1_3_line_3 |  | 2 | 4 | 0.024434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1213-2_1_3_line_4 |  | 3 | 5 | 0.036766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1213-2_1_3_line_5 |  | 4 | 6 | 0.090306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1213-2_1_3_line_6 |  | 5 | 7 | 0.01166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1213-2_1_3_line_7 |  | 6 | 10 | 0.040088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1213-2_1_3_line_8 |  | 6 | 11 | 0.12149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1213-2_1_3_line_9 |  | 7 | 23 | 0.032527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1213-2_1_3_line_10 |  | 8 | 9 | 0.050264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1213-2_1_3_line_11 |  | 9 | 10 | 0.002169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1213-2_1_3_line_12 |  | 12 | 13 | 0.02204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1213-2_1_3_line_13 |  | 13 | 14 | 0.019635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1213-2_1_3_line_14 |  | 13 | 15 | 0.011952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1213-2_1_3_line_15 |  | 14 | 16 | 0.018357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1213-2_1_3_line_16 |  | 15 | 17 | 0.1922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1213-2_1_3_line_17 |  | 16 | 18 | 0.038471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1213-2_1_3_line_18 |  | 17 | 19 | 0.025125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1213-2_1_3_line_19 |  | 18 | 20 | 0.023195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1213-2_1_3_line_20 |  | 19 | 27 | 0.0082991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1213-2_1_3_line_21 |  | 20 | 21 | 0.088142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1213-2_1_3_line_22 |  | 21 | 22 | 0.14777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1213-2_1_3_line_23 |  | 23 | 24 | 0.12308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1213-2_1_3_line_24 |  | 24 | 25 | 0.082004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1213-2_1_3_line_25 |  | 24 | 26 | 0.064313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1213-2_1_3_line_26 |  | 25 | 34 | 0.043711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1213-2_1_3_line_27 |  | 26 | 28 | 0.068761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1213-2_1_3_line_28 |  | 27 | 28 | 0.08017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1213-2_1_3_line_29 |  | 28 | 29 | 0.041957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1213-2_1_3_line_30 |  | 29 | 30 | 0.13608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1213-2_1_3_line_31 |  | 30 | 31 | 0.028494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1213-2_1_3_line_32 |  | 31 | 32 | 0.14591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1213-2_1_3_line_33 |  | 32 | 33 | 0.16779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1213-2_1_3_line_34 |  | 33 | 37 | 0.057678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1213-2_1_3_line_35 |  | 33 | 38 | 0.06016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1213-2_1_3_line_36 |  | 34 | 35 | 0.029682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1213-2_1_3_line_37 |  | 35 | 36 | 0.0020583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1213-2_1_3_line_38 |  | 37 | 39 | 0.086975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1213-2_1_3_trafo_46 | 0.63 MVA 20/0.4 kV | 40 | 24 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2691782.1701 | 1189822.6777 | 2691788.1076 | 1189778.891 | 2691788.1076 | 1189778.891
1 | 2691776.1741 | 1189767.0898 | 2691788.1076 | 1189778.891
2 | 2691809.9761 | 1189874.9515 | 2691778.3428 | 1189865.0296 | 2691778.5871 | 1189849.1009 | 2691782.1701 | 1189822.6777
3 | 2691776.1741 | 1189767.0898 | 2691772.3594 | 1189763.3174 | 2691759.9334 | 1189748.8524
4 | 2691809.9761 | 1189874.9515 | 2691817.6631 | 1189877.3625 | 2691845.5245 | 1189884.2897
5 | 2691759.9334 | 1189748.8524 | 2691752.2089 | 1189739.8603 | 2691745.9709 | 1189713.9037 | 2691732.9117 | 1189680.6269 | 2691730.2784 | 1189664.8362
6 | 2691856.8399 | 1189887.103 | 2691845.5245 | 1189884.2897
7 | 2691731.487 | 1189625.2684 | 2691728.8314 | 1189632.8339 | 2691729.5937 | 1189660.73 | 2691730.2784 | 1189664.8362
8 | 2691730.2784 | 1189664.8362 | 2691615.4844 | 1189704.622
9 | 2691856.8399 | 1189887.103 | 2691832.9572 | 1189909.1851
10 | 2691732.2054 | 1189623.2218 | 2691734.6618 | 1189616.2237 | 2691742.821 | 1189574.1609
11 | 2691732.2054 | 1189623.2218 | 2691731.487 | 1189625.2684
12 | 2691458.9653 | 1189847.5091 | 2691444.1411 | 1189831.1997
13 | 2691458.9653 | 1189847.5091 | 2691457.901 | 1189867.1148
14 | 2691470.7733 | 1189845.4548 | 2691458.9653 | 1189847.5091
15 | 2691457.901 | 1189867.1148 | 2691457.4365 | 1189875.6703 | 2691457.9141 | 1189885.4477
16 | 2691470.7733 | 1189845.4548 | 2691475.7014 | 1189870.346 | 2691482.7711 | 1189885.3636 | 2691491.2423 | 1189898.5125 | 2691496.2562 | 1189904.315 | 2691521.3198 | 1189934.206 | 2691530.5083 | 1189943.8304 | 2691540.3702 | 1189960.7809 | 2691550.7438 | 1189994.6389 | 2691561.0108 | 1190011.3083
17 | 2691457.9141 | 1189885.4477 | 2691458.3893 | 1189895.1751 | 2691459.0163 | 1189910.0386 | 2691461.6236 | 1189923.6464
18 | 2691561.0108 | 1190011.3083 | 2691562.9937 | 1190014.5278 | 2691579.3157 | 1190028.282
19 | 2691469.9375 | 1189945.1608 | 2691467.3999 | 1189935.9054 | 2691461.8771 | 1189924.9696 | 2691461.6236 | 1189923.6464
20 | 2691585.6619 | 1190033.6299 | 2691579.3157 | 1190028.282
21 | 2691450.7905 | 1190030.5453 | 2691469.9452 | 1189961.4939 | 2691470.8315 | 1189948.4213 | 2691469.9375 | 1189945.1608
22 | 2691306.8171 | 1190007.8446 | 2691324.7531 | 1190019.5367 | 2691345.9817 | 1190024.3747 | 2691450.7905 | 1190030.5453
23 | 2691742.588 | 1189992.7409 | 2691832.9572 | 1189909.1851
24 | 2691742.588 | 1189992.7409 | 2691687.9537 | 1189931.5872
25 | 2691742.588 | 1189992.7409 | 2691696.3757 | 1190037.4693
26 | 2691720.5438 | 1189902.4578 | 2691687.9537 | 1189931.5872 | 2691687.9537 | 1189931.5872
27 | 2691646.9675 | 1190085.2911 | 2691696.3757 | 1190037.4693
28 | 2691646.9675 | 1190085.2911 | 2691585.6619 | 1190033.6299
29 | 2691646.9675 | 1190085.2911 | 2691616.842 | 1190114.4953
30 | 2691519.9235 | 1190209.9828 | 2691533.6888 | 1190195.106 | 2691616.842 | 1190114.4953
31 | 2691519.9235 | 1190209.9828 | 2691540.2633 | 1190229.9954
32 | 2691540.2633 | 1190229.9954 | 2691614.1689 | 1190155.6784 | 2691643.032 | 1190126.4111
33 | 2691764.5594 | 1190010.8002 | 2691721.9462 | 1190049.1384 | 2691690.7512 | 1190078.0235 | 2691643.032 | 1190126.4111
34 | 2691764.5594 | 1190010.8002 | 2691765.8741 | 1190012.1101 | 2691779.5306 | 1190025.7726 | 2691778.5296 | 1190031.8611 | 2691794.4902 | 1190046.4707 | 2691798.5046 | 1190054.2595
35 | 2691764.5594 | 1190010.8002 | 2691780.4827 | 1189996.0238 | 2691815.3219 | 1189979.7865
36 | 2691720.5438 | 1189902.4578 | 2691742.6743 | 1189882.6773
37 | 2691744.2089 | 1189881.3057 | 2691742.6743 | 1189882.6773
38 | 2691798.5046 | 1190054.2595 | 2691794.226 | 1190055.2389 | 2691734.2076 | 1190111.9678

## bus_geodata
| x | y | coords
0 | 2691788.1076 | 1189778.891
1 | 2691782.1701 | 1189822.6777
2 | 2691776.1741 | 1189767.0898
3 | 2691809.9761 | 1189874.9515
4 | 2691759.9334 | 1189748.8524
5 | 2691845.5245 | 1189884.2897
6 | 2691730.2784 | 1189664.8362
7 | 2691856.8399 | 1189887.103
8 | 2691742.821 | 1189574.1609
9 | 2691732.2054 | 1189623.2218
10 | 2691731.487 | 1189625.2684
11 | 2691615.4844 | 1189704.622
12 | 2691444.1411 | 1189831.1997
13 | 2691458.9653 | 1189847.5091
14 | 2691457.901 | 1189867.1148
15 | 2691470.7733 | 1189845.4548
16 | 2691457.9141 | 1189885.4477
17 | 2691561.0108 | 1190011.3083
18 | 2691461.6236 | 1189923.6464
19 | 2691579.3157 | 1190028.282
20 | 2691469.9375 | 1189945.1608
21 | 2691450.7905 | 1190030.5453
22 | 2691306.8171 | 1190007.8446
23 | 2691832.9572 | 1189909.1851
24 | 2691742.588 | 1189992.7409
25 | 2691687.9537 | 1189931.5872
26 | 2691696.3757 | 1190037.4693
27 | 2691585.6619 | 1190033.6299
28 | 2691646.9675 | 1190085.2911
29 | 2691616.842 | 1190114.4953
30 | 2691519.9235 | 1190209.9828
31 | 2691540.2633 | 1190229.9954
32 | 2691643.032 | 1190126.4111
33 | 2691764.5594 | 1190010.8002
34 | 2691720.5438 | 1189902.4578
35 | 2691742.6743 | 1189882.6773
36 | 2691744.2089 | 1189881.3057
37 | 2691798.5046 | 1190054.2595
38 | 2691815.3219 | 1189979.7865
39 | 2691734.2076 | 1190111.9678
40 | 2691646.9675 | 1190085.2911

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99726 | -0.052764 | 0.0024077 | 0.00060343
1 | 0.99746 | -0.048929 | 0.0045844 | 0.0011489
2 | 0.99722 | -0.053513 | 0.00016127 | 4.0417e-05
3 | 0.99812 | -0.036279 | 0.00012016 | 3.0116e-05
4 | 0.99717 | -0.054533 | 0.00080426 | 0.00020157
5 | 0.99844 | -0.030066 | 0.00030465 | 7.6354e-05
6 | 0.99704 | -0.057029 | 0.00013164 | 3.2993e-05
7 | 0.99854 | -0.028034 | 0 | 0
8 | 0.997 | -0.057874 | 0.0002173 | 5.446e-05
9 | 0.99701 | -0.057682 | 0.00020829 | 5.2203e-05
10 | 0.99701 | -0.057666 | 0.00047802 | 0.0001198
11 | 0.99698 | -0.058168 | 0.00053255 | 0.00013347
12 | 0.99045 | -0.18204 | 0.0010573 | 0.00026499
13 | 0.99047 | -0.18163 | 0 | 0
14 | 0.99041 | -0.18275 | 0.00045035 | 0.00011287
15 | 0.99052 | -0.18072 | 0 | 0
16 | 0.99037 | -0.18364 | 0.00048689 | 0.00012203
17 | 0.99127 | -0.16616 | 0.0011203 | 0.00028078
18 | 0.99029 | -0.1852 | 0.00044887 | 0.0001125
19 | 0.99139 | -0.16375 | 0.0025508 | 0.00063929
20 | 0.99025 | -0.18595 | 0.00033626 | 8.4274e-05
21 | 0.99013 | -0.18826 | 0 | 0
22 | 0.98993 | -0.19214 | 0.0014739 | 0.00036939
23 | 0.99884 | -0.022368 | 0.00044453 | 0.00011141
24 | 1 | 0 | -0.12387 | -0.031141
25 | 0.99693 | -0.058978 | 0.010875 | 0.0027255
26 | 0.99588 | -0.078073 | 0.010873 | 0.0027251
27 | 0.99145 | -0.16258 | 0.0016068 | 0.0004027
28 | 0.99215 | -0.14902 | 0 | 0
29 | 0.99024 | -0.18544 | 0.0095956 | 0.0024049
30 | 0.98525 | -0.28106 | 0 | 0
31 | 0.9842 | -0.3012 | 0 | 0
32 | 0.97886 | -0.40502 | 0.0058748 | 0.0014724
33 | 0.97362 | -0.50766 | 0 | 0
34 | 0.99572 | -0.082203 | 0.0103 | 0.0025813
35 | 0.99518 | -0.092623 | 0.004086 | 0.0010241
36 | 0.99515 | -0.093198 | 0.015873 | 0.0039782
37 | 0.97287 | -0.52245 | 0 | 0
38 | 0.97253 | -0.52926 | 0.019506 | 0.0048886
39 | 0.97174 | -0.54479 | 0.013932 | 0.0034918
40 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0049415 | -0.0012341 | 0.0049424 | 0.0012341 | 9.0043e-07 | -3.7616e-10 | 0.0073717 | 0.0073715 | 0.0073717 | 0.99726 | -0.052764 | 0.99746 | -0.048929 | 2.0252
1 | 0.0025338 | 0.00063069 | -0.0025337 | -0.00063085 | 8.9888e-08 | -1.6144e-07 | 0.0037791 | 0.0037792 | 0.0037792 | 0.99726 | -0.052764 | 0.99722 | -0.053513 | 1.0382
2 | -0.0095267 | -0.0023831 | 0.0095325 | 0.0023857 | 5.736e-06 | 2.6817e-06 | 0.01421 | 0.01421 | 0.01421 | 0.99746 | -0.048929 | 0.99812 | -0.036279 | 3.904
3 | 0.0023724 | 0.00059044 | -0.0023723 | -0.00059068 | 1.1474e-07 | -2.4534e-07 | 0.0035386 | 0.0035387 | 0.0035387 | 0.99722 | -0.053513 | 0.99717 | -0.054533 | 0.97217
4 | -0.0096526 | -0.0024159 | 0.0096555 | 0.0024172 | 2.8546e-06 | 1.3463e-06 | 0.014389 | 0.014389 | 0.014389 | 0.99812 | -0.036279 | 0.99844 | -0.030066 | 3.9531
5 | 0.001568 | 0.00038911 | -0.0015679 | -0.00039017 | 1.8523e-07 | -1.0594e-06 | 0.0023385 | 0.002339 | 0.002339 | 0.99717 | -0.054533 | 0.99704 | -0.057029 | 0.64257
6 | -0.0099601 | -0.0024936 | 0.0099611 | 0.002494 | 9.6333e-07 | 4.6402e-07 | 0.014843 | 0.014843 | 0.014843 | 0.99844 | -0.030066 | 0.99854 | -0.028034 | 4.0778
7 | 0.00090364 | 0.00022528 | -0.00090361 | -0.00022578 | 2.7328e-08 | -5.0531e-07 | 0.0013482 | 0.0013484 | 0.0013484 | 0.99704 | -0.057029 | 0.99701 | -0.057666 | 0.37044
8 | 0.00053258 | 0.0001319 | -0.00053255 | -0.00013347 | 2.8763e-08 | -1.566e-06 | 0.00079428 | 0.00079484 | 0.00079484 | 0.99704 | -0.057029 | 0.99698 | -0.058168 | 0.21836
9 | -0.0099611 | -0.002494 | 0.0099638 | 0.0024953 | 2.6873e-06 | 1.2943e-06 | 0.014843 | 0.014843 | 0.014843 | 0.99854 | -0.028034 | 0.99884 | -0.022368 | 4.0778
10 | -0.0002173 | -5.446e-05 | 0.0002173 | 5.3806e-05 | 1.9811e-09 | -6.5421e-07 | 0.00032432 | 0.00032409 | 0.00032432 | 0.997 | -0.057874 | 0.99701 | -0.057682 | 0.089098
11 | -0.00042559 | -0.00010601 | 0.00042559 | 0.00010598 | 3.2791e-10 | -2.8076e-08 | 0.00063496 | 0.00063495 | 0.00063496 | 0.99701 | -0.057682 | 0.99701 | -0.057666 | 0.17444
12 | -0.0010573 | -0.00026499 | 0.0010573 | 0.00026472 | 2.0853e-08 | -2.7031e-07 | 0.0015885 | 0.0015884 | 0.0015885 | 0.99045 | -0.18204 | 0.99047 | -0.18163 | 0.43639
13 | 0.0031972 | 0.00079735 | -0.003197 | -0.00079749 | 1.6978e-07 | -1.4403e-07 | 0.0048019 | 0.004802 | 0.004802 | 0.99047 | -0.18163 | 0.99041 | -0.18275 | 1.3192
14 | -0.0042545 | -0.0010621 | 0.0042547 | 0.001062 | 1.8302e-07 | -3.6701e-08 | 0.0063902 | 0.0063902 | 0.0063902 | 0.99047 | -0.18163 | 0.99052 | -0.18072 | 1.7556
15 | 0.0027467 | 0.00068463 | -0.0027466 | -0.00068479 | 1.1716e-07 | -1.6125e-07 | 0.0041253 | 0.0041254 | 0.0041254 | 0.99041 | -0.18275 | 0.99037 | -0.18364 | 1.1334
16 | -0.0042547 | -0.001062 | 0.0042577 | 0.0010614 | 2.9427e-06 | -5.9244e-07 | 0.0063902 | 0.0063893 | 0.0063902 | 0.99052 | -0.18072 | 0.99127 | -0.16616 | 1.7555
17 | 0.0022597 | 0.00056276 | -0.0022595 | -0.00056315 | 1.6618e-07 | -3.8864e-07 | 0.0033939 | 0.0033941 | 0.0033941 | 0.99037 | -0.18364 | 0.99029 | -0.1852 | 0.93243
18 | -0.005378 | -0.0013422 | 0.0053786 | 0.0013423 | 6.1377e-07 | 6.8874e-08 | 0.0080711 | 0.008071 | 0.0080711 | 0.99127 | -0.16616 | 0.99139 | -0.16375 | 2.2173
19 | 0.0018106 | 0.00045065 | -0.0018106 | -0.00045091 | 6.4336e-08 | -2.5724e-07 | 0.0027196 | 0.0027197 | 0.0027197 | 0.99029 | -0.1852 | 0.99025 | -0.18595 | 0.74717
20 | -0.0079294 | -0.0019816 | 0.0079299 | 0.0019818 | 4.4068e-07 | 1.7502e-07 | 0.0119 | 0.0119 | 0.0119 | 0.99139 | -0.16375 | 0.99145 | -0.16258 | 3.2691
21 | 0.0014743 | 0.00036664 | -0.0014742 | -0.00036767 | 1.6211e-07 | -1.03e-06 | 0.0022144 | 0.0022148 | 0.0022148 | 0.99025 | -0.18595 | 0.99013 | -0.18826 | 0.60846
22 | 0.0014742 | 0.00036767 | -0.0014739 | -0.00036939 | 2.719e-07 | -1.7261e-06 | 0.0022148 | 0.0022155 | 0.0022155 | 0.99013 | -0.18826 | 0.98993 | -0.19214 | 0.60865
23 | -0.010408 | -0.0026067 | 0.010419 | 0.0026122 | 1.1095e-05 | 5.4883e-06 | 0.015505 | 0.015505 | 0.015505 | 0.99884 | -0.022368 | 1 | 0 | 4.2597
24 | 0.041294 | 0.010409 | -0.041178 | -0.010336 | 0.00011619 | 7.3286e-05 | 0.061467 | 0.061467 | 0.061467 | 1 | 0 | 0.99693 | -0.058978 | 16.8866
25 | 0.070512 | 0.018119 | -0.070246 | -0.01795 | 0.00026631 | 0.0001696 | 0.10508 | 0.10508 | 0.10508 | 1 | 0 | 0.99588 | -0.078073 | 28.8686
26 | 0.030303 | 0.0076107 | -0.030269 | -0.0075898 | 3.3542e-05 | 2.0897e-05 | 0.045236 | 0.045236 | 0.045236 | 0.99693 | -0.058978 | 0.99572 | -0.082203 | 12.4274
27 | 0.059372 | 0.015224 | -0.059169 | -0.015095 | 0.00020349 | 0.00012934 | 0.088836 | 0.088836 | 0.088836 | 0.99588 | -0.078073 | 0.99215 | -0.14902 | 24.4055
28 | -0.0095366 | -0.0023845 | 0.0095428 | 0.0023874 | 6.1571e-06 | 2.906e-06 | 0.014311 | 0.014311 | 0.014311 | 0.99145 | -0.16258 | 0.99215 | -0.14902 | 3.9316
29 | 0.049626 | 0.012708 | -0.049539 | -0.012652 | 8.7388e-05 | 5.5388e-05 | 0.074526 | 0.074526 | 0.074526 | 0.99215 | -0.14902 | 0.99024 | -0.18544 | 20.4741
30 | 0.039943 | 0.010248 | -0.039759 | -0.010131 | 0.00018437 | 0.00011625 | 0.060107 | 0.060107 | 0.060107 | 0.99024 | -0.18544 | 0.98525 | -0.28106 | 16.513
31 | 0.039759 | 0.010131 | -0.03972 | -0.010107 | 3.8605e-05 | 2.4345e-05 | 0.060107 | 0.060108 | 0.060108 | 0.98525 | -0.28106 | 0.9842 | -0.3012 | 16.5131
32 | 0.03972 | 0.010107 | -0.039523 | -0.0099823 | 0.00019769 | 0.00012468 | 0.060108 | 0.060108 | 0.060108 | 0.9842 | -0.3012 | 0.97886 | -0.40502 | 16.5133
33 | 0.033648 | 0.0085099 | -0.033483 | -0.0084065 | 0.00016481 | 0.00010338 | 0.051178 | 0.051178 | 0.051178 | 0.97886 | -0.40502 | 0.97362 | -0.50766 | 14.06
34 | 0.013957 | 0.0035058 | -0.013947 | -0.0035002 | 9.8442e-06 | 5.5835e-06 | 0.021334 | 0.021334 | 0.021334 | 0.97362 | -0.50766 | 0.97287 | -0.52245 | 5.861
35 | 0.019526 | 0.0049008 | -0.019506 | -0.0048886 | 2.0095e-05 | 1.2113e-05 | 0.029845 | 0.029845 | 0.029845 | 0.97362 | -0.50766 | 0.97253 | -0.52926 | 8.1992
36 | 0.01997 | 0.0050085 | -0.01996 | -0.0050025 | 9.9138e-06 | 5.9589e-06 | 0.029844 | 0.029844 | 0.029844 | 0.99572 | -0.082203 | 0.99518 | -0.092623 | 8.1989
37 | 0.015874 | 0.0039784 | -0.015873 | -0.0039782 | 4.3481e-07 | 2.5153e-07 | 0.023735 | 0.023735 | 0.023735 | 0.99518 | -0.092623 | 0.99515 | -0.093198 | 6.5205
38 | 0.013947 | 0.0035002 | -0.013932 | -0.0034918 | 1.4845e-05 | 8.422e-06 | 0.021334 | 0.021334 | 0.021334 | 0.97287 | -0.52245 | 0.97174 | -0.54479 | 5.8611

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.12387 | 0.031141

## res_load
| p_mw | q_mvar
0 | 0.0024077 | 0.00060343
1 | 0.0045844 | 0.0011489
2 | 0.00016127 | 4.0417e-05
3 | 0.00012016 | 3.0116e-05
4 | 0.00080426 | 0.00020157
5 | 0.00030465 | 7.6354e-05
6 | 0.00013164 | 3.2993e-05
7 | 0.0002173 | 5.446e-05
8 | 0.00020829 | 5.2203e-05
9 | 0.00047802 | 0.0001198
10 | 0.00053255 | 0.00013347
11 | 0.0010573 | 0.00026499
12 | 0.00045035 | 0.00011287
13 | 0.00048689 | 0.00012203
14 | 0.0011203 | 0.00028078
15 | 0.00044887 | 0.0001125
16 | 0.0025508 | 0.00063929
17 | 0.00033626 | 8.4274e-05
18 | 0.0014739 | 0.00036939
19 | 0.00044453 | 0.00011141
20 | 0.010875 | 0.0027255
21 | 0.010873 | 0.0027251
22 | 0.0016068 | 0.0004027
23 | 0.0095956 | 0.0024049
24 | 0.0058748 | 0.0014724
25 | 0.0103 | 0.0025813
26 | 0.004086 | 0.0010241
27 | 0.015873 | 0.0039782
28 | 0.019506 | 0.0048886
29 | 0.013932 | 0.0034918

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1