## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1301-12_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1301-12_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1301-12_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1301-12_0_3_node_138 | 0.4 | n |  | TRUE
4 | bus_LV_1301-12_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1301-12_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1301-12_0_3_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1301-12_0_3_node_140 | 0.4 | n |  | TRUE
8 | bus_LV_1301-12_0_3_node_141 | 0.4 | n |  | TRUE
9 | bus_LV_1301-12_0_3_node_145 | 0.4 | n |  | TRUE
10 | bus_LV_1301-12_0_3_node_146 | 0.4 | n |  | TRUE
11 | bus_LV_1301-12_0_3_node_4 | 0.4 | n |  | TRUE
12 | bus_LV_1301-12_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1301-12_0_3_node_49 | 0.4 | n |  | TRUE
14 | bus_LV_1301-12_0_3_node_50 | 0.4 | n |  | TRUE
15 | bus_LV_1301-12_0_3_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1301-12_0_3_node_48 | 0.4 | n |  | TRUE
17 | bus_LV_1301-12_0_3_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_1301-12_0_3_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1301-12_0_3_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1301-12_0_3_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_1301-12_0_3_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_1301-12_0_3_node_110 | 0.4 | n |  | TRUE
23 | bus_LV_1301-12_0_3_node_37 | 0.4 | n |  | TRUE
24 | bus_LV_1301-12_0_3_node_38 | 0.4 | n |  | TRUE
25 | bus_LV_1301-12_0_3_node_39 | 0.4 | n |  | TRUE
26 | bus_LV_1301-12_0_3_node_40 | 0.4 | n |  | TRUE
27 | bus_LV_1301-12_0_3_node_42 | 0.4 | n |  | TRUE
28 | bus_LV_1301-12_0_3_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_1301-12_0_3_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_1301-12_0_3_node_12 | 0.4 | n |  | TRUE
31 | bus_LV_1301-12_0_3_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_1301-12_0_3_node_11 | 0.4 | n |  | TRUE
33 | bus_LV_1301-12_0_3_node_46 | 0.4 | n |  | TRUE
34 | bus_LV_1301-12_0_3_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_1301-12_0_3_node_92 | 0.4 | n |  | TRUE
36 | bus_LV_1301-12_0_3_node_13 | 0.4 | n |  | TRUE
37 | bus_LV_1301-12_0_3_node_17 | 0.4 | n |  | TRUE
38 | bus_LV_1301-12_0_3_node_18 | 0.4 | n |  | TRUE
39 | bus_LV_1301-12_0_3_node_126 | 0.4 | n |  | TRUE
40 | bus_LV_1301-12_0_3_node_24 | 0.4 | n |  | TRUE
41 | bus_LV_1301-12_0_3_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_1301-12_0_3_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_1301-12_0_3_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_1301-12_0_3_node_125 | 0.4 | n |  | TRUE
45 | bus_LV_1301-12_0_3_node_127 | 0.4 | n |  | TRUE
46 | bus_LV_1301-12_0_3_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_1301-12_0_3_node_21 | 0.4 | n |  | TRUE
48 | bus_LV_1301-12_0_3_node_109 | 0.4 | n |  | TRUE
49 | bus_LV_1301-12_0_3_node_111 | 0.4 | n |  | TRUE
50 | bus_LV_1301-12_0_3_node_107 | 0.4 | n |  | TRUE
51 | bus_LV_1301-12_0_3_node_105 | 0.4 | n |  | TRUE
52 | bus_LV_1301-12_0_3_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_1301-12_0_3_node_28 | 0.4 | n |  | TRUE
54 | bus_LV_1301-12_0_3_node_30 | 0.4 | n |  | TRUE
55 | bus_LV_1301-12_0_3_node_31 | 0.4 | n |  | TRUE
56 | bus_LV_1301-12_0_3_node_33 | 0.4 | n |  | TRUE
57 | bus_LV_1301-12_0_3_node_32 | 0.4 | n |  | TRUE
58 | bus_LV_1301-12_0_3_node_34 | 0.4 | n |  | TRUE
59 | bus_LV_1301-12_0_3_node_35 | 0.4 | n |  | TRUE
60 | bus_LV_1301-12_0_3_node_36 | 0.4 | n |  | TRUE
61 | bus_LV_1301-12_0_3_node_139 | 0.4 | n |  | TRUE
62 | bus_LV_1301-12_0_3_node_47 | 0.4 | n |  | TRUE
63 | bus_LV_1301-12_0_3_node_114 | 0.4 | n |  | TRUE
64 | bus_LV_1301-12_0_3_node_41 | 0.4 | n |  | TRUE
65 | bus_LV_1301-12_0_3_node_116 | 0.4 | n |  | TRUE
66 | bus_LV_1301-12_0_3_node_121 | 0.4 | n |  | TRUE
67 | bus_LV_1301-12_0_3_node_44 | 0.4 | n |  | TRUE
68 | bus_LV_1301-12_0_3_node_115 | 0.4 | n |  | TRUE
69 | bus_LV_1301-12_0_3_node_63 | 0.4 | n |  | TRUE
70 | bus_LV_1301-12_0_3_node_65 | 0.4 | n |  | TRUE
71 | bus_LV_1301-12_0_3_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_1301-12_0_3_node_113 | 0.4 | n |  | TRUE
73 | bus_LV_1301-12_0_3_node_45 | 0.4 | n |  | TRUE
74 | bus_LV_1301-12_0_3_node_51 | 0.4 | n |  | TRUE
75 | bus_LV_1301-12_0_3_node_52 | 0.4 | n |  | TRUE
76 | bus_LV_1301-12_0_3_node_53 | 0.4 | n |  | TRUE
77 | bus_LV_1301-12_0_3_node_54 | 0.4 | n |  | TRUE
78 | bus_LV_1301-12_0_3_node_55 | 0.4 | n |  | TRUE
79 | bus_LV_1301-12_0_3_node_68 | 0.4 | n |  | TRUE
80 | bus_LV_1301-12_0_3_node_71 | 0.4 | n |  | TRUE
81 | bus_LV_1301-12_0_3_node_70 | 0.4 | n |  | TRUE
82 | bus_LV_1301-12_0_3_node_72 | 0.4 | n |  | TRUE
83 | bus_LV_1301-12_0_3_node_56 | 0.4 | n |  | TRUE
84 | bus_LV_1301-12_0_3_node_57 | 0.4 | n |  | TRUE
85 | bus_LV_1301-12_0_3_node_58 | 0.4 | n |  | TRUE
86 | bus_LV_1301-12_0_3_node_60 | 0.4 | n |  | TRUE
87 | bus_LV_1301-12_0_3_node_117 | 0.4 | n |  | TRUE
88 | bus_LV_1301-12_0_3_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_1301-12_0_3_node_119 | 0.4 | n |  | TRUE
90 | bus_LV_1301-12_0_3_node_61 | 0.4 | n |  | TRUE
91 | bus_LV_1301-12_0_3_node_62 | 0.4 | n |  | TRUE
92 | bus_LV_1301-12_0_3_node_64 | 0.4 | n |  | TRUE
93 | bus_LV_1301-12_0_3_node_66 | 0.4 | n |  | TRUE
94 | bus_LV_1301-12_0_3_node_112 | 0.4 | n |  | TRUE
95 | bus_LV_1301-12_0_3_node_67 | 0.4 | n |  | TRUE
96 | bus_LV_1301-12_0_3_node_69 | 0.4 | n |  | TRUE
97 | bus_LV_1301-12_0_3_node_120 | 0.4 | n |  | TRUE
98 | bus_LV_1301-12_0_3_node_74 | 0.4 | n |  | TRUE
99 | bus_LV_1301-12_0_3_node_75 | 0.4 | n |  | TRUE
100 | bus_LV_1301-12_0_3_node_76 | 0.4 | n |  | TRUE
101 | bus_LV_1301-12_0_3_node_77 | 0.4 | n |  | TRUE
102 | bus_LV_1301-12_0_3_node_78 | 0.4 | n |  | TRUE
103 | bus_LV_1301-12_0_3_node_90 | 0.4 | n |  | TRUE
104 | bus_LV_1301-12_0_3_node_88 | 0.4 | n |  | TRUE
105 | bus_LV_1301-12_0_3_node_79 | 0.4 | n |  | TRUE
106 | bus_LV_1301-12_0_3_node_80 | 0.4 | n |  | TRUE
107 | bus_LV_1301-12_0_3_node_81 | 0.4 | n |  | TRUE
108 | bus_LV_1301-12_0_3_node_82 | 0.4 | n |  | TRUE
109 | bus_LV_1301-12_0_3_node_83 | 0.4 | n |  | TRUE
110 | bus_LV_1301-12_0_3_node_136 | 0.4 | n |  | TRUE
111 | bus_LV_1301-12_0_3_node_87 | 0.4 | n |  | TRUE
112 | bus_LV_1301-12_0_3_node_84 | 0.4 | n |  | TRUE
113 | bus_LV_1301-12_0_3_node_85 | 0.4 | n |  | TRUE
114 | bus_LV_1301-12_0_3_node_86 | 0.4 | n |  | TRUE
115 | bus_LV_1301-12_0_3_node_99 | 0.4 | n |  | TRUE
116 | bus_LV_1301-12_0_3_node_100 | 0.4 | n |  | TRUE
117 | bus_LV_1301-12_0_3_node_89 | 0.4 | n |  | TRUE
118 | bus_LV_1301-12_0_3_node_91 | 0.4 | n |  | TRUE
119 | bus_LV_1301-12_0_3_node_103 | 0.4 | n |  | TRUE
120 | bus_LV_1301-12_0_3_node_147 | 0.4 | n |  | TRUE
121 | bus_LV_1301-12_0_3_node_96 | 0.4 | n |  | TRUE
122 | bus_LV_1301-12_0_3_node_101 | 0.4 | n |  | TRUE
123 | bus_LV_1301-12_0_3_node_93 | 0.4 | n |  | TRUE
124 | bus_LV_1301-12_0_3_node_94 | 0.4 | n |  | TRUE
125 | bus_LV_1301-12_0_3_node_95 | 0.4 | n |  | TRUE
126 | bus_LV_1301-12_0_3_node_97 | 0.4 | n |  | TRUE
127 | bus_LV_1301-12_0_3_node_98 | 0.4 | n |  | TRUE
128 | bus_LV_1301-12_0_3_node_108 | 0.4 | n |  | TRUE
129 | bus_LV_1301-12_0_3_node_106 | 0.4 | n |  | TRUE
130 | bus_LV_1301-12_0_3_node_102 | 0.4 | n |  | TRUE
131 | bus_LV_1301-12_0_3_node_104 | 0.4 | n |  | TRUE
132 | bus_LV_1301-12_0_3_node_144 | 0.4 | n |  | TRUE
133 | bus_LV_1301-12_0_3_node_142 | 0.4 | n |  | TRUE
134 | bus_LV_1301-12_0_3_node_122 | 0.4 | n |  | TRUE
135 | bus_LV_1301-12_0_3_node_123 | 0.4 | n |  | TRUE
136 | bus_LV_1301-12_0_3_node_124 | 0.4 | n |  | TRUE
137 | bus_LV_1301-12_0_3_node_131 | 0.4 | n |  | TRUE
138 | bus_LV_1301-12_0_3_node_133 | 0.4 | n |  | TRUE
139 | bus_LV_1301-12_0_3_node_129 | 0.4 | n |  | TRUE
140 | bus_LV_1301-12_0_3_node_134 | 0.4 | n |  | TRUE
141 | bus_LV_1301-12_0_3_node_128 | 0.4 | n |  | TRUE
142 | bus_LV_1301-12_0_3_node_135 | 0.4 | n |  | TRUE
143 | bus_LV_1301-12_0_3_node_130 | 0.4 | n |  | TRUE
144 | bus_LV_1301-12_0_3_node_143 | 0.4 | n |  | TRUE
145 | bus_MV_17_0_node_9 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1301-12_0_3_load_0 | 0 | 0.0090329 | 0.0022638 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1301-12_0_3_load_1 | 1 | 0.0023315 | 0.00058434 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1301-12_0_3_load_138 | 3 | 0.0016885 | 0.00042317 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1301-12_0_3_load_3 | 4 | 0.01996 | 0.0050023 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1301-12_0_3_load_146 | 10 | 0.0025261 | 0.0006331 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1301-12_0_3_load_49 | 13 | 0.0062761 | 0.0015729 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1301-12_0_3_load_50 | 14 | 0.0036734 | 0.00092064 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1301-12_0_3_load_48 | 16 | 0.0024164 | 0.00060561 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1301-12_0_3_load_22 | 17 | 0.006454 | 0.0016175 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1301-12_0_3_load_19 | 18 | 0.030127 | 0.0075506 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1301-12_0_3_load_14 | 19 | 0.0020447 | 0.00051244 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1301-12_0_3_load_110 | 22 | 0.002499 | 0.0006263 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1301-12_0_3_load_38 | 24 | 0.022703 | 0.0056899 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1301-12_0_3_load_39 | 25 | 0.0068996 | 0.0017292 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1301-12_0_3_load_29 | 29 | 0.00061207 | 0.0001534 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1301-12_0_3_load_11 | 32 | 0.0010996 | 0.00027559 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1301-12_0_3_load_20 | 34 | 0.0085704 | 0.0021479 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1301-12_0_3_load_17 | 37 | 0.00048173 | 0.00012073 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1301-12_0_3_load_18 | 38 | 0.0016019 | 0.00040147 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1301-12_0_3_load_126 | 39 | 0.0010009 | 0.00025086 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1301-12_0_3_load_25 | 41 | 0.00087129 | 0.00021837 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1301-12_0_3_load_23 | 42 | 0.00086818 | 0.00021759 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1301-12_0_3_load_125 | 44 | 0.0016114 | 0.00040384 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1301-12_0_3_load_127 | 45 | 0.00076126 | 0.00019079 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1301-12_0_3_load_27 | 46 | 0.0014532 | 0.00036421 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1301-12_0_3_load_109 | 48 | 0.0037439 | 0.0009383 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1301-12_0_3_load_111 | 49 | 0.0027681 | 0.00069376 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1301-12_0_3_load_107 | 50 | 0.00040195 | 0.00010074 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1301-12_0_3_load_105 | 51 | 0.00068039 | 0.00017052 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1301-12_0_3_load_43 | 52 | 0.015933 | 0.0039933 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1301-12_0_3_load_28 | 53 | 0.0013392 | 0.00033563 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1301-12_0_3_load_30 | 54 | 0.0033855 | 0.0008485 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1301-12_0_3_load_31 | 55 | 0.0022697 | 0.00056883 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1301-12_0_3_load_33 | 56 | 0.0014184 | 0.00035549 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1301-12_0_3_load_32 | 57 | 0.0019539 | 0.0004897 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1301-12_0_3_load_35 | 59 | 0.00076048 | 0.0001906 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1301-12_0_3_load_36 | 60 | 0.00049758 | 0.00012471 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1301-12_0_3_load_139 | 61 | 0.00041283 | 0.00010347 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1301-12_0_3_load_47 | 62 | 0.0076652 | 0.0019211 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1301-12_0_3_load_114 | 63 | 0.0024328 | 0.00060972 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1301-12_0_3_load_121 | 66 | 0.0044328 | 0.001111 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1301-12_0_3_load_115 | 68 | 0.0057002 | 0.0014286 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1301-12_0_3_load_113 | 72 | 0.0023009 | 0.00057665 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1301-12_0_3_load_45 | 73 | 0.0039845 | 0.00099862 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1301-12_0_3_load_51 | 74 | 0.00072536 | 0.00018179 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1301-12_0_3_load_52 | 75 | 0.00079274 | 0.00019868 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1301-12_0_3_load_53 | 76 | 0.0006116 | 0.00015328 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1301-12_0_3_load_54 | 77 | 0.00061633 | 0.00015447 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1301-12_0_3_load_55 | 78 | 0.0019609 | 0.00049146 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1301-12_0_3_load_68 | 79 | 0.0019757 | 0.00049515 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1301-12_0_3_load_71 | 80 | 0.00068847 | 0.00017255 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1301-12_0_3_load_70 | 81 | 0.00021838 | 5.473e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1301-12_0_3_load_72 | 82 | 0.0035664 | 0.00089382 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1301-12_0_3_load_56 | 83 | 0.003943 | 0.00098822 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1301-12_0_3_load_57 | 84 | 0.0017086 | 0.00042821 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1301-12_0_3_load_58 | 85 | 0.0021351 | 0.00053511 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1301-12_0_3_load_60 | 86 | 0.0042301 | 0.0010602 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1301-12_0_3_load_117 | 87 | 0.00063562 | 0.0001593 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1301-12_0_3_load_73 | 88 | 0.0032379 | 0.00081149 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1301-12_0_3_load_119 | 89 | 0.0058997 | 0.0014786 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1301-12_0_3_load_61 | 90 | 0.00048328 | 0.00012112 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1301-12_0_3_load_62 | 91 | 0.00075685 | 0.00018969 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1301-12_0_3_load_64 | 92 | 0.0005656 | 0.00014175 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1301-12_0_3_load_112 | 94 | 0.010908 | 0.0027338 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1301-12_0_3_load_69 | 96 | 0.0012723 | 0.00031888 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1301-12_0_3_load_120 | 97 | 0.0036158 | 0.00090621 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1301-12_0_3_load_74 | 98 | 0.00080267 | 0.00020117 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1301-12_0_3_load_75 | 99 | 0.0010863 | 0.00027226 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1301-12_0_3_load_76 | 100 | 0.0028133 | 0.00070507 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1301-12_0_3_load_77 | 101 | 0.0015582 | 0.00039052 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1301-12_0_3_load_78 | 102 | 0.0011066 | 0.00027735 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1301-12_0_3_load_88 | 104 | 0.0015535 | 0.00038934 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1301-12_0_3_load_79 | 105 | 0.00045159 | 0.00011318 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1301-12_0_3_load_80 | 106 | 0.00020186 | 5.0592e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1301-12_0_3_load_82 | 108 | 0.00026748 | 6.7038e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1301-12_0_3_load_136 | 110 | 0.00010446 | 2.6181e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1301-12_0_3_load_84 | 112 | 0.00031783 | 7.9655e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1301-12_0_3_load_85 | 113 | 0.001836 | 0.00046014 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1301-12_0_3_load_99 | 115 | 0.00038543 | 9.6598e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1301-12_0_3_load_89 | 117 | 0.00046045 | 0.0001154 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1301-12_0_3_load_103 | 119 | 0.00057209 | 0.00014338 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1301-12_0_3_load_147 | 120 | 0.00026912 | 6.7448e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1301-12_0_3_load_101 | 122 | 0.00074411 | 0.00018649 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1301-12_0_3_load_93 | 123 | 0.00054404 | 0.00013635 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1301-12_0_3_load_94 | 124 | 0.0010609 | 0.00026588 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1301-12_0_3_load_97 | 126 | 0.00098899 | 0.00024786 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1301-12_0_3_load_98 | 127 | 0.00025752 | 6.4541e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1301-12_0_3_load_108 | 128 | 0.00024005 | 6.0162e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1301-12_0_3_load_106 | 129 | 0.00051421 | 0.00012887 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1301-12_0_3_load_102 | 130 | 0.00080192 | 0.00020098 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1301-12_0_3_load_104 | 131 | 0.00049197 | 0.0001233 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1301-12_0_3_load_144 | 132 | 0.0023642 | 0.00059252 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1301-12_0_3_load_122 | 134 | 0.0037628 | 0.00094304 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1301-12_0_3_load_133 | 138 | 0.00089127 | 0.00022337 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1301-12_0_3_load_129 | 139 | 0.0051743 | 0.0012968 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1301-12_0_3_load_134 | 140 | 0.00033161 | 8.3109e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1301-12_0_3_load_128 | 141 | 0.0012267 | 0.00030744 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1301-12_0_3_load_135 | 142 | 0.00058568 | 0.00014678 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1301-12_0_3_load_130 | 143 | 0.00065561 | 0.00016431 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1301-12_0_3_load_143 | 144 | 0.0006424 | 0.000161 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1301-12_0_3_line_0 |  | 0 | 1 | 0.066159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1301-12_0_3_line_1 |  | 0 | 2 | 0.034646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1301-12_0_3_line_2 |  | 1 | 3 | 0.22709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1301-12_0_3_line_3 |  | 2 | 4 | 0.0194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1301-12_0_3_line_4 |  | 2 | 5 | 0.067915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1301-12_0_3_line_5 |  | 2 | 6 | 0.052473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1301-12_0_3_line_6 |  | 3 | 7 | 0.028157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1301-12_0_3_line_7 |  | 5 | 14 | 0.011748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1301-12_0_3_line_8 |  | 5 | 11 | 0.024845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1301-12_0_3_line_9 |  | 6 | 17 | 0.030069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1301-12_0_3_line_10 |  | 6 | 18 | 0.025149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1301-12_0_3_line_11 |  | 7 | 8 | 0.008239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1301-12_0_3_line_12 |  | 8 | 132 | 0.070749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1301-12_0_3_line_13 |  | 8 | 9 | 0.039212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1301-12_0_3_line_14 |  | 9 | 10 | 0.048553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1301-12_0_3_line_15 |  | 11 | 12 | 0.02125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1301-12_0_3_line_16 |  | 11 | 13 | 0.013703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1301-12_0_3_line_17 |  | 12 | 15 | 0.011579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1301-12_0_3_line_18 |  | 12 | 16 | 0.01949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1301-12_0_3_line_19 |  | 13 | 20 | 0.016529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1301-12_0_3_line_20 |  | 15 | 19 | 0.024114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1301-12_0_3_line_21 |  | 16 | 33 | 0.0051862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1301-12_0_3_line_22 |  | 17 | 26 | 0.033878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1301-12_0_3_line_23 |  | 18 | 34 | 0.031211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1301-12_0_3_line_24 |  | 20 | 21 | 0.060034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1301-12_0_3_line_25 |  | 21 | 22 | 0.051855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1301-12_0_3_line_26 |  | 22 | 35 | 0.071197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1301-12_0_3_line_27 |  | 23 | 24 | 0.0638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1301-12_0_3_line_28 |  | 23 | 25 | 0.015648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1301-12_0_3_line_29 |  | 23 | 26 | 0.017836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1301-12_0_3_line_30 |  | 23 | 27 | 0.011289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1301-12_0_3_line_31 |  | 25 | 63 | 0.0162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1301-12_0_3_line_32 |  | 26 | 52 | 0.0061455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1301-12_0_3_line_33 |  | 27 | 67 | 0.00349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1301-12_0_3_line_34 |  | 28 | 29 | 0.0096381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1301-12_0_3_line_35 |  | 28 | 30 | 0.021898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1301-12_0_3_line_36 |  | 28 | 31 | 0.1959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1301-12_0_3_line_37 |  | 29 | 46 | 0.005996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1301-12_0_3_line_38 |  | 30 | 32 | 0.008969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1301-12_0_3_line_39 |  | 31 | 39 | 0.027264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1301-12_0_3_line_40 |  | 31 | 36 | 0.00419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1301-12_0_3_line_41 |  | 33 | 62 | 0.020796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1301-12_0_3_line_42 |  | 33 | 59 | 0.013467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1301-12_0_3_line_43 |  | 34 | 47 | 0.041086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1301-12_0_3_line_44 |  | 35 | 119 | 0.026581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1301-12_0_3_line_45 |  | 35 | 103 | 0.027298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1301-12_0_3_line_46 |  | 36 | 37 | 0.027033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1301-12_0_3_line_47 |  | 36 | 38 | 0.11435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1301-12_0_3_line_48 |  | 37 | 40 | 0.022495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1301-12_0_3_line_49 |  | 39 | 45 | 0.013718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1301-12_0_3_line_50 |  | 40 | 41 | 0.049429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1301-12_0_3_line_51 |  | 40 | 42 | 0.04207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1301-12_0_3_line_52 |  | 41 | 43 | 0.010229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1301-12_0_3_line_53 |  | 43 | 44 | 0.071905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1301-12_0_3_line_54 |  | 45 | 141 | 0.056068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1301-12_0_3_line_55 |  | 46 | 53 | 0.052898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1301-12_0_3_line_56 |  | 47 | 48 | 0.020589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1301-12_0_3_line_57 |  | 48 | 49 | 0.034257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1301-12_0_3_line_58 |  | 50 | 51 | 0.026552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1301-12_0_3_line_59 |  | 51 | 131 | 0.0015317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1301-12_0_3_line_60 |  | 53 | 54 | 0.013223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1301-12_0_3_line_61 |  | 54 | 55 | 0.028951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1301-12_0_3_line_62 |  | 55 | 56 | 0.022953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1301-12_0_3_line_63 |  | 56 | 57 | 0.025994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1301-12_0_3_line_64 |  | 57 | 58 | 0.028215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1301-12_0_3_line_65 |  | 58 | 59 | 0.022632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1301-12_0_3_line_66 |  | 58 | 60 | 0.024814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1301-12_0_3_line_67 |  | 60 | 61 | 0.023999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1301-12_0_3_line_68 |  | 63 | 68 | 0.013083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1301-12_0_3_line_69 |  | 64 | 65 | 0.003877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1301-12_0_3_line_70 |  | 64 | 66 | 0.010282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1301-12_0_3_line_71 |  | 65 | 72 | 0.0030473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1301-12_0_3_line_72 |  | 65 | 68 | 0.01851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1301-12_0_3_line_73 |  | 67 | 73 | 0.025683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1301-12_0_3_line_74 |  | 69 | 70 | 0.002991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1301-12_0_3_line_75 |  | 69 | 71 | 0.031386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1301-12_0_3_line_76 |  | 70 | 94 | 0.080376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1301-12_0_3_line_77 |  | 70 | 72 | 0.053213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1301-12_0_3_line_78 |  | 70 | 82 | 0.017063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1301-12_0_3_line_79 |  | 71 | 88 | 0.022903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1301-12_0_3_line_80 |  | 71 | 84 | 0.078387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1301-12_0_3_line_81 |  | 74 | 75 | 0.068979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1301-12_0_3_line_82 |  | 74 | 76 | 0.022784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1301-12_0_3_line_83 |  | 75 | 77 | 0.016587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1301-12_0_3_line_84 |  | 76 | 78 | 0.074418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1301-12_0_3_line_85 |  | 77 | 79 | 0.01657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1301-12_0_3_line_86 |  | 78 | 80 | 0.023671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1301-12_0_3_line_87 |  | 79 | 81 | 0.073516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1301-12_0_3_line_88 |  | 80 | 82 | 0.01044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1301-12_0_3_line_89 |  | 81 | 96 | 0.0097459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1301-12_0_3_line_90 |  | 83 | 84 | 0.043592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1301-12_0_3_line_91 |  | 83 | 85 | 0.13299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1301-12_0_3_line_92 |  | 85 | 86 | 0.02489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1301-12_0_3_line_93 |  | 85 | 87 | 0.18301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1301-12_0_3_line_94 |  | 88 | 89 | 0.0038361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1301-12_0_3_line_95 |  | 89 | 97 | 0.020407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1301-12_0_3_line_96 |  | 90 | 91 | 0.083117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1301-12_0_3_line_97 |  | 91 | 92 | 0.036419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1301-12_0_3_line_98 |  | 92 | 93 | 0.084527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1301-12_0_3_line_99 |  | 93 | 95 | 0.003354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1301-12_0_3_line_100 |  | 95 | 96 | 0.045011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1301-12_0_3_line_101 |  | 98 | 99 | 0.017185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1301-12_0_3_line_102 |  | 98 | 100 | 0.040825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1301-12_0_3_line_103 |  | 99 | 101 | 0.039513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1301-12_0_3_line_104 |  | 101 | 102 | 0.020089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1301-12_0_3_line_105 |  | 102 | 103 | 0.02338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1301-12_0_3_line_106 |  | 103 | 104 | 0.02103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1301-12_0_3_line_107 |  | 104 | 117 | 0.14497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1301-12_0_3_line_108 |  | 105 | 106 | 0.03544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1301-12_0_3_line_109 |  | 105 | 107 | 0.05759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1301-12_0_3_line_110 |  | 107 | 108 | 0.024008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1301-12_0_3_line_111 |  | 107 | 109 | 0.078697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1301-12_0_3_line_112 |  | 109 | 110 | 0.00055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1301-12_0_3_line_113 |  | 110 | 111 | 0.33446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1301-12_0_3_line_114 |  | 111 | 114 | 0.099492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1301-12_0_3_line_115 |  | 112 | 113 | 0.00012066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1301-12_0_3_line_116 |  | 112 | 114 | 0.089084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1301-12_0_3_line_117 |  | 113 | 115 | 0.23065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1301-12_0_3_line_118 |  | 115 | 116 | 0.29782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1301-12_0_3_line_119 |  | 116 | 120 | 0.15952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1301-12_0_3_line_120 |  | 116 | 121 | 0.14761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1301-12_0_3_line_121 |  | 116 | 118 | 0.10079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1301-12_0_3_line_122 |  | 117 | 118 | 0.020558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1301-12_0_3_line_123 |  | 119 | 122 | 0.02606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1301-12_0_3_line_124 |  | 121 | 124 | 0.054425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1301-12_0_3_line_125 |  | 122 | 130 | 0.033873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1301-12_0_3_line_126 |  | 123 | 124 | 0.038412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1301-12_0_3_line_127 |  | 123 | 125 | 0.10003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1301-12_0_3_line_128 |  | 125 | 126 | 0.008664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1301-12_0_3_line_129 |  | 125 | 127 | 0.048718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1301-12_0_3_line_130 |  | 127 | 128 | 0.024847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1301-12_0_3_line_131 |  | 128 | 129 | 0.10553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1301-12_0_3_line_132 |  | 129 | 131 | 0.065225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1301-12_0_3_line_133 |  | 132 | 133 | 0.066334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1301-12_0_3_line_134 |  | 133 | 144 | 0.021894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1301-12_0_3_line_135 |  | 133 | 140 | 0.22556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1301-12_0_3_line_136 |  | 134 | 135 | 0.068795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1301-12_0_3_line_137 |  | 135 | 136 | 0.19707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1301-12_0_3_line_138 |  | 136 | 137 | 0.038671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1301-12_0_3_line_139 |  | 136 | 138 | 0.070193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1301-12_0_3_line_140 |  | 137 | 139 | 0.13087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1301-12_0_3_line_141 |  | 138 | 140 | 0.0135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_1301-12_0_3_line_142 |  | 139 | 143 | 0.017192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_1301-12_0_3_line_143 |  | 141 | 142 | 0.001714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1301-12_0_3_trafo_22 | 0.63 MVA 20/0.4 kV | 145 | 17 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2697932.2652 | 1222795.1492 | 2697932.5096 | 1222795.3944 | 2697937.0942 | 1222800.2844 | 2697940.9487 | 1222808.9762 | 2697947.0191 | 1222814.391 | 2697961.4756 | 1222816.7861 | 2697974.3027 | 1222816.3302 | 2697987.641 | 1222812.1485
1 | 2697905.3385 | 1222773.6988 | 2697920.2191 | 1222783.0613 | 2697932.2652 | 1222795.1492
2 | 2697987.641 | 1222812.1485 | 2698056.5093 | 1223028.545
3 | 2697905.3385 | 1222773.6988 | 2697891.6845 | 1222787.4797
4 | 2697941.0339 | 1222724.0727 | 2697943.4656 | 1222726.1141 | 2697918.3552 | 1222754.8105 | 2697910.4332 | 1222763.264 | 2697913.2777 | 1222765.5791 | 2697905.3385 | 1222773.6988
5 | 2697884.9418 | 1222790.6978 | 2697901.7316 | 1222772.5387 | 2697910.4332 | 1222763.264 | 2697913.2777 | 1222765.5791 | 2697905.3385 | 1222773.6988
6 | 2698037.6571 | 1223048.3717 | 2698043.6955 | 1223046.0362 | 2698056.5093 | 1223028.545
7 | 2697941.0339 | 1222724.0727 | 2697932.0409 | 1222716.5134
8 | 2697941.0339 | 1222724.0727 | 2697956.7052 | 1222704.7611
9 | 2697884.9418 | 1222790.6978 | 2697864.4943 | 1222812.7441
10 | 2697884.9418 | 1222790.6978 | 2697862.5278 | 1222779.2928
11 | 2698033.0539 | 1223055.212 | 2698037.6571 | 1223048.3717
12 | 2698033.0539 | 1223055.212 | 2698003.65 | 1223099.6374 | 2697994.2942 | 1223114.3961
13 | 2698069.9153 | 1223054.474 | 2698060.5348 | 1223050.1831 | 2698053.8922 | 1223050.9743 | 2698042.0026 | 1223056.2489 | 2698036.6009 | 1223056.7715 | 2698033.0539 | 1223055.212
14 | 2698069.9153 | 1223054.474 | 2698043.019 | 1223094.8971
15 | 2697956.7052 | 1222704.7611 | 2697962.7025 | 1222698.0328 | 2697965.7071 | 1222700.2949 | 2697968.4754 | 1222702.631 | 2697971.7133 | 1222699.0151
16 | 2697956.7052 | 1222704.7611 | 2697946.0789 | 1222696.1093
17 | 2697971.7133 | 1222699.0151 | 2697968.834 | 1222696.5104 | 2697973.7723 | 1222690.5207
18 | 2697971.7133 | 1222699.0151 | 2697987.0143 | 1222711.0878
19 | 2697933.261 | 1222685.673 | 2697946.0789 | 1222696.1093
20 | 2697973.7723 | 1222690.5207 | 2697988.9635 | 1222671.7933
21 | 2697991.0858 | 1222714.3003 | 2697987.0143 | 1222711.0878
22 | 2697841.4564 | 1222837.5832 | 2697864.4943 | 1222812.7441
23 | 2697862.5278 | 1222779.2928 | 2697834.7107 | 1222765.1385
24 | 2697908.2729 | 1222631.3123 | 2697927.1875 | 1222677.2116 | 2697933.261 | 1222685.673
25 | 2697908.2729 | 1222631.3123 | 2697902.0742 | 1222614.3205 | 2697897.1118 | 1222596.882 | 2697893.3343 | 1222589.0255 | 2697888.6848 | 1222583.9002
26 | 2697833.1212 | 1222539.4562 | 2697861.3093 | 1222563.0472 | 2697887.6718 | 1222582.7835 | 2697888.6848 | 1222583.9002
27 | 2697831.4035 | 1222850.6273 | 2697840.5095 | 1222859.65 | 2697843.8995 | 1222860.6175 | 2697857.866 | 1222861.9035 | 2697861.6995 | 1222860.8102 | 2697870.2037 | 1222854.3009 | 2697883.4111 | 1222841.0147
28 | 2697831.4035 | 1222850.6273 | 2697821.0366 | 1222862.3484
29 | 2697841.4564 | 1222837.5832 | 2697830.3502 | 1222849.6426 | 2697831.4035 | 1222850.6273
30 | 2697822.7642 | 1222853.3651 | 2697826.0622 | 1222854.3867 | 2697830.3502 | 1222849.6426 | 2697831.4035 | 1222850.6273
31 | 2697821.0366 | 1222862.3484 | 2697810.3039 | 1222874.4831
32 | 2697841.4564 | 1222837.5832 | 2697837.1286 | 1222833.2201
33 | 2697819.4208 | 1222852.3317 | 2697822.7642 | 1222853.3651
34 | 2698050.2519 | 1222600.7266 | 2698057.8815 | 1222606.6157
35 | 2698035.9872 | 1222613.8233 | 2698048.0272 | 1222599.011 | 2698050.2519 | 1222600.7266
36 | 2698050.2519 | 1222600.7266 | 2698048.0272 | 1222599.011 | 2698070.4129 | 1222573.239 | 2698081.8283 | 1222562.2748 | 2698091.3552 | 1222556.3497 | 2698100.8514 | 1222554.5938 | 2698112.6422 | 1222554.9105 | 2698148.2793 | 1222560.9799 | 2698164.6316 | 1222562.0724 | 2698178.5254 | 1222560.4448 | 2698195.431 | 1222556.0537 | 2698209.3923 | 1222549.8796 | 2698219.1399 | 1222544.3809
37 | 2698057.8815 | 1222606.6157 | 2698062.628 | 1222610.2794
38 | 2698035.9872 | 1222613.8233 | 2698033.8632 | 1222611.52 | 2698037.4252 | 1222606.8973
39 | 2698219.1399 | 1222544.3809 | 2698223.1568 | 1222548.7391 | 2698228.9355 | 1222551.6031 | 2698237.6445 | 1222550.2014 | 2698243.3476 | 1222548.1342
40 | 2698219.1399 | 1222544.3809 | 2698215.1167 | 1222543.1692
41 | 2697991.0858 | 1222714.3003 | 2698007.0301 | 1222727.7056
42 | 2697991.0858 | 1222714.3003 | 2698000.0941 | 1222704.2902
43 | 2697798.0926 | 1222746.506 | 2697834.7107 | 1222765.1385
44 | 2697833.1212 | 1222539.4562 | 2697807.6845 | 1222547.1719
45 | 2697833.1212 | 1222539.4562 | 2697811.9296 | 1222522.1735
46 | 2698215.1167 | 1222543.1692 | 2698223.3175 | 1222536.244 | 2698232.1188 | 1222526.9603 | 2698233.9723 | 1222523.9839
47 | 2698123.7925 | 1222476.3049 | 2698182.4939 | 1222528.1983 | 2698195.1231 | 1222536.557 | 2698204.9718 | 1222540.0997 | 2698215.1167 | 1222543.1692
48 | 2698244.5942 | 1222504.1943 | 2698239.1164 | 1222515.7233 | 2698233.9723 | 1222523.9839
49 | 2698243.3476 | 1222548.1342 | 2698245.5661 | 1222547.33 | 2698255.2304 | 1222541.363
50 | 2698244.5942 | 1222504.1943 | 2698258.9053 | 1222469.4946 | 2698261.9699 | 1222458.002
51 | 2698244.5942 | 1222504.1943 | 2698220.2113 | 1222502.9134 | 2698203.6924 | 1222496.6867
52 | 2698264.8556 | 1222448.1887 | 2698262.1643 | 1222457.273 | 2698261.9699 | 1222458.002
53 | 2698264.8556 | 1222448.1887 | 2698242.1566 | 1222434.5044 | 2698219.7813 | 1222403.0351 | 2698219.8933 | 1222396.2489
54 | 2698255.2304 | 1222541.363 | 2698255.2304 | 1222541.363 | 2698264.9197 | 1222530.6708 | 2698287.8833 | 1222495.9363
55 | 2698062.628 | 1222610.2794 | 2698097.4871 | 1222637.1861 | 2698102.2461 | 1222643.002 | 2698102.7073 | 1222644.2686
56 | 2697798.0926 | 1222746.506 | 2697791.6623 | 1222752.8271 | 2697787.6379 | 1222761.3782 | 2697787.0464 | 1222763.415
57 | 2697791.2949 | 1222793.1831 | 2697781.5672 | 1222782.2823 | 2697787.0464 | 1222763.415
58 | 2697650.8326 | 1222671.5847 | 2697627.1678 | 1222659.5447
59 | 2697625.8026 | 1222658.8502 | 2697627.1678 | 1222659.5447
60 | 2698107.2318 | 1222656.6939 | 2698102.7073 | 1222644.2686
61 | 2698107.2318 | 1222656.6939 | 2698107.2318 | 1222656.6939 | 2698080.0784 | 1222666.7374
62 | 2698080.0784 | 1222666.7374 | 2698077.6185 | 1222667.6472 | 2698070.0926 | 1222672.7603 | 2698062.6555 | 1222681.1769
63 | 2698041.6744 | 1222688.4332 | 2698044.2718 | 1222690.1919 | 2698049.7408 | 1222691.5941 | 2698054.5401 | 1222690.3611 | 2698062.6555 | 1222681.1769
64 | 2698015.2331 | 1222687.4675 | 2698028.5037 | 1222684.0502 | 2698035.2169 | 1222684.0607 | 2698041.6744 | 1222688.4332
65 | 2698015.2331 | 1222687.4675 | 2698000.0941 | 1222704.2902
66 | 2698015.2331 | 1222687.4675 | 2698030.5971 | 1222667.9826
67 | 2698045.4565 | 1222649.1377 | 2698030.5971 | 1222667.9826
68 | 2697801.636 | 1222884.2832 | 2697810.3039 | 1222874.4831
69 | 2697786.5645 | 1222895.4672 | 2697789.3726 | 1222898.1485
70 | 2697786.5645 | 1222895.4672 | 2697784.1905 | 1222893.1488 | 2697789.0382 | 1222888.1489
71 | 2697789.3726 | 1222898.1485 | 2697787.313 | 1222900.3944
72 | 2697789.3726 | 1222898.1485 | 2697801.636 | 1222884.2832
73 | 2697819.4208 | 1222852.3317 | 2697794.8251 | 1222844.7
74 | 2697748.9231 | 1222936.7118 | 2697750.7732 | 1222939.0661
75 | 2697748.9231 | 1222936.7118 | 2697728.3779 | 1222912.9355
76 | 2697818.2822 | 1222946.0464 | 2697792.3451 | 1222959.1297 | 2697786.4669 | 1222961.4126 | 2697777.6617 | 1222961.3235 | 2697767.9277 | 1222959.1398 | 2697750.7732 | 1222939.0661
77 | 2697750.7732 | 1222939.0661 | 2697765.5446 | 1222924.1313 | 2697787.313 | 1222900.3944
78 | 2697750.7732 | 1222939.0661 | 2697745.4813 | 1222943.9827 | 2697738.0439 | 1222950.4254
79 | 2697728.3779 | 1222912.9355 | 2697743.7429 | 1222895.9518
80 | 2697728.3779 | 1222912.9355 | 2697698.8682 | 1222887.2106 | 2697667.5871 | 1222872.8094 | 2697663.8279 | 1222869.8218
81 | 2697628.3404 | 1223022.3666 | 2697622.9863 | 1223025.7314 | 2697605.1023 | 1223036.7016 | 2697595.4244 | 1223044.0482 | 2697586.9449 | 1223052.3262 | 2697577.5841 | 1223064.8484 | 2697576.4757 | 1223066.5607
82 | 2697628.3404 | 1223022.3666 | 2697647.6314 | 1223010.243
83 | 2697576.4757 | 1223066.5607 | 2697567.4623 | 1223080.4851
84 | 2697647.6314 | 1223010.243 | 2697675.8166 | 1222992.5297 | 2697710.7036 | 1222970.7471
85 | 2697558.458 | 1223094.3953 | 2697567.4623 | 1223080.4851
86 | 2697710.7036 | 1222970.7471 | 2697713.3314 | 1222969.1063 | 2697730.1398 | 1222957.2444
87 | 2697510.0324 | 1223149.1112 | 2697522.8744 | 1223138.2821 | 2697533.2029 | 1223128.7112 | 2697544.5271 | 1223114.3976 | 2697553.1632 | 1223102.5751 | 2697558.458 | 1223094.3953
88 | 2697738.0439 | 1222950.4254 | 2697730.3147 | 1222957.1209 | 2697730.1398 | 1222957.2444
89 | 2697510.0324 | 1223149.1112 | 2697509.6682 | 1223149.4182 | 2697502.0305 | 1223154.6708
90 | 2697632.1753 | 1222840.61 | 2697636.1457 | 1222847.8205 | 2697663.8279 | 1222869.8218
91 | 2697632.1753 | 1222840.61 | 2697624.036 | 1222825.8285 | 2697608.8807 | 1222810.9917 | 2697523.973 | 1222768.5814 | 2697523.973 | 1222768.5814
92 | 2697523.973 | 1222768.5814 | 2697539.4386 | 1222749.0791
93 | 2697523.973 | 1222768.5814 | 2697415.5206 | 1222915.9888
94 | 2697746.3165 | 1222893.1071 | 2697743.7429 | 1222895.9518
95 | 2697760.007 | 1222877.9742 | 2697746.3165 | 1222893.1071
96 | 2697604.6294 | 1223033.4898 | 2697594.823 | 1223040.4802 | 2697584.2742 | 1223050.5145 | 2697576.645 | 1223060.5966 | 2697552.642 | 1223097.3199
97 | 2697530.8438 | 1223126.3769 | 2697533.9205 | 1223123.3413 | 2697542.8782 | 1223112.2579 | 2697552.642 | 1223097.3199
98 | 2697460.1499 | 1223170.8894 | 2697481.8598 | 1223162.0052 | 2697498.1554 | 1223153.9663 | 2697508.2166 | 1223147.2818 | 2697520.9834 | 1223136.1052 | 2697530.8438 | 1223126.3769
99 | 2697460.1499 | 1223170.8894 | 2697461.457 | 1223173.9797
100 | 2697461.457 | 1223173.9797 | 2697483.5844 | 1223164.6131 | 2697498.8667 | 1223156.8466 | 2697502.0305 | 1223154.6708
101 | 2697895.7049 | 1222473.5155 | 2697879.7149 | 1222479.8125
102 | 2697895.7049 | 1222473.5155 | 2697895.7049 | 1222473.5155 | 2697903.9683 | 1222466.9245 | 2697913.8366 | 1222438.3239
103 | 2697879.7149 | 1222479.8125 | 2697842.9499 | 1222494.2907
104 | 2697825.8933 | 1222504.2651 | 2697832.0942 | 1222498.5657 | 2697842.9499 | 1222494.2907
105 | 2697811.9296 | 1222522.1735 | 2697814.2788 | 1222514.9403 | 2697825.8933 | 1222504.2651
106 | 2697811.9296 | 1222522.1735 | 2697795.3288 | 1222509.2632
107 | 2697795.3288 | 1222509.2632 | 2697777.1526 | 1222495.1276 | 2697725.2157 | 1222442.2152 | 2697689.0654 | 1222410.9357
108 | 2697398.1883 | 1221400.9062 | 2697433.4671 | 1221404.2775
109 | 2697340.9251 | 1221394.7783 | 2697392.7308 | 1221400.3847 | 2697398.1883 | 1221400.9062
110 | 2697340.9251 | 1221394.7783 | 2697328.4322 | 1221395.4969 | 2697316.9376 | 1221395.4583
111 | 2697340.9251 | 1221394.7783 | 2697343.3031 | 1221405.2579 | 2697371.6402 | 1221438.7448 | 2697392.9632 | 1221450.1682
112 | 2697393.3767 | 1221450.5308 | 2697392.9632 | 1221450.1682
113 | 2697393.3767 | 1221450.5308 | 2697585.2412 | 1221724.4878
114 | 2697546.8256 | 1221815.3896 | 2697547.1446 | 1221813.9827 | 2697558.462 | 1221774.3066 | 2697574.1807 | 1221739.684 | 2697585.2412 | 1221724.4878
115 | 2697524.1234 | 1221901.6568 | 2697524.1541 | 1221901.5401
116 | 2697546.8256 | 1221815.3896 | 2697524.1541 | 1221901.5401
117 | 2697524.1234 | 1221901.6568 | 2697648.2383 | 1222096.0619
118 | 2697571.8493 | 1222383.9144 | 2697648.2383 | 1222096.0619
119 | 2697414.8727 | 1222366.1651 | 2697516.1299 | 1222365.8333 | 2697527.574 | 1222367.8888 | 2697571.8493 | 1222383.9144
120 | 2697509.7025 | 1222515.9458 | 2697522.286 | 1222504.0101 | 2697530.6363 | 1222491.1599 | 2697542.0175 | 1222467.4183 | 2697571.8493 | 1222383.9144
121 | 2697571.8493 | 1222383.9144 | 2697656.2447 | 1222397.7743 | 2697671.5625 | 1222400.4497
122 | 2697671.5625 | 1222400.4497 | 2697679.3674 | 1222403.7578 | 2697682.8105 | 1222406.1271 | 2697686.2461 | 1222408.4962 | 2697689.0654 | 1222410.9357
123 | 2697782.7463 | 1222554.7365 | 2697807.6845 | 1222547.1719
124 | 2697509.7025 | 1222515.9458 | 2697504.5541 | 1222526.4468 | 2697509.8389 | 1222548.36 | 2697490.163 | 1222552.8794
125 | 2697782.7463 | 1222554.7365 | 2697750.3316 | 1222564.5689
126 | 2697456.1089 | 1222569.2072 | 2697474.8654 | 1222556.3931 | 2697490.163 | 1222552.8794
127 | 2697395.967 | 1222648.4898 | 2697420.4967 | 1222608.3403 | 2697454.0598 | 1222570.6071 | 2697456.1089 | 1222569.2072
128 | 2697395.967 | 1222648.4898 | 2697387.3981 | 1222647.2102
129 | 2697395.967 | 1222648.4898 | 2697417.1366 | 1222647.2352 | 2697438.0468 | 1222638.6601 | 2697442.3538 | 1222636.2996
130 | 2697442.3538 | 1222636.2996 | 2697462.1584 | 1222625.4453 | 2697464.32 | 1222624.7743
131 | 2697464.32 | 1222624.7743 | 2697484.6813 | 1222618.4535 | 2697508.7971 | 1222617.4921 | 2697543.2705 | 1222621.9043 | 2697567.0539 | 1222630.6033
132 | 2697625.8026 | 1222658.8502 | 2697618.259 | 1222655.0122 | 2697573.6966 | 1222633.0329 | 2697567.0539 | 1222630.6033
133 | 2697954.9922 | 1223167.752 | 2697960.5218 | 1223161.2939 | 2697985.5829 | 1223128.1381 | 2697994.2942 | 1223114.3961
134 | 2697954.9922 | 1223167.752 | 2697959.8075 | 1223167.3642 | 2697967.7444 | 1223161.2015 | 2697973.1 | 1223156.6712
135 | 2697814.138 | 1223343.9287 | 2697954.9922 | 1223167.752
136 | 2697610.8957 | 1223490.8313 | 2697608.2227 | 1223494.7236 | 2697603.3998 | 1223502.9838 | 2697601.6965 | 1223514.8088 | 2697604.4732 | 1223523.5494 | 2697623.1897 | 1223549.1189 | 2697624.3152 | 1223550.3967
137 | 2697610.8957 | 1223490.8313 | 2697631.4339 | 1223494.593 | 2697646.4854 | 1223490.6815 | 2697662.4444 | 1223482.3151 | 2697675.0142 | 1223467.4106 | 2697689.4 | 1223443.0737 | 2697709.7919 | 1223418.3463 | 2697722.8706 | 1223402.9499 | 2697729.7682 | 1223388.4528 | 2697734.0342 | 1223372.0889 | 2697741.3193 | 1223365.4037
138 | 2697741.3193 | 1223365.4037 | 2697741.6187 | 1223359.182 | 2697748.6378 | 1223352.0699 | 2697758.8231 | 1223337.827 | 2697759.4426 | 1223332.9003
139 | 2697741.3193 | 1223365.4037 | 2697752.5776 | 1223371.2594 | 2697765.7062 | 1223361.6125 | 2697780.558 | 1223346.8014 | 2697798.0326 | 1223344.5535 | 2697800.6483 | 1223344.452
140 | 2697759.4426 | 1223332.9003 | 2697747.527 | 1223339.8096 | 2697704.4559 | 1223360.851 | 2697669.714 | 1223376.759 | 2697640.7229 | 1223387.5859
141 | 2697814.138 | 1223343.9287 | 2697800.6483 | 1223344.452
142 | 2697640.7229 | 1223387.5859 | 2697629.9 | 1223391.6277 | 2697624.6014 | 1223393.5565
143 | 2698287.8833 | 1222495.9363 | 2698288.8286 | 1222494.5065

## bus_geodata
| x | y | coords
0 | 2697932.2652 | 1222795.1492
1 | 2697987.641 | 1222812.1485
2 | 2697905.3385 | 1222773.6988
3 | 2698056.5093 | 1223028.545
4 | 2697891.6845 | 1222787.4797
5 | 2697941.0339 | 1222724.0727
6 | 2697884.9418 | 1222790.6978
7 | 2698037.6571 | 1223048.3718
8 | 2698033.0539 | 1223055.212
9 | 2698069.9153 | 1223054.474
10 | 2698043.019 | 1223094.8971
11 | 2697956.7052 | 1222704.7611
12 | 2697971.7133 | 1222699.0151
13 | 2697946.0789 | 1222696.1093
14 | 2697932.0409 | 1222716.5134
15 | 2697973.7723 | 1222690.5207
16 | 2697987.0143 | 1222711.0878
17 | 2697864.4943 | 1222812.7441
18 | 2697862.5278 | 1222779.2928
19 | 2697988.9635 | 1222671.7933
20 | 2697933.261 | 1222685.673
21 | 2697908.2729 | 1222631.3123
22 | 2697888.6848 | 1222583.9002
23 | 2697831.4036 | 1222850.6273
24 | 2697883.4111 | 1222841.0147
25 | 2697821.0366 | 1222862.3484
26 | 2697841.4564 | 1222837.5832
27 | 2697822.7642 | 1222853.3651
28 | 2698050.2519 | 1222600.7266
29 | 2698057.8815 | 1222606.6157
30 | 2698035.9872 | 1222613.8233
31 | 2698219.1399 | 1222544.3809
32 | 2698037.4252 | 1222606.8973
33 | 2697991.0858 | 1222714.3003
34 | 2697834.7107 | 1222765.1385
35 | 2697833.1212 | 1222539.4562
36 | 2698215.1166 | 1222543.1692
37 | 2698233.9723 | 1222523.9839
38 | 2698123.7925 | 1222476.3049
39 | 2698243.3476 | 1222548.1342
40 | 2698244.5942 | 1222504.1943
41 | 2698261.9699 | 1222458.002
42 | 2698203.6924 | 1222496.6867
43 | 2698264.8556 | 1222448.1887
44 | 2698219.8933 | 1222396.2489
45 | 2698255.2304 | 1222541.363
46 | 2698062.628 | 1222610.2794
47 | 2697798.0926 | 1222746.506
48 | 2697787.0464 | 1222763.415
49 | 2697791.2949 | 1222793.1831
50 | 2697650.8326 | 1222671.5847
51 | 2697627.1678 | 1222659.5447
52 | 2697837.1286 | 1222833.2201
53 | 2698102.7073 | 1222644.2686
54 | 2698107.2318 | 1222656.6939
55 | 2698080.0784 | 1222666.7374
56 | 2698062.6555 | 1222681.1769
57 | 2698041.6744 | 1222688.4332
58 | 2698015.2331 | 1222687.4675
59 | 2698000.0941 | 1222704.2902
60 | 2698030.5971 | 1222667.9826
61 | 2698045.4565 | 1222649.1377
62 | 2698007.0301 | 1222727.7056
63 | 2697810.3039 | 1222874.4831
64 | 2697786.5645 | 1222895.4672
65 | 2697789.3726 | 1222898.1485
66 | 2697789.0382 | 1222888.1489
67 | 2697819.4208 | 1222852.3317
68 | 2697801.636 | 1222884.2832
69 | 2697748.9231 | 1222936.7118
70 | 2697750.7732 | 1222939.0661
71 | 2697728.3779 | 1222912.9355
72 | 2697787.313 | 1222900.3944
73 | 2697794.8251 | 1222844.7
74 | 2697628.3404 | 1223022.3666
75 | 2697576.4757 | 1223066.5607
76 | 2697647.6314 | 1223010.243
77 | 2697567.4623 | 1223080.4851
78 | 2697710.7036 | 1222970.7471
79 | 2697558.458 | 1223094.3953
80 | 2697730.1398 | 1222957.2444
81 | 2697510.0324 | 1223149.1112
82 | 2697738.0439 | 1222950.4254
83 | 2697632.1753 | 1222840.61
84 | 2697663.8279 | 1222869.8218
85 | 2697523.973 | 1222768.5814
86 | 2697539.4386 | 1222749.0791
87 | 2697415.5206 | 1222915.9888
88 | 2697743.7429 | 1222895.9518
89 | 2697746.3165 | 1222893.1071
90 | 2697604.6294 | 1223033.4898
91 | 2697552.642 | 1223097.3199
92 | 2697530.8438 | 1223126.3769
93 | 2697460.1499 | 1223170.8894
94 | 2697818.2822 | 1222946.0464
95 | 2697461.457 | 1223173.9797
96 | 2697502.0305 | 1223154.6708
97 | 2697760.007 | 1222877.9742
98 | 2697895.7049 | 1222473.5155
99 | 2697879.7149 | 1222479.8125
100 | 2697913.8366 | 1222438.3239
101 | 2697842.9499 | 1222494.2907
102 | 2697825.8933 | 1222504.2651
103 | 2697811.9296 | 1222522.1735
104 | 2697795.3288 | 1222509.2632
105 | 2697398.1883 | 1221400.9062
106 | 2697433.4671 | 1221404.2775
107 | 2697340.9251 | 1221394.7783
108 | 2697316.9376 | 1221395.4583
109 | 2697392.9632 | 1221450.1682
110 | 2697393.3767 | 1221450.5308
111 | 2697585.2412 | 1221724.4878
112 | 2697524.1541 | 1221901.5401
113 | 2697524.1234 | 1221901.6568
114 | 2697546.8256 | 1221815.3896
115 | 2697648.2383 | 1222096.0619
116 | 2697571.8493 | 1222383.9144
117 | 2697689.0654 | 1222410.9357
118 | 2697671.5625 | 1222400.4497
119 | 2697807.6845 | 1222547.1719
120 | 2697414.8727 | 1222366.1651
121 | 2697509.7025 | 1222515.9458
122 | 2697782.7463 | 1222554.7365
123 | 2697456.1089 | 1222569.2072
124 | 2697490.163 | 1222552.8794
125 | 2697395.967 | 1222648.4898
126 | 2697387.3981 | 1222647.2102
127 | 2697442.3538 | 1222636.2996
128 | 2697464.32 | 1222624.7743
129 | 2697567.0539 | 1222630.6033
130 | 2697750.3316 | 1222564.5689
131 | 2697625.8026 | 1222658.8502
132 | 2697994.2942 | 1223114.3961
133 | 2697954.9922 | 1223167.752
134 | 2697624.3152 | 1223550.3967
135 | 2697610.8957 | 1223490.8313
136 | 2697741.3193 | 1223365.4037
137 | 2697759.4426 | 1223332.9003
138 | 2697800.6483 | 1223344.452
139 | 2697640.7229 | 1223387.5859
140 | 2697814.138 | 1223343.9287
141 | 2698287.8833 | 1222495.9363
142 | 2698288.8286 | 1222494.5065
143 | 2697624.6014 | 1223393.5565
144 | 2697973.1 | 1223156.6712
145 | 2697884.9418 | 1222790.6978

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99106 | -0.17098 | 0.0090329 | 0.0022638
1 | 0.98982 | -0.19497 | 0.0023315 | 0.00058434
2 | 0.992 | -0.15289 | 0 | 0
3 | 0.98604 | -0.26827 | 0.0016885 | 0.00042317
4 | 0.99164 | -0.15975 | 0.01996 | 0.0050023
5 | 0.98765 | -0.23677 | 0 | 0
6 | 0.99774 | -0.043085 | 0 | 0
7 | 0.98561 | -0.27654 | 0 | 0
8 | 0.98549 | -0.27896 | 0 | 0
9 | 0.9854 | -0.28074 | 0 | 0
10 | 0.98528 | -0.28295 | 0.0025261 | 0.0006331
11 | 0.98615 | -0.266 | 0 | 0
12 | 0.98543 | -0.27987 | 0 | 0
13 | 0.98577 | -0.27322 | 0.0062761 | 0.0015729
14 | 0.98761 | -0.23754 | 0.0036734 | 0.00092064
15 | 0.98541 | -0.28029 | 0 | 0
16 | 0.98482 | -0.29188 | 0.0024164 | 0.00060561
17 | 1 | 0 | -0.28328 | -0.071595
18 | 0.9967 | -0.063015 | 0.030127 | 0.0075506
19 | 0.98537 | -0.28118 | 0.0020447 | 0.00051244
20 | 0.98542 | -0.28007 | 0 | 0
21 | 0.98414 | -0.305 | 0 | 0
22 | 0.98304 | -0.32657 | 0.002499 | 0.0006263
23 | 0.99482 | -0.099201 | 0 | 0
24 | 0.9935 | -0.12475 | 0.022703 | 0.0056899
25 | 0.99378 | -0.11916 | 0.0068996 | 0.0017292
26 | 0.99643 | -0.068138 | 0 | 0
27 | 0.99478 | -0.099994 | 0 | 0
28 | 0.98102 | -0.36608 | 0 | 0
29 | 0.98111 | -0.36431 | 0.00061207 | 0.0001534
30 | 0.981 | -0.36651 | 0 | 0
31 | 0.97939 | -0.39815 | 0 | 0
32 | 0.98099 | -0.36669 | 0.0010996 | 0.00027559
33 | 0.98466 | -0.29486 | 0 | 0
34 | 0.99627 | -0.071279 | 0.0085704 | 0.0021479
35 | 0.98169 | -0.35306 | 0 | 0
36 | 0.97936 | -0.39857 | 0 | 0
37 | 0.97927 | -0.40045 | 0.00048173 | 0.00012073
38 | 0.97919 | -0.4019 | 0.0016019 | 0.00040147
39 | 0.97929 | -0.39992 | 0.0010009 | 0.00025086
40 | 0.9792 | -0.40183 | 0 | 0
41 | 0.97908 | -0.40406 | 0.00087129 | 0.00021837
42 | 0.97916 | -0.40249 | 0.00086818 | 0.00021759
43 | 0.97907 | -0.40436 | 0 | 0
44 | 0.97896 | -0.40647 | 0.0016114 | 0.00040384
45 | 0.97926 | -0.40057 | 0.00076126 | 0.00019079
46 | 0.98117 | -0.36314 | 0.0014532 | 0.00036421
47 | 0.99603 | -0.075981 | 0 | 0
48 | 0.99591 | -0.078337 | 0.0037439 | 0.0009383
49 | 0.99582 | -0.080004 | 0.0027681 | 0.00069376
50 | 0.97679 | -0.4496 | 0.00040195 | 0.00010074
51 | 0.9768 | -0.4494 | 0.00068039 | 0.00017052
52 | 0.99635 | -0.069857 | 0.015933 | 0.0039933
53 | 0.98176 | -0.35147 | 0.0013392 | 0.00033563
54 | 0.98193 | -0.34823 | 0.0033855 | 0.0008485
55 | 0.98238 | -0.33938 | 0.0022697 | 0.00056883
56 | 0.98279 | -0.33142 | 0.0014184 | 0.00035549
57 | 0.98328 | -0.32176 | 0.0019539 | 0.0004897
58 | 0.98387 | -0.31029 | 0 | 0
59 | 0.98436 | -0.30073 | 0.00076048 | 0.0001906
60 | 0.98385 | -0.3107 | 0.00049758 | 0.00012471
61 | 0.98384 | -0.31087 | 0.00041283 | 0.00010347
62 | 0.98452 | -0.29772 | 0.0076652 | 0.0019211
63 | 0.99281 | -0.1379 | 0.0024328 | 0.00060972
64 | 0.99106 | -0.1716 | 0 | 0
65 | 0.99108 | -0.1713 | 0 | 0
66 | 0.99102 | -0.17241 | 0.0044328 | 0.001111
67 | 0.99476 | -0.10024 | 0 | 0
68 | 0.99205 | -0.15249 | 0.0057002 | 0.0014286
69 | 0.98839 | -0.22342 | 0 | 0
70 | 0.98846 | -0.22206 | 0 | 0
71 | 0.98765 | -0.23766 | 0 | 0
72 | 0.99093 | -0.17416 | 0.0023009 | 0.00057665
73 | 0.99467 | -0.10204 | 0.0039845 | 0.00099862
74 | 0.98721 | -0.24632 | 0.00072536 | 0.00018179
75 | 0.98679 | -0.25458 | 0.00079274 | 0.00019868
76 | 0.98737 | -0.2433 | 0.0006116 | 0.00015328
77 | 0.9867 | -0.25634 | 0.00061633 | 0.00015447
78 | 0.98791 | -0.23262 | 0.0019609 | 0.00049146
79 | 0.98662 | -0.2579 | 0.0019757 | 0.00049515
80 | 0.98813 | -0.22839 | 0.00068847 | 0.00017255
81 | 0.9864 | -0.26226 | 0.00021838 | 5.473e-05
82 | 0.98823 | -0.2264 | 0.0035664 | 0.00089382
83 | 0.9863 | -0.26397 | 0.003943 | 0.00098822
84 | 0.98674 | -0.25542 | 0.0017086 | 0.00042821
85 | 0.98545 | -0.28069 | 0.0021351 | 0.00053511
86 | 0.98535 | -0.28258 | 0.0042301 | 0.0010602
87 | 0.98534 | -0.28279 | 0.00063562 | 0.0001593
88 | 0.98739 | -0.24288 | 0.0032379 | 0.00081149
89 | 0.98735 | -0.24354 | 0.0058997 | 0.0014786
90 | 0.98607 | -0.26864 | 0.00048328 | 0.00012112
91 | 0.98611 | -0.26792 | 0.00075685 | 0.00018969
92 | 0.98615 | -0.26711 | 0.0005656 | 0.00014175
93 | 0.98629 | -0.26437 | 0 | 0
94 | 0.98765 | -0.23771 | 0.010908 | 0.0027338
95 | 0.98629 | -0.26426 | 0 | 0
96 | 0.98637 | -0.2628 | 0.0012723 | 0.00031888
97 | 0.98729 | -0.24486 | 0.0036158 | 0.00090621
98 | 0.98072 | -0.37208 | 0.00080267 | 0.00020117
99 | 0.98078 | -0.37095 | 0.0010863 | 0.00027226
100 | 0.98061 | -0.37416 | 0.0028133 | 0.00070507
101 | 0.98095 | -0.36758 | 0.0015582 | 0.00039052
102 | 0.98107 | -0.3653 | 0.0011066 | 0.00027735
103 | 0.98122 | -0.36218 | 0 | 0
104 | 0.98101 | -0.36641 | 0.0015535 | 0.00038934
105 | 0.97646 | -0.45653 | 0.00045159 | 0.00011318
106 | 0.97646 | -0.45666 | 0.00020186 | 5.0592e-05
107 | 0.9765 | -0.45584 | 0 | 0
108 | 0.97649 | -0.45595 | 0.00026748 | 6.7038e-05
109 | 0.97656 | -0.4545 | 0 | 0
110 | 0.97656 | -0.45449 | 0.00010446 | 2.6181e-05
111 | 0.97688 | -0.44816 | 0 | 0
112 | 0.97706 | -0.44456 | 0.00031783 | 7.9655e-05
113 | 0.97706 | -0.44455 | 0.001836 | 0.00046014
114 | 0.97698 | -0.44626 | 0 | 0
115 | 0.97774 | -0.43106 | 0.00038543 | 9.6598e-05
116 | 0.97872 | -0.41154 | 0 | 0
117 | 0.97974 | -0.39151 | 0.00046045 | 0.0001154
118 | 0.97957 | -0.3949 | 0 | 0
119 | 0.98164 | -0.35408 | 0.00057209 | 0.00014338
120 | 0.97868 | -0.41232 | 0.00026912 | 6.7448e-05
121 | 0.97801 | -0.42551 | 0 | 0
122 | 0.9816 | -0.35481 | 0.00074411 | 0.00018649
123 | 0.97761 | -0.43355 | 0.00054404 | 0.00013635
124 | 0.97775 | -0.43066 | 0.0010609 | 0.00026588
125 | 0.97728 | -0.4401 | 0 | 0
126 | 0.97727 | -0.44025 | 0.00098899 | 0.00024786
127 | 0.97716 | -0.4424 | 0.00025752 | 6.4541e-05
128 | 0.9771 | -0.44346 | 0.00024005 | 6.0162e-05
129 | 0.9769 | -0.4475 | 0.00051421 | 0.00012887
130 | 0.98157 | -0.3553 | 0.00080192 | 0.00020098
131 | 0.9768 | -0.44937 | 0.00049197 | 0.0001233
132 | 0.98458 | -0.29657 | 0.0023642 | 0.00059252
133 | 0.98388 | -0.31027 | 0 | 0
134 | 0.97994 | -0.38732 | 0.0037628 | 0.00094304
135 | 0.98018 | -0.38262 | 0 | 0
136 | 0.98087 | -0.36916 | 0 | 0
137 | 0.98066 | -0.37325 | 0 | 0
138 | 0.98149 | -0.35695 | 0.00089127 | 0.00022337
139 | 0.97996 | -0.38709 | 0.0051743 | 0.0012968
140 | 0.98162 | -0.35439 | 0.00033161 | 8.3109e-05
141 | 0.97917 | -0.40242 | 0.0012267 | 0.00030744
142 | 0.97917 | -0.40243 | 0.00058568 | 0.00014678
143 | 0.97995 | -0.3873 | 0.00065561 | 0.00016431
144 | 0.98387 | -0.31053 | 0.0006424 | 0.000161
145 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.020521 | 0.0051858 | -0.020498 | -0.0051715 | 2.3577e-05 | 1.4238e-05 | 0.030827 | 0.030827 | 0.030827 | 0.99106 | -0.17098 | 0.98982 | -0.19497 | 8.469
1 | -0.029554 | -0.0074496 | 0.02958 | 0.0074656 | 2.56e-05 | 1.5937e-05 | 0.044389 | 0.044389 | 0.044389 | 0.99106 | -0.17098 | 0.992 | -0.15289 | 12.1948
2 | 0.018166 | 0.0045872 | -0.018103 | -0.0045494 | 6.3573e-05 | 3.7779e-05 | 0.027322 | 0.027323 | 0.027323 | 0.98982 | -0.19497 | 0.98604 | -0.26827 | 7.5063
3 | 0.019966 | 0.0050063 | -0.01996 | -0.0050023 | 6.5257e-06 | 3.9261e-06 | 0.02995 | 0.02995 | 0.02995 | 0.992 | -0.15289 | 0.99164 | -0.15975 | 8.2281
4 | 0.069943 | 0.017731 | -0.069662 | -0.017552 | 0.00028072 | 0.00017879 | 0.10499 | 0.10499 | 0.10499 | 0.992 | -0.15289 | 0.98765 | -0.23677 | 28.8427
5 | -0.11949 | -0.030202 | 0.12012 | 0.030607 | 0.00063278 | 0.0004043 | 0.17933 | 0.17933 | 0.17933 | 0.992 | -0.15289 | 0.99774 | -0.043085 | 49.2655
6 | 0.016414 | 0.0041262 | -0.016408 | -0.0041225 | 6.4811e-06 | 3.7889e-06 | 0.024775 | 0.024775 | 0.024775 | 0.98604 | -0.26827 | 0.98561 | -0.27654 | 6.8064
7 | 0.0036735 | 0.00092057 | -0.0036734 | -0.00092064 | 1.3495e-07 | -6.397e-08 | 0.0055346 | 0.0055346 | 0.0055346 | 0.98765 | -0.23677 | 0.98761 | -0.23754 | 1.5205
8 | 0.065989 | 0.016631 | -0.065896 | -0.016573 | 9.2152e-05 | 5.866e-05 | 0.099453 | 0.099453 | 0.099453 | 0.98765 | -0.23677 | 0.98615 | -0.266 | 27.3223
9 | -0.16538 | -0.041968 | 0.16573 | 0.042187 | 0.0003435 | 0.00021905 | 0.24683 | 0.24683 | 0.24683 | 0.99774 | -0.043085 | 1 | 0 | 33.9058
10 | 0.045261 | 0.011362 | -0.045218 | -0.011334 | 4.298e-05 | 2.7179e-05 | 0.067508 | 0.067509 | 0.067509 | 0.99774 | -0.043085 | 0.9967 | -0.063015 | 18.5463
11 | 0.016408 | 0.0041225 | -0.016406 | -0.0041214 | 1.8964e-06 | 1.1087e-06 | 0.024775 | 0.024775 | 0.024775 | 0.98561 | -0.27654 | 0.98549 | -0.27896 | 6.8064
12 | 0.013879 | 0.0034891 | -0.013868 | -0.0034825 | 1.1656e-05 | 6.5595e-06 | 0.020961 | 0.020961 | 0.020961 | 0.98549 | -0.27896 | 0.98458 | -0.29657 | 5.7585
13 | 0.0025266 | 0.00063228 | -0.0025263 | -0.00063265 | 2.1398e-07 | -3.6262e-07 | 0.0038146 | 0.0038148 | 0.0038148 | 0.98549 | -0.27896 | 0.9854 | -0.28074 | 1.048
14 | 0.0025263 | 0.00063265 | -0.0025261 | -0.0006331 | 2.6498e-07 | -4.4886e-07 | 0.0038148 | 0.003815 | 0.003815 | 0.9854 | -0.28074 | 0.98528 | -0.28295 | 1.0481
15 | 0.036467 | 0.0091768 | -0.036443 | -0.0091616 | 2.414e-05 | 1.5179e-05 | 0.05504 | 0.05504 | 0.05504 | 0.98615 | -0.266 | 0.98543 | -0.27987 | 15.1208
16 | 0.029429 | 0.0073957 | -0.029419 | -0.0073894 | 1.0136e-05 | 6.3125e-06 | 0.044413 | 0.044414 | 0.044414 | 0.98615 | -0.266 | 0.98577 | -0.27322 | 12.2015
17 | 0.0020448 | 0.00051207 | -0.0020447 | -0.00051219 | 4.1393e-08 | -1.2102e-07 | 0.0030875 | 0.0030876 | 0.0030876 | 0.98543 | -0.27987 | 0.98541 | -0.28029 | 0.84823
18 | 0.034398 | 0.0086496 | -0.034379 | -0.0086372 | 1.9727e-05 | 1.2377e-05 | 0.051952 | 0.051952 | 0.051952 | 0.98543 | -0.27987 | 0.98482 | -0.29188 | 14.2726
19 | 0.023143 | 0.0058165 | -0.023135 | -0.0058118 | 7.5671e-06 | 4.6323e-06 | 0.03494 | 0.03494 | 0.03494 | 0.98577 | -0.27322 | 0.98542 | -0.28007 | 9.5989
20 | 0.0020447 | 0.00051219 | -0.0020447 | -0.00051244 | 8.6208e-08 | -2.5201e-07 | 0.0030876 | 0.0030877 | 0.0030877 | 0.98541 | -0.28029 | 0.98537 | -0.28118 | 0.84826
21 | 0.031962 | 0.0080316 | -0.031958 | -0.0080288 | 4.5373e-06 | 2.8379e-06 | 0.048301 | 0.048301 | 0.048301 | 0.98482 | -0.29188 | 0.98466 | -0.29486 | 13.2695
22 | 0.11591 | 0.029408 | -0.11553 | -0.029166 | 0.00037846 | 0.00024177 | 0.1726 | 0.1726 | 0.1726 | 1 | 0 | 0.99643 | -0.068138 | 47.4168
23 | 0.015091 | 0.0037837 | -0.015085 | -0.0037803 | 5.9412e-06 | 3.3958e-06 | 0.02253 | 0.02253 | 0.02253 | 0.9967 | -0.063015 | 0.99627 | -0.071279 | 6.1896
24 | 0.023135 | 0.0058118 | -0.023108 | -0.005795 | 2.7484e-05 | 1.6826e-05 | 0.03494 | 0.03494 | 0.03494 | 0.98542 | -0.28007 | 0.98414 | -0.305 | 9.599
25 | 0.023108 | 0.005795 | -0.023084 | -0.0057805 | 2.374e-05 | 1.4535e-05 | 0.03494 | 0.03494 | 0.03494 | 0.98414 | -0.305 | 0.98304 | -0.32657 | 9.599
26 | 0.020585 | 0.0051542 | -0.020559 | -0.0051385 | 2.592e-05 | 1.5687e-05 | 0.031158 | 0.031158 | 0.031158 | 0.98304 | -0.32657 | 0.98169 | -0.35306 | 8.5599
27 | 0.022731 | 0.0057068 | -0.022703 | -0.0056899 | 2.7662e-05 | 1.6877e-05 | 0.034003 | 0.034003 | 0.034003 | 0.99482 | -0.099201 | 0.9935 | -0.12475 | 9.3416
28 | 0.072729 | 0.018372 | -0.07266 | -0.018328 | 6.951e-05 | 4.4283e-05 | 0.10884 | 0.10884 | 0.10884 | 0.99482 | -0.099201 | 0.99378 | -0.11916 | 29.9005
29 | -0.099445 | -0.025077 | 0.099593 | 0.025172 | 0.0001481 | 9.4551e-05 | 0.1488 | 0.1488 | 0.1488 | 0.99482 | -0.099201 | 0.99643 | -0.068138 | 40.8795
30 | 0.0039851 | 0.00099844 | -0.0039849 | -0.00099849 | 1.5041e-07 | -5.0305e-08 | 0.0059607 | 0.0059607 | 0.0059607 | 0.99482 | -0.099201 | 0.99478 | -0.099994 | 1.6376
31 | 0.06576 | 0.016599 | -0.065701 | -0.016561 | 5.895e-05 | 3.7518e-05 | 0.098507 | 0.098507 | 0.098507 | 0.99378 | -0.11916 | 0.99281 | -0.1379 | 27.0623
32 | 0.015935 | 0.003994 | -0.015933 | -0.0039933 | 1.305e-06 | 7.5513e-07 | 0.023796 | 0.023796 | 0.023796 | 0.99643 | -0.068138 | 0.99635 | -0.069857 | 6.5374
33 | 0.0039849 | 0.00099849 | -0.0039849 | -0.00099851 | 4.65e-08 | -1.5549e-08 | 0.0059607 | 0.0059607 | 0.0059607 | 0.99478 | -0.099994 | 0.99476 | -0.10024 | 1.6376
34 | -0.010124 | -0.0025351 | 0.010125 | 0.0025355 | 8.5225e-07 | 4.2374e-07 | 0.015356 | 0.015356 | 0.015356 | 0.98102 | -0.36608 | 0.98111 | -0.36431 | 4.2186
35 | 0.0010996 | 0.00027522 | -0.0010996 | -0.00027548 | 2.2842e-08 | -2.6186e-07 | 0.0016678 | 0.0016679 | 0.0016679 | 0.98102 | -0.36608 | 0.981 | -0.36651 | 0.45821
36 | 0.0090247 | 0.0022599 | -0.0090109 | -0.0022536 | 1.3765e-05 | 6.3402e-06 | 0.013688 | 0.013689 | 0.013689 | 0.98102 | -0.36608 | 0.97939 | -0.39815 | 3.7607
37 | -0.010737 | -0.0026889 | 0.010738 | 0.0026893 | 5.9624e-07 | 3.0587e-07 | 0.016284 | 0.016284 | 0.016284 | 0.98111 | -0.36431 | 0.98117 | -0.36314 | 4.4737
38 | 0.0010996 | 0.00027548 | -0.0010996 | -0.00027559 | 9.3567e-09 | -1.0725e-07 | 0.0016679 | 0.0016679 | 0.0016679 | 0.981 | -0.36651 | 0.98099 | -0.36669 | 0.45822
39 | 0.0035751 | 0.00089497 | -0.0035748 | -0.00089512 | 3.0161e-07 | -1.5002e-07 | 0.0054314 | 0.0054315 | 0.0054315 | 0.97939 | -0.39815 | 0.97929 | -0.39992 | 1.4922
40 | 0.0054358 | 0.0013586 | -0.0054357 | -0.0013586 | 1.0714e-07 | 1.5843e-08 | 0.0082575 | 0.0082575 | 0.0082575 | 0.97939 | -0.39815 | 0.97936 | -0.39857 | 2.2686
41 | 0.0076662 | 0.0019215 | -0.0076652 | -0.0019211 | 1.0467e-06 | 4.054e-07 | 0.011585 | 0.011585 | 0.011585 | 0.98466 | -0.29486 | 0.98452 | -0.29772 | 3.1828
42 | 0.024291 | 0.0061073 | -0.024285 | -0.0061031 | 6.8077e-06 | 4.1857e-06 | 0.036716 | 0.036716 | 0.036716 | 0.98466 | -0.29486 | 0.98436 | -0.30073 | 10.0868
43 | 0.0065144 | 0.0016324 | -0.0065129 | -0.001632 | 1.4586e-06 | 3.9861e-07 | 0.0097297 | 0.0097299 | 0.0097299 | 0.99627 | -0.071279 | 0.99603 | -0.075981 | 2.673
44 | 0.0021183 | 0.00052987 | -0.0021182 | -0.00053014 | 1.0274e-07 | -2.703e-07 | 0.0032105 | 0.0032106 | 0.0032106 | 0.98169 | -0.35306 | 0.98164 | -0.35408 | 0.88203
45 | 0.018441 | 0.0046086 | -0.018433 | -0.0046038 | 7.9957e-06 | 4.7723e-06 | 0.027948 | 0.027948 | 0.027948 | 0.98169 | -0.35306 | 0.98122 | -0.36218 | 7.678
46 | 0.0038336 | 0.00095839 | -0.0038332 | -0.00095851 | 3.4383e-07 | -1.2008e-07 | 0.0058238 | 0.0058239 | 0.0058239 | 0.97936 | -0.39857 | 0.97927 | -0.40045 | 1.6
47 | 0.0016021 | 0.00040019 | -0.0016019 | -0.00040147 | 2.5404e-07 | -1.276e-06 | 0.0024338 | 0.0024343 | 0.0024343 | 0.97936 | -0.39857 | 0.97919 | -0.4019 | 0.66876
48 | 0.0033515 | 0.00083777 | -0.0033513 | -0.00083792 | 2.1872e-07 | -1.4301e-07 | 0.0050919 | 0.005092 | 0.005092 | 0.97927 | -0.40045 | 0.9792 | -0.40183 | 1.3989
49 | 0.0025739 | 0.00064426 | -0.0025738 | -0.00064439 | 7.8671e-08 | -1.2224e-07 | 0.0039106 | 0.0039107 | 0.0039107 | 0.97929 | -0.39992 | 0.97926 | -0.40057 | 1.0744
50 | 0.0024831 | 0.00062084 | -0.0024828 | -0.0006213 | 2.6386e-07 | -4.5283e-07 | 0.0037728 | 0.0037731 | 0.0037731 | 0.9792 | -0.40183 | 0.97908 | -0.40406 | 1.0366
51 | 0.00086821 | 0.00021708 | -0.00086818 | -0.00021759 | 2.7458e-08 | -5.1161e-07 | 0.0013192 | 0.0013194 | 0.0013194 | 0.9792 | -0.40183 | 0.97916 | -0.40249 | 0.36246
52 | 0.0016115 | 0.00040293 | -0.0016115 | -0.00040304 | 2.3004e-08 | -1.1392e-07 | 0.0024489 | 0.0024489 | 0.0024489 | 0.97908 | -0.40406 | 0.97907 | -0.40436 | 0.67278
53 | 0.0016115 | 0.00040304 | -0.0016114 | -0.00040384 | 1.6173e-07 | -8.0066e-07 | 0.0024489 | 0.0024492 | 0.0024492 | 0.97907 | -0.40436 | 0.97896 | -0.40647 | 0.67287
54 | 0.0018125 | 0.0004536 | -0.0018124 | -0.0004542 | 1.5948e-07 | -6.0325e-07 | 0.0027539 | 0.0027542 | 0.0027542 | 0.97926 | -0.40057 | 0.97917 | -0.40242 | 0.75665
55 | -0.012191 | -0.0030535 | 0.012198 | 0.0030571 | 6.7803e-06 | 3.6709e-06 | 0.018488 | 0.018488 | 0.018488 | 0.98117 | -0.36314 | 0.98176 | -0.35147 | 5.0791
56 | 0.0065129 | 0.001632 | -0.0065122 | -0.0016318 | 7.3093e-07 | 1.9986e-07 | 0.0097299 | 0.00973 | 0.00973 | 0.99603 | -0.075981 | 0.99591 | -0.078337 | 2.6731
57 | 0.0027684 | 0.00069345 | -0.0027681 | -0.00069376 | 2.1978e-07 | -3.0506e-07 | 0.0041361 | 0.0041363 | 0.0041363 | 0.99591 | -0.078337 | 0.99582 | -0.080004 | 1.1363
58 | -0.00040195 | -0.00010074 | 0.00040195 | 0.00010041 | 3.7323e-09 | -3.2997e-07 | 0.00061231 | 0.00061219 | 0.00061231 | 0.97679 | -0.4496 | 0.9768 | -0.4494 | 0.16822
59 | -0.0010823 | -0.00027093 | 0.0010823 | 0.00027091 | 1.5612e-09 | -1.8174e-08 | 0.0016487 | 0.0016487 | 0.0016487 | 0.9768 | -0.4494 | 0.9768 | -0.44937 | 0.45293
60 | -0.013537 | -0.0033928 | 0.013539 | 0.0033939 | 2.0875e-06 | 1.1688e-06 | 0.020518 | 0.020517 | 0.020518 | 0.98176 | -0.35147 | 0.98193 | -0.34823 | 5.6367
61 | -0.016925 | -0.0042424 | 0.016932 | 0.0042466 | 7.1417e-06 | 4.2043e-06 | 0.025648 | 0.025648 | 0.025648 | 0.98193 | -0.34823 | 0.98238 | -0.33938 | 7.0461
62 | -0.019201 | -0.0048155 | 0.019209 | 0.0048198 | 7.2816e-06 | 4.3695e-06 | 0.029086 | 0.029086 | 0.029086 | 0.98238 | -0.33938 | 0.98279 | -0.33142 | 7.9906
63 | -0.020627 | -0.0051753 | 0.020637 | 0.0051811 | 9.5089e-06 | 5.7561e-06 | 0.031233 | 0.031233 | 0.031233 | 0.98279 | -0.33142 | 0.98328 | -0.32176 | 8.5805
64 | -0.022591 | -0.0056708 | 0.022603 | 0.0056783 | 1.2368e-05 | 7.5576e-06 | 0.03419 | 0.03419 | 0.03419 | 0.98328 | -0.32176 | 0.98387 | -0.31029 | 9.3928
65 | -0.023513 | -0.0059059 | 0.023524 | 0.0059125 | 1.0736e-05 | 6.5833e-06 | 0.035567 | 0.035566 | 0.035567 | 0.98387 | -0.31029 | 0.98436 | -0.30073 | 9.771
66 | 0.00091044 | 0.00022757 | -0.00091042 | -0.00022787 | 1.7638e-08 | -3.0382e-07 | 0.0013767 | 0.0013769 | 0.0013769 | 0.98387 | -0.31029 | 0.98385 | -0.3107 | 0.37826
67 | 0.00041284 | 0.00010316 | -0.00041283 | -0.00010347 | 3.508e-09 | -3.0251e-07 | 0.00062428 | 0.00062439 | 0.00062439 | 0.98385 | -0.3107 | 0.98384 | -0.31087 | 0.17154
68 | 0.063269 | 0.015952 | -0.063224 | -0.015923 | 4.4149e-05 | 2.8086e-05 | 0.094861 | 0.094861 | 0.094861 | 0.99281 | -0.1379 | 0.99205 | -0.15249 | 26.0606
69 | -0.0044329 | -0.0011109 | 0.004433 | 0.0011109 | 6.4405e-08 | -8.7398e-09 | 0.0066557 | 0.0066557 | 0.0066557 | 0.99106 | -0.1716 | 0.99108 | -0.1713 | 1.8285
70 | 0.0044329 | 0.0011109 | -0.0044328 | -0.001111 | 1.7081e-07 | -2.3171e-08 | 0.0066557 | 0.0066558 | 0.0066558 | 0.99106 | -0.1716 | 0.99102 | -0.17241 | 1.8285
71 | 0.05304 | 0.013351 | -0.053032 | -0.013346 | 7.2505e-06 | 4.6011e-06 | 0.079655 | 0.079655 | 0.079655 | 0.99108 | -0.1713 | 0.99093 | -0.17416 | 21.8832
72 | -0.057472 | -0.014462 | 0.057524 | 0.014495 | 5.171e-05 | 3.2856e-05 | 0.086311 | 0.086311 | 0.086311 | 0.99108 | -0.1713 | 0.99205 | -0.15249 | 23.7117
73 | 0.0039849 | 0.00099851 | -0.0039845 | -0.00099862 | 3.422e-07 | -1.1438e-07 | 0.0059607 | 0.0059608 | 0.0059608 | 0.99476 | -0.10024 | 0.99467 | -0.10204 | 1.6376
74 | -0.025448 | -0.0063874 | 0.02545 | 0.0063884 | 1.6466e-06 | 1.0155e-06 | 0.038315 | 0.038315 | 0.038315 | 0.98839 | -0.22342 | 0.98846 | -0.22206 | 10.5262
75 | 0.025448 | 0.0063874 | -0.025431 | -0.0063767 | 1.7279e-05 | 1.0656e-05 | 0.038315 | 0.038315 | 0.038315 | 0.98839 | -0.22342 | 0.98765 | -0.23766 | 10.5262
76 | 0.010916 | 0.002738 | -0.010908 | -0.0027338 | 8.1405e-06 | 4.1805e-06 | 0.016434 | 0.016434 | 0.016434 | 0.98846 | -0.22206 | 0.98765 | -0.23771 | 4.5149
77 | -0.050616 | -0.012696 | 0.050731 | 0.01277 | 0.00011587 | 7.3471e-05 | 0.0762 | 0.0762 | 0.0762 | 0.98846 | -0.22206 | 0.99093 | -0.17416 | 20.9341
78 | 0.01425 | 0.00357 | -0.014247 | -0.0035683 | 2.9443e-06 | 1.6657e-06 | 0.021451 | 0.021451 | 0.021451 | 0.98846 | -0.22206 | 0.98823 | -0.2264 | 5.8931
79 | 0.012757 | 0.0031981 | -0.012754 | -0.0031963 | 3.1728e-06 | 1.7376e-06 | 0.01922 | 0.01922 | 0.01922 | 0.98765 | -0.23766 | 0.98739 | -0.24288 | 5.2804
80 | 0.012674 | 0.0031786 | -0.012663 | -0.0031728 | 1.0718e-05 | 5.8575e-06 | 0.019095 | 0.019095 | 0.019095 | 0.98765 | -0.23766 | 0.98674 | -0.25542 | 5.246
81 | 0.0066859 | 0.0016719 | -0.0066833 | -0.0016711 | 2.6264e-06 | 7.9931e-07 | 0.010076 | 0.010077 | 0.010077 | 0.98721 | -0.24632 | 0.98679 | -0.25458 | 2.7683
82 | -0.0074112 | -0.0018537 | 0.0074123 | 0.0018541 | 1.0659e-06 | 3.9084e-07 | 0.01117 | 0.011169 | 0.01117 | 0.98721 | -0.24632 | 0.98737 | -0.2433 | 3.0686
83 | 0.0058905 | 0.0014724 | -0.00589 | -0.0014723 | 4.9062e-07 | 1.0212e-07 | 0.0088812 | 0.0088812 | 0.0088812 | 0.98679 | -0.25458 | 0.9867 | -0.25634 | 2.4399
84 | -0.0080239 | -0.0020073 | 0.008028 | 0.002009 | 4.0798e-06 | 1.6587e-06 | 0.012091 | 0.012091 | 0.012091 | 0.98737 | -0.2433 | 0.98791 | -0.23262 | 3.3218
85 | 0.0052737 | 0.0013178 | -0.0052733 | -0.0013178 | 3.9291e-07 | 3.9832e-08 | 0.0079517 | 0.0079518 | 0.0079518 | 0.9867 | -0.25634 | 0.98662 | -0.2579 | 2.1846
86 | -0.0099889 | -0.0025005 | 0.0099909 | 0.0025014 | 2.009e-06 | 9.8264e-07 | 0.015044 | 0.015044 | 0.015044 | 0.98791 | -0.23262 | 0.98813 | -0.22839 | 4.1331
87 | 0.0032976 | 0.00082265 | -0.003297 | -0.00082315 | 6.816e-07 | -5.024e-07 | 0.0049721 | 0.0049725 | 0.0049725 | 0.98662 | -0.2579 | 0.9864 | -0.26226 | 1.3661
88 | -0.010679 | -0.002674 | 0.01068 | 0.0026745 | 1.0124e-06 | 5.1421e-07 | 0.016081 | 0.016081 | 0.016081 | 0.98813 | -0.22839 | 0.98823 | -0.2264 | 4.4179
89 | 0.0030786 | 0.00076842 | -0.0030785 | -0.0007685 | 7.8789e-08 | -7.3976e-08 | 0.0046431 | 0.0046431 | 0.0046431 | 0.9864 | -0.26226 | 0.98637 | -0.2628 | 1.2756
90 | -0.01095 | -0.0027423 | 0.010954 | 0.0027446 | 4.4607e-06 | 2.2983e-06 | 0.016519 | 0.016519 | 0.016519 | 0.9863 | -0.26397 | 0.98674 | -0.25542 | 4.5382
91 | 0.0070068 | 0.0017541 | -0.0070012 | -0.0017522 | 5.5726e-06 | 1.8707e-06 | 0.01057 | 0.010571 | 0.010571 | 0.9863 | -0.26397 | 0.98545 | -0.28069 | 2.9041
92 | 0.0042304 | 0.0010601 | -0.0042301 | -0.0010602 | 3.8087e-07 | -7.3319e-08 | 0.0063879 | 0.006388 | 0.006388 | 0.98545 | -0.28069 | 0.98535 | -0.28258 | 1.7549
93 | 0.00063568 | 0.00015701 | -0.00063562 | -0.0001593 | 6.3176e-08 | -2.2908e-06 | 0.00095905 | 0.00095988 | 0.00095988 | 0.98545 | -0.28069 | 0.98534 | -0.28279 | 0.2637
94 | 0.0095161 | 0.0023848 | -0.0095158 | -0.0023847 | 2.9585e-07 | 1.4028e-07 | 0.014341 | 0.014341 | 0.014341 | 0.98739 | -0.24288 | 0.98735 | -0.24354 | 3.9398
95 | 0.003616 | 0.00090609 | -0.0036158 | -0.00090621 | 2.2727e-07 | -1.1552e-07 | 0.0054496 | 0.0054497 | 0.0054497 | 0.98735 | -0.24354 | 0.98729 | -0.24486 | 1.4972
96 | -0.00048328 | -0.00012112 | 0.0004833 | 0.00012007 | 1.6569e-08 | -1.0497e-06 | 0.00072929 | 0.00072892 | 0.00072929 | 0.98607 | -0.26864 | 0.98611 | -0.26792 | 0.20035
97 | -0.0012402 | -0.00030976 | 0.0012402 | 0.00030932 | 4.7804e-08 | -4.3403e-07 | 0.001871 | 0.0018708 | 0.001871 | 0.98611 | -0.26792 | 0.98615 | -0.26711 | 0.51401
98 | -0.0018058 | -0.00045108 | 0.001806 | 0.00045015 | 2.3521e-07 | -9.2804e-07 | 0.0027243 | 0.0027239 | 0.0027243 | 0.98615 | -0.26711 | 0.98629 | -0.26437 | 0.74843
99 | -0.001806 | -0.00045015 | 0.001806 | 0.00045011 | 9.3319e-09 | -3.6831e-08 | 0.0027239 | 0.0027239 | 0.0027239 | 0.98629 | -0.26437 | 0.98629 | -0.26426 | 0.74832
100 | -0.001806 | -0.00045011 | 0.0018062 | 0.00044962 | 1.2522e-07 | -4.9433e-07 | 0.0027239 | 0.0027237 | 0.0027239 | 0.98629 | -0.26426 | 0.98637 | -0.2628 | 0.74832
101 | -0.0036162 | -0.00090591 | 0.0036164 | 0.00090581 | 1.94e-07 | -9.2703e-08 | 0.0054866 | 0.0054866 | 0.0054866 | 0.98072 | -0.37208 | 0.98078 | -0.37095 | 1.5073
102 | 0.0028136 | 0.00070474 | -0.0028133 | -0.00070507 | 2.7899e-07 | -3.3654e-07 | 0.0042688 | 0.004269 | 0.004269 | 0.98072 | -0.37208 | 0.98061 | -0.37416 | 1.1728
103 | -0.0047027 | -0.0011781 | 0.0047035 | 0.0011781 | 7.5425e-07 | -1.6015e-08 | 0.0071347 | 0.0071345 | 0.0071347 | 0.98078 | -0.37095 | 0.98095 | -0.36758 | 1.9601
104 | -0.0062617 | -0.0015686 | 0.0062624 | 0.0015688 | 6.7963e-07 | 1.8132e-07 | 0.0094982 | 0.0094981 | 0.0094982 | 0.98095 | -0.36758 | 0.98107 | -0.3653 | 2.6094
105 | -0.007369 | -0.0018461 | 0.0073701 | 0.0018465 | 1.0952e-06 | 4.0565e-07 | 0.011177 | 0.011176 | 0.011177 | 0.98107 | -0.3653 | 0.98122 | -0.36218 | 3.0705
106 | 0.011063 | 0.0027573 | -0.011061 | -0.0027562 | 2.2183e-06 | 1.1541e-06 | 0.016771 | 0.016771 | 0.016771 | 0.98122 | -0.36218 | 0.98101 | -0.36641 | 4.6075
107 | 0.0095073 | 0.0023668 | -0.009496 | -0.0023614 | 1.1297e-05 | 5.4023e-06 | 0.014415 | 0.014416 | 0.014416 | 0.98101 | -0.36641 | 0.97974 | -0.39151 | 3.9604
108 | 0.00020187 | 5.0149e-05 | -0.00020186 | -5.0592e-05 | 1.257e-09 | -4.425e-07 | 0.00030746 | 0.00030762 | 0.00030762 | 0.97646 | -0.45653 | 0.97646 | -0.45666 | 0.084511
109 | -0.00065345 | -0.00016333 | 0.00065348 | 0.00016262 | 2.1403e-08 | -7.0673e-07 | 0.00099563 | 0.00099537 | 0.00099563 | 0.97646 | -0.45653 | 0.9765 | -0.45584 | 0.27352
110 | 0.00026749 | 6.6739e-05 | -0.00026748 | -6.7038e-05 | 1.4954e-09 | -2.9938e-07 | 0.0004075 | 0.0004076 | 0.0004076 | 0.9765 | -0.45584 | 0.97649 | -0.45595 | 0.11198
111 | -0.00092096 | -0.00022936 | 0.00092102 | 0.00022841 | 5.8065e-08 | -9.4739e-07 | 0.0014029 | 0.0014025 | 0.0014029 | 0.9765 | -0.45584 | 0.97656 | -0.4545 | 0.3854
112 | -0.00092102 | -0.00022841 | 0.00092102 | 0.00022841 | 4.0574e-10 | -6.6217e-09 | 0.0014025 | 0.0014025 | 0.0014025 | 0.97656 | -0.4545 | 0.97656 | -0.45449 | 0.38531
113 | -0.0010255 | -0.00025459 | 0.0010258 | 0.0002506 | 3.056e-07 | -3.9904e-06 | 0.0015617 | 0.0015602 | 0.0015617 | 0.97656 | -0.45449 | 0.97688 | -0.44816 | 0.42903
114 | -0.0010258 | -0.0002506 | 0.0010259 | 0.00024941 | 9.0795e-08 | -1.1876e-06 | 0.0015602 | 0.0015598 | 0.0015602 | 0.97688 | -0.44816 | 0.97698 | -0.44626 | 0.42863
115 | -0.0013438 | -0.000328 | 0.0013438 | 0.000328 | 1.8965e-10 | -1.3898e-09 | 0.0020434 | 0.0020434 | 0.0020434 | 0.97706 | -0.44456 | 0.97706 | -0.44455 | 0.56138
116 | 0.001026 | 0.00024835 | -0.0010259 | -0.00024941 | 8.1254e-08 | -1.0636e-06 | 0.0015594 | 0.0015598 | 0.0015598 | 0.97706 | -0.44456 | 0.97698 | -0.44626 | 0.42851
117 | -0.0031798 | -0.00078814 | 0.0031818 | 0.00078654 | 2.0253e-06 | -1.5945e-06 | 0.0048395 | 0.0048384 | 0.0048395 | 0.97706 | -0.44455 | 0.97774 | -0.43106 | 1.3295
118 | -0.0035672 | -0.00088314 | 0.0035705 | 0.0008815 | 3.2861e-06 | -1.6358e-06 | 0.005425 | 0.0054237 | 0.005425 | 0.97774 | -0.43106 | 0.97872 | -0.41154 | 1.4904
119 | 0.00026913 | 6.545e-05 | -0.00026912 | -6.7448e-05 | 9.9979e-09 | -1.9982e-06 | 0.00040847 | 0.00040918 | 0.00040918 | 0.97872 | -0.41154 | 0.97868 | -0.41232 | 0.11241
120 | 0.0051873 | 0.0012951 | -0.0051839 | -0.0012948 | 3.4417e-06 | 3.4902e-07 | 0.0078849 | 0.0078855 | 0.0078855 | 0.97872 | -0.41154 | 0.97801 | -0.42551 | 2.1664
121 | -0.009027 | -0.0022421 | 0.0090341 | 0.0022454 | 7.1111e-06 | 3.2834e-06 | 0.013717 | 0.013717 | 0.013717 | 0.97872 | -0.41154 | 0.97957 | -0.3949 | 3.7684
122 | 0.0090355 | 0.002246 | -0.0090341 | -0.0022454 | 1.4504e-06 | 6.6944e-07 | 0.013716 | 0.013717 | 0.013717 | 0.97974 | -0.39151 | 0.97957 | -0.3949 | 3.7683
123 | 0.0015461 | 0.00038676 | -0.001546 | -0.00038705 | 5.3669e-08 | -2.9509e-07 | 0.0023434 | 0.0023435 | 0.0023435 | 0.98164 | -0.35408 | 0.9816 | -0.35481 | 0.64382
124 | 0.0051839 | 0.0012948 | -0.0051826 | -0.0012947 | 1.2691e-06 | 1.2945e-07 | 0.0078855 | 0.0078858 | 0.0078858 | 0.97801 | -0.42551 | 0.97775 | -0.43066 | 2.1664
125 | 0.00080194 | 0.00020056 | -0.00080192 | -0.00020098 | 1.877e-08 | -4.1617e-07 | 0.0012155 | 0.0012157 | 0.0012157 | 0.9816 | -0.35481 | 0.98157 | -0.3553 | 0.33398
126 | -0.0041212 | -0.0010289 | 0.0041217 | 0.0010288 | 5.6652e-07 | -1.1912e-07 | 0.0062714 | 0.0062713 | 0.0062714 | 0.97761 | -0.43355 | 0.97775 | -0.43066 | 1.7229
127 | 0.0035771 | 0.00089255 | -0.003576 | -0.00089309 | 1.1116e-06 | -5.424e-07 | 0.0054434 | 0.0054438 | 0.0054438 | 0.97761 | -0.43355 | 0.97728 | -0.4401 | 1.4956
128 | 0.000989 | 0.00024776 | -0.00098899 | -0.00024786 | 7.3673e-09 | -1.0384e-07 | 0.0015058 | 0.0015059 | 0.0015059 | 0.97728 | -0.4401 | 0.97727 | -0.44025 | 0.4137
129 | 0.002587 | 0.00064533 | -0.0025868 | -0.00064576 | 2.8333e-07 | -4.2903e-07 | 0.003938 | 0.0039382 | 0.0039382 | 0.97728 | -0.4401 | 0.97716 | -0.4424 | 1.0819
130 | 0.0023292 | 0.00058122 | -0.0023291 | -0.00058145 | 1.1717e-07 | -2.3625e-07 | 0.003546 | 0.0035462 | 0.0035462 | 0.97716 | -0.4424 | 0.9771 | -0.44346 | 0.97422
131 | 0.0020891 | 0.00052129 | -0.0020887 | -0.00052236 | 4.0041e-07 | -1.0653e-06 | 0.0031806 | 0.0031811 | 0.0031811 | 0.9771 | -0.44346 | 0.9769 | -0.4475 | 0.87392
132 | 0.0015745 | 0.00039348 | -0.0015743 | -0.00039421 | 1.4065e-07 | -7.2653e-07 | 0.0023978 | 0.0023981 | 0.0023981 | 0.9769 | -0.4475 | 0.9768 | -0.44937 | 0.65882
133 | 0.011503 | 0.00289 | -0.011496 | -0.002886 | 7.5208e-06 | 3.9703e-06 | 0.017388 | 0.017388 | 0.017388 | 0.98458 | -0.29657 | 0.98388 | -0.31027 | 4.777
134 | 0.00064241 | 0.00016073 | -0.0006424 | -0.000161 | 7.7494e-09 | -2.7309e-07 | 0.00097148 | 0.00097158 | 0.00097158 | 0.98388 | -0.31027 | 0.98387 | -0.31053 | 0.26692
135 | 0.010854 | 0.0027253 | -0.010831 | -0.0027136 | 2.2798e-05 | 1.1733e-05 | 0.016417 | 0.016418 | 0.016418 | 0.98388 | -0.31027 | 0.98162 | -0.35439 | 4.5104
136 | -0.0037628 | -0.00094304 | 0.0037636 | 0.00094272 | 8.4217e-07 | -3.2793e-07 | 0.0057137 | 0.0057134 | 0.0057137 | 0.97994 | -0.38732 | 0.98018 | -0.38262 | 1.5697
137 | -0.0037636 | -0.00094272 | 0.003766 | 0.00094177 | 2.4119e-06 | -9.4205e-07 | 0.0057134 | 0.0057125 | 0.0057134 | 0.98018 | -0.38262 | 0.98087 | -0.36916 | 1.5696
138 | 0.0058349 | 0.001462 | -0.0058338 | -0.0014617 | 1.1363e-06 | 2.3919e-07 | 0.0088517 | 0.0088518 | 0.0088518 | 0.98087 | -0.36916 | 0.98066 | -0.37325 | 2.4318
139 | -0.009601 | -0.0024037 | 0.0096066 | 0.0024064 | 5.5832e-06 | 2.6867e-06 | 0.014564 | 0.014564 | 0.014564 | 0.98087 | -0.36916 | 0.98149 | -0.35695 | 4.0011
140 | 0.0058338 | 0.0014617 | -0.00583 | -0.0014609 | 3.8456e-06 | 8.1122e-07 | 0.0088518 | 0.0088524 | 0.0088524 | 0.98066 | -0.37325 | 0.97996 | -0.38709 | 2.432
141 | -0.010498 | -0.0026298 | 0.010499 | 0.0026304 | 1.2823e-06 | 6.5001e-07 | 0.015915 | 0.015915 | 0.015915 | 0.98149 | -0.35695 | 0.98162 | -0.35439 | 4.3723
142 | 0.00065561 | 0.0001641 | -0.00065561 | -0.00016431 | 6.3887e-09 | -2.125e-07 | 0.00099544 | 0.00099552 | 0.00099552 | 0.97996 | -0.38709 | 0.97995 | -0.3873 | 0.27349
143 | 0.00058568 | 0.00014676 | -0.00058568 | -0.00014678 | 5.0925e-10 | -2.1234e-08 | 0.00089003 | 0.00089004 | 0.00089004 | 0.97917 | -0.40242 | 0.97917 | -0.40243 | 0.24452

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28974 | 0.073213

## res_load
| p_mw | q_mvar
0 | 0.0090329 | 0.0022638
1 | 0.0023315 | 0.00058434
2 | 0.0016885 | 0.00042317
3 | 0.01996 | 0.0050023
4 | 0.0025261 | 0.0006331
5 | 0.0062761 | 0.0015729
6 | 0.0036734 | 0.00092064
7 | 0.0024164 | 0.00060561
8 | 0.006454 | 0.0016175
9 | 0.030127 | 0.0075506
10 | 0.0020447 | 0.00051244
11 | 0.002499 | 0.0006263
12 | 0.022703 | 0.0056899
13 | 0.0068996 | 0.0017292
14 | 0.00061207 | 0.0001534
15 | 0.0010996 | 0.00027559
16 | 0.0085704 | 0.0021479
17 | 0.00048173 | 0.00012073
18 | 0.0016019 | 0.00040147
19 | 0.0010009 | 0.00025086
20 | 0.00087129 | 0.00021837
21 | 0.00086818 | 0.00021759
22 | 0.0016114 | 0.00040384
23 | 0.00076126 | 0.00019079
24 | 0.0014532 | 0.00036421
25 | 0.0037439 | 0.0009383
26 | 0.0027681 | 0.00069376
27 | 0.00040195 | 0.00010074
28 | 0.00068039 | 0.00017052
29 | 0.015933 | 0.0039933
30 | 0.0013392 | 0.00033563
31 | 0.0033855 | 0.0008485
32 | 0.0022697 | 0.00056883
33 | 0.0014184 | 0.00035549
34 | 0.0019539 | 0.0004897
35 | 0.00076048 | 0.0001906
36 | 0.00049758 | 0.00012471
37 | 0.00041283 | 0.00010347
38 | 0.0076652 | 0.0019211
39 | 0.0024328 | 0.00060972
40 | 0.0044328 | 0.001111
41 | 0.0057002 | 0.0014286
42 | 0.0023009 | 0.00057665
43 | 0.0039845 | 0.00099862
44 | 0.00072536 | 0.00018179
45 | 0.00079274 | 0.00019868
46 | 0.0006116 | 0.00015328
47 | 0.00061633 | 0.00015447
48 | 0.0019609 | 0.00049146
49 | 0.0019757 | 0.00049515
50 | 0.00068847 | 0.00017255
51 | 0.00021838 | 5.473e-05
52 | 0.0035664 | 0.00089382
53 | 0.003943 | 0.00098822
54 | 0.0017086 | 0.00042821
55 | 0.0021351 | 0.00053511
56 | 0.0042301 | 0.0010602
57 | 0.00063562 | 0.0001593
58 | 0.0032379 | 0.00081149
59 | 0.0058997 | 0.0014786
60 | 0.00048328 | 0.00012112
61 | 0.00075685 | 0.00018969
62 | 0.0005656 | 0.00014175
63 | 0.010908 | 0.0027338
64 | 0.0012723 | 0.00031888
65 | 0.0036158 | 0.00090621
66 | 0.00080267 | 0.00020117
67 | 0.0010863 | 0.00027226
68 | 0.0028133 | 0.00070507
69 | 0.0015582 | 0.00039052
70 | 0.0011066 | 0.00027735
71 | 0.0015535 | 0.00038934
72 | 0.00045159 | 0.00011318
73 | 0.00020186 | 5.0592e-05
74 | 0.00026748 | 6.7038e-05
75 | 0.00010446 | 2.6181e-05
76 | 0.00031783 | 7.9655e-05
77 | 0.001836 | 0.00046014
78 | 0.00038543 | 9.6598e-05
79 | 0.00046045 | 0.0001154
80 | 0.00057209 | 0.00014338
81 | 0.00026912 | 6.7448e-05
82 | 0.00074411 | 0.00018649
83 | 0.00054404 | 0.00013635
84 | 0.0010609 | 0.00026588
85 | 0.00098899 | 0.00024786
86 | 0.00025752 | 6.4541e-05
87 | 0.00024005 | 6.0162e-05
88 | 0.00051421 | 0.00012887
89 | 0.00080192 | 0.00020098
90 | 0.00049197 | 0.0001233
91 | 0.0023642 | 0.00059252
92 | 0.0037628 | 0.00094304
93 | 0.00089127 | 0.00022337
94 | 0.0051743 | 0.0012968
95 | 0.00033161 | 8.3109e-05
96 | 0.0012267 | 0.00030744
97 | 0.00058568 | 0.00014678
98 | 0.00065561 | 0.00016431
99 | 0.0006424 | 0.000161

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1