## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1301-16_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1301-16_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1301-16_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1301-16_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1301-16_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1301-16_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1301-16_0_6_node_105 | 0.4 | n |  | TRUE
7 | bus_LV_1301-16_0_6_node_103 | 0.4 | n |  | TRUE
8 | bus_LV_1301-16_0_6_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_1301-16_0_6_node_78 | 0.4 | n |  | TRUE
10 | bus_LV_1301-16_0_6_node_109 | 0.4 | n |  | TRUE
11 | bus_LV_1301-16_0_6_node_107 | 0.4 | n |  | TRUE
12 | bus_LV_1301-16_0_6_node_101 | 0.4 | n |  | TRUE
13 | bus_LV_1301-16_0_6_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_1301-16_0_6_node_79 | 0.4 | n |  | TRUE
15 | bus_LV_1301-16_0_6_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_1301-16_0_6_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1301-16_0_6_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_1301-16_0_6_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1301-16_0_6_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1301-16_0_6_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1301-16_0_6_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_1301-16_0_6_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_1301-16_0_6_node_91 | 0.4 | n |  | TRUE
24 | bus_LV_1301-16_0_6_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_1301-16_0_6_node_34 | 0.4 | n |  | TRUE
26 | bus_LV_1301-16_0_6_node_92 | 0.4 | n |  | TRUE
27 | bus_LV_1301-16_0_6_node_76 | 0.4 | n |  | TRUE
28 | bus_LV_1301-16_0_6_node_77 | 0.4 | n |  | TRUE
29 | bus_LV_1301-16_0_6_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_1301-16_0_6_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_1301-16_0_6_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_1301-16_0_6_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_1301-16_0_6_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_1301-16_0_6_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_1301-16_0_6_node_50 | 0.4 | n |  | TRUE
36 | bus_LV_1301-16_0_6_node_47 | 0.4 | n |  | TRUE
37 | bus_LV_1301-16_0_6_node_18 | 0.4 | n |  | TRUE
38 | bus_LV_1301-16_0_6_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_1301-16_0_6_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_1301-16_0_6_node_57 | 0.4 | n |  | TRUE
41 | bus_LV_1301-16_0_6_node_95 | 0.4 | n |  | TRUE
42 | bus_LV_1301-16_0_6_node_48 | 0.4 | n |  | TRUE
43 | bus_LV_1301-16_0_6_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_1301-16_0_6_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_1301-16_0_6_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_1301-16_0_6_node_21 | 0.4 | n |  | TRUE
47 | bus_LV_1301-16_0_6_node_22 | 0.4 | n |  | TRUE
48 | bus_LV_1301-16_0_6_node_97 | 0.4 | n |  | TRUE
49 | bus_LV_1301-16_0_6_node_23 | 0.4 | n |  | TRUE
50 | bus_LV_1301-16_0_6_node_24 | 0.4 | n |  | TRUE
51 | bus_LV_1301-16_0_6_node_93 | 0.4 | n |  | TRUE
52 | bus_LV_1301-16_0_6_node_94 | 0.4 | n |  | TRUE
53 | bus_LV_1301-16_0_6_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_1301-16_0_6_node_111 | 0.4 | n |  | TRUE
55 | bus_LV_1301-16_0_6_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_1301-16_0_6_node_31 | 0.4 | n |  | TRUE
57 | bus_LV_1301-16_0_6_node_58 | 0.4 | n |  | TRUE
58 | bus_LV_1301-16_0_6_node_30 | 0.4 | n |  | TRUE
59 | bus_LV_1301-16_0_6_node_72 | 0.4 | n |  | TRUE
60 | bus_LV_1301-16_0_6_node_59 | 0.4 | n |  | TRUE
61 | bus_LV_1301-16_0_6_node_38 | 0.4 | n |  | TRUE
62 | bus_LV_1301-16_0_6_node_39 | 0.4 | n |  | TRUE
63 | bus_LV_1301-16_0_6_node_40 | 0.4 | n |  | TRUE
64 | bus_LV_1301-16_0_6_node_110 | 0.4 | n |  | TRUE
65 | bus_LV_1301-16_0_6_node_41 | 0.4 | n |  | TRUE
66 | bus_LV_1301-16_0_6_node_106 | 0.4 | n |  | TRUE
67 | bus_LV_1301-16_0_6_node_42 | 0.4 | n |  | TRUE
68 | bus_LV_1301-16_0_6_node_43 | 0.4 | n |  | TRUE
69 | bus_LV_1301-16_0_6_node_44 | 0.4 | n |  | TRUE
70 | bus_LV_1301-16_0_6_node_45 | 0.4 | n |  | TRUE
71 | bus_LV_1301-16_0_6_node_46 | 0.4 | n |  | TRUE
72 | bus_LV_1301-16_0_6_node_61 | 0.4 | n |  | TRUE
73 | bus_LV_1301-16_0_6_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_1301-16_0_6_node_49 | 0.4 | n |  | TRUE
75 | bus_LV_1301-16_0_6_node_65 | 0.4 | n |  | TRUE
76 | bus_LV_1301-16_0_6_node_66 | 0.4 | n |  | TRUE
77 | bus_LV_1301-16_0_6_node_96 | 0.4 | n |  | TRUE
78 | bus_LV_1301-16_0_6_node_51 | 0.4 | n |  | TRUE
79 | bus_LV_1301-16_0_6_node_52 | 0.4 | n |  | TRUE
80 | bus_LV_1301-16_0_6_node_53 | 0.4 | n |  | TRUE
81 | bus_LV_1301-16_0_6_node_54 | 0.4 | n |  | TRUE
82 | bus_LV_1301-16_0_6_node_55 | 0.4 | n |  | TRUE
83 | bus_LV_1301-16_0_6_node_56 | 0.4 | n |  | TRUE
84 | bus_LV_1301-16_0_6_node_63 | 0.4 | n |  | TRUE
85 | bus_LV_1301-16_0_6_node_71 | 0.4 | n |  | TRUE
86 | bus_LV_1301-16_0_6_node_64 | 0.4 | n |  | TRUE
87 | bus_LV_1301-16_0_6_node_141 | 0.4 | n |  | TRUE
88 | bus_LV_1301-16_0_6_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_1301-16_0_6_node_62 | 0.4 | n |  | TRUE
90 | bus_LV_1301-16_0_6_node_69 | 0.4 | n |  | TRUE
91 | bus_LV_1301-16_0_6_node_70 | 0.4 | n |  | TRUE
92 | bus_LV_1301-16_0_6_node_67 | 0.4 | n |  | TRUE
93 | bus_LV_1301-16_0_6_node_68 | 0.4 | n |  | TRUE
94 | bus_LV_1301-16_0_6_node_74 | 0.4 | n |  | TRUE
95 | bus_LV_1301-16_0_6_node_75 | 0.4 | n |  | TRUE
96 | bus_LV_1301-16_0_6_node_140 | 0.4 | n |  | TRUE
97 | bus_LV_1301-16_0_6_node_138 | 0.4 | n |  | TRUE
98 | bus_LV_1301-16_0_6_node_139 | 0.4 | n |  | TRUE
99 | bus_LV_1301-16_0_6_node_81 | 0.4 | n |  | TRUE
100 | bus_LV_1301-16_0_6_node_82 | 0.4 | n |  | TRUE
101 | bus_LV_1301-16_0_6_node_80 | 0.4 | n |  | TRUE
102 | bus_LV_1301-16_0_6_node_129 | 0.4 | n |  | TRUE
103 | bus_LV_1301-16_0_6_node_128 | 0.4 | n |  | TRUE
104 | bus_LV_1301-16_0_6_node_83 | 0.4 | n |  | TRUE
105 | bus_LV_1301-16_0_6_node_84 | 0.4 | n |  | TRUE
106 | bus_LV_1301-16_0_6_node_85 | 0.4 | n |  | TRUE
107 | bus_LV_1301-16_0_6_node_89 | 0.4 | n |  | TRUE
108 | bus_LV_1301-16_0_6_node_87 | 0.4 | n |  | TRUE
109 | bus_LV_1301-16_0_6_node_86 | 0.4 | n |  | TRUE
110 | bus_LV_1301-16_0_6_node_88 | 0.4 | n |  | TRUE
111 | bus_LV_1301-16_0_6_node_90 | 0.4 | n |  | TRUE
112 | bus_LV_1301-16_0_6_node_99 | 0.4 | n |  | TRUE
113 | bus_LV_1301-16_0_6_node_98 | 0.4 | n |  | TRUE
114 | bus_LV_1301-16_0_6_node_100 | 0.4 | n |  | TRUE
115 | bus_LV_1301-16_0_6_node_136 | 0.4 | n |  | TRUE
116 | bus_LV_1301-16_0_6_node_116 | 0.4 | n |  | TRUE
117 | bus_LV_1301-16_0_6_node_102 | 0.4 | n |  | TRUE
118 | bus_LV_1301-16_0_6_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_1301-16_0_6_node_108 | 0.4 | n |  | TRUE
120 | bus_LV_1301-16_0_6_node_112 | 0.4 | n |  | TRUE
121 | bus_LV_1301-16_0_6_node_113 | 0.4 | n |  | TRUE
122 | bus_LV_1301-16_0_6_node_114 | 0.4 | n |  | TRUE
123 | bus_LV_1301-16_0_6_node_115 | 0.4 | n |  | TRUE
124 | bus_LV_1301-16_0_6_node_126 | 0.4 | n |  | TRUE
125 | bus_LV_1301-16_0_6_node_127 | 0.4 | n |  | TRUE
126 | bus_LV_1301-16_0_6_node_117 | 0.4 | n |  | TRUE
127 | bus_LV_1301-16_0_6_node_118 | 0.4 | n |  | TRUE
128 | bus_LV_1301-16_0_6_node_119 | 0.4 | n |  | TRUE
129 | bus_LV_1301-16_0_6_node_120 | 0.4 | n |  | TRUE
130 | bus_LV_1301-16_0_6_node_121 | 0.4 | n |  | TRUE
131 | bus_LV_1301-16_0_6_node_124 | 0.4 | n |  | TRUE
132 | bus_LV_1301-16_0_6_node_137 | 0.4 | n |  | TRUE
133 | bus_LV_1301-16_0_6_node_122 | 0.4 | n |  | TRUE
134 | bus_LV_1301-16_0_6_node_123 | 0.4 | n |  | TRUE
135 | bus_LV_1301-16_0_6_node_125 | 0.4 | n |  | TRUE
136 | bus_LV_1301-16_0_6_node_133 | 0.4 | n |  | TRUE
137 | bus_LV_1301-16_0_6_node_134 | 0.4 | n |  | TRUE
138 | bus_LV_1301-16_0_6_node_132 | 0.4 | n |  | TRUE
139 | bus_LV_1301-16_0_6_node_130 | 0.4 | n |  | TRUE
140 | bus_LV_1301-16_0_6_node_131 | 0.4 | n |  | TRUE
141 | bus_LV_1301-16_0_6_node_135 | 0.4 | n |  | TRUE
142 | bus_MV_17_0_node_20 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1301-16_0_6_load_0 | 0 | 0.0005966 | 0.00014952 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1301-16_0_6_load_1 | 1 | 0.00085913 | 0.00021532 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1301-16_0_6_load_4 | 4 | 0.0022 | 0.00055137 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1301-16_0_6_load_5 | 5 | 0.0037835 | 0.00094824 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1301-16_0_6_load_12 | 8 | 0.0020636 | 0.00051719 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1301-16_0_6_load_78 | 9 | 0.0027655 | 0.0006931 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1301-16_0_6_load_109 | 10 | 0.00030492 | 7.6419e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1301-16_0_6_load_107 | 11 | 0.0011752 | 0.00029453 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1301-16_0_6_load_101 | 12 | 0.00075026 | 0.00018803 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1301-16_0_6_load_13 | 13 | 0.0030072 | 0.00075368 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1301-16_0_6_load_79 | 14 | 0.0029928 | 0.00075008 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1301-16_0_6_load_6 | 15 | 0.0096049 | 0.0024072 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1301-16_0_6_load_7 | 16 | 0.0054642 | 0.0013695 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1301-16_0_6_load_9 | 18 | 0.0028196 | 0.00070665 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1301-16_0_6_load_10 | 19 | 0.0029691 | 0.00074413 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1301-16_0_6_load_11 | 20 | 0.002808 | 0.00070375 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1301-16_0_6_load_27 | 21 | 0.0037172 | 0.00093163 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1301-16_0_6_load_33 | 22 | 0.0045816 | 0.0011482 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1301-16_0_6_load_91 | 23 | 0.0036557 | 0.00091621 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1301-16_0_6_load_26 | 24 | 0.0026698 | 0.0006691 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1301-16_0_6_load_34 | 25 | 0.0031736 | 0.00079538 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1301-16_0_6_load_92 | 26 | 0.0044272 | 0.0011096 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1301-16_0_6_load_76 | 27 | 0.0034591 | 0.00086693 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1301-16_0_6_load_77 | 28 | 0.00095115 | 0.00023838 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1301-16_0_6_load_14 | 29 | 0.005758 | 0.0014431 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1301-16_0_6_load_20 | 34 | 0.0019194 | 0.00048105 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1301-16_0_6_load_50 | 35 | 0.0036664 | 0.00091889 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1301-16_0_6_load_47 | 36 | 0.0038631 | 0.00096818 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1301-16_0_6_load_18 | 37 | 0.0018754 | 0.00047002 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1301-16_0_6_load_28 | 38 | 0.0017233 | 0.0004319 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1301-16_0_6_load_25 | 39 | 0.003041 | 0.00076214 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1301-16_0_6_load_57 | 40 | 0.0013431 | 0.00033662 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1301-16_0_6_load_95 | 41 | 0.0024966 | 0.00062571 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1301-16_0_6_load_48 | 42 | 0.0028752 | 0.0007206 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1301-16_0_6_load_35 | 45 | 0.0023306 | 0.00058411 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1301-16_0_6_load_21 | 46 | 0.00050961 | 0.00012772 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1301-16_0_6_load_97 | 48 | 0.00065766 | 0.00016483 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1301-16_0_6_load_23 | 49 | 0.0018409 | 0.00046137 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1301-16_0_6_load_93 | 51 | 0.0011928 | 0.00029895 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1301-16_0_6_load_94 | 52 | 0.00051733 | 0.00012966 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1301-16_0_6_load_111 | 54 | 0.00084303 | 0.00021128 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1301-16_0_6_load_31 | 56 | 0.0013936 | 0.00034926 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1301-16_0_6_load_30 | 58 | 0.0028505 | 0.00071441 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1301-16_0_6_load_72 | 59 | 0.0028684 | 0.00071889 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1301-16_0_6_load_59 | 60 | 0.0033737 | 0.00084552 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1301-16_0_6_load_38 | 61 | 0.0011291 | 0.00028297 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1301-16_0_6_load_39 | 62 | 0.0002497 | 6.258e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1301-16_0_6_load_40 | 63 | 0.00038411 | 9.6266e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1301-16_0_6_load_110 | 64 | 0.00039706 | 9.9513e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1301-16_0_6_load_41 | 65 | 0.00046151 | 0.00011566 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1301-16_0_6_load_106 | 66 | 0.00044244 | 0.00011089 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1301-16_0_6_load_42 | 67 | 0.0018641 | 0.00046719 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1301-16_0_6_load_43 | 68 | 0.0040269 | 0.0010092 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1301-16_0_6_load_44 | 69 | 0.0020059 | 0.00050274 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1301-16_0_6_load_45 | 70 | 0.0013598 | 0.0003408 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1301-16_0_6_load_46 | 71 | 0.0035583 | 0.00089178 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1301-16_0_6_load_60 | 73 | 0.0013808 | 0.00034607 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1301-16_0_6_load_49 | 74 | 0.0056545 | 0.0014171 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1301-16_0_6_load_65 | 75 | 0.0024132 | 0.00060479 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1301-16_0_6_load_66 | 76 | 0.0067805 | 0.0016993 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1301-16_0_6_load_96 | 77 | 0.0029636 | 0.00074275 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1301-16_0_6_load_51 | 78 | 0.0023307 | 0.00058414 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1301-16_0_6_load_52 | 79 | 0.0024408 | 0.00061171 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1301-16_0_6_load_54 | 81 | 0.0018587 | 0.00046583 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1301-16_0_6_load_55 | 82 | 0.0022287 | 0.00055855 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1301-16_0_6_load_56 | 83 | 0.0035099 | 0.00087965 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1301-16_0_6_load_63 | 84 | 0.0021095 | 0.0005287 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1301-16_0_6_load_64 | 86 | 0.0067259 | 0.0016857 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1301-16_0_6_load_141 | 87 | 0.0021348 | 0.00053504 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1301-16_0_6_load_73 | 88 | 0.0028572 | 0.00071609 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1301-16_0_6_load_62 | 89 | 0.0048561 | 0.0012171 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1301-16_0_6_load_69 | 90 | 0.0016264 | 0.0004076 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1301-16_0_6_load_70 | 91 | 0.0075466 | 0.0018914 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1301-16_0_6_load_67 | 92 | 0.0036507 | 0.00091494 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1301-16_0_6_load_68 | 93 | 0.0042668 | 0.0010693 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1301-16_0_6_load_74 | 94 | 0.00020594 | 5.1615e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1301-16_0_6_load_139 | 98 | 6.7748e-05 | 1.6979e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1301-16_0_6_load_81 | 99 | 0.0020189 | 0.00050598 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1301-16_0_6_load_82 | 100 | 0.0024753 | 0.00062036 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1301-16_0_6_load_80 | 101 | 0.003117 | 0.0007812 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1301-16_0_6_load_129 | 102 | 0.0058142 | 0.0014572 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1301-16_0_6_load_128 | 103 | 0.0036171 | 0.00090653 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1301-16_0_6_load_83 | 104 | 0.0024632 | 0.00061734 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1301-16_0_6_load_84 | 105 | 0.0025058 | 0.00062803 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1301-16_0_6_load_85 | 106 | 0.0026097 | 0.00065405 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1301-16_0_6_load_89 | 107 | 0.0030132 | 0.00075518 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1301-16_0_6_load_87 | 108 | 0.0034822 | 0.00087272 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1301-16_0_6_load_86 | 109 | 0.0025116 | 0.00062946 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1301-16_0_6_load_88 | 110 | 0.0065868 | 0.0016508 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1301-16_0_6_load_90 | 111 | 0.0043363 | 0.0010868 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1301-16_0_6_load_99 | 112 | 0.0036118 | 0.0009052 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1301-16_0_6_load_100 | 114 | 0.0035811 | 0.00089751 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1301-16_0_6_load_136 | 115 | 0.0035561 | 0.00089125 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1301-16_0_6_load_116 | 116 | 0.0057451 | 0.0014399 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1301-16_0_6_load_102 | 117 | 0.00047049 | 0.00011792 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1301-16_0_6_load_104 | 118 | 0.00049388 | 0.00012378 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1301-16_0_6_load_108 | 119 | 0.00056303 | 0.00014111 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1301-16_0_6_load_112 | 120 | 0.0034322 | 0.00086019 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1301-16_0_6_load_113 | 121 | 0.004348 | 0.0010897 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1301-16_0_6_load_114 | 122 | 0.0019275 | 0.00048307 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1301-16_0_6_load_115 | 123 | 0.003827 | 0.00095915 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1301-16_0_6_load_126 | 124 | 0.003621 | 0.00090752 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1301-16_0_6_load_127 | 125 | 0.0029276 | 0.00073372 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1301-16_0_6_load_117 | 126 | 0.003279 | 0.00082179 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1301-16_0_6_load_118 | 127 | 0.0047911 | 0.0012008 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1301-16_0_6_load_119 | 128 | 0.0027101 | 0.00067921 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1301-16_0_6_load_120 | 129 | 0.0043129 | 0.0010809 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1301-16_0_6_load_121 | 130 | 0.0023011 | 0.00057671 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1301-16_0_6_load_124 | 131 | 0.0030743 | 0.00077048 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1301-16_0_6_load_137 | 132 | 0.0032228 | 0.00080771 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1301-16_0_6_load_122 | 133 | 0.0046952 | 0.0011767 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1301-16_0_6_load_123 | 134 | 0.0051016 | 0.0012786 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1301-16_0_6_load_125 | 135 | 0.0041444 | 0.0010387 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1301-16_0_6_load_134 | 137 | 0.0029479 | 0.0007388 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_1301-16_0_6_load_132 | 138 | 0.0050327 | 0.0012613 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_1301-16_0_6_load_130 | 139 | 0.0045198 | 0.0011328 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_1301-16_0_6_load_131 | 140 | 0.0031202 | 0.000782 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_1301-16_0_6_load_135 | 141 | 0.0047255 | 0.0011843 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 112 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1301-16_0_6_line_0 |  | 0 | 1 | 0.032918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1301-16_0_6_line_1 |  | 0 | 2 | 0.015902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1301-16_0_6_line_2 |  | 1 | 3 | 0.040443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1301-16_0_6_line_3 |  | 2 | 4 | 0.021498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1301-16_0_6_line_4 |  | 2 | 5 | 0.068163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1301-16_0_6_line_5 |  | 3 | 6 | 0.011214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1301-16_0_6_line_6 |  | 3 | 7 | 0.071273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1301-16_0_6_line_7 |  | 4 | 8 | 0.013135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1301-16_0_6_line_8 |  | 5 | 9 | 0.045786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1301-16_0_6_line_9 |  | 6 | 10 | 0.040076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1301-16_0_6_line_10 |  | 6 | 11 | 0.031712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1301-16_0_6_line_11 |  | 7 | 12 | 0.028173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1301-16_0_6_line_12 |  | 8 | 13 | 0.066149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1301-16_0_6_line_13 |  | 9 | 14 | 0.014765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1301-16_0_6_line_14 |  | 11 | 119 | 0.019196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1301-16_0_6_line_15 |  | 12 | 117 | 0.038171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1301-16_0_6_line_16 |  | 13 | 27 | 0.029136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1301-16_0_6_line_17 |  | 14 | 101 | 0.019703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1301-16_0_6_line_18 |  | 15 | 16 | 0.038982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1301-16_0_6_line_19 |  | 15 | 17 | 0.0035087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1301-16_0_6_line_20 |  | 16 | 18 | 0.032486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_1301-16_0_6_line_21 |  | 17 | 19 | 0.026407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1301-16_0_6_line_22 |  | 17 | 20 | 0.075565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_1301-16_0_6_line_23 |  | 18 | 21 | 0.023505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_1301-16_0_6_line_24 |  | 19 | 22 | 0.018975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1301-16_0_6_line_25 |  | 20 | 23 | 0.016652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1301-16_0_6_line_26 |  | 21 | 24 | 0.021013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1301-16_0_6_line_27 |  | 22 | 25 | 0.03369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1301-16_0_6_line_28 |  | 23 | 26 | 0.056091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1301-16_0_6_line_29 |  | 24 | 39 | 0.020052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_1301-16_0_6_line_30 |  | 25 | 37 | 0.027924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1301-16_0_6_line_31 |  | 26 | 113 | 0.0035247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_1301-16_0_6_line_32 |  | 27 | 28 | 0.0052497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1301-16_0_6_line_33 |  | 28 | 99 | 0.00050695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_1301-16_0_6_line_34 |  | 29 | 30 | 0.020137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1301-16_0_6_line_35 |  | 29 | 31 | 0.015928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1301-16_0_6_line_36 |  | 30 | 32 | 0.01608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1301-16_0_6_line_37 |  | 31 | 33 | 0.003125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_1301-16_0_6_line_38 |  | 31 | 34 | 0.027033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_1301-16_0_6_line_39 |  | 32 | 35 | 0.020074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1301-16_0_6_line_40 |  | 32 | 36 | 0.0069603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1301-16_0_6_line_41 |  | 33 | 38 | 0.014522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1301-16_0_6_line_42 |  | 33 | 39 | 0.037424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_1301-16_0_6_line_43 |  | 34 | 40 | 0.015633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_1301-16_0_6_line_44 |  | 35 | 41 | 0.00068686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1301-16_0_6_line_45 |  | 36 | 42 | 0.020965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1301-16_0_6_line_46 |  | 40 | 44 | 0.037038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1301-16_0_6_line_47 |  | 41 | 77 | 0.01756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1301-16_0_6_line_48 |  | 42 | 74 | 0.005353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1301-16_0_6_line_49 |  | 43 | 44 | 0.03044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1301-16_0_6_line_50 |  | 43 | 45 | 0.022385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1301-16_0_6_line_51 |  | 44 | 55 | 0.019703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1301-16_0_6_line_52 |  | 44 | 57 | 0.010286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1301-16_0_6_line_53 |  | 46 | 47 | 0.040275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1301-16_0_6_line_54 |  | 46 | 48 | 0.19018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1301-16_0_6_line_55 |  | 47 | 49 | 0.036908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1301-16_0_6_line_56 |  | 47 | 50 | 0.005065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1301-16_0_6_line_57 |  | 48 | 52 | 0.17974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1301-16_0_6_line_58 |  | 49 | 53 | 0.051254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1301-16_0_6_line_59 |  | 50 | 54 | 0.011204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1301-16_0_6_line_60 |  | 51 | 52 | 0.013687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1301-16_0_6_line_61 |  | 53 | 55 | 0.0085117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1301-16_0_6_line_62 |  | 53 | 56 | 0.019263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1301-16_0_6_line_63 |  | 56 | 58 | 0.00027831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1301-16_0_6_line_64 |  | 57 | 59 | 0.01665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1301-16_0_6_line_65 |  | 57 | 60 | 0.014858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1301-16_0_6_line_66 |  | 59 | 88 | 0.016557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1301-16_0_6_line_67 |  | 60 | 70 | 0.023574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1301-16_0_6_line_68 |  | 61 | 62 | 0.028281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1301-16_0_6_line_69 |  | 62 | 63 | 0.0049263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1301-16_0_6_line_70 |  | 63 | 65 | 0.0031054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1301-16_0_6_line_71 |  | 64 | 65 | 0.071374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1301-16_0_6_line_72 |  | 64 | 66 | 0.0075081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1301-16_0_6_line_73 |  | 66 | 118 | 0.014912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1301-16_0_6_line_74 |  | 67 | 68 | 0.0047995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1301-16_0_6_line_75 |  | 67 | 69 | 0.024929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1301-16_0_6_line_76 |  | 68 | 70 | 0.024019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1301-16_0_6_line_77 |  | 69 | 71 | 0.005311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1301-16_0_6_line_78 |  | 71 | 72 | 0.017482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1301-16_0_6_line_79 |  | 72 | 73 | 0.01679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1301-16_0_6_line_80 |  | 73 | 81 | 0.016341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1301-16_0_6_line_81 |  | 74 | 75 | 0.030951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1301-16_0_6_line_82 |  | 75 | 76 | 0.013208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1301-16_0_6_line_83 |  | 76 | 92 | 0.011571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1301-16_0_6_line_84 |  | 78 | 79 | 0.010527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1301-16_0_6_line_85 |  | 78 | 80 | 0.016014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1301-16_0_6_line_86 |  | 79 | 81 | 0.032071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1301-16_0_6_line_87 |  | 80 | 82 | 0.014167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1301-16_0_6_line_88 |  | 80 | 83 | 0.015429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1301-16_0_6_line_89 |  | 82 | 84 | 0.00050329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1301-16_0_6_line_90 |  | 83 | 85 | 0.025885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1301-16_0_6_line_91 |  | 84 | 86 | 0.017426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1301-16_0_6_line_92 |  | 85 | 87 | 0.51734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1301-16_0_6_line_93 |  | 87 | 96 | 0.055768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1301-16_0_6_line_94 |  | 89 | 90 | 0.00039787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1301-16_0_6_line_95 |  | 90 | 91 | 0.017009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1301-16_0_6_line_96 |  | 91 | 93 | 0.014223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1301-16_0_6_line_97 |  | 92 | 93 | 0.029332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1301-16_0_6_line_98 |  | 94 | 95 | 0.008063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1301-16_0_6_line_99 |  | 94 | 96 | 0.27052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1301-16_0_6_line_100 |  | 95 | 97 | 0.26522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1301-16_0_6_line_101 |  | 97 | 98 | 0.01104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1301-16_0_6_line_102 |  | 99 | 100 | 0.0149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_1301-16_0_6_line_103 |  | 100 | 104 | 0.0015021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_1301-16_0_6_line_104 |  | 101 | 102 | 0.017028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1301-16_0_6_line_105 |  | 102 | 103 | 0.0088049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1301-16_0_6_line_106 |  | 103 | 139 | 0.02326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1301-16_0_6_line_107 |  | 104 | 105 | 0.00073272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_1301-16_0_6_line_108 |  | 105 | 106 | 0.018062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_1301-16_0_6_line_109 |  | 106 | 107 | 0.0042322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_1301-16_0_6_line_110 |  | 107 | 108 | 0.017933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_1301-16_0_6_line_111 |  | 108 | 109 | 0.0022188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
112 | LV_1301-16_0_6_line_112 |  | 109 | 110 | 0.038654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_1301-16_0_6_line_113 |  | 110 | 111 | 0.016271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
114 | LV_1301-16_0_6_line_114 |  | 111 | 112 | 0.012449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_1301-16_0_6_line_115 |  | 112 | 113 | 0.020562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
116 | LV_1301-16_0_6_line_116 |  | 113 | 114 | 0.016108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1301-16_0_6_line_117 |  | 114 | 115 | 0.03443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1301-16_0_6_line_118 |  | 115 | 116 | 0.014972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1301-16_0_6_line_119 |  | 116 | 122 | 0.012173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1301-16_0_6_line_120 |  | 117 | 118 | 0.0060725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1301-16_0_6_line_121 |  | 120 | 121 | 0.025862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1301-16_0_6_line_122 |  | 120 | 122 | 0.017854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1301-16_0_6_line_123 |  | 121 | 123 | 0.025728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1301-16_0_6_line_124 |  | 123 | 124 | 0.016586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1301-16_0_6_line_125 |  | 124 | 125 | 0.0004285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1301-16_0_6_line_126 |  | 126 | 127 | 0.0027549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1301-16_0_6_line_127 |  | 126 | 128 | 0.020614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1301-16_0_6_line_128 |  | 127 | 129 | 0.02333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1301-16_0_6_line_129 |  | 128 | 130 | 2.8468e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1301-16_0_6_line_130 |  | 129 | 131 | 0.0051085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1301-16_0_6_line_131 |  | 130 | 132 | 0.00047255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1301-16_0_6_line_132 |  | 131 | 133 | 0.019717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1301-16_0_6_line_133 |  | 133 | 134 | 9.6143e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1301-16_0_6_line_134 |  | 134 | 135 | 0.023632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1301-16_0_6_line_135 |  | 135 | 136 | 0.022577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1301-16_0_6_line_136 |  | 136 | 137 | 0.016456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1301-16_0_6_line_137 |  | 136 | 138 | 0.0042971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1301-16_0_6_line_138 |  | 137 | 141 | 0.0049232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1301-16_0_6_line_139 |  | 138 | 140 | 0.024723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1301-16_0_6_line_140 |  | 139 | 140 | 0.0018966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1301-16_0_6_trafo_99 | 0.63 MVA 20/0.4 kV | 142 | 112 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2698732.0086 | 1221673.413 | 2698736.076 | 1221656.3407 | 2698740.1235 | 1221641.5151
1 | 2698728.4192 | 1221688.9036 | 2698729.2341 | 1221685.0588 | 2698732.0086 | 1221673.413
2 | 2698738.7294 | 1221601.1343 | 2698740.3061 | 1221625.4555 | 2698740.2039 | 1221641.2206 | 2698740.1235 | 1221641.5151
3 | 2698728.4192 | 1221688.9036 | 2698726.0589 | 1221697.1815 | 2698722.249 | 1221709.4959
4 | 2698728.4192 | 1221688.9036 | 2698734.412 | 1221689.4145 | 2698742.7051 | 1221696.2457 | 2698755.1552 | 1221746.1188
5 | 2698728.4405 | 1221596.6049 | 2698738.7294 | 1221601.1343
6 | 2698757.4045 | 1221534.1851 | 2698747.1043 | 1221552.2828 | 2698740.7705 | 1221565.9097 | 2698738.6819 | 1221578.3839 | 2698738.0778 | 1221591.0162 | 2698738.7294 | 1221601.1343
7 | 2698722.249 | 1221709.4959 | 2698719.3167 | 1221718.9742 | 2698718.7136 | 1221722.1304
8 | 2698766.8805 | 1221790.3776 | 2698756.6274 | 1221752.0163 | 2698755.1552 | 1221746.1188
9 | 2698728.4405 | 1221596.6049 | 2698722.9269 | 1221594.1785 | 2698711.4749 | 1221586.1273 | 2698697.6354 | 1221571.5209
10 | 2698728.4405 | 1221596.6049 | 2698731.2699 | 1221575.1476 | 2698725.34 | 1221567.0098
11 | 2698757.4045 | 1221534.1851 | 2698778.3531 | 1221553.0226
12 | 2698722.0761 | 1221785.72 | 2698713.6824 | 1221769.5724 | 2698713.3763 | 1221750.0645 | 2698718.7136 | 1221722.1304
13 | 2698772.5984 | 1221803.8786 | 2698768.4783 | 1221796.3555 | 2698766.8805 | 1221790.3776
14 | 2698711.7264 | 1221558.156 | 2698717.6721 | 1221556.4867 | 2698725.34 | 1221567.0098
15 | 2698778.3531 | 1221553.0226 | 2698782.1713 | 1221556.4561 | 2698783.4217 | 1221562.9482 | 2698778.3602 | 1221588.8838
16 | 2698722.0761 | 1221785.72 | 2698733.8718 | 1221808.4125 | 2698735.9718 | 1221811.2876
17 | 2698772.5984 | 1221803.8786 | 2698778.655 | 1221814.9376 | 2698784.4149 | 1221819.0793
18 | 2698937.8863 | 1222052.3745 | 2698942.2246 | 1222050.5987 | 2698949.8558 | 1222046.0889 | 2698954.1039 | 1222038.8099 | 2698955.6634 | 1222032.6203 | 2698954.9158 | 1222022.0271
19 | 2698954.6688 | 1222018.527 | 2698954.9158 | 1222022.0271
20 | 2698937.8863 | 1222052.3745 | 2698932.9055 | 1222054.4133 | 2698912.9499 | 1222057.7842 | 2698906.0839 | 1222057.795
21 | 2698954.6688 | 1222018.527 | 2698928.2663 | 1222019.0341
22 | 2698954.6688 | 1222018.527 | 2698951.3622 | 1222010.6998 | 2698939.0366 | 1221998.6754 | 2698903.7641 | 1221976.8961 | 2698896.9118 | 1221972.0477
23 | 2698906.0839 | 1222057.795 | 2698882.5788 | 1222057.832
24 | 2698928.2663 | 1222019.0341 | 2698920.8444 | 1222019.1767 | 2698909.293 | 1222019.1227
25 | 2698896.9118 | 1221972.0477 | 2698883.3185 | 1221962.4296
26 | 2698861.5679 | 1222058.0197 | 2698869.5537 | 1222057.8525 | 2698882.5788 | 1222057.832
27 | 2698875.6036 | 1222018.9652 | 2698909.293 | 1222019.1227
28 | 2698839.0708 | 1221928.081 | 2698856.7258 | 1221943.6136 | 2698883.3185 | 1221962.4296
29 | 2698861.5679 | 1222058.0197 | 2698841.5205 | 1222058.4394
30 | 2698875.6036 | 1222018.9652 | 2698852.8813 | 1222018.859 | 2698847.6814 | 1222018.9878
31 | 2698836.4246 | 1221925.7528 | 2698839.0708 | 1221928.081
32 | 2698739.0682 | 1221815.527 | 2698735.9718 | 1221811.2876
33 | 2698739.3672 | 1221815.9364 | 2698739.0682 | 1221815.527
34 | 2698805.0432 | 1222020.0438 | 2698804.5819 | 1222040.176
35 | 2698804.217 | 1222056.1002 | 2698804.5819 | 1222040.176
36 | 2698805.0432 | 1222020.0438 | 2698805.1432 | 1222003.9673
37 | 2698804.217 | 1222056.1002 | 2698804.1044 | 1222059.2228
38 | 2698804.217 | 1222056.1002 | 2698777.2524 | 1222058.0248
39 | 2698805.1432 | 1222003.9673 | 2698805.2483 | 1221995.3518 | 2698816.7048 | 1221995.542
40 | 2698805.1432 | 1222003.9673 | 2698802.6964 | 1222003.7488 | 2698800.742 | 1222003.5718 | 2698799.3865 | 1222002.96 | 2698798.4383 | 1222002.4995
41 | 2698804.1044 | 1222059.2228 | 2698806.7317 | 1222070.9637 | 2698807.6483 | 1222073.28
42 | 2698804.1044 | 1222059.2228 | 2698841.5205 | 1222058.4394
43 | 2698761.6586 | 1222059.1378 | 2698777.2524 | 1222058.0248
44 | 2698817.3916 | 1221995.5534 | 2698816.7048 | 1221995.542
45 | 2698798.4383 | 1222002.4995 | 2698798.4383 | 1222002.4995 | 2698797.5978 | 1222001.0289 | 2698796.5948 | 1221995.6418 | 2698787.5499 | 1221985.2301
46 | 2698724.7144 | 1222061.7747 | 2698761.6586 | 1222059.1378
47 | 2698834.9494 | 1221995.845 | 2698817.3916 | 1221995.5534
48 | 2698787.5499 | 1221985.2301 | 2698784.0393 | 1221981.189
49 | 2698724.7144 | 1222061.7747 | 2698724.6124 | 1222065.1754 | 2698751.546 | 1222062.8092
50 | 2698751.546 | 1222062.8092 | 2698751.6718 | 1222085.1938
51 | 2698724.7144 | 1222061.7747 | 2698704.9978 | 1222063.0932
52 | 2698725.0215 | 1222051.4946 | 2698724.7144 | 1222061.7747
53 | 2698615.0907 | 1222079.9713 | 2698605.9106 | 1222082.7435 | 2698576.742 | 1222092.2723
54 | 2698576.742 | 1222092.2723 | 2698518.6432 | 1222273.3573
55 | 2698615.0907 | 1222079.9713 | 2698635.2932 | 1222073.5903 | 2698650.7302 | 1222070.6104
56 | 2698614.7648 | 1222074.9179 | 2698615.0907 | 1222079.9713
57 | 2698372.8345 | 1222378.4509 | 2698518.6432 | 1222273.3573
58 | 2698701.8199 | 1222066.6987 | 2698652.9047 | 1222070.1907 | 2698650.7302 | 1222070.6104
59 | 2698614.7648 | 1222074.9179 | 2698616.7262 | 1222069.6355 | 2698620.8847 | 1222065.9306
60 | 2698364.3058 | 1222389.1552 | 2698364.3058 | 1222389.1552 | 2698372.8345 | 1222378.4509
61 | 2698701.8199 | 1222066.6987 | 2698706.6582 | 1222066.3564 | 2698704.9978 | 1222063.0932
62 | 2698701.8199 | 1222066.6987 | 2698701.9308 | 1222085.9613
63 | 2698701.9324 | 1222086.2396 | 2698701.9308 | 1222085.9613
64 | 2698725.0215 | 1222051.4946 | 2698736.756 | 1222049.7769 | 2698741.5074 | 1222049.17
65 | 2698725.0215 | 1222051.4946 | 2698725.4708 | 1222036.6436
66 | 2698756.4853 | 1222042.6656 | 2698749.4319 | 1222047.1074 | 2698744.2295 | 1222048.8223 | 2698741.5074 | 1222049.17
67 | 2698723.3989 | 1222013.4119 | 2698724.455 | 1222015.6708 | 2698725.8275 | 1222024.8557 | 2698725.4708 | 1222036.6436
68 | 2698867.8742 | 1221663.0128 | 2698849.702 | 1221655.3026 | 2698842.7279 | 1221650.3722
69 | 2698840.5275 | 1221645.9646 | 2698842.7279 | 1221650.3722 | 2698842.7279 | 1221650.3722
70 | 2698839.2541 | 1221643.15 | 2698839.3135 | 1221643.5329 | 2698840.5275 | 1221645.9646
71 | 2698772.9027 | 1221616.8485 | 2698839.2541 | 1221643.15
72 | 2698774.3408 | 1221609.4794 | 2698772.9027 | 1221616.8485
73 | 2698777.197 | 1221594.8438 | 2698774.3408 | 1221609.4794
74 | 2698704.0519 | 1221992.8573 | 2698707.7685 | 1221995.8941
75 | 2698704.0519 | 1221992.8573 | 2698697.9308 | 1221987.8558 | 2698684.5138 | 1221977.3759
76 | 2698723.3989 | 1222013.4119 | 2698719.8392 | 1222005.7984 | 2698715.4461 | 1222002.1674 | 2698707.7685 | 1221995.8941
77 | 2698680.3283 | 1221974.1067 | 2698684.5138 | 1221977.3759
78 | 2698666.5723 | 1221963.3187 | 2698673.904 | 1221969.0887 | 2698680.3283 | 1221974.1067
79 | 2698666.5723 | 1221963.3187 | 2698660.0043 | 1221958.1617 | 2698654.242 | 1221951.9952
80 | 2698654.242 | 1221951.9952 | 2698654.242 | 1221951.9952 | 2698641.633 | 1221956.5674 | 2698638.9382 | 1221957.7135
81 | 2698762.5848 | 1221958.9023 | 2698778.3262 | 1221974.6126 | 2698784.0393 | 1221981.189
82 | 2698753.2358 | 1221949.5717 | 2698762.5848 | 1221958.9023
83 | 2698753.2358 | 1221949.5717 | 2698752.3025 | 1221948.6403 | 2698744.3764 | 1221942.1375
84 | 2698620.5474 | 1221938.9818 | 2698618.2258 | 1221942.0583 | 2698615.0183 | 1221947.9093
85 | 2698629.85 | 1221925.9504 | 2698623.8031 | 1221934.6676 | 2698620.5474 | 1221938.9818
86 | 2698638.9382 | 1221957.7135 | 2698636.3993 | 1221958.7934 | 2698627.9557 | 1221960.1434 | 2698621.1406 | 1221958.9074 | 2698615.2259 | 1221954.1506 | 2698615.0183 | 1221947.9093 | 2698615.0183 | 1221947.9093
87 | 2698629.85 | 1221925.9504 | 2698640.0721 | 1221916.1423
88 | 2698629.85 | 1221925.9504 | 2698627.0941 | 1221924.6928 | 2698618.6715 | 1221915.592
89 | 2698640.4352 | 1221915.7938 | 2698640.0721 | 1221916.1423
90 | 2698601.4272 | 1221896.3698 | 2698603.1709 | 1221899.1896 | 2698610.6969 | 1221906.9753 | 2698618.6715 | 1221915.592
91 | 2698653.0089 | 1221903.7293 | 2698640.4352 | 1221915.7938
92 | 2698601.4272 | 1221896.3698 | 2698088.2024 | 1221831.2706
93 | 2698088.2024 | 1221831.2706 | 2698079.2265 | 1221835.915 | 2698069.5459 | 1221839.5915 | 2698058.46 | 1221840.6097 | 2698034.9688 | 1221834.3074
94 | 2698697.0634 | 1221929.4936 | 2698697.3363 | 1221929.2041
95 | 2698697.3363 | 1221929.2041 | 2698699.3486 | 1221927.0693 | 2698709.2782 | 1221917.0934 | 2698709.2782 | 1221917.0934
96 | 2698721.6993 | 1221923.5328 | 2698716.9741 | 1221919.6561 | 2698709.2782 | 1221917.0934
97 | 2698721.6993 | 1221923.5328 | 2698744.3764 | 1221942.1375
98 | 2697794.5754 | 1221693.822 | 2697800.6541 | 1221699.1193
99 | 2697800.6541 | 1221699.1193 | 2698034.9688 | 1221834.3074
100 | 2697794.5754 | 1221693.822 | 2697784.4691 | 1221428.7902
101 | 2697774.2821 | 1221424.4643 | 2697784.4691 | 1221428.7902
102 | 2698739.3672 | 1221815.9364 | 2698748.1557 | 1221827.9687
103 | 2698749.0417 | 1221829.1817 | 2698748.1557 | 1221827.9687
104 | 2698798.5754 | 1221828.5194 | 2698791.0331 | 1221823.8381 | 2698784.4149 | 1221819.0793
105 | 2698798.5754 | 1221828.5194 | 2698806.0564 | 1221833.1627
106 | 2698825.9569 | 1221845.2035 | 2698812.1272 | 1221836.9307 | 2698806.0564 | 1221833.1627
107 | 2698749.4739 | 1221829.7734 | 2698749.0417 | 1221829.1817
108 | 2698760.1273 | 1221844.3591 | 2698749.4739 | 1221829.7734
109 | 2698762.6236 | 1221847.7768 | 2698760.1273 | 1221844.3591
110 | 2698773.201 | 1221862.2582 | 2698762.6236 | 1221847.7768
111 | 2698774.5096 | 1221864.05 | 2698773.201 | 1221862.2582
112 | 2698798.3659 | 1221894.4434 | 2698784.0119 | 1221877.0596 | 2698774.5096 | 1221864.05
113 | 2698798.3659 | 1221894.4434 | 2698798.3659 | 1221894.4434 | 2698810.9314 | 1221904.7806
114 | 2698810.9314 | 1221904.7806 | 2698820.5453 | 1221912.6895
115 | 2698836.4246 | 1221925.7528 | 2698820.5453 | 1221912.6895
116 | 2698836.4246 | 1221925.7528 | 2698839.8711 | 1221924.2534 | 2698843.4092 | 1221922.7221 | 2698851.6476 | 1221924.7898
117 | 2698851.6476 | 1221924.7898 | 2698885.0418 | 1221933.1708
118 | 2698899.2398 | 1221937.788 | 2698892.9412 | 1221935.1533 | 2698885.0418 | 1221933.1708
119 | 2698899.2398 | 1221937.788 | 2698910.4698 | 1221942.4856
120 | 2698778.3602 | 1221588.8838 | 2698777.197 | 1221594.8438
121 | 2698927.5053 | 1221947.0803 | 2698927.5053 | 1221947.0803 | 2698942.9171 | 1221940.0424 | 2698951.7133 | 1221938.569
122 | 2698910.4698 | 1221942.4856 | 2698913.1483 | 1221943.606 | 2698919.9142 | 1221946.4315 | 2698927.5053 | 1221947.0803
123 | 2698977.1722 | 1221934.9105 | 2698964.9572 | 1221936.3505 | 2698951.7133 | 1221938.569
124 | 2698977.1722 | 1221934.9105 | 2698993.6443 | 1221932.9687
125 | 2698994.0699 | 1221932.9185 | 2698993.6443 | 1221932.9687
126 | 2698945.4444 | 1221874.3621 | 2698948.1981 | 1221874.2808
127 | 2698968.7718 | 1221873.14 | 2698959.9485 | 1221873.9338 | 2698948.1981 | 1221874.2808
128 | 2698922.1249 | 1221875.0507 | 2698945.4444 | 1221874.3621
129 | 2698968.8002 | 1221873.1374 | 2698968.7718 | 1221873.14
130 | 2698917.0392 | 1221874.5677 | 2698922.1249 | 1221875.0507 | 2698922.1249 | 1221875.0507
131 | 2698969.2708 | 1221873.0951 | 2698968.8002 | 1221873.1374
132 | 2698917.0392 | 1221874.5677 | 2698897.4103 | 1221872.7038
133 | 2698897.4103 | 1221872.7038 | 2698897.3146 | 1221872.6947
134 | 2698874.297 | 1221867.4135 | 2698895.5827 | 1221872.5303 | 2698897.3146 | 1221872.6947
135 | 2698853.0941 | 1221859.8936 | 2698865.7189 | 1221865.3515 | 2698874.297 | 1221867.4135
136 | 2698853.0941 | 1221859.8936 | 2698851.8561 | 1221865.4548 | 2698848.5455 | 1221875.6915
137 | 2698853.0941 | 1221859.8936 | 2698849.1504 | 1221858.187
138 | 2698847.0306 | 1221880.3758 | 2698848.5455 | 1221875.6915
139 | 2698849.1504 | 1221858.187 | 2698843.7686 | 1221855.8582 | 2698827.5846 | 1221846.1771
140 | 2698825.9569 | 1221845.2035 | 2698827.5846 | 1221846.1771

## bus_geodata
| x | y | coords
0 | 2698732.0086 | 1221673.413
1 | 2698740.1235 | 1221641.5151
2 | 2698728.4192 | 1221688.9036
3 | 2698738.7294 | 1221601.1343
4 | 2698722.249 | 1221709.4959
5 | 2698755.1552 | 1221746.1188
6 | 2698728.4405 | 1221596.6049
7 | 2698757.4045 | 1221534.1851
8 | 2698718.7136 | 1221722.1304
9 | 2698766.8805 | 1221790.3776
10 | 2698697.6354 | 1221571.5209
11 | 2698725.34 | 1221567.0098
12 | 2698778.3531 | 1221553.0226
13 | 2698722.0761 | 1221785.72
14 | 2698772.5984 | 1221803.8786
15 | 2698954.9158 | 1222022.0271
16 | 2698937.8863 | 1222052.3745
17 | 2698954.6688 | 1222018.527
18 | 2698906.0839 | 1222057.795
19 | 2698928.2663 | 1222019.0341
20 | 2698896.9118 | 1221972.0477
21 | 2698882.5788 | 1222057.832
22 | 2698909.293 | 1222019.1227
23 | 2698883.3185 | 1221962.4296
24 | 2698861.5679 | 1222058.0197
25 | 2698875.6036 | 1222018.9652
26 | 2698839.0708 | 1221928.081
27 | 2698735.9718 | 1221811.2876
28 | 2698739.0682 | 1221815.527
29 | 2698804.5819 | 1222040.176
30 | 2698805.0432 | 1222020.0438
31 | 2698804.217 | 1222056.1002
32 | 2698805.1432 | 1222003.9673
33 | 2698804.1045 | 1222059.2228
34 | 2698777.2524 | 1222058.0248
35 | 2698816.7048 | 1221995.542
36 | 2698798.4383 | 1222002.4995
37 | 2698847.6814 | 1222018.9878
38 | 2698807.6483 | 1222073.28
39 | 2698841.5205 | 1222058.4394
40 | 2698761.6586 | 1222059.1378
41 | 2698817.3916 | 1221995.5534
42 | 2698787.5499 | 1221985.2301
43 | 2698751.546 | 1222062.8092
44 | 2698724.7144 | 1222061.7747
45 | 2698751.6718 | 1222085.1938
46 | 2698576.742 | 1222092.2723
47 | 2698615.0907 | 1222079.9713
48 | 2698518.6432 | 1222273.3573
49 | 2698650.7302 | 1222070.6104
50 | 2698614.7648 | 1222074.9179
51 | 2698364.3058 | 1222389.1552
52 | 2698372.8345 | 1222378.4509
53 | 2698701.8199 | 1222066.6987
54 | 2698620.8847 | 1222065.9306
55 | 2698704.9978 | 1222063.0932
56 | 2698701.9308 | 1222085.9613
57 | 2698725.0215 | 1222051.4946
58 | 2698701.9324 | 1222086.2396
59 | 2698741.5074 | 1222049.17
60 | 2698725.4708 | 1222036.6436
61 | 2698867.8742 | 1221663.0128
62 | 2698842.7279 | 1221650.3722
63 | 2698840.5275 | 1221645.9646
64 | 2698772.9027 | 1221616.8485
65 | 2698839.2541 | 1221643.15
66 | 2698774.3408 | 1221609.4794
67 | 2698704.0519 | 1221992.8573
68 | 2698707.7685 | 1221995.8941
69 | 2698684.5138 | 1221977.3759
70 | 2698723.3989 | 1222013.4119
71 | 2698680.3283 | 1221974.1067
72 | 2698666.5723 | 1221963.3187
73 | 2698654.242 | 1221951.9952
74 | 2698784.0393 | 1221981.189
75 | 2698762.5848 | 1221958.9023
76 | 2698753.2358 | 1221949.5717
77 | 2698834.9494 | 1221995.845
78 | 2698620.5474 | 1221938.9818
79 | 2698615.0183 | 1221947.9093
80 | 2698629.85 | 1221925.9504
81 | 2698638.9382 | 1221957.7135
82 | 2698640.0721 | 1221916.1423
83 | 2698618.6715 | 1221915.592
84 | 2698640.4352 | 1221915.7938
85 | 2698601.4272 | 1221896.3698
86 | 2698653.0089 | 1221903.7293
87 | 2698088.2024 | 1221831.2706
88 | 2698756.4853 | 1222042.6656
89 | 2698697.0634 | 1221929.4936
90 | 2698697.3363 | 1221929.2041
91 | 2698709.2782 | 1221917.0934
92 | 2698744.3764 | 1221942.1375
93 | 2698721.6993 | 1221923.5328
94 | 2697800.6541 | 1221699.1193
95 | 2697794.5754 | 1221693.822
96 | 2698034.9688 | 1221834.3074
97 | 2697784.4691 | 1221428.7902
98 | 2697774.2821 | 1221424.4643
99 | 2698739.3672 | 1221815.9364
100 | 2698748.1557 | 1221827.9687
101 | 2698784.4149 | 1221819.0793
102 | 2698798.5754 | 1221828.5194
103 | 2698806.0564 | 1221833.1627
104 | 2698749.0417 | 1221829.1817
105 | 2698749.4739 | 1221829.7734
106 | 2698760.1273 | 1221844.3591
107 | 2698762.6236 | 1221847.7768
108 | 2698773.201 | 1221862.2582
109 | 2698774.5096 | 1221864.05
110 | 2698798.3658 | 1221894.4434
111 | 2698810.9314 | 1221904.7806
112 | 2698820.5453 | 1221912.6895
113 | 2698836.4246 | 1221925.7528
114 | 2698851.6476 | 1221924.7898
115 | 2698885.0418 | 1221933.1708
116 | 2698899.2398 | 1221937.788
117 | 2698778.3602 | 1221588.8838
118 | 2698777.197 | 1221594.8438
119 | 2698711.7264 | 1221558.156
120 | 2698927.5053 | 1221947.0803
121 | 2698951.7133 | 1221938.569
122 | 2698910.4698 | 1221942.4856
123 | 2698977.1722 | 1221934.9105
124 | 2698993.6443 | 1221932.9687
125 | 2698994.0699 | 1221932.9185
126 | 2698948.1981 | 1221874.2808
127 | 2698945.4444 | 1221874.3621
128 | 2698968.7718 | 1221873.14
129 | 2698922.1249 | 1221875.0507
130 | 2698968.8001 | 1221873.1374
131 | 2698917.0392 | 1221874.5677
132 | 2698969.2708 | 1221873.0951
133 | 2698897.4103 | 1221872.7038
134 | 2698897.3146 | 1221872.6947
135 | 2698874.297 | 1221867.4135
136 | 2698853.0941 | 1221859.8936
137 | 2698848.5455 | 1221875.6915
138 | 2698849.1504 | 1221858.187
139 | 2698825.9569 | 1221845.2035
140 | 2698827.5846 | 1221846.1771
141 | 2698847.0306 | 1221880.3758
142 | 2698836.4246 | 1221925.7528

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9885 | -0.21839 | 0.0005966 | 0.00014952
1 | 0.98827 | -0.22291 | 0.00085913 | 0.00021532
2 | 0.98862 | -0.21603 | 0 | 0
3 | 0.98802 | -0.22784 | 0 | 0
4 | 0.99039 | -0.18222 | 0.0022 | 0.00055137
5 | 0.98354 | -0.31388 | 0.0037835 | 0.00094824
6 | 0.988 | -0.22825 | 0 | 0
7 | 0.9877 | -0.23393 | 0 | 0
8 | 0.9915 | -0.1611 | 0.0020636 | 0.00051719
9 | 0.98028 | -0.37703 | 0.0027655 | 0.0006931
10 | 0.98798 | -0.22847 | 0.00030492 | 7.6419e-05
11 | 0.98795 | -0.22923 | 0.0011752 | 0.00029453
12 | 0.98758 | -0.23634 | 0.00075026 | 0.00018803
13 | 0.99435 | -0.10693 | 0.0030072 | 0.00075368
14 | 0.97927 | -0.39674 | 0.0029928 | 0.00075008
15 | 0.99079 | -0.17524 | 0.0096049 | 0.0024072
16 | 0.98911 | -0.20765 | 0.0054642 | 0.0013695
17 | 0.99096 | -0.17213 | 0 | 0
18 | 0.98775 | -0.23369 | 0.0028196 | 0.00070665
19 | 0.99065 | -0.17804 | 0.0029691 | 0.00074413
20 | 0.99474 | -0.099769 | 0.002808 | 0.00070375
21 | 0.9868 | -0.25218 | 0.0037172 | 0.00093163
22 | 0.99048 | -0.18128 | 0.0045816 | 0.0011482
23 | 0.99559 | -0.083623 | 0.0036557 | 0.00091621
24 | 0.98596 | -0.26827 | 0.0026698 | 0.0006691
25 | 0.99033 | -0.18431 | 0.0031736 | 0.00079538
26 | 0.99851 | -0.028242 | 0.0044272 | 0.0011096
27 | 0.99521 | -0.09057 | 0.0034591 | 0.00086693
28 | 0.99537 | -0.087518 | 0.00095115 | 0.00023838
29 | 0.98279 | -0.32986 | 0.005758 | 0.0014431
30 | 0.98181 | -0.34902 | 0 | 0
31 | 0.98365 | -0.31308 | 0 | 0
32 | 0.98103 | -0.36434 | 0 | 0
33 | 0.98377 | -0.31082 | 0 | 0
34 | 0.98287 | -0.32828 | 0.0019194 | 0.00048105
35 | 0.98086 | -0.36766 | 0.0036664 | 0.00091889
36 | 0.98075 | -0.36983 | 0.0038631 | 0.00096818
37 | 0.99028 | -0.18524 | 0.0018754 | 0.00047002
38 | 0.98375 | -0.31127 | 0.0017233 | 0.0004319
39 | 0.98519 | -0.28333 | 0.003041 | 0.00076214
40 | 0.98243 | -0.33681 | 0.0013431 | 0.00033662
41 | 0.98085 | -0.36773 | 0.0024966 | 0.00062571
42 | 0.97997 | -0.38492 | 0.0028752 | 0.0007206
43 | 0.98034 | -0.37772 | 0 | 0
44 | 0.9804 | -0.37643 | 0 | 0
45 | 0.98029 | -0.37866 | 0.0023306 | 0.00058411
46 | 0.97965 | -0.39126 | 0.00050961 | 0.00012772
47 | 0.97976 | -0.38915 | 0 | 0
48 | 0.97923 | -0.39948 | 0.00065766 | 0.00016483
49 | 0.97989 | -0.38665 | 0.0018409 | 0.00046137
50 | 0.97975 | -0.38923 | 0 | 0
51 | 0.97893 | -0.40537 | 0.0011928 | 0.00029895
52 | 0.97895 | -0.40508 | 0.00051733 | 0.00012966
53 | 0.98015 | -0.38146 | 0 | 0
54 | 0.97975 | -0.3894 | 0.00084303 | 0.00021128
55 | 0.98023 | -0.37994 | 0 | 0
56 | 0.98007 | -0.38294 | 0.0013936 | 0.00034926
57 | 0.97996 | -0.38519 | 0 | 0
58 | 0.98007 | -0.38296 | 0.0028505 | 0.00071441
59 | 0.97987 | -0.38692 | 0.0028684 | 0.00071889
60 | 0.97939 | -0.39632 | 0.0033737 | 0.00084552
61 | 0.98717 | -0.24428 | 0.0011291 | 0.00028297
62 | 0.9872 | -0.24371 | 0.0002497 | 6.258e-05
63 | 0.98721 | -0.24359 | 0.00038411 | 9.6266e-05
64 | 0.98736 | -0.24065 | 0.00039706 | 9.9513e-05
65 | 0.98721 | -0.24349 | 0.00046151 | 0.00011566
66 | 0.98738 | -0.2403 | 0.00044244 | 0.00011089
67 | 0.9776 | -0.43135 | 0.0018641 | 0.00046719
68 | 0.97775 | -0.42851 | 0.0040269 | 0.0010092
69 | 0.97689 | -0.44527 | 0.0020059 | 0.00050274
70 | 0.97856 | -0.41254 | 0.0013598 | 0.0003408
71 | 0.97675 | -0.44805 | 0.0035583 | 0.00089178
72 | 0.97635 | -0.45605 | 0 | 0
73 | 0.97596 | -0.46374 | 0.0013808 | 0.00034607
74 | 0.97979 | -0.38849 | 0.0056545 | 0.0014171
75 | 0.9789 | -0.40601 | 0.0024132 | 0.00060479
76 | 0.97855 | -0.41291 | 0.0067805 | 0.0016993
77 | 0.98081 | -0.36867 | 0.0029636 | 0.00074275
78 | 0.97476 | -0.48735 | 0.0023307 | 0.00058414
79 | 0.97495 | -0.48362 | 0.0024408 | 0.00061171
80 | 0.97451 | -0.49236 | 0 | 0
81 | 0.9756 | -0.47081 | 0.0018587 | 0.00046583
82 | 0.97436 | -0.49523 | 0.0022287 | 0.00055855
83 | 0.97442 | -0.49404 | 0.0035099 | 0.00087965
84 | 0.97436 | -0.49532 | 0.0021095 | 0.0005287
85 | 0.97436 | -0.4952 | 0 | 0
86 | 0.97425 | -0.49747 | 0.0067259 | 0.0016857
87 | 0.9732 | -0.51837 | 0.0021348 | 0.00053504
88 | 0.97982 | -0.38778 | 0.0028572 | 0.00071609
89 | 0.97752 | -0.433 | 0.0048561 | 0.0012171
90 | 0.97753 | -0.43297 | 0.0016264 | 0.0004076
91 | 0.97763 | -0.43095 | 0.0075466 | 0.0018914
92 | 0.97831 | -0.41754 | 0.0036507 | 0.00091494
93 | 0.97781 | -0.42732 | 0.0042668 | 0.0010693
94 | 0.97312 | -0.5201 | 0.00020594 | 5.1615e-05
95 | 0.97312 | -0.52011 | 0 | 0
96 | 0.97319 | -0.51867 | 0 | 0
97 | 0.97311 | -0.52046 | 0 | 0
98 | 0.9731 | -0.52048 | 6.7748e-05 | 1.6979e-05
99 | 0.99539 | -0.087221 | 0.0020189 | 0.00050598
100 | 0.99586 | -0.078306 | 0.0024753 | 0.00062036
101 | 0.97798 | -0.42203 | 0.003117 | 0.0007812
102 | 0.97691 | -0.44297 | 0.0058142 | 0.0014572
103 | 0.9764 | -0.45288 | 0.0036171 | 0.00090653
104 | 0.99591 | -0.077386 | 0.0024632 | 0.00061734
105 | 0.99593 | -0.076927 | 0.0025058 | 0.00062803
106 | 0.99654 | -0.065346 | 0.0026097 | 0.00065405
107 | 0.99669 | -0.06257 | 0.0030132 | 0.00075518
108 | 0.99733 | -0.0505 | 0.0034822 | 0.00087272
109 | 0.99741 | -0.048963 | 0.0025116 | 0.00062946
110 | 0.99885 | -0.021653 | 0.0065868 | 0.0016508
111 | 0.99949 | -0.0095575 | 0.0043363 | 0.0010868
112 | 1 | 0 | -0.34509 | -0.088027
113 | 0.9987 | -0.024682 | 0 | 0
114 | 0.99821 | -0.033967 | 0.0035811 | 0.00089751
115 | 0.99729 | -0.051683 | 0.0035561 | 0.00089125
116 | 0.99694 | -0.058463 | 0.0057451 | 0.0014399
117 | 0.98744 | -0.23909 | 0.00047049 | 0.00011792
118 | 0.98742 | -0.23948 | 0.00049388 | 0.00012378
119 | 0.98794 | -0.22943 | 0.00056303 | 0.00014111
120 | 0.99642 | -0.068441 | 0.0034322 | 0.00086019
121 | 0.99608 | -0.075129 | 0.004348 | 0.0010897
122 | 0.99672 | -0.062752 | 0.0019275 | 0.00048307
123 | 0.99583 | -0.07982 | 0.003827 | 0.00095915
124 | 0.99573 | -0.081729 | 0.003621 | 0.00090752
125 | 0.99573 | -0.081751 | 0.0029276 | 0.00073372
126 | 0.97126 | -0.5543 | 0.003279 | 0.00082179
127 | 0.97128 | -0.55371 | 0.0047911 | 0.0012008
128 | 0.9711 | -0.55743 | 0.0027101 | 0.00067921
129 | 0.97164 | -0.54669 | 0.0043129 | 0.0010809
130 | 0.9711 | -0.55744 | 0.0023011 | 0.00057671
131 | 0.97174 | -0.54474 | 0.0030743 | 0.00077048
132 | 0.9711 | -0.55747 | 0.0032228 | 0.00080771
133 | 0.97217 | -0.53612 | 0.0046952 | 0.0011767
134 | 0.97218 | -0.53607 | 0.0051016 | 0.0012786
135 | 0.97292 | -0.52149 | 0.0041444 | 0.0010387
136 | 0.97371 | -0.50586 | 0 | 0
137 | 0.97359 | -0.50818 | 0.0029479 | 0.0007388
138 | 0.97389 | -0.50228 | 0.0050327 | 0.0012613
139 | 0.97514 | -0.47757 | 0.0045198 | 0.0011328
140 | 0.97505 | -0.47943 | 0.0031202 | 0.000782
141 | 0.97357 | -0.5086 | 0.0047255 | 0.0011843
142 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0076872 | 0.0019233 | -0.0076856 | -0.0019227 | 1.6527e-06 | 6.3581e-07 | 0.011571 | 0.011571 | 0.011571 | 0.9885 | -0.21839 | 0.98827 | -0.22291 | 3.1788
1 | -0.0082838 | -0.0020729 | 0.0082847 | 0.0020733 | 9.2708e-07 | 3.8946e-07 | 0.012469 | 0.012469 | 0.012469 | 0.9885 | -0.21839 | 0.98862 | -0.21603 | 3.4255
2 | 0.0068264 | 0.0017074 | -0.0068248 | -0.0017069 | 1.6019e-06 | 5.0712e-07 | 0.010277 | 0.010277 | 0.010277 | 0.98827 | -0.22291 | 0.98802 | -0.22784 | 2.8234
3 | -0.089429 | -0.022824 | 0.089575 | 0.022918 | 0.00014638 | 9.3409e-05 | 0.13475 | 0.13475 | 0.13475 | 0.98862 | -0.21603 | 0.99039 | -0.18222 | 37.0194
4 | 0.081144 | 0.020751 | -0.080762 | -0.020507 | 0.00038221 | 0.00024375 | 0.12228 | 0.12228 | 0.12228 | 0.98862 | -0.21603 | 0.98354 | -0.31388 | 33.5941
5 | 0.0020433 | 0.00051083 | -0.0020432 | -0.00051095 | 3.9812e-08 | -1.1813e-07 | 0.0030768 | 0.0030769 | 0.0030769 | 0.98802 | -0.22784 | 0.988 | -0.22825 | 0.8453
6 | 0.0047816 | 0.0011961 | -0.0047802 | -0.0011961 | 1.3858e-06 | -2.5574e-08 | 0.0072005 | 0.0072008 | 0.0072008 | 0.98802 | -0.22784 | 0.9877 | -0.23393 | 1.9782
7 | -0.091775 | -0.023469 | 0.091869 | 0.023529 | 9.3878e-05 | 5.9913e-05 | 0.13806 | 0.13806 | 0.13806 | 0.99039 | -0.18222 | 0.9915 | -0.1611 | 37.9274
8 | 0.076979 | 0.019559 | -0.076745 | -0.01941 | 0.00023327 | 0.00014871 | 0.11656 | 0.11656 | 0.11656 | 0.98354 | -0.31388 | 0.98028 | -0.37703 | 32.0216
9 | 0.00030492 | 7.5908e-05 | -0.00030492 | -7.6419e-05 | 3.1683e-09 | -5.1119e-07 | 0.00045906 | 0.00045924 | 0.00045924 | 0.988 | -0.22825 | 0.98798 | -0.22847 | 0.12616
10 | 0.0017383 | 0.00043504 | -0.0017382 | -0.0004354 | 8.1501e-08 | -3.5393e-07 | 0.0026178 | 0.002618 | 0.002618 | 0.988 | -0.22825 | 0.98795 | -0.22923 | 0.71923
11 | 0.0047802 | 0.0011961 | -0.0047796 | -0.0011961 | 5.4781e-07 | -9.9277e-09 | 0.0072008 | 0.007201 | 0.007201 | 0.9877 | -0.23393 | 0.98758 | -0.23634 | 1.9783
12 | -0.093933 | -0.024046 | 0.09418 | 0.024203 | 0.00024711 | 0.00015644 | 0.14115 | 0.14115 | 0.14115 | 0.9915 | -0.1611 | 0.99435 | -0.10693 | 19.3891
13 | 0.07398 | 0.018717 | -0.07391 | -0.018673 | 6.9903e-05 | 4.4552e-05 | 0.11236 | 0.11236 | 0.11236 | 0.98028 | -0.37703 | 0.97927 | -0.39674 | 30.8683
14 | 0.00056303 | 0.00014086 | -0.00056303 | -0.00014111 | 5.1762e-09 | -2.4249e-07 | 0.00084793 | 0.00084802 | 0.00084802 | 0.98795 | -0.22923 | 0.98794 | -0.22943 | 0.23297
15 | 0.0040294 | 0.0010081 | -0.0040288 | -0.0010082 | 5.2751e-07 | -1.5074e-07 | 0.0060705 | 0.0060707 | 0.0060707 | 0.98758 | -0.23634 | 0.98744 | -0.23909 | 1.6678
16 | -0.097187 | -0.024956 | 0.097265 | 0.025005 | 7.7262e-05 | 4.8313e-05 | 0.14565 | 0.14565 | 0.14565 | 0.99435 | -0.10693 | 0.99521 | -0.09057 | 13.3381
17 | 0.070917 | 0.017923 | -0.070831 | -0.017868 | 8.5884e-05 | 5.4718e-05 | 0.10781 | 0.10781 | 0.10781 | 0.97927 | -0.39674 | 0.97798 | -0.42203 | 29.619
18 | 0.14164 | 0.036036 | -0.14142 | -0.035897 | 0.00022089 | 0.00013987 | 0.21291 | 0.21291 | 0.21291 | 0.99079 | -0.17524 | 0.98911 | -0.20765 | 19.4974
19 | -0.15124 | -0.038444 | 0.15127 | 0.038458 | 2.2667e-05 | 1.4371e-05 | 0.22734 | 0.22734 | 0.22734 | 0.99079 | -0.17524 | 0.99096 | -0.17213 | 20.8183
20 | 0.13595 | 0.034527 | -0.13578 | -0.03442 | 0.00017014 | 0.00010764 | 0.20469 | 0.20469 | 0.20469 | 0.98911 | -0.20765 | 0.98775 | -0.23369 | 18.7446
21 | 0.012606 | 0.0031601 | -0.012602 | -0.0031582 | 3.5481e-06 | 1.9307e-06 | 0.018929 | 0.018929 | 0.018929 | 0.99096 | -0.17213 | 0.99065 | -0.17804 | 5.2002
22 | -0.16387 | -0.041618 | 0.16444 | 0.041982 | 0.00057284 | 0.00036368 | 0.24626 | 0.24626 | 0.24626 | 0.99096 | -0.17213 | 0.99474 | -0.099769 | 22.5517
23 | 0.13296 | 0.033713 | -0.13285 | -0.033638 | 0.00011805 | 7.4649e-05 | 0.20044 | 0.20044 | 0.20044 | 0.98775 | -0.23369 | 0.9868 | -0.25218 | 18.3557
24 | 0.0096329 | 0.0024141 | -0.0096314 | -0.0024134 | 1.4897e-06 | 7.0914e-07 | 0.014469 | 0.014469 | 0.014469 | 0.99065 | -0.17804 | 0.99048 | -0.18128 | 3.975
25 | -0.16725 | -0.042686 | 0.16738 | 0.042769 | 0.00013058 | 8.292e-05 | 0.25046 | 0.25046 | 0.25046 | 0.99474 | -0.099769 | 0.99559 | -0.083623 | 22.9362
26 | 0.12913 | 0.032707 | -0.12903 | -0.032644 | 9.9711e-05 | 6.301e-05 | 0.19484 | 0.19484 | 0.19484 | 0.9868 | -0.25218 | 0.98596 | -0.26827 | 17.8424
27 | 0.0050498 | 0.0012651 | -0.0050491 | -0.0012651 | 7.2709e-07 | 3.1791e-08 | 0.0075862 | 0.0075864 | 0.0075864 | 0.99048 | -0.18128 | 0.99033 | -0.18431 | 2.0842
28 | -0.17104 | -0.043685 | 0.1715 | 0.043977 | 0.00045924 | 0.00029172 | 0.25593 | 0.25593 | 0.25593 | 0.99559 | -0.083623 | 0.99851 | -0.028242 | 23.4366
29 | 0.12636 | 0.031974 | -0.12627 | -0.031917 | 9.1257e-05 | 5.7638e-05 | 0.19081 | 0.19081 | 0.19081 | 0.98596 | -0.26827 | 0.98519 | -0.28333 | 17.4735
30 | 0.0018755 | 0.00046971 | -0.0018754 | -0.00047002 | 8.3152e-08 | -3.0606e-07 | 0.0028179 | 0.002818 | 0.002818 | 0.99033 | -0.18431 | 0.99028 | -0.18524 | 0.77418
31 | -0.17593 | -0.045086 | 0.17596 | 0.045105 | 3.0364e-05 | 1.9295e-05 | 0.26252 | 0.26252 | 0.26252 | 0.99851 | -0.028242 | 0.9987 | -0.024682 | 24.0407
32 | -0.10072 | -0.025871 | 0.10074 | 0.025881 | 1.4927e-05 | 9.3489e-06 | 0.15082 | 0.15082 | 0.15082 | 0.99521 | -0.09057 | 0.99537 | -0.087518 | 13.8117
33 | -0.10169 | -0.026119 | 0.10169 | 0.02612 | 1.4688e-06 | 9.2027e-07 | 0.15225 | 0.15225 | 0.15225 | 0.99537 | -0.087518 | 0.99539 | -0.087221 | 13.9419
34 | 0.052846 | 0.013315 | -0.052798 | -0.013284 | 4.8376e-05 | 3.0706e-05 | 0.080038 | 0.080038 | 0.080038 | 0.98279 | -0.32986 | 0.98181 | -0.34902 | 21.9885
35 | -0.058604 | -0.014758 | 0.058652 | 0.014788 | 4.7055e-05 | 2.9913e-05 | 0.088756 | 0.088756 | 0.088756 | 0.98279 | -0.32986 | 0.98365 | -0.31308 | 24.3836
36 | 0.052798 | 0.013284 | -0.052759 | -0.013259 | 3.8629e-05 | 2.4519e-05 | 0.080038 | 0.080038 | 0.080038 | 0.98181 | -0.34902 | 0.98103 | -0.36434 | 21.9886
37 | -0.12133 | -0.030612 | 0.12134 | 0.030621 | 1.3169e-05 | 8.3092e-06 | 0.18361 | 0.18361 | 0.18361 | 0.98365 | -0.31308 | 0.98377 | -0.31082 | 16.8142
38 | 0.062676 | 0.015825 | -0.062631 | -0.015796 | 4.5606e-05 | 2.8502e-05 | 0.094855 | 0.094855 | 0.094855 | 0.98365 | -0.31308 | 0.98287 | -0.32828 | 13.0296
39 | 0.0091282 | 0.0022879 | -0.0091268 | -0.0022872 | 1.4431e-06 | 6.7018e-07 | 0.013846 | 0.013846 | 0.013846 | 0.98103 | -0.36434 | 0.98086 | -0.36766 | 3.8038
40 | 0.043631 | 0.010971 | -0.04362 | -0.010964 | 1.1436e-05 | 7.2313e-06 | 0.066193 | 0.066193 | 0.066193 | 0.98103 | -0.36434 | 0.98075 | -0.36983 | 18.1848
41 | 0.0017234 | 0.00043174 | -0.0017233 | -0.0004319 | 3.7003e-08 | -1.607e-07 | 0.0026066 | 0.0026067 | 0.0026067 | 0.98377 | -0.31082 | 0.98375 | -0.31127 | 0.71612
42 | -0.12306 | -0.031052 | 0.12323 | 0.031155 | 0.00016222 | 0.00010239 | 0.18622 | 0.18622 | 0.18622 | 0.98377 | -0.31082 | 0.98519 | -0.28333 | 17.0529
43 | 0.060711 | 0.015315 | -0.060687 | -0.0153 | 2.4783e-05 | 1.5465e-05 | 0.091949 | 0.09195 | 0.09195 | 0.98287 | -0.32828 | 0.98243 | -0.33681 | 12.6304
44 | 0.0054603 | 0.0013683 | -0.0054603 | -0.0013683 | 1.7674e-08 | 2.6421e-09 | 0.0082836 | 0.0082836 | 0.0082836 | 0.98086 | -0.36766 | 0.98085 | -0.36773 | 2.2757
45 | 0.039757 | 0.009996 | -0.039728 | -0.0099779 | 2.8617e-05 | 1.805e-05 | 0.060332 | 0.060332 | 0.060332 | 0.98075 | -0.36983 | 0.97997 | -0.38492 | 16.5746
46 | 0.059344 | 0.014963 | -0.059231 | -0.014892 | 0.00011229 | 7.1399e-05 | 0.089915 | 0.089915 | 0.089915 | 0.98243 | -0.33681 | 0.9804 | -0.37643 | 24.702
47 | 0.0029637 | 0.00074261 | -0.0029636 | -0.00074275 | 1.3312e-07 | -1.3643e-07 | 0.0044961 | 0.0044962 | 0.0044962 | 0.98085 | -0.36773 | 0.98081 | -0.36867 | 1.2352
48 | 0.036853 | 0.0092573 | -0.036847 | -0.0092534 | 6.2874e-06 | 3.9565e-06 | 0.055966 | 0.055966 | 0.055966 | 0.97997 | -0.38492 | 0.97979 | -0.38849 | 15.3752
49 | -0.0023307 | -0.00058389 | 0.0023309 | 0.0005836 | 1.4285e-07 | -2.924e-07 | 0.0035376 | 0.0035375 | 0.0035376 | 0.98034 | -0.37772 | 0.9804 | -0.37643 | 0.97187
50 | 0.0023307 | 0.00058389 | -0.0023306 | -0.00058411 | 1.0506e-07 | -2.1499e-07 | 0.0035376 | 0.0035377 | 0.0035377 | 0.98034 | -0.37772 | 0.98029 | -0.37866 | 0.9719
51 | 0.0098116 | 0.0024542 | -0.00981 | -0.0024534 | 1.6381e-06 | 8e-07 | 0.01489 | 0.01489 | 0.01489 | 0.9804 | -0.37643 | 0.98023 | -0.37994 | 4.0907
52 | 0.047089 | 0.011854 | -0.047069 | -0.011841 | 1.9713e-05 | 1.2486e-05 | 0.071488 | 0.071488 | 0.071488 | 0.9804 | -0.37643 | 0.97996 | -0.38519 | 19.6396
53 | -0.0028788 | -0.00071722 | 0.0028791 | 0.0007169 | 2.8857e-07 | -3.2247e-07 | 0.0043712 | 0.004371 | 0.0043712 | 0.97965 | -0.39126 | 0.97976 | -0.38915 | 1.2009
54 | 0.0023692 | 0.0005895 | -0.0023683 | -0.0005913 | 9.2301e-07 | -1.8027e-06 | 0.0035971 | 0.003598 | 0.003598 | 0.97965 | -0.39126 | 0.97923 | -0.39948 | 0.98846
55 | -0.0037222 | -0.00092798 | 0.0037226 | 0.0009278 | 4.4202e-07 | -1.8198e-07 | 0.0056513 | 0.0056511 | 0.0056513 | 0.97976 | -0.38915 | 0.97989 | -0.38665 | 1.5526
56 | 0.00084304 | 0.00021108 | -0.00084304 | -0.00021115 | 3.1135e-09 | -6.1794e-08 | 0.0012803 | 0.0012803 | 0.0012803 | 0.97976 | -0.38915 | 0.97975 | -0.38923 | 0.35174
57 | 0.0017106 | 0.00042648 | -0.0017102 | -0.00042844 | 4.5529e-07 | -1.969e-06 | 0.0025986 | 0.0025994 | 0.0025994 | 0.97923 | -0.39948 | 0.97895 | -0.40508 | 0.71413
58 | -0.0055635 | -0.0013892 | 0.0055649 | 0.0013894 | 1.3713e-06 | 2.3179e-07 | 0.0084467 | 0.0084464 | 0.0084467 | 0.97989 | -0.38665 | 0.98015 | -0.38146 | 2.3205
59 | 0.00084304 | 0.00021115 | -0.00084303 | -0.00021128 | 6.8877e-09 | -1.3669e-07 | 0.0012803 | 0.0012804 | 0.0012804 | 0.97975 | -0.38923 | 0.97975 | -0.3894 | 0.35175
60 | -0.0011928 | -0.00029895 | 0.0011928 | 0.00029879 | 1.6872e-08 | -1.6128e-07 | 0.0018131 | 0.0018131 | 0.0018131 | 0.97893 | -0.40537 | 0.97895 | -0.40508 | 0.49811
61 | -0.0098093 | -0.002453 | 0.00981 | 0.0024534 | 7.0769e-07 | 3.4563e-07 | 0.01489 | 0.01489 | 0.01489 | 0.98015 | -0.38146 | 0.98023 | -0.37994 | 4.0907
62 | 0.0042444 | 0.0010636 | -0.0042441 | -0.0010637 | 2.9993e-07 | -5.0808e-08 | 0.0064436 | 0.0064437 | 0.0064437 | 0.98015 | -0.38146 | 0.98007 | -0.38294 | 1.7703
63 | 0.0028505 | 0.00071441 | -0.0028505 | -0.00071441 | 1.9546e-09 | -2.2561e-09 | 0.0043279 | 0.0043279 | 0.0043279 | 0.98007 | -0.38294 | 0.98007 | -0.38296 | 1.189
64 | 0.0057262 | 0.0014349 | -0.0057258 | -0.0014348 | 4.7203e-07 | 9.2357e-08 | 0.0086949 | 0.008695 | 0.008695 | 0.97996 | -0.38519 | 0.97987 | -0.38692 | 2.3887
65 | 0.041343 | 0.010407 | -0.041321 | -0.010393 | 2.1969e-05 | 1.3873e-05 | 0.062793 | 0.062793 | 0.062793 | 0.97996 | -0.38519 | 0.97939 | -0.39632 | 17.2509
66 | 0.0028574 | 0.00071596 | -0.0028572 | -0.00071609 | 1.169e-07 | -1.3374e-07 | 0.0043391 | 0.0043392 | 0.0043392 | 0.97987 | -0.38692 | 0.97982 | -0.38778 | 1.1921
67 | 0.037947 | 0.0095471 | -0.037918 | -0.0095286 | 2.9398e-05 | 1.8519e-05 | 0.057667 | 0.057668 | 0.057668 | 0.97939 | -0.39632 | 0.97856 | -0.41254 | 15.8427
68 | -0.0011291 | -0.00028297 | 0.0011291 | 0.00028263 | 3.0716e-08 | -3.4192e-07 | 0.0017019 | 0.0017018 | 0.0017019 | 0.98717 | -0.24428 | 0.9872 | -0.24371 | 0.46756
69 | -0.0013788 | -0.00034521 | 0.0013788 | 0.00034515 | 7.9782e-09 | -5.788e-08 | 0.0020782 | 0.0020781 | 0.0020782 | 0.9872 | -0.24371 | 0.98721 | -0.24359 | 0.57092
70 | -0.0017629 | -0.00044142 | 0.0017629 | 0.00044139 | 8.2218e-09 | -3.4444e-08 | 0.0026571 | 0.0026571 | 0.0026571 | 0.98721 | -0.24359 | 0.98721 | -0.24349 | 0.72997
71 | 0.0022247 | 0.00055633 | -0.0022244 | -0.00055705 | 3.0083e-07 | -7.2019e-07 | 0.0033524 | 0.0033527 | 0.0033527 | 0.98736 | -0.24065 | 0.98721 | -0.24349 | 0.92107
72 | -0.0026218 | -0.00065584 | 0.0026218 | 0.00065578 | 4.3946e-08 | -6.7903e-08 | 0.0039508 | 0.0039507 | 0.0039508 | 0.98736 | -0.24065 | 0.98738 | -0.2403 | 1.0854
73 | -0.0030643 | -0.00076666 | 0.0030644 | 0.00076655 | 1.1923e-07 | -1.1443e-07 | 0.0046175 | 0.0046175 | 0.0046175 | 0.98738 | -0.2403 | 0.98742 | -0.23948 | 1.2686
74 | -0.032499 | -0.0081583 | 0.032503 | 0.008161 | 4.4049e-06 | 2.759e-06 | 0.049472 | 0.049471 | 0.049472 | 0.9776 | -0.43135 | 0.97775 | -0.42851 | 13.5911
75 | 0.030635 | 0.0076911 | -0.030614 | -0.0076784 | 2.0331e-05 | 1.2699e-05 | 0.046634 | 0.046634 | 0.046634 | 0.9776 | -0.43135 | 0.97689 | -0.44527 | 12.8116
76 | -0.03653 | -0.0091703 | 0.036558 | 0.0091878 | 2.7844e-05 | 1.7518e-05 | 0.0556 | 0.0556 | 0.0556 | 0.97775 | -0.42851 | 0.97856 | -0.41254 | 15.2747
77 | 0.028608 | 0.0071757 | -0.028605 | -0.0071733 | 3.7823e-06 | 2.3542e-06 | 0.043579 | 0.043579 | 0.043579 | 0.97689 | -0.44527 | 0.97675 | -0.44805 | 11.9722
78 | 0.025046 | 0.0062815 | -0.025037 | -0.0062756 | 9.5452e-06 | 5.8902e-06 | 0.038158 | 0.038158 | 0.038158 | 0.97675 | -0.44805 | 0.97635 | -0.45605 | 10.483
79 | 0.025037 | 0.0062756 | -0.025028 | -0.00627 | 9.1678e-06 | 5.6575e-06 | 0.038158 | 0.038158 | 0.038158 | 0.97635 | -0.45605 | 0.97596 | -0.46374 | 10.483
80 | 0.023647 | 0.0059239 | -0.023639 | -0.005919 | 7.965e-06 | 4.8935e-06 | 0.036053 | 0.036053 | 0.036053 | 0.97596 | -0.46374 | 0.9756 | -0.47081 | 9.9047
81 | 0.031192 | 0.0078362 | -0.031166 | -0.00782 | 2.6054e-05 | 1.6285e-05 | 0.047378 | 0.047378 | 0.047378 | 0.97979 | -0.38849 | 0.9789 | -0.40601 | 13.0161
82 | 0.028753 | 0.0072152 | -0.028743 | -0.0072093 | 9.4635e-06 | 5.8907e-06 | 0.04371 | 0.04371 | 0.04371 | 0.9789 | -0.40601 | 0.97855 | -0.41291 | 12.0083
83 | 0.021963 | 0.0055099 | -0.021958 | -0.005507 | 4.8404e-06 | 2.9525e-06 | 0.0334 | 0.0334 | 0.0334 | 0.97855 | -0.41291 | 0.97831 | -0.41754 | 9.1757
84 | -0.019323 | -0.0048313 | 0.019326 | 0.0048334 | 3.4337e-06 | 2.0663e-06 | 0.029493 | 0.029493 | 0.029493 | 0.97476 | -0.48735 | 0.97495 | -0.48362 | 8.1025
85 | 0.016992 | 0.0042472 | -0.016988 | -0.0042448 | 4.0393e-06 | 2.3856e-06 | 0.025935 | 0.025935 | 0.025935 | 0.97476 | -0.48735 | 0.97451 | -0.49236 | 7.125
86 | -0.021767 | -0.0054451 | 0.02178 | 0.0054532 | 1.3271e-05 | 8.0931e-06 | 0.033218 | 0.033218 | 0.033218 | 0.97495 | -0.48362 | 0.9756 | -0.47081 | 9.1259
87 | 0.011066 | 0.002774 | -0.011065 | -0.0027732 | 1.5169e-06 | 7.9434e-07 | 0.016898 | 0.016898 | 0.016898 | 0.97451 | -0.49236 | 0.97436 | -0.49523 | 4.6423
88 | 0.0059216 | 0.0014708 | -0.0059212 | -0.0014707 | 4.7256e-07 | 1.1022e-07 | 0.0090373 | 0.0090373 | 0.0090373 | 0.97451 | -0.49236 | 0.97442 | -0.49404 | 2.4828
89 | 0.0088361 | 0.0022146 | -0.0088361 | -0.0022146 | 3.4368e-08 | 1.5727e-08 | 0.013494 | 0.013494 | 0.013494 | 0.97436 | -0.49523 | 0.97436 | -0.49532 | 3.7072
90 | 0.0024113 | 0.00059107 | -0.0024112 | -0.00059131 | 1.3128e-07 | -2.384e-07 | 0.0036775 | 0.0036776 | 0.0036776 | 0.97442 | -0.49404 | 0.97436 | -0.4952 | 1.0103
91 | 0.0067266 | 0.0016859 | -0.0067259 | -0.0016857 | 6.8959e-07 | 2.2433e-07 | 0.010273 | 0.010273 | 0.010273 | 0.97436 | -0.49532 | 0.97425 | -0.49747 | 2.8222
92 | 0.0024112 | 0.00059131 | -0.0024086 | -0.00059606 | 2.6255e-06 | -4.7556e-06 | 0.0036776 | 0.0036799 | 0.0036799 | 0.97436 | -0.4952 | 0.9732 | -0.51837 | 1.011
93 | 0.00027372 | 6.1022e-05 | -0.00027371 | -6.1713e-05 | 3.6196e-09 | -6.9063e-07 | 0.00041592 | 0.00041614 | 0.00041614 | 0.9732 | -0.51837 | 0.97319 | -0.51867 | 0.11432
94 | -0.0048561 | -0.0012171 | 0.0048561 | 0.0012171 | 8.1529e-09 | 2.3003e-10 | 0.0073921 | 0.0073921 | 0.0073921 | 0.97752 | -0.433 | 0.97753 | -0.43297 | 2.0308
95 | -0.0064825 | -0.0016247 | 0.0064831 | 0.0016248 | 6.2108e-07 | 1.8424e-07 | 0.0098678 | 0.0098677 | 0.0098678 | 0.97753 | -0.43297 | 0.97763 | -0.43095 | 2.7109
96 | -0.01403 | -0.0035162 | 0.014032 | 0.0035176 | 2.4322e-06 | 1.3782e-06 | 0.021354 | 0.021354 | 0.021354 | 0.97763 | -0.43095 | 0.97781 | -0.42732 | 5.8665
97 | 0.018307 | 0.004592 | -0.018299 | -0.0045869 | 8.5298e-06 | 5.0909e-06 | 0.027847 | 0.027847 | 0.027847 | 0.97831 | -0.41754 | 0.97781 | -0.42732 | 7.6503
98 | 6.7749e-05 | 1.3448e-05 | -6.7749e-05 | -1.3548e-05 | 3.1741e-11 | -1.0015e-07 | 0.00010245 | 0.00010248 | 0.00010248 | 0.97312 | -0.5201 | 0.97312 | -0.52011 | 0.028153
99 | -0.00027369 | -6.5062e-05 | 0.00027371 | 6.1713e-05 | 1.7614e-08 | -3.3497e-06 | 0.00041727 | 0.00041614 | 0.00041727 | 0.97312 | -0.5201 | 0.97319 | -0.51867 | 0.11463
100 | 6.7749e-05 | 1.3548e-05 | -6.7748e-05 | -1.6842e-05 | 1.0549e-09 | -3.2943e-06 | 0.00010248 | 0.00010355 | 0.00010355 | 0.97312 | -0.52011 | 0.97311 | -0.52046 | 0.028447
101 | 6.7748e-05 | 1.6842e-05 | -6.7748e-05 | -1.6979e-05 | 4.4407e-11 | -1.3712e-07 | 0.00010355 | 0.0001036 | 0.0001036 | 0.97311 | -0.52046 | 0.9731 | -0.52048 | 0.028461
102 | -0.10371 | -0.026626 | 0.10376 | 0.026654 | 4.4899e-05 | 2.8154e-05 | 0.15526 | 0.15526 | 0.15526 | 0.99539 | -0.087221 | 0.99586 | -0.078306 | 14.2183
103 | -0.10623 | -0.027275 | 0.10624 | 0.027278 | 4.7445e-06 | 2.9779e-06 | 0.15896 | 0.15896 | 0.15896 | 0.99586 | -0.078306 | 0.99591 | -0.077386 | 14.5569
104 | 0.067714 | 0.017087 | -0.067646 | -0.017043 | 6.7838e-05 | 4.3203e-05 | 0.10307 | 0.10307 | 0.10307 | 0.97798 | -0.42203 | 0.97691 | -0.44297 | 28.3161
105 | 0.061832 | 0.015586 | -0.061803 | -0.015568 | 2.9308e-05 | 1.8647e-05 | 0.094214 | 0.094215 | 0.094215 | 0.97691 | -0.44297 | 0.9764 | -0.45288 | 25.8831
106 | 0.058186 | 0.014661 | -0.058117 | -0.014617 | 6.863e-05 | 4.3633e-05 | 0.088702 | 0.088702 | 0.088702 | 0.9764 | -0.45288 | 0.97514 | -0.47757 | 24.3688
107 | -0.1087 | -0.027895 | 0.1087 | 0.027896 | 2.4228e-06 | 1.522e-06 | 0.16264 | 0.16264 | 0.16264 | 0.99591 | -0.077386 | 0.99593 | -0.076927 | 14.894
108 | -0.11121 | -0.028524 | 0.11127 | 0.028564 | 6.2504e-05 | 3.9297e-05 | 0.16639 | 0.16639 | 0.16639 | 0.99593 | -0.076927 | 0.99654 | -0.065346 | 15.2368
109 | -0.11388 | -0.029218 | 0.11389 | 0.029227 | 1.534e-05 | 9.652e-06 | 0.17028 | 0.17028 | 0.17028 | 0.99654 | -0.065346 | 0.99669 | -0.06257 | 15.5936
110 | -0.11691 | -0.029983 | 0.11698 | 0.030026 | 6.8478e-05 | 4.3124e-05 | 0.17478 | 0.17478 | 0.17478 | 0.99669 | -0.06257 | 0.99733 | -0.0505 | 16.0056
111 | -0.12046 | -0.030898 | 0.12047 | 0.030904 | 8.9837e-06 | 5.6627e-06 | 0.17998 | 0.17998 | 0.17998 | 0.99733 | -0.0505 | 0.99741 | -0.048963 | 16.4813
112 | -0.12298 | -0.031534 | 0.12314 | 0.031636 | 0.00016309 | 0.00010286 | 0.18372 | 0.18372 | 0.18372 | 0.99741 | -0.048963 | 0.99885 | -0.021653 | 16.8244
113 | -0.12973 | -0.033287 | 0.1298 | 0.033335 | 7.6181e-05 | 4.8116e-05 | 0.19353 | 0.19353 | 0.19353 | 0.99885 | -0.021653 | 0.99949 | -0.0095575 | 17.723
114 | -0.13414 | -0.034422 | 0.1342 | 0.034461 | 6.2239e-05 | 3.9343e-05 | 0.19999 | 0.19999 | 0.19999 | 0.99949 | -0.0095575 | 1 | 0 | 18.3141
115 | 0.20924 | 0.053566 | -0.20899 | -0.053406 | 0.00024979 | 0.00015906 | 0.31175 | 0.31175 | 0.31175 | 1 | 0 | 0.9987 | -0.024682 | 28.5481
116 | 0.03303 | 0.0083011 | -0.033016 | -0.008292 | 1.4635e-05 | 9.1555e-06 | 0.049222 | 0.049222 | 0.049222 | 0.9987 | -0.024682 | 0.99821 | -0.033967 | 13.5225
117 | 0.029434 | 0.0073945 | -0.02941 | -0.007379 | 2.4864e-05 | 1.5463e-05 | 0.043884 | 0.043884 | 0.043884 | 0.99821 | -0.033967 | 0.99729 | -0.051683 | 12.056
118 | 0.025853 | 0.0064877 | -0.025845 | -0.0064826 | 8.3557e-06 | 5.1523e-06 | 0.038578 | 0.038578 | 0.038578 | 0.99729 | -0.051683 | 0.99694 | -0.058463 | 10.5983
119 | 0.0201 | 0.0050427 | -0.020096 | -0.0050403 | 4.1091e-06 | 2.4711e-06 | 0.030003 | 0.030003 | 0.030003 | 0.99694 | -0.058463 | 0.99672 | -0.062752 | 8.2425
120 | 0.0035583 | 0.00089029 | -0.0035583 | -0.00089032 | 6.5464e-08 | -3.5779e-08 | 0.0053617 | 0.0053617 | 0.0053617 | 0.98744 | -0.23909 | 0.98742 | -0.23948 | 1.473
121 | 0.014731 | 0.0036941 | -0.014727 | -0.0036914 | 4.6938e-06 | 2.6673e-06 | 0.022 | 0.022 | 0.022 | 0.99642 | -0.068441 | 0.99608 | -0.075129 | 6.0439
122 | -0.018163 | -0.0045543 | 0.018168 | 0.0045572 | 4.9263e-06 | 2.9202e-06 | 0.027125 | 0.027125 | 0.027125 | 0.99642 | -0.068441 | 0.99672 | -0.062752 | 7.452
123 | 0.010379 | 0.0026017 | -0.010376 | -0.0026005 | 2.3193e-06 | 1.1495e-06 | 0.015505 | 0.015505 | 0.015505 | 0.99608 | -0.075129 | 0.99583 | -0.07982 | 4.2595
124 | 0.0065492 | 0.0016414 | -0.0065486 | -0.0016412 | 5.9566e-07 | 1.6546e-07 | 0.0097861 | 0.0097862 | 0.0097862 | 0.99583 | -0.07982 | 0.99573 | -0.081729 | 2.6885
125 | 0.0029276 | 0.00073371 | -0.0029276 | -0.00073372 | 3.0753e-09 | -3.6052e-09 | 0.0043749 | 0.0043749 | 0.0043749 | 0.99573 | -0.081729 | 0.99573 | -0.081751 | 1.2019
126 | -0.011514 | -0.0028859 | 0.011514 | 0.0028861 | 3.2148e-07 | 1.7165e-07 | 0.01764 | 0.01764 | 0.01764 | 0.97126 | -0.5543 | 0.97128 | -0.55371 | 4.8463
127 | 0.0082352 | 0.0020642 | -0.008234 | -0.0020636 | 1.2306e-06 | 5.3248e-07 | 0.012617 | 0.012617 | 0.012617 | 0.97126 | -0.5543 | 0.9711 | -0.55743 | 3.4662
128 | -0.016306 | -0.0040869 | 0.016311 | 0.0040901 | 5.4593e-06 | 3.2051e-06 | 0.02498 | 0.02498 | 0.02498 | 0.97128 | -0.55371 | 0.97164 | -0.54669 | 6.8628
129 | 0.0055239 | 0.0013844 | -0.0055239 | -0.0013844 | 7.6847e-10 | 1.3616e-10 | 0.0084643 | 0.0084643 | 0.0084643 | 0.9711 | -0.55743 | 0.9711 | -0.55744 | 2.3254
130 | -0.020624 | -0.005171 | 0.020626 | 0.0051721 | 1.9112e-06 | 1.1599e-06 | 0.031585 | 0.031585 | 0.031585 | 0.97164 | -0.54669 | 0.97174 | -0.54474 | 8.6773
131 | 0.0032228 | 0.00080771 | -0.0032228 | -0.00080771 | 4.3216e-09 | -3.0807e-09 | 0.0049383 | 0.0049383 | 0.0049383 | 0.9711 | -0.55744 | 0.9711 | -0.55747 | 1.3567
132 | -0.0237 | -0.0059426 | 0.02371 | 0.0059486 | 9.7391e-06 | 5.9886e-06 | 0.036293 | 0.036293 | 0.036293 | 0.97174 | -0.54474 | 0.97217 | -0.53612 | 9.9705
133 | -0.028405 | -0.0071254 | 0.028405 | 0.0071254 | 6.8157e-08 | 4.2429e-08 | 0.043479 | 0.043479 | 0.043479 | 0.97217 | -0.53612 | 0.97218 | -0.53607 | 11.9449
134 | -0.033507 | -0.008404 | 0.03353 | 0.0084186 | 2.3311e-05 | 1.4626e-05 | 0.051288 | 0.051288 | 0.051288 | 0.97218 | -0.53607 | 0.97292 | -0.52149 | 14.0901
135 | -0.037674 | -0.0094573 | 0.037703 | 0.009475 | 2.8115e-05 | 1.7713e-05 | 0.057626 | 0.057626 | 0.057626 | 0.97292 | -0.52149 | 0.97371 | -0.50586 | 15.8314
136 | 0.0076743 | 0.0019235 | -0.0076735 | -0.0019231 | 8.488e-07 | 3.3857e-07 | 0.011728 | 0.011728 | 0.011728 | 0.97371 | -0.50586 | 0.97359 | -0.50818 | 3.222
137 | -0.045377 | -0.011398 | 0.045385 | 0.011403 | 7.751e-06 | 4.9072e-06 | 0.069354 | 0.069354 | 0.069354 | 0.97371 | -0.50586 | 0.97389 | -0.50228 | 19.0534
138 | 0.0047256 | 0.0011843 | -0.0047255 | -0.0011843 | 9.6308e-08 | 4.1622e-10 | 0.0072226 | 0.0072226 | 0.0072226 | 0.97359 | -0.50818 | 0.97357 | -0.5086 | 1.9842
139 | -0.050417 | -0.012665 | 0.050472 | 0.0127 | 5.503e-05 | 3.4911e-05 | 0.077044 | 0.077044 | 0.077044 | 0.97389 | -0.50228 | 0.97505 | -0.47943 | 21.1659
140 | 0.053597 | 0.013485 | -0.053593 | -0.013482 | 4.7597e-06 | 3.0225e-06 | 0.081805 | 0.081805 | 0.081805 | 0.97514 | -0.47757 | 0.97505 | -0.47943 | 22.474

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3487 | 0.088932

## res_load
| p_mw | q_mvar
0 | 0.0005966 | 0.00014952
1 | 0.00085913 | 0.00021532
2 | 0.0022 | 0.00055137
3 | 0.0037835 | 0.00094824
4 | 0.0020636 | 0.00051719
5 | 0.0027655 | 0.0006931
6 | 0.00030492 | 7.6419e-05
7 | 0.0011752 | 0.00029453
8 | 0.00075026 | 0.00018803
9 | 0.0030072 | 0.00075368
10 | 0.0029928 | 0.00075008
11 | 0.0096049 | 0.0024072
12 | 0.0054642 | 0.0013695
13 | 0.0028196 | 0.00070665
14 | 0.0029691 | 0.00074413
15 | 0.002808 | 0.00070375
16 | 0.0037172 | 0.00093163
17 | 0.0045816 | 0.0011482
18 | 0.0036557 | 0.00091621
19 | 0.0026698 | 0.0006691
20 | 0.0031736 | 0.00079538
21 | 0.0044272 | 0.0011096
22 | 0.0034591 | 0.00086693
23 | 0.00095115 | 0.00023838
24 | 0.005758 | 0.0014431
25 | 0.0019194 | 0.00048105
26 | 0.0036664 | 0.00091889
27 | 0.0038631 | 0.00096818
28 | 0.0018754 | 0.00047002
29 | 0.0017233 | 0.0004319
30 | 0.003041 | 0.00076214
31 | 0.0013431 | 0.00033662
32 | 0.0024966 | 0.00062571
33 | 0.0028752 | 0.0007206
34 | 0.0023306 | 0.00058411
35 | 0.00050961 | 0.00012772
36 | 0.00065766 | 0.00016483
37 | 0.0018409 | 0.00046137
38 | 0.0011928 | 0.00029895
39 | 0.00051733 | 0.00012966
40 | 0.00084303 | 0.00021128
41 | 0.0013936 | 0.00034926
42 | 0.0028505 | 0.00071441
43 | 0.0028684 | 0.00071889
44 | 0.0033737 | 0.00084552
45 | 0.0011291 | 0.00028297
46 | 0.0002497 | 6.258e-05
47 | 0.00038411 | 9.6266e-05
48 | 0.00039706 | 9.9513e-05
49 | 0.00046151 | 0.00011566
50 | 0.00044244 | 0.00011089
51 | 0.0018641 | 0.00046719
52 | 0.0040269 | 0.0010092
53 | 0.0020059 | 0.00050274
54 | 0.0013598 | 0.0003408
55 | 0.0035583 | 0.00089178
56 | 0.0013808 | 0.00034607
57 | 0.0056545 | 0.0014171
58 | 0.0024132 | 0.00060479
59 | 0.0067805 | 0.0016993
60 | 0.0029636 | 0.00074275
61 | 0.0023307 | 0.00058414
62 | 0.0024408 | 0.00061171
63 | 0.0018587 | 0.00046583
64 | 0.0022287 | 0.00055855
65 | 0.0035099 | 0.00087965
66 | 0.0021095 | 0.0005287
67 | 0.0067259 | 0.0016857
68 | 0.0021348 | 0.00053504
69 | 0.0028572 | 0.00071609
70 | 0.0048561 | 0.0012171
71 | 0.0016264 | 0.0004076
72 | 0.0075466 | 0.0018914
73 | 0.0036507 | 0.00091494
74 | 0.0042668 | 0.0010693
75 | 0.00020594 | 5.1615e-05
76 | 6.7748e-05 | 1.6979e-05
77 | 0.0020189 | 0.00050598
78 | 0.0024753 | 0.00062036
79 | 0.003117 | 0.0007812
80 | 0.0058142 | 0.0014572
81 | 0.0036171 | 0.00090653
82 | 0.0024632 | 0.00061734
83 | 0.0025058 | 0.00062803
84 | 0.0026097 | 0.00065405
85 | 0.0030132 | 0.00075518
86 | 0.0034822 | 0.00087272
87 | 0.0025116 | 0.00062946
88 | 0.0065868 | 0.0016508
89 | 0.0043363 | 0.0010868
90 | 0.0036118 | 0.0009052
91 | 0.0035811 | 0.00089751
92 | 0.0035561 | 0.00089125
93 | 0.0057451 | 0.0014399
94 | 0.00047049 | 0.00011792
95 | 0.00049388 | 0.00012378
96 | 0.00056303 | 0.00014111
97 | 0.0034322 | 0.00086019
98 | 0.004348 | 0.0010897
99 | 0.0019275 | 0.00048307
100 | 0.003827 | 0.00095915
101 | 0.003621 | 0.00090752
102 | 0.0029276 | 0.00073372
103 | 0.003279 | 0.00082179
104 | 0.0047911 | 0.0012008
105 | 0.0027101 | 0.00067921
106 | 0.0043129 | 0.0010809
107 | 0.0023011 | 0.00057671
108 | 0.0030743 | 0.00077048
109 | 0.0032228 | 0.00080771
110 | 0.0046952 | 0.0011767
111 | 0.0051016 | 0.0012786
112 | 0.0041444 | 0.0010387
113 | 0.0029479 | 0.0007388
114 | 0.0050327 | 0.0012613
115 | 0.0045198 | 0.0011328
116 | 0.0031202 | 0.000782
117 | 0.0047255 | 0.0011843

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1