## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1301-17_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1301-17_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1301-17_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1301-17_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1301-17_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1301-17_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1301-17_0_4_node_59 | 0.4 | n |  | TRUE
7 | bus_LV_1301-17_0_4_node_122 | 0.4 | n |  | TRUE
8 | bus_LV_1301-17_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1301-17_0_4_node_57 | 0.4 | n |  | TRUE
10 | bus_LV_1301-17_0_4_node_56 | 0.4 | n |  | TRUE
11 | bus_LV_1301-17_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1301-17_0_4_node_55 | 0.4 | n |  | TRUE
13 | bus_LV_1301-17_0_4_node_124 | 0.4 | n |  | TRUE
14 | bus_LV_1301-17_0_4_node_84 | 0.4 | n |  | TRUE
15 | bus_LV_1301-17_0_4_node_54 | 0.4 | n |  | TRUE
16 | bus_LV_1301-17_0_4_node_86 | 0.4 | n |  | TRUE
17 | bus_LV_1301-17_0_4_node_83 | 0.4 | n |  | TRUE
18 | bus_LV_1301-17_0_4_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_1301-17_0_4_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_1301-17_0_4_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_1301-17_0_4_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_1301-17_0_4_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_1301-17_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_1301-17_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_1301-17_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1301-17_0_4_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_1301-17_0_4_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_1301-17_0_4_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_1301-17_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1301-17_0_4_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_1301-17_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1301-17_0_4_node_120 | 0.4 | n |  | TRUE
33 | bus_LV_1301-17_0_4_node_119 | 0.4 | n |  | TRUE
34 | bus_LV_1301-17_0_4_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_1301-17_0_4_node_117 | 0.4 | n |  | TRUE
36 | bus_LV_1301-17_0_4_node_118 | 0.4 | n |  | TRUE
37 | bus_LV_1301-17_0_4_node_116 | 0.4 | n |  | TRUE
38 | bus_LV_1301-17_0_4_node_121 | 0.4 | n |  | TRUE
39 | bus_LV_1301-17_0_4_node_114 | 0.4 | n |  | TRUE
40 | bus_LV_1301-17_0_4_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_1301-17_0_4_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_1301-17_0_4_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_1301-17_0_4_node_99 | 0.4 | n |  | TRUE
44 | bus_LV_1301-17_0_4_node_103 | 0.4 | n |  | TRUE
45 | bus_LV_1301-17_0_4_node_100 | 0.4 | n |  | TRUE
46 | bus_LV_1301-17_0_4_node_98 | 0.4 | n |  | TRUE
47 | bus_LV_1301-17_0_4_node_115 | 0.4 | n |  | TRUE
48 | bus_LV_1301-17_0_4_node_110 | 0.4 | n |  | TRUE
49 | bus_LV_1301-17_0_4_node_109 | 0.4 | n |  | TRUE
50 | bus_LV_1301-17_0_4_node_113 | 0.4 | n |  | TRUE
51 | bus_LV_1301-17_0_4_node_112 | 0.4 | n |  | TRUE
52 | bus_LV_1301-17_0_4_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_1301-17_0_4_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_1301-17_0_4_node_22 | 0.4 | n |  | TRUE
55 | bus_LV_1301-17_0_4_node_23 | 0.4 | n |  | TRUE
56 | bus_LV_1301-17_0_4_node_24 | 0.4 | n |  | TRUE
57 | bus_LV_1301-17_0_4_node_25 | 0.4 | n |  | TRUE
58 | bus_LV_1301-17_0_4_node_26 | 0.4 | n |  | TRUE
59 | bus_LV_1301-17_0_4_node_27 | 0.4 | n |  | TRUE
60 | bus_LV_1301-17_0_4_node_41 | 0.4 | n |  | TRUE
61 | bus_LV_1301-17_0_4_node_33 | 0.4 | n |  | TRUE
62 | bus_LV_1301-17_0_4_node_30 | 0.4 | n |  | TRUE
63 | bus_LV_1301-17_0_4_node_44 | 0.4 | n |  | TRUE
64 | bus_LV_1301-17_0_4_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_1301-17_0_4_node_79 | 0.4 | n |  | TRUE
66 | bus_LV_1301-17_0_4_node_34 | 0.4 | n |  | TRUE
67 | bus_LV_1301-17_0_4_node_62 | 0.4 | n |  | TRUE
68 | bus_LV_1301-17_0_4_node_35 | 0.4 | n |  | TRUE
69 | bus_LV_1301-17_0_4_node_36 | 0.4 | n |  | TRUE
70 | bus_LV_1301-17_0_4_node_31 | 0.4 | n |  | TRUE
71 | bus_LV_1301-17_0_4_node_42 | 0.4 | n |  | TRUE
72 | bus_LV_1301-17_0_4_node_97 | 0.4 | n |  | TRUE
73 | bus_LV_1301-17_0_4_node_107 | 0.4 | n |  | TRUE
74 | bus_LV_1301-17_0_4_node_111 | 0.4 | n |  | TRUE
75 | bus_LV_1301-17_0_4_node_106 | 0.4 | n |  | TRUE
76 | bus_LV_1301-17_0_4_node_108 | 0.4 | n |  | TRUE
77 | bus_LV_1301-17_0_4_node_96 | 0.4 | n |  | TRUE
78 | bus_LV_1301-17_0_4_node_80 | 0.4 | n |  | TRUE
79 | bus_LV_1301-17_0_4_node_101 | 0.4 | n |  | TRUE
80 | bus_LV_1301-17_0_4_node_102 | 0.4 | n |  | TRUE
81 | bus_LV_1301-17_0_4_node_104 | 0.4 | n |  | TRUE
82 | bus_LV_1301-17_0_4_node_105 | 0.4 | n |  | TRUE
83 | bus_LV_1301-17_0_4_node_82 | 0.4 | n |  | TRUE
84 | bus_LV_1301-17_0_4_node_32 | 0.4 | n |  | TRUE
85 | bus_LV_1301-17_0_4_node_72 | 0.4 | n |  | TRUE
86 | bus_LV_1301-17_0_4_node_73 | 0.4 | n |  | TRUE
87 | bus_LV_1301-17_0_4_node_74 | 0.4 | n |  | TRUE
88 | bus_LV_1301-17_0_4_node_77 | 0.4 | n |  | TRUE
89 | bus_LV_1301-17_0_4_node_78 | 0.4 | n |  | TRUE
90 | bus_LV_1301-17_0_4_node_123 | 0.4 | n |  | TRUE
91 | bus_LV_1301-17_0_4_node_93 | 0.4 | n |  | TRUE
92 | bus_LV_1301-17_0_4_node_91 | 0.4 | n |  | TRUE
93 | bus_LV_1301-17_0_4_node_92 | 0.4 | n |  | TRUE
94 | bus_LV_1301-17_0_4_node_94 | 0.4 | n |  | TRUE
95 | bus_LV_1301-17_0_4_node_95 | 0.4 | n |  | TRUE
96 | bus_LV_1301-17_0_4_node_65 | 0.4 | n |  | TRUE
97 | bus_LV_1301-17_0_4_node_64 | 0.4 | n |  | TRUE
98 | bus_LV_1301-17_0_4_node_39 | 0.4 | n |  | TRUE
99 | bus_LV_1301-17_0_4_node_43 | 0.4 | n |  | TRUE
100 | bus_LV_1301-17_0_4_node_45 | 0.4 | n |  | TRUE
101 | bus_LV_1301-17_0_4_node_47 | 0.4 | n |  | TRUE
102 | bus_LV_1301-17_0_4_node_48 | 0.4 | n |  | TRUE
103 | bus_LV_1301-17_0_4_node_49 | 0.4 | n |  | TRUE
104 | bus_LV_1301-17_0_4_node_50 | 0.4 | n |  | TRUE
105 | bus_LV_1301-17_0_4_node_52 | 0.4 | n |  | TRUE
106 | bus_LV_1301-17_0_4_node_53 | 0.4 | n |  | TRUE
107 | bus_LV_1301-17_0_4_node_90 | 0.4 | n |  | TRUE
108 | bus_LV_1301-17_0_4_node_60 | 0.4 | n |  | TRUE
109 | bus_LV_1301-17_0_4_node_61 | 0.4 | n |  | TRUE
110 | bus_LV_1301-17_0_4_node_63 | 0.4 | n |  | TRUE
111 | bus_LV_1301-17_0_4_node_125 | 0.4 | n |  | TRUE
112 | bus_LV_1301-17_0_4_node_89 | 0.4 | n |  | TRUE
113 | bus_LV_1301-17_0_4_node_69 | 0.4 | n |  | TRUE
114 | bus_LV_1301-17_0_4_node_66 | 0.4 | n |  | TRUE
115 | bus_LV_1301-17_0_4_node_71 | 0.4 | n |  | TRUE
116 | bus_LV_1301-17_0_4_node_70 | 0.4 | n |  | TRUE
117 | bus_LV_1301-17_0_4_node_67 | 0.4 | n |  | TRUE
118 | bus_LV_1301-17_0_4_node_68 | 0.4 | n |  | TRUE
119 | bus_LV_1301-17_0_4_node_85 | 0.4 | n |  | TRUE
120 | bus_LV_1301-17_0_4_node_87 | 0.4 | n |  | TRUE
121 | bus_LV_1301-17_0_4_node_88 | 0.4 | n |  | TRUE
122 | bus_MV_135_0_node_48 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1301-17_0_4_load_0 | 0 | 0.0004495 | 0.00011266 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1301-17_0_4_load_1 | 1 | 0.00019478 | 4.8816e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1301-17_0_4_load_3 | 3 | 0.00028425 | 7.1239e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1301-17_0_4_load_4 | 4 | 0.00022108 | 5.5409e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1301-17_0_4_load_5 | 5 | 0.00018173 | 4.5545e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1301-17_0_4_load_59 | 6 | 0.00026324 | 6.5975e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1301-17_0_4_load_122 | 7 | 0.00035339 | 8.8568e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1301-17_0_4_load_57 | 9 | 0.00019104 | 4.788e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1301-17_0_4_load_55 | 12 | 0.00042872 | 0.00010745 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1301-17_0_4_load_124 | 13 | 0.00030226 | 7.5754e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1301-17_0_4_load_86 | 16 | 0.001145 | 0.00028698 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1301-17_0_4_load_83 | 17 | 0.00017276 | 4.3298e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1301-17_0_4_load_8 | 18 | 0.0009992 | 0.00025042 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1301-17_0_4_load_9 | 19 | 0.0018408 | 0.00046135 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1301-17_0_4_load_10 | 20 | 0.0094416 | 0.0023663 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1301-17_0_4_load_11 | 21 | 0.0015965 | 0.00040012 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1301-17_0_4_load_12 | 22 | 0.0023561 | 0.00059049 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1301-17_0_4_load_13 | 23 | 0.0010926 | 0.00027384 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1301-17_0_4_load_15 | 25 | 0.00018443 | 4.6223e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1301-17_0_4_load_21 | 26 | 0.00014756 | 3.6983e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1301-17_0_4_load_16 | 28 | 0.0003032 | 7.5988e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1301-17_0_4_load_17 | 29 | 0.00034512 | 8.6495e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1301-17_0_4_load_19 | 30 | 0.00024126 | 6.0465e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1301-17_0_4_load_120 | 32 | 0.0019973 | 0.00050056 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1301-17_0_4_load_119 | 33 | 0.0012873 | 0.00032262 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1301-17_0_4_load_28 | 34 | 0.00022728 | 5.6962e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1301-17_0_4_load_117 | 35 | 0.00143 | 0.0003584 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1301-17_0_4_load_118 | 36 | 0.0028747 | 0.00072047 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1301-17_0_4_load_116 | 37 | 0.0028698 | 0.00071925 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1301-17_0_4_load_121 | 38 | 0.001187 | 0.00029749 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1301-17_0_4_load_40 | 40 | 0.00065158 | 0.0001633 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1301-17_0_4_load_37 | 41 | 0.0003941 | 9.8771e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1301-17_0_4_load_29 | 42 | 0.00025498 | 6.3903e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1301-17_0_4_load_103 | 44 | 0.0015672 | 0.00039277 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1301-17_0_4_load_100 | 45 | 0.0021671 | 0.00054313 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1301-17_0_4_load_98 | 46 | 0.0024092 | 0.0006038 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1301-17_0_4_load_115 | 47 | 0.0011229 | 0.00028142 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1301-17_0_4_load_110 | 48 | 0.0021995 | 0.00055125 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1301-17_0_4_load_109 | 49 | 0.0024648 | 0.00061774 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1301-17_0_4_load_113 | 50 | 0.0016052 | 0.00040231 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1301-17_0_4_load_112 | 51 | 0.001625 | 0.00040727 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1301-17_0_4_load_46 | 52 | 0.00045703 | 0.00011454 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1301-17_0_4_load_38 | 53 | 0.00015352 | 3.8476e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1301-17_0_4_load_22 | 54 | 0.00026629 | 6.6738e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1301-17_0_4_load_23 | 55 | 0.00029619 | 7.4232e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1301-17_0_4_load_25 | 57 | 0.00047979 | 0.00012025 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1301-17_0_4_load_41 | 60 | 0.00021175 | 5.307e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1301-17_0_4_load_30 | 62 | 0.0020282 | 0.00050831 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1301-17_0_4_load_44 | 63 | 0.00029714 | 7.447e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1301-17_0_4_load_51 | 64 | 0.0054477 | 0.0013653 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1301-17_0_4_load_31 | 70 | 0.0020976 | 0.0005257 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1301-17_0_4_load_42 | 71 | 0.0003507 | 8.7894e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1301-17_0_4_load_97 | 72 | 0.0010152 | 0.00025444 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1301-17_0_4_load_107 | 73 | 0.0016125 | 0.00040413 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1301-17_0_4_load_111 | 74 | 0.0021945 | 0.00055 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1301-17_0_4_load_106 | 75 | 0.0018044 | 0.00045224 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1301-17_0_4_load_108 | 76 | 0.0019169 | 0.00048042 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1301-17_0_4_load_101 | 79 | 0.0010927 | 0.00027385 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1301-17_0_4_load_102 | 80 | 0.0010077 | 0.00025256 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1301-17_0_4_load_104 | 81 | 0.00086151 | 0.00021591 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1301-17_0_4_load_105 | 82 | 0.0018116 | 0.00045402 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1301-17_0_4_load_82 | 83 | 0.00098195 | 0.0002461 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1301-17_0_4_load_32 | 84 | 0.00064185 | 0.00016086 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1301-17_0_4_load_72 | 85 | 0.0010084 | 0.00025274 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1301-17_0_4_load_73 | 86 | 0.0014129 | 0.00035411 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1301-17_0_4_load_74 | 87 | 0.0010912 | 0.00027347 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1301-17_0_4_load_77 | 88 | 0.00049736 | 0.00012465 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1301-17_0_4_load_123 | 90 | 0.00032978 | 8.2651e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1301-17_0_4_load_93 | 91 | 0.0010773 | 0.00027 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1301-17_0_4_load_91 | 92 | 0.00069871 | 0.00017511 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1301-17_0_4_load_92 | 93 | 0.001525 | 0.0003822 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1301-17_0_4_load_94 | 94 | 0.00085565 | 0.00021445 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1301-17_0_4_load_95 | 95 | 0.0007121 | 0.00017847 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1301-17_0_4_load_64 | 97 | 0.0021548 | 0.00054004 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1301-17_0_4_load_39 | 98 | 0.000537 | 0.00013459 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1301-17_0_4_load_43 | 99 | 0.00016968 | 4.2525e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1301-17_0_4_load_45 | 100 | 0.00055993 | 0.00014033 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1301-17_0_4_load_47 | 101 | 0.00048336 | 0.00012114 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1301-17_0_4_load_48 | 102 | 0.00082137 | 0.00020586 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1301-17_0_4_load_49 | 103 | 0.00037227 | 9.33e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1301-17_0_4_load_50 | 104 | 0.00078873 | 0.00019767 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1301-17_0_4_load_52 | 105 | 0.00047762 | 0.0001197 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1301-17_0_4_load_53 | 106 | 0.00034938 | 8.7564e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1301-17_0_4_load_60 | 108 | 0.00085158 | 0.00021343 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1301-17_0_4_load_125 | 111 | 0.0012321 | 0.00030879 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1301-17_0_4_load_69 | 113 | 0.00098314 | 0.0002464 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1301-17_0_4_load_66 | 114 | 0.00059898 | 0.00015012 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1301-17_0_4_load_71 | 115 | 0.00054571 | 0.00013677 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1301-17_0_4_load_70 | 116 | 0.0005669 | 0.00014208 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1301-17_0_4_load_67 | 117 | 0.00062331 | 0.00015622 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1301-17_0_4_load_68 | 118 | 0.00040673 | 0.00010194 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1301-17_0_4_load_88 | 121 | 0.00033541 | 8.4061e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1301-17_0_4_line_0 |  | 0 | 1 | 0.16707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1301-17_0_4_line_1 |  | 0 | 2 | 0.1418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1301-17_0_4_line_2 |  | 1 | 3 | 0.47793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1301-17_0_4_line_3 |  | 2 | 4 | 0.13088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1301-17_0_4_line_4 |  | 2 | 5 | 0.27584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1301-17_0_4_line_5 |  | 3 | 8 | 0.36346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1301-17_0_4_line_6 |  | 4 | 9 | 0.046468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1301-17_0_4_line_7 |  | 5 | 10 | 0.3893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1301-17_0_4_line_8 |  | 6 | 7 | 0.2447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1301-17_0_4_line_9 |  | 7 | 107 | 0.29425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1301-17_0_4_line_10 |  | 8 | 11 | 0.096802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1301-17_0_4_line_11 |  | 10 | 12 | 0.3633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1301-17_0_4_line_12 |  | 11 | 13 | 0.35695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1301-17_0_4_line_13 |  | 11 | 14 | 0.3135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1301-17_0_4_line_14 |  | 13 | 15 | 0.87687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1301-17_0_4_line_15 |  | 14 | 16 | 0.42454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1301-17_0_4_line_16 |  | 14 | 17 | 0.27453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1301-17_0_4_line_17 |  | 15 | 105 | 0.27346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1301-17_0_4_line_18 |  | 16 | 68 | 0.016605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1301-17_0_4_line_19 |  | 17 | 119 | 0.074627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1301-17_0_4_line_20 |  | 18 | 19 | 0.032309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1301-17_0_4_line_21 |  | 18 | 20 | 0.05328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1301-17_0_4_line_22 |  | 19 | 21 | 0.046378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1301-17_0_4_line_23 |  | 20 | 22 | 0.028491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1301-17_0_4_line_24 |  | 21 | 23 | 0.042428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1301-17_0_4_line_25 |  | 22 | 24 | 0.096001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1301-17_0_4_line_26 |  | 24 | 25 | 0.44062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1301-17_0_4_line_27 |  | 25 | 26 | 0.20212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1301-17_0_4_line_28 |  | 26 | 27 | 0.12179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1301-17_0_4_line_29 |  | 27 | 31 | 0.033202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1301-17_0_4_line_30 |  | 27 | 28 | 0.20778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1301-17_0_4_line_31 |  | 28 | 29 | 0.017246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_1301-17_0_4_line_32 |  | 29 | 30 | 0.043878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1301-17_0_4_line_33 |  | 30 | 34 | 0.018644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_1301-17_0_4_line_34 |  | 31 | 40 | 0.097353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1301-17_0_4_line_35 |  | 31 | 41 | 0.062796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1301-17_0_4_line_36 |  | 32 | 33 | 0.020784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1301-17_0_4_line_37 |  | 33 | 36 | 0.014762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1301-17_0_4_line_38 |  | 34 | 42 | 0.032991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_1301-17_0_4_line_39 |  | 35 | 36 | 0.003227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1301-17_0_4_line_40 |  | 35 | 37 | 0.021519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1301-17_0_4_line_41 |  | 37 | 47 | 0.0086084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1301-17_0_4_line_42 |  | 38 | 39 | 0.01099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1301-17_0_4_line_43 |  | 39 | 48 | 0.011371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1301-17_0_4_line_44 |  | 39 | 50 | 0.0075526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1301-17_0_4_line_45 |  | 40 | 52 | 0.013319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1301-17_0_4_line_46 |  | 41 | 53 | 0.01679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1301-17_0_4_line_47 |  | 42 | 59 | 0.010474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_1301-17_0_4_line_48 |  | 43 | 44 | 0.0053231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1301-17_0_4_line_49 |  | 43 | 45 | 0.082549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1301-17_0_4_line_50 |  | 43 | 46 | 0.035889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1301-17_0_4_line_51 |  | 44 | 47 | 0.0046292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1301-17_0_4_line_52 |  | 45 | 79 | 0.013578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1301-17_0_4_line_53 |  | 46 | 72 | 0.036931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_1301-17_0_4_line_54 |  | 48 | 49 | 0.033918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1301-17_0_4_line_55 |  | 49 | 76 | 0.050274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1301-17_0_4_line_56 |  | 50 | 51 | 0.026434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1301-17_0_4_line_57 |  | 51 | 74 | 0.025366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1301-17_0_4_line_58 |  | 53 | 98 | 0.016578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1301-17_0_4_line_59 |  | 54 | 55 | 0.011951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1301-17_0_4_line_60 |  | 54 | 56 | 0.03355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1301-17_0_4_line_61 |  | 55 | 57 | 0.02524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1301-17_0_4_line_62 |  | 56 | 58 | 0.072816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_1301-17_0_4_line_63 |  | 56 | 59 | 0.065256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_1301-17_0_4_line_64 |  | 57 | 60 | 0.0027163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1301-17_0_4_line_65 |  | 58 | 61 | 0.030773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_1301-17_0_4_line_66 |  | 58 | 62 | 0.017345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1301-17_0_4_line_67 |  | 59 | 63 | 0.017033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1301-17_0_4_line_68 |  | 61 | 64 | 0.026775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1301-17_0_4_line_69 |  | 61 | 65 | 0.55331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_1301-17_0_4_line_70 |  | 62 | 70 | 0.024331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1301-17_0_4_line_71 |  | 63 | 71 | 0.015466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1301-17_0_4_line_72 |  | 64 | 69 | 0.0082252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1301-17_0_4_line_73 |  | 65 | 90 | 0.3426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1301-17_0_4_line_74 |  | 65 | 89 | 0.004035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_1301-17_0_4_line_75 |  | 66 | 67 | 0.031754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1301-17_0_4_line_76 |  | 66 | 68 | 0.07279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1301-17_0_4_line_77 |  | 67 | 96 | 0.16261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1301-17_0_4_line_78 |  | 67 | 97 | 0.053751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1301-17_0_4_line_79 |  | 68 | 69 | 0.032473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1301-17_0_4_line_80 |  | 70 | 84 | 0.014144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1301-17_0_4_line_81 |  | 71 | 99 | 0.021423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1301-17_0_4_line_82 |  | 72 | 77 | 0.034719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_1301-17_0_4_line_83 |  | 73 | 74 | 0.0047391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1301-17_0_4_line_84 |  | 73 | 75 | 0.022621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1301-17_0_4_line_85 |  | 75 | 82 | 0.0011578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1301-17_0_4_line_86 |  | 76 | 83 | 0.026061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1301-17_0_4_line_87 |  | 77 | 78 | 0.073684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_1301-17_0_4_line_88 |  | 78 | 91 | 0.015564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1301-17_0_4_line_89 |  | 78 | 89 | 0.18586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_1301-17_0_4_line_90 |  | 79 | 80 | 0.017559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1301-17_0_4_line_91 |  | 80 | 81 | 0.0020695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1301-17_0_4_line_92 |  | 81 | 82 | 0.020883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1301-17_0_4_line_93 |  | 83 | 87 | 0.011377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1301-17_0_4_line_94 |  | 85 | 86 | 0.50402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1301-17_0_4_line_95 |  | 86 | 87 | 0.20221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1301-17_0_4_line_96 |  | 88 | 89 | 0.31952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1301-17_0_4_line_97 |  | 91 | 92 | 0.062424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1301-17_0_4_line_98 |  | 92 | 93 | 0.027228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1301-17_0_4_line_99 |  | 93 | 94 | 0.072056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1301-17_0_4_line_100 |  | 94 | 95 | 0.019335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1301-17_0_4_line_101 |  | 96 | 113 | 0.058826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1301-17_0_4_line_102 |  | 96 | 114 | 0.024899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1301-17_0_4_line_103 |  | 99 | 100 | 0.055819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1301-17_0_4_line_104 |  | 100 | 101 | 0.050306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1301-17_0_4_line_105 |  | 101 | 102 | 0.068646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1301-17_0_4_line_106 |  | 102 | 103 | 0.1055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1301-17_0_4_line_107 |  | 103 | 104 | 0.06033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1301-17_0_4_line_108 |  | 105 | 106 | 0.097314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1301-17_0_4_line_109 |  | 107 | 112 | 0.17981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1301-17_0_4_line_110 |  | 108 | 109 | 0.2797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1301-17_0_4_line_111 |  | 109 | 110 | 0.27634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1301-17_0_4_line_112 |  | 110 | 111 | 0.008379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1301-17_0_4_line_113 |  | 111 | 115 | 0.5442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1301-17_0_4_line_114 |  | 112 | 121 | 0.085105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1301-17_0_4_line_115 |  | 114 | 117 | 0.011588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1301-17_0_4_line_116 |  | 115 | 116 | 0.10186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1301-17_0_4_line_117 |  | 116 | 118 | 0.036775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1301-17_0_4_line_118 |  | 117 | 118 | 0.068022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1301-17_0_4_line_119 |  | 119 | 120 | 0.14913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1301-17_0_4_line_120 |  | 120 | 121 | 0.2338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1301-17_0_4_trafo_16 | 0.63 MVA 20/0.4 kV | 122 | 28 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31
0 | 2701671.154 | 1216362.5067 | 2701679.9045 | 1216367.1243 | 2701708.8553 | 1216377.192 | 2701725.9324 | 1216389.292 | 2701753.635 | 1216397.7375 | 2701784.4736 | 1216409.7503 | 2701821.4928 | 1216415.1419 | 2701825.8954 | 1216419.4091
1 | 2701542.3659 | 1216313.5084 | 2701554.7805 | 1216328.297 | 2701594.6597 | 1216335.6818 | 2701635.0172 | 1216343.5087 | 2701659.915 | 1216356.5758 | 2701671.154 | 1216362.5067
2 | 2701825.8954 | 1216419.4091 | 2701847.3243 | 1216440.1788 | 2701889.5535 | 1216459.7255 | 2701911.9017 | 1216463.2989 | 2701936.2667 | 1216460.8472 | 2701946.3998 | 1216448.256 | 2701957.4041 | 1216441.1058 | 2701963.7427 | 1216425.2696 | 2701966.9941 | 1216422.5344 | 2701971.1507 | 1216424.5958 | 2701973.6112 | 1216421.9249 | 2701975.6004 | 1216418.8457 | 2701981.0874 | 1216420.3739 | 2701986.1167 | 1216420.2488 | 2701988.2081 | 1216414.7473 | 2701990.3181 | 1216401.5074 | 2702001.6274 | 1216390.304 | 2702009.5544 | 1216380.6106 | 2702025.55 | 1216371.5779 | 2702042.5511 | 1216358.3818 | 2702040.2268 | 1216353.5385 | 2702048.7591 | 1216351.0717 | 2702056.6571 | 1216355.4879 | 2702065.7824 | 1216355.6442 | 2702077.7708 | 1216365.5343 | 2702087.5052 | 1216374.4629 | 2702098.8007 | 1216380.4718 | 2702142.6867 | 1216382.6474 | 2702153.2683 | 1216384.2299 | 2702177.0115 | 1216397.2461 | 2702207.2958 | 1216414.0772 | 2702209.4899 | 1216416.4338
3 | 2701542.3659 | 1216313.5084 | 2701535.511 | 1216317.8169 | 2701523.8052 | 1216317.1281 | 2701500.3686 | 1216310.0907 | 2701485.6392 | 1216305.9036 | 2701474.8143 | 1216303.8734 | 2701462.1942 | 1216306.4827 | 2701454.5806 | 1216311.6456 | 2701443.1005 | 1216319.5559 | 2701432.1932 | 1216322.817 | 2701419.3526 | 1216323.2099
4 | 2701542.3659 | 1216313.5084 | 2701546.6718 | 1216306.8214 | 2701547.3979 | 1216293.1797 | 2701547.6367 | 1216279.1738 | 2701551.4179 | 1216267.1853 | 2701560.1777 | 1216252.702 | 2701582.7231 | 1216225.1778 | 2701587.2484 | 1216213.202 | 2701590.1788 | 1216200.3428 | 2701594.2965 | 1216190.4504 | 2701600.3594 | 1216181.8254 | 2701608.072 | 1216175.33 | 2701637.6747 | 1216156.1544 | 2701659.7451 | 1216142.2654 | 2701674.1744 | 1216135.1286 | 2701689.776 | 1216131.8369 | 2701704.5856 | 1216131.3447 | 2701713.9898 | 1216129.4149
5 | 2702543.2218 | 1216560.4065 | 2702209.4899 | 1216416.4338
6 | 2701389.2201 | 1216354.4194 | 2701395.7793 | 1216338.92 | 2701402.3374 | 1216330.1809 | 2701409.206 | 1216325.5056 | 2701419.3526 | 1216323.2099 | 2701419.3526 | 1216323.2099
7 | 2701686.7106 | 1215877.6488 | 2701686.012 | 1215889.6565 | 2701684.3541 | 1215907.5854 | 2701681.5532 | 1215919.9575 | 2701680.392 | 1215930.1449 | 2701681.8156 | 1215940.6211 | 2701687.865 | 1215954.612 | 2701697.7659 | 1215967.2009 | 2701711.2406 | 1215979.9732 | 2701723.4423 | 1215987.6868 | 2701738.1892 | 1215990.8852 | 2701754.0553 | 1215995.6928 | 2701799.5543 | 1216015.6393 | 2701810.7348 | 1216024.8812 | 2701817.6049 | 1216037.93 | 2701820.4411 | 1216052.8335 | 2701814.2148 | 1216063.8794 | 2701782.4864 | 1216082.5064 | 2701753.9938 | 1216090.8814 | 2701743.6695 | 1216095.9866 | 2701732.8576 | 1216107.8549 | 2701722.3612 | 1216123.0421 | 2701713.9898 | 1216129.4149
8 | 2701752.1727 | 1217091.9578 | 2701752.2941 | 1217093.6313 | 2701722.8219 | 1217093.4058 | 2701687.6571 | 1217075.2595 | 2701681.9629 | 1217064.9995 | 2701678.6339 | 1217047.3969 | 2701644.2342 | 1217016.8773 | 2701595.9454 | 1216981.5178 | 2701564.6903 | 1216971.3779 | 2701559.065 | 1216971.1767
9 | 2701971.6657 | 1217032.7705 | 2701917.5058 | 1217030.4536 | 2701873.0206 | 1217034.2847 | 2701851.8593 | 1217038.248 | 2701847.575 | 1217051.6733 | 2701809.8987 | 1217041.4223 | 2701783.9155 | 1217024.9668 | 2701770.2867 | 1217021.8096 | 2701749.5838 | 1217056.2695 | 2701752.1727 | 1217091.9578
10 | 2702543.2218 | 1216560.4065 | 2702555.0575 | 1216559.2537 | 2702571.932 | 1216556.0974 | 2702578.5556 | 1216554.2211 | 2702595.6288 | 1216571.7163 | 2702612.2936 | 1216604.0929
11 | 2701686.7106 | 1215877.6488 | 2701343.1019 | 1215759.6713
12 | 2702612.2936 | 1216604.0929 | 2702628.2815 | 1216584.9545 | 2702634.9569 | 1216583.1571 | 2702644.9833 | 1216582.5627 | 2702698.8711 | 1216611.9007 | 2702703.3085 | 1216613.9453 | 2702714.4856 | 1216616.195 | 2702764.6086 | 1216612.8343 | 2702779.5164 | 1216607.9101 | 2702789.1753 | 1216600.8828 | 2702795.4678 | 1216593.1191 | 2702801.4419 | 1216581.8029 | 2702800.7934 | 1216574.4976 | 2702792.0623 | 1216555.9227 | 2702786.5379 | 1216541.6172 | 2702777.4811 | 1216530.909 | 2702775.1652 | 1216514.1682 | 2702774.9993 | 1216501.7788 | 2702774.0688 | 1216494.0906 | 2702769.7681 | 1216492.4819 | 2702765.5752 | 1216495.1893 | 2702763.7649 | 1216499.7614 | 2702761.8718 | 1216509.1354 | 2702754.923 | 1216526.7727
13 | 2702674.4294 | 1216897.6501 | 2702659.5832 | 1216873.4993 | 2702644.2641 | 1216837.1207 | 2702641.9359 | 1216816.6771 | 2702650.3905 | 1216776.4051 | 2702656.4368 | 1216734.4348 | 2702654.8754 | 1216715.3277 | 2702650.8001 | 1216699.3238 | 2702639.3502 | 1216678.5452 | 2702619.4182 | 1216644.9781 | 2702609.5671 | 1216622.6259 | 2702611.0604 | 1216610.8765 | 2702612.2936 | 1216604.0929
14 | 2702754.923 | 1216526.7727 | 2702931.5564 | 1215667.8749
15 | 2702674.4294 | 1216897.6501 | 2702691.8741 | 1216927.8722 | 2702703.2152 | 1216946.5587 | 2702711.9159 | 1216964.6771 | 2702720.3583 | 1216993.3653 | 2702777.3321 | 1217145.0447 | 2702832.2177 | 1217286.448 | 2702834.1127 | 1217290.0546
16 | 2702674.4294 | 1216897.6501 | 2702665.3556 | 1216902.4861 | 2702643.4713 | 1216887.5319 | 2702624.3304 | 1216883.4549 | 2702568.3317 | 1216901.8597 | 2702559.3411 | 1216911.5674 | 2702537.8342 | 1216917.0235 | 2702516.3798 | 1216926.4834 | 2702507.1294 | 1216951.2976 | 2702502.4517 | 1216974.2557 | 2702493.2073 | 1216983.281 | 2702474.6016 | 1216993.5684 | 2702458.3598 | 1216994.4565
17 | 2702931.5564 | 1215667.8749 | 2702921.3712 | 1215670.1006 | 2702914.7207 | 1215675.2228 | 2702908.159 | 1215685.7614 | 2702899.945 | 1215694.7816 | 2702889.7178 | 1215700.7649 | 2702877.3588 | 1215705.2882 | 2702852.6998 | 1215703.8839 | 2702825.8658 | 1215696.4935 | 2702818.3514 | 1215697.1088 | 2702810.9862 | 1215700.5287 | 2702804.146 | 1215705.6477 | 2702795.6591 | 1215708.4922 | 2702790.2454 | 1215707.0868 | 2702786.6151 | 1215700.4862 | 2702782.6728 | 1215689.9551 | 2702779.0285 | 1215683.7212 | 2702770.6898 | 1215677.9734 | 2702764.0378 | 1215672.6216 | 2702761.3337 | 1215666.0369 | 2702762.9885 | 1215657.2814 | 2702768.092 | 1215644.0934 | 2702769.3606 | 1215635.7093 | 2702766.5226 | 1215626.3204 | 2702763.2375 | 1215620.8376 | 2702758.6044 | 1215617.7667 | 2702750.0028 | 1215616.6843 | 2702750.0028 | 1215616.6843
18 | 2702845.1536 | 1217300.648 | 2702838.7382 | 1217298.8583 | 2702834.1127 | 1217290.0546
19 | 2702412.2778 | 1216942.2939 | 2702417.9484 | 1216967.1091 | 2702435.7199 | 1216982.8034 | 2702458.3598 | 1216994.4565
20 | 2703734.8136 | 1216191.9429 | 2703743.5875 | 1216182.0404 | 2703757.3303 | 1216168.8073
21 | 2703734.8136 | 1216191.9429 | 2703729.6747 | 1216197.7428 | 2703712.8078 | 1216209.5244 | 2703692.6844 | 1216224.2849
22 | 2703776.9677 | 1216135.3302 | 2703778.0668 | 1216135.3182 | 2703781.3939 | 1216137.8891 | 2703781.6579 | 1216141.9188 | 2703780.7332 | 1216146.6061 | 2703771.6606 | 1216155.1765 | 2703757.7993 | 1216168.3557 | 2703757.3303 | 1216168.8073
23 | 2703692.6844 | 1216224.2849 | 2703692.6844 | 1216224.2849 | 2703673.0407 | 1216240.7216 | 2703671.0954 | 1216242.8428
24 | 2703776.9677 | 1216135.3302 | 2703772.1801 | 1216135.3825 | 2703764.7002 | 1216139.2773 | 2703753.6871 | 1216143.2773 | 2703741.5381 | 1216144.9115 | 2703736.3065 | 1216144.9528
25 | 2703605.4551 | 1216312.6091 | 2703615.9409 | 1216300.4826 | 2703627.22 | 1216290.7718 | 2703639.7078 | 1216279.2473 | 2703653.6493 | 1216261.8662 | 2703671.0954 | 1216242.8428
26 | 2703605.4551 | 1216312.6091 | 2703501.8145 | 1216385.3939 | 2703494.9958 | 1216401.0868 | 2703484.2136 | 1216424.1827 | 2703469.9564 | 1216441.4253 | 2703456.0267 | 1216455.5603 | 2703421.5979 | 1216486.9409 | 2703386.8178 | 1216518.4489 | 2703372.8837 | 1216526.7354 | 2703365.9395 | 1216530.8735 | 2703357.3291 | 1216533.0035 | 2703319.1411 | 1216537.3112 | 2703306.4029 | 1216538.8248 | 2703293.9965 | 1216541.3449 | 2703283.0567 | 1216546.8704 | 2703273.3682 | 1216553.3738 | 2703263.3152 | 1216562.5062 | 2703262.6279 | 1216563.3014
27 | 2703262.6279 | 1216563.3014 | 2703254.4346 | 1216572.7819 | 2703249.1238 | 1216584.3315 | 2703245.044 | 1216596.7141 | 2703242.3777 | 1216616.4821 | 2703241.3396 | 1216636.9454 | 2703241.4482 | 1216656.9616 | 2703240.8535 | 1216680.7572 | 2703238.1096 | 1216699.7454 | 2703233.9846 | 1216717.8091 | 2703225.0989 | 1216741.5388 | 2703218.1712 | 1216756.5494
28 | 2703151.994 | 1216858.7236 | 2703215.7417 | 1216761.8135 | 2703218.1712 | 1216756.5494
29 | 2703151.994 | 1216858.7236 | 2703144.1293 | 1216852.472 | 2703123.2018 | 1216842.3915
30 | 2703151.994 | 1216858.7236 | 2703148.121 | 1216864.8832 | 2703143.3269 | 1216872.4946 | 2703041.3071 | 1217034.5686
31 | 2703041.3071 | 1217034.5686 | 2703032.1197 | 1217049.1642
32 | 2703008.7455 | 1217086.2978 | 2703032.1197 | 1217049.1642
33 | 2702998.8135 | 1217102.0763 | 2703008.7455 | 1217086.2978
34 | 2703123.2018 | 1216842.3915 | 2703111.3402 | 1216845.066 | 2703063.8657 | 1216852.5614 | 2703048.347 | 1216851.559 | 2703027.8111 | 1216844.9264
35 | 2703123.2018 | 1216842.3915 | 2703098.9324 | 1216824.4589 | 2703086.1621 | 1216808.56 | 2703083.7346 | 1216796.5761 | 2703083.7346 | 1216796.5761
36 | 2703677.1975 | 1217433.6483 | 2703677.1975 | 1217433.6483 | 2703658.4268 | 1217442.5712
37 | 2703645.0945 | 1217448.9088 | 2703658.4268 | 1217442.5712
38 | 2702998.8135 | 1217102.0763 | 2702982.5325 | 1217127.9412 | 2702981.0248 | 1217129.8445
39 | 2703645.0945 | 1217448.9088 | 2703642.18 | 1217450.2943
40 | 2703622.7641 | 1217459.5726 | 2703625.7952 | 1217458.083 | 2703642.18 | 1217450.2943
41 | 2703615.0382 | 1217463.3693 | 2703622.7641 | 1217459.5726
42 | 2703701.1503 | 1217496.121 | 2703690.6018 | 1217499.3064
43 | 2703690.6018 | 1217499.3064 | 2703689.7037 | 1217503.3604 | 2703688.1322 | 1217510.4055
44 | 2703690.6018 | 1217499.3064 | 2703683.1896 | 1217500.7555
45 | 2703015.1368 | 1216840.8328 | 2703027.8111 | 1216844.9264
46 | 2703083.7346 | 1216796.5761 | 2703090.1508 | 1216781.0609
47 | 2702974.5216 | 1217138.0545 | 2702981.0248 | 1217129.8445
48 | 2703606.1062 | 1217467.7587 | 2703610.8836 | 1217465.411
49 | 2703606.1062 | 1217467.7587 | 2703595.07 | 1217473.6711 | 2703583.7634 | 1217482.4698 | 2703558.4827 | 1217509.8278 | 2703552.4244 | 1217527.2573
50 | 2703606.1062 | 1217467.7587 | 2703604.2236 | 1217465.5578 | 2703600.2134 | 1217464.7541 | 2703585.6253 | 1217466.6575 | 2703576.5263 | 1217469.8905 | 2703572.777 | 1217472.4413
51 | 2703610.8836 | 1217465.411 | 2703615.0382 | 1217463.3693
52 | 2703552.4244 | 1217527.2573 | 2703565.9206 | 1217528.7426
53 | 2703540.1925 | 1217472.0907 | 2703545.4949 | 1217477.3344 | 2703552.2065 | 1217479.5304 | 2703559.0228 | 1217479.6378 | 2703567.4904 | 1217476.0379 | 2703572.777 | 1217472.4413
54 | 2703669.5568 | 1217536.7646 | 2703676.84 | 1217533.1246 | 2703680.7857 | 1217528.9013 | 2703686.9366 | 1217515.7656 | 2703688.1322 | 1217510.4055
55 | 2703624.6939 | 1217559.4474 | 2703632.7233 | 1217555.1731 | 2703669.5568 | 1217536.7646
56 | 2703657.2466 | 1217505.8275 | 2703683.1896 | 1217500.7555
57 | 2703632.3771 | 1217510.8181 | 2703643.0776 | 1217508.5975 | 2703657.2466 | 1217505.8275
58 | 2703096.4861 | 1216765.7413 | 2703090.1508 | 1216781.0609
59 | 2702905.808 | 1217170.0277 | 2702895.9308 | 1217163.2994
60 | 2702933.5363 | 1217188.9162 | 2702905.808 | 1217170.0277
61 | 2702877.2803 | 1217146.4641 | 2702889.0714 | 1217158.6268 | 2702895.9308 | 1217163.2994
62 | 2702933.5363 | 1217188.9162 | 2702917.4807 | 1217213.323 | 2702908.065 | 1217236.199 | 2702905.0853 | 1217254.8498
63 | 2702933.5363 | 1217188.9162 | 2702974.5216 | 1217138.0545
64 | 2702875.3896 | 1217144.5138 | 2702877.2803 | 1217146.4641
65 | 2702905.0853 | 1217254.8498 | 2702901.8662 | 1217280.7572 | 2702897.3723 | 1217282.0138
66 | 2702905.0853 | 1217254.8498 | 2702892.0475 | 1217243.4101
67 | 2702974.5216 | 1217138.0545 | 2702972.3187 | 1217135.9149 | 2702963.5913 | 1217125.0168
68 | 2702897.3723 | 1217282.0138 | 2702888.5924 | 1217286.1207 | 2702874.4958 | 1217295.7691
69 | 2702897.3723 | 1217282.0138 | 2703333.6667 | 1217622.3062
70 | 2702892.0475 | 1217243.4101 | 2702891.525 | 1217242.9516 | 2702881.4907 | 1217221.5514
71 | 2702953.9239 | 1217112.9449 | 2702963.5913 | 1217125.0168
72 | 2702867.7083 | 1217300.4149 | 2702874.4958 | 1217295.7691
73 | 2703333.6667 | 1217622.3062 | 2703312.5096 | 1217684.7174 | 2703273.1152 | 1217783.9725 | 2703269.8411 | 1217822.6101 | 2703278.2624 | 1217858.4151 | 2703311.909 | 1217946.5714
74 | 2703333.6667 | 1217622.3062 | 2703337.7136 | 1217622.2986
75 | 2702786.1189 | 1217322.6898 | 2702805.7089 | 1217347.7234
76 | 2702805.7089 | 1217347.7234 | 2702815.4691 | 1217340.9202 | 2702816.8838 | 1217334.6179 | 2702837.696 | 1217320.5224 | 2702844.6005 | 1217315.9717 | 2702851.6214 | 1217311.712 | 2702845.1536 | 1217300.648
77 | 2702786.1189 | 1217322.6898 | 2702774.1598 | 1217279.5972 | 2702765.1742 | 1217261.307 | 2702755.1797 | 1217245.1565 | 2702735.1244 | 1217225.4967 | 2702709.4123 | 1217200.1132 | 2702697.8533 | 1217191.4522
78 | 2702786.1189 | 1217322.6898 | 2702781.3857 | 1217324.1759 | 2702769.84 | 1217320.93 | 2702753.3894 | 1217306.2359 | 2702745.9262 | 1217302.2488 | 2702739.7843 | 1217303.5481
79 | 2702845.1536 | 1217300.648 | 2702851.6214 | 1217311.712 | 2702867.7083 | 1217300.4149
80 | 2702871.5107 | 1217211.9539 | 2702880.035 | 1217218.4468 | 2702881.4907 | 1217221.5514
81 | 2702953.9239 | 1217112.9449 | 2702940.5327 | 1217096.223
82 | 2703511.6774 | 1217452.4402 | 2703536.7169 | 1217468.6535 | 2703540.1925 | 1217472.0907
83 | 2703632.3771 | 1217510.8181 | 2703627.7368 | 1217511.781
84 | 2703605.6405 | 1217516.5685 | 2703607.088 | 1217516.066 | 2703627.7368 | 1217511.781
85 | 2703604.5467 | 1217516.9483 | 2703605.6405 | 1217516.5685
86 | 2703601.689 | 1217571.6936 | 2703624.6939 | 1217559.4474
87 | 2703465.9817 | 1217509.8768 | 2703471.2575 | 1217501.6292 | 2703485.6666 | 1217479.4412 | 2703503.8505 | 1217459.7985 | 2703511.6774 | 1217452.4402
88 | 2703465.9817 | 1217509.8768 | 2703480.0517 | 1217516.5305
89 | 2703337.7136 | 1217622.2986 | 2703339.0801 | 1217617.9302 | 2703342.7084 | 1217608.353 | 2703346.3774 | 1217602.1232 | 2703349.0676 | 1217599.7904 | 2703351.477 | 1217598.7648 | 2703354.126 | 1217598.8108 | 2703355.3377 | 1217591.1152 | 2703362.213 | 1217592.6244 | 2703371.4685 | 1217592.6071 | 2703380.0485 | 1217591.2661 | 2703390.1388 | 1217588.2056 | 2703399.3835 | 1217584.8747 | 2703411.529 | 1217578.4586 | 2703427.5628 | 1217564.1155 | 2703442.7426 | 1217546.0549 | 2703465.9817 | 1217509.8768
90 | 2703582.8637 | 1217524.476 | 2703577.4729 | 1217526.3475 | 2703566.944 | 1217528.8552 | 2703565.9206 | 1217528.7426
91 | 2703582.8637 | 1217524.476 | 2703584.8187 | 1217523.7972
92 | 2703604.5467 | 1217516.9483 | 2703584.8187 | 1217523.7972
93 | 2703601.689 | 1217571.6936 | 2703599.4102 | 1217572.9066 | 2703594.4221 | 1217580.1505
94 | 2703643.4388 | 1217823.3186 | 2703634.3597 | 1217821.9486 | 2703625.5489 | 1217831.3355 | 2703613.994 | 1217863.6022 | 2703592.2919 | 1217895.6813 | 2703584.3352 | 1217891.3287 | 2703586.9 | 1217865.6549 | 2703581.2293 | 1217826.7728 | 2703575.7562 | 1217800.9703 | 2703576.6137 | 1217776.1118 | 2703586.6063 | 1217757.2719 | 2703586.0939 | 1217751.8147 | 2703579.1565 | 1217751.7051 | 2703558.0097 | 1217761.011 | 2703547.0573 | 1217773.4852 | 2703540.3241 | 1217796.1289 | 2703535.4369 | 1217809.5425 | 2703530.0433 | 1217808.8483 | 2703524.0951 | 1217805.1201 | 2703511.7712 | 1217784.2577 | 2703503.6824 | 1217763.0353 | 2703494.9339 | 1217731.2717 | 2703494.1352 | 1217704.2718 | 2703496.5236 | 1217688.2907 | 2703492.2356 | 1217684.7025 | 2703486.4492 | 1217684.324 | 2703472.9228 | 1217687.6359 | 2703465.4296 | 1217696.1797
95 | 2703465.4296 | 1217696.1797 | 2703465.1616 | 1217696.4853 | 2703458.6437 | 1217697.5729 | 2703454.3405 | 1217693.5398 | 2703454.4513 | 1217688.0377 | 2703462.9199 | 1217672.5625 | 2703481.0827 | 1217658.4678 | 2703506.5937 | 1217642.7106 | 2703531.1887 | 1217632.4749 | 2703540.4121 | 1217621.6385 | 2703554.7793 | 1217617.5741 | 2703569.1709 | 1217614.2885 | 2703573.5422 | 1217610.4729 | 2703594.4221 | 1217580.1505
96 | 2703337.7136 | 1217622.2986 | 2703349.7377 | 1217629.8681 | 2703371.4634 | 1217672.5088 | 2703389.1318 | 1217682.5113 | 2703398.6929 | 1217705.5493 | 2703378.3652 | 1217701.7939 | 2703371.3375 | 1217706.442 | 2703381.9513 | 1217718.268 | 2703397.961 | 1217735.0244 | 2703402.5641 | 1217748.0136 | 2703412.6301 | 1217768.2027 | 2703421.7873 | 1217782.5719 | 2703435.1024 | 1217794.0335 | 2703440.7003 | 1217801.7584 | 2703448.2137 | 1217804.5464 | 2703447.3048 | 1217808.3556 | 2703455.5791 | 1217818.9068 | 2703450.3319 | 1217819.4049 | 2703455.2333 | 1217826.1393 | 2703461.6154 | 1217827.6178 | 2703468.1392 | 1217835.3589 | 2703466.679 | 1217843.1728
97 | 2703472.217 | 1217553.3857 | 2703471.5991 | 1217552.7606 | 2703468.3329 | 1217548.9123 | 2703470.9159 | 1217541.8298 | 2703477.3895 | 1217538.0617 | 2703491.1387 | 1217533.7418 | 2703494.4161 | 1217530.83 | 2703495.4071 | 1217527.9785 | 2703490.0497 | 1217521.2584 | 2703480.0517 | 1217516.5305
98 | 2703472.217 | 1217553.3857 | 2703475.8148 | 1217557.0258 | 2703497.2736 | 1217551.7007
99 | 2703497.2736 | 1217551.7007 | 2703515.0093 | 1217547.2995 | 2703533.2186 | 1217557.2007 | 2703544.6623 | 1217558.4115 | 2703552.0833 | 1217577.8766 | 2703551.4768 | 1217578.2563
100 | 2703532.8273 | 1217581.0211 | 2703537.2083 | 1217580.142 | 2703548.1609 | 1217580.3324 | 2703551.4768 | 1217578.2563
101 | 2702697.8533 | 1217191.4522 | 2702692.0619 | 1217182.0902 | 2702690.108 | 1217173.4281 | 2702691.1622 | 1217166.4524 | 2702693.6249 | 1217159.2564 | 2702698.9121 | 1217151.1862 | 2702710.7546 | 1217142.5285
102 | 2702697.8533 | 1217191.4522 | 2702677.9276 | 1217176.5215
103 | 2702940.5327 | 1217096.223 | 2702939.199 | 1217094.5576 | 2702934.3832 | 1217084.5562 | 2702932.3011 | 1217069.7096 | 2702932.2736 | 1217051.9743 | 2702930.1927 | 1217042.339
104 | 2702899.6675 | 1217003.1983 | 2702907.2162 | 1217013.7476 | 2702921.8255 | 1217027.3652 | 2702929.3981 | 1217038.6595 | 2702930.1927 | 1217042.339
105 | 2702899.6675 | 1217003.1983 | 2702896.4211 | 1216998.6616 | 2702882.5029 | 1216966.1314 | 2702873.6118 | 1216941.0378 | 2702873.4068 | 1216939.9952
106 | 2702849.4983 | 1216839.3763 | 2702848.5308 | 1216841.2448 | 2702847.0927 | 1216847.1353 | 2702847.1071 | 1216855.0968 | 2702853.3898 | 1216876.9097 | 2702866.5339 | 1216905.0455 | 2702873.4068 | 1216939.9952
107 | 2702849.4983 | 1216839.3763 | 2702855.7263 | 1216827.3479 | 2702857.8353 | 1216816.9102 | 2702854.6994 | 1216792.7166 | 2702857.766 | 1216781.3837
108 | 2702750.0028 | 1215616.6843 | 2702744.0529 | 1215613.7797 | 2702737.082 | 1215615.9055 | 2702731.0129 | 1215619.9149 | 2702722.0317 | 1215618.826 | 2702713.4871 | 1215613.9976 | 2702709.7246 | 1215604.0368 | 2702711.7677 | 1215594.3429 | 2702719.3049 | 1215581.3969 | 2702721.8699 | 1215573.5911 | 2702723.7595 | 1215562.2267 | 2702723.8877 | 1215560.2323
109 | 2702147.032 | 1217014.8495 | 2702122.1765 | 1217012.3774 | 2702088.1138 | 1217007.5015 | 2702079.9393 | 1217008.64 | 2702066.2073 | 1217017.7113 | 2702024.1037 | 1217029.2209 | 2701995.7165 | 1217031.2365 | 2701971.6657 | 1217032.7705
110 | 2702094.4202 | 1217796.0827 | 2702111.6278 | 1217798.9574 | 2702123.9794 | 1217799.8919 | 2702139.2125 | 1217799.6973 | 2702157.3607 | 1217797.7514 | 2702166.6346 | 1217795.7534 | 2702174.4596 | 1217793.6861 | 2702185.5042 | 1217790.2619 | 2702200.3597 | 1217784.2012 | 2702211.7372 | 1217778.192 | 2702220.3837 | 1217772.0582 | 2702238.987 | 1217758.2008 | 2702253.9808 | 1217744.9819 | 2702271.5022 | 1217725.6132 | 2702285.3352 | 1217705.7253 | 2702295.6114 | 1217685.6095 | 2702307.7758 | 1217656.4417
111 | 2702201.9718 | 1217584.5308 | 2702196.792 | 1217596.5839 | 2702193.2112 | 1217607.9195 | 2702190.6386 | 1217622.0076 | 2702189.692 | 1217633.8109 | 2702188.3696 | 1217643.1838 | 2702186.4887 | 1217654.1261 | 2702185.1228 | 1217666.0334 | 2702184.0393 | 1217679.6245 | 2702183.9826 | 1217689.1192 | 2702183.4109 | 1217697.6599 | 2702180.9907 | 1217703.3113 | 2702176.2851 | 1217705.8769 | 2702173.4457 | 1217704.9832 | 2702168.8398 | 1217701.7352 | 2702151.6975 | 1217701.2299 | 2702135.8123 | 1217701.8025 | 2702128.3356 | 1217705.6882 | 2702121.3267 | 1217719.4891 | 2702113.4494 | 1217734.3425 | 2702103.9339 | 1217745.9989 | 2702096.0026 | 1217764.0092 | 2702092.7672 | 1217779.576 | 2702094.4202 | 1217796.0827
112 | 2702203.6993 | 1217576.3323 | 2702201.9718 | 1217584.5308
113 | 2702532.2249 | 1217142.487 | 2702203.6993 | 1217576.3323
114 | 2702147.032 | 1217014.8495 | 2702215.3569 | 1217020.4915 | 2702230.8536 | 1217026.2948
115 | 2702677.9276 | 1217176.5215 | 2702668.6542 | 1217169.5728
116 | 2702596.0544 | 1217097.858 | 2702581.0118 | 1217082.2177 | 2702551.3356 | 1217105.7349 | 2702542.5306 | 1217114.8232 | 2702536.7806 | 1217126.4103 | 2702532.2249 | 1217142.487
117 | 2702596.0544 | 1217097.858 | 2702596.5946 | 1217098.4197 | 2702602.9415 | 1217116.5419 | 2702609.5337 | 1217125.2727 | 2702614.2185 | 1217128.7831
118 | 2702668.6542 | 1217169.5728 | 2702614.2185 | 1217128.7831
119 | 2702412.2778 | 1216942.2939 | 2702389.1272 | 1216944.8758 | 2702371.8239 | 1216939.9195 | 2702319.7262 | 1216920.5 | 2702284.432 | 1216919.2155 | 2702275.2586 | 1216921.4708 | 2702270.3178 | 1216927.0789
120 | 2702270.3178 | 1216927.0789 | 2702270.4638 | 1216931.8404 | 2702291.7375 | 1216955.867 | 2702307.1516 | 1216962.5029 | 2702312.9921 | 1216969.9418 | 2702311.7911 | 1216976.2035 | 2702305.4286 | 1216979.2631 | 2702297.6983 | 1216977.9628 | 2702257.1038 | 1216951.5029 | 2702251.2665 | 1216951.8363 | 2702248.2094 | 1216956.0869 | 2702249.4708 | 1216962.224 | 2702257.1246 | 1216972.4071 | 2702256.3007 | 1217008.4519 | 2702251.2273 | 1217020.4623 | 2702243.2921 | 1217025.3519 | 2702230.8536 | 1217026.2948

## bus_geodata
| x | y | coords
0 | 2701671.154 | 1216362.5067
1 | 2701825.8954 | 1216419.4091
2 | 2701542.3659 | 1216313.5084
3 | 2702209.4899 | 1216416.4338
4 | 2701419.3526 | 1216323.2099
5 | 2701713.9898 | 1216129.4149
6 | 2701559.065 | 1216971.1767
7 | 2701752.1727 | 1217091.9578
8 | 2702543.2218 | 1216560.4065
9 | 2701389.2201 | 1216354.4194
10 | 2701686.7106 | 1215877.6488
11 | 2702612.2936 | 1216604.0929
12 | 2701343.1019 | 1215759.6713
13 | 2702754.923 | 1216526.7727
14 | 2702674.4294 | 1216897.6501
15 | 2702931.5564 | 1215667.8749
16 | 2702834.1127 | 1217290.0546
17 | 2702458.3598 | 1216994.4565
18 | 2703734.8136 | 1216191.9429
19 | 2703757.3303 | 1216168.8073
20 | 2703692.6844 | 1216224.2849
21 | 2703776.9677 | 1216135.3302
22 | 2703671.0954 | 1216242.8428
23 | 2703736.3065 | 1216144.9528
24 | 2703605.4551 | 1216312.6091
25 | 2703262.6279 | 1216563.3014
26 | 2703218.1712 | 1216756.5494
27 | 2703151.994 | 1216858.7236
28 | 2703041.3071 | 1217034.5686
29 | 2703032.1197 | 1217049.1642
30 | 2703008.7455 | 1217086.2978
31 | 2703123.2018 | 1216842.3915
32 | 2703677.1975 | 1217433.6483
33 | 2703658.4268 | 1217442.5712
34 | 2702998.8135 | 1217102.0763
35 | 2703642.18 | 1217450.2943
36 | 2703645.0945 | 1217448.9088
37 | 2703622.7641 | 1217459.5726
38 | 2703701.1503 | 1217496.121
39 | 2703690.6018 | 1217499.3064
40 | 2703027.8111 | 1216844.9264
41 | 2703083.7346 | 1216796.5761
42 | 2702981.0248 | 1217129.8445
43 | 2703606.1062 | 1217467.7587
44 | 2703610.8836 | 1217465.411
45 | 2703552.4244 | 1217527.2573
46 | 2703572.777 | 1217472.4413
47 | 2703615.0382 | 1217463.3693
48 | 2703688.1322 | 1217510.4055
49 | 2703669.5568 | 1217536.7646
50 | 2703683.1896 | 1217500.7555
51 | 2703657.2466 | 1217505.8275
52 | 2703015.1368 | 1216840.8328
53 | 2703090.1508 | 1216781.0609
54 | 2702905.808 | 1217170.0277
55 | 2702895.9308 | 1217163.2994
56 | 2702933.5363 | 1217188.9162
57 | 2702877.2803 | 1217146.4641
58 | 2702905.0853 | 1217254.8498
59 | 2702974.5216 | 1217138.0545
60 | 2702875.3896 | 1217144.5138
61 | 2702897.3723 | 1217282.0138
62 | 2702892.0475 | 1217243.4101
63 | 2702963.5913 | 1217125.0168
64 | 2702874.4958 | 1217295.7691
65 | 2703333.6667 | 1217622.3062
66 | 2702805.7089 | 1217347.7234
67 | 2702786.1189 | 1217322.6898
68 | 2702845.1536 | 1217300.648
69 | 2702867.7083 | 1217300.4149
70 | 2702881.4907 | 1217221.5514
71 | 2702953.9239 | 1217112.9449
72 | 2703540.1925 | 1217472.0907
73 | 2703627.7368 | 1217511.781
74 | 2703632.3771 | 1217510.8181
75 | 2703605.6405 | 1217516.5685
76 | 2703624.6939 | 1217559.4474
77 | 2703511.6774 | 1217452.4402
78 | 2703465.9817 | 1217509.8768
79 | 2703565.9206 | 1217528.7426
80 | 2703582.8637 | 1217524.476
81 | 2703584.8187 | 1217523.7972
82 | 2703604.5467 | 1217516.9483
83 | 2703601.689 | 1217571.6936
84 | 2702871.5107 | 1217211.9539
85 | 2703643.4388 | 1217823.3186
86 | 2703465.4296 | 1217696.1797
87 | 2703594.4221 | 1217580.1505
88 | 2703466.679 | 1217843.1728
89 | 2703337.7136 | 1217622.2986
90 | 2703311.909 | 1217946.5714
91 | 2703480.0517 | 1217516.5305
92 | 2703472.217 | 1217553.3857
93 | 2703497.2736 | 1217551.7007
94 | 2703551.4768 | 1217578.2563
95 | 2703532.8273 | 1217581.0211
96 | 2702697.8533 | 1217191.4522
97 | 2702739.7843 | 1217303.5481
98 | 2703096.4861 | 1216765.7413
99 | 2702940.5327 | 1217096.223
100 | 2702930.1927 | 1217042.339
101 | 2702899.6675 | 1217003.1983
102 | 2702873.4068 | 1216939.9952
103 | 2702849.4983 | 1216839.3763
104 | 2702857.766 | 1216781.3837
105 | 2702750.0028 | 1215616.6843
106 | 2702723.8877 | 1215560.2323
107 | 2701971.6657 | 1217032.7705
108 | 2702307.7758 | 1217656.4417
109 | 2702094.4202 | 1217796.0827
110 | 2702201.9718 | 1217584.5308
111 | 2702203.6993 | 1217576.3323
112 | 2702147.032 | 1217014.8495
113 | 2702710.7546 | 1217142.5285
114 | 2702677.9276 | 1217176.5215
115 | 2702532.2249 | 1217142.487
116 | 2702596.0544 | 1217097.858
117 | 2702668.6542 | 1217169.5728
118 | 2702614.2185 | 1217128.7831
119 | 2702412.2778 | 1216942.2939
120 | 2702270.3178 | 1216927.0789
121 | 2702230.8536 | 1217026.2948
122 | 2702974.5216 | 1217138.0545

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98786 | -0.23799 | 0.0004495 | 0.00011266
1 | 0.98809 | -0.23346 | 0.00019478 | 4.8816e-05
2 | 0.98773 | -0.24069 | 0 | 0
3 | 0.98881 | -0.21876 | 0.00028425 | 7.1239e-05
4 | 0.98768 | -0.24166 | 0.00022108 | 5.5409e-05
5 | 0.98758 | -0.24384 | 0.00018173 | 4.5545e-05
6 | 0.98946 | -0.20543 | 0.00026324 | 6.5975e-05
7 | 0.98952 | -0.20426 | 0.00035339 | 8.8568e-05
8 | 0.98946 | -0.20566 | 0 | 0
9 | 0.98767 | -0.24182 | 0.00019104 | 4.788e-05
10 | 0.98742 | -0.24695 | 0 | 0
11 | 0.98963 | -0.20217 | 0 | 0
12 | 0.98728 | -0.24978 | 0.00042872 | 0.00010745
13 | 0.98926 | -0.20964 | 0.00030226 | 7.5754e-05
14 | 0.99051 | -0.18422 | 0 | 0
15 | 0.9886 | -0.22298 | 0 | 0
16 | 0.99213 | -0.15104 | 0.001145 | 0.00028698
17 | 0.99023 | -0.18993 | 0.00017276 | 4.3298e-05
18 | 0.98168 | -0.35264 | 0.0009992 | 0.00025042
19 | 0.98155 | -0.35529 | 0.0018408 | 0.00046135
20 | 0.98195 | -0.34731 | 0.0094416 | 0.0023663
21 | 0.98143 | -0.35755 | 0.0015965 | 0.00040012
22 | 0.98235 | -0.3396 | 0.0023561 | 0.00059049
23 | 0.98139 | -0.35839 | 0.0010926 | 0.00027384
24 | 0.98388 | -0.30959 | 0 | 0
25 | 0.99094 | -0.17297 | 0.00018443 | 4.6223e-05
26 | 0.99421 | -0.11026 | 0.00014756 | 3.6983e-05
27 | 0.99619 | -0.072338 | 0 | 0
28 | 1 | 0 | -0.10315 | -0.025876
29 | 0.99958 | -0.008067 | 0.00034512 | 8.6495e-05
30 | 0.9985 | -0.028533 | 0.00024126 | 6.0465e-05
31 | 0.99613 | -0.073621 | 0 | 0
32 | 0.97755 | -0.4327 | 0.0019973 | 0.00050056
33 | 0.97759 | -0.43194 | 0.0012873 | 0.00032262
34 | 0.99804 | -0.037215 | 0.00022728 | 5.6962e-05
35 | 0.97765 | -0.43069 | 0.00143 | 0.0003584
36 | 0.97763 | -0.43105 | 0.0028747 | 0.00072047
37 | 0.9778 | -0.42771 | 0.0028698 | 0.00071925
38 | 0.97331 | -0.51622 | 0.001187 | 0.00029749
39 | 0.97332 | -0.51598 | 0 | 0
40 | 0.99603 | -0.075521 | 0.00065158 | 0.0001633
41 | 0.99607 | -0.07482 | 0.0003941 | 9.8771e-05
42 | 0.99724 | -0.052555 | 0.00025498 | 6.3903e-05
43 | 0.978 | -0.42382 | 0 | 0
44 | 0.97793 | -0.42509 | 0.0015672 | 0.00039277
45 | 0.97584 | -0.46615 | 0.0021671 | 0.00054313
46 | 0.97937 | -0.39689 | 0.0024092 | 0.0006038
47 | 0.97788 | -0.42607 | 0.0011229 | 0.00028142
48 | 0.9732 | -0.5183 | 0.0021995 | 0.00055125
49 | 0.97292 | -0.52386 | 0.0024648 | 0.00061774
50 | 0.9734 | -0.51427 | 0.0016052 | 0.00040231
51 | 0.97375 | -0.50752 | 0.001625 | 0.00040727
52 | 0.99602 | -0.075628 | 0.00045703 | 0.00011454
53 | 0.99606 | -0.075024 | 0.00015352 | 3.8476e-05
54 | 0.99544 | -0.08701 | 0.00026629 | 6.6738e-05
55 | 0.99542 | -0.087218 | 0.00029619 | 7.4232e-05
56 | 0.99547 | -0.086269 | 0 | 0
57 | 0.99541 | -0.087525 | 0.00047979 | 0.00012025
58 | 0.99382 | -0.11803 | 0 | 0
59 | 0.99698 | -0.057414 | 0 | 0
60 | 0.99541 | -0.087535 | 0.00021175 | 5.307e-05
61 | 0.99316 | -0.13062 | 0 | 0
62 | 0.99374 | -0.11949 | 0.0020282 | 0.00050831
63 | 0.99692 | -0.058566 | 0.00029714 | 7.447e-05
64 | 0.9927 | -0.13962 | 0.0054477 | 0.0013653
65 | 0.98453 | -0.29644 | 0 | 0
66 | 0.99168 | -0.15974 | 0 | 0
67 | 0.99145 | -0.16426 | 0 | 0
68 | 0.99221 | -0.1494 | 0 | 0
69 | 0.9926 | -0.1416 | 0 | 0
70 | 0.99368 | -0.12067 | 0.0020976 | 0.0005257
71 | 0.99687 | -0.059531 | 0.0003507 | 8.7894e-05
72 | 0.98012 | -0.38226 | 0.0010152 | 0.00025444
73 | 0.97419 | -0.49874 | 0.0016125 | 0.00040413
74 | 0.97411 | -0.50028 | 0.0021945 | 0.00055
75 | 0.9746 | -0.49071 | 0.0018044 | 0.00045224
76 | 0.97262 | -0.52982 | 0.0019169 | 0.00048042
77 | 0.9806 | -0.37289 | 0 | 0
78 | 0.98162 | -0.35302 | 0 | 0
79 | 0.97552 | -0.47259 | 0.0010927 | 0.00027385
80 | 0.97511 | -0.48057 | 0.0010077 | 0.00025256
81 | 0.97507 | -0.48148 | 0.00086151 | 0.00021591
82 | 0.97462 | -0.49026 | 0.0018116 | 0.00045402
83 | 0.97251 | -0.53199 | 0.00098195 | 0.0002461
84 | 0.99367 | -0.12083 | 0.00064185 | 0.00016086
85 | 0.97154 | -0.55128 | 0.0010084 | 0.00025274
86 | 0.97202 | -0.54183 | 0.0014129 | 0.00035411
87 | 0.97247 | -0.53273 | 0.0010912 | 0.00027347
88 | 0.98433 | -0.30054 | 0.00049736 | 0.00012465
89 | 0.98447 | -0.29765 | 0 | 0
90 | 0.98443 | -0.29851 | 0.00032978 | 8.2651e-05
91 | 0.98155 | -0.35439 | 0.0010773 | 0.00027
92 | 0.98133 | -0.35868 | 0.00069871 | 0.00017511
93 | 0.98126 | -0.36021 | 0.001525 | 0.0003822
94 | 0.98115 | -0.36226 | 0.00085565 | 0.00021445
95 | 0.98114 | -0.3625 | 0.0007121 | 0.00017847
96 | 0.99058 | -0.18116 | 0 | 0
97 | 0.99134 | -0.16631 | 0.0021548 | 0.00054004
98 | 0.99605 | -0.07518 | 0.000537 | 0.00013459
99 | 0.99681 | -0.060736 | 0.00016968 | 4.2525e-05
100 | 0.99666 | -0.063709 | 0.00055993 | 0.00014033
101 | 0.99655 | -0.065894 | 0.00048336 | 0.00012114
102 | 0.99642 | -0.06829 | 0.00082137 | 0.00020586
103 | 0.99631 | -0.070448 | 0.00037227 | 9.33e-05
104 | 0.99627 | -0.071284 | 0.00078873 | 0.00019767
105 | 0.98839 | -0.22705 | 0.00047762 | 0.0001197
106 | 0.98836 | -0.22766 | 0.00034938 | 8.7564e-05
107 | 0.98968 | -0.20097 | 0 | 0
108 | 0.98838 | -0.22467 | 0.00085158 | 0.00021343
109 | 0.98859 | -0.2204 | 0 | 0
110 | 0.98881 | -0.21614 | 0 | 0
111 | 0.98882 | -0.21601 | 0.0012321 | 0.00030879
112 | 0.98978 | -0.19893 | 0 | 0
113 | 0.99053 | -0.18219 | 0.00098314 | 0.0002464
114 | 0.99047 | -0.18332 | 0.00059898 | 0.00015012
115 | 0.98985 | -0.19555 | 0.00054571 | 0.00013677
116 | 0.9901 | -0.19072 | 0.0005669 | 0.00014208
117 | 0.99043 | -0.18419 | 0.00062331 | 0.00015622
118 | 0.9902 | -0.1886 | 0.00040673 | 0.00010194
119 | 0.99016 | -0.19125 | 0 | 0
120 | 0.99003 | -0.19387 | 0 | 0
121 | 0.98983 | -0.19796 | 0.00033541 | 8.4061e-05
122 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0014724 | -0.00035192 | 0.0014727 | 0.00034997 | 3.0644e-07 | -1.9433e-06 | 0.002212 | 0.0022112 | 0.002212 | 0.98786 | -0.23799 | 0.98809 | -0.23346 | 0.60768
1 | 0.0010229 | 0.00023926 | -0.0010228 | -0.000241 | 1.2533e-07 | -1.735e-06 | 0.0015349 | 0.0015355 | 0.0015355 | 0.98786 | -0.23799 | 0.98773 | -0.24069 | 0.42185
2 | -0.0016675 | -0.00039879 | 0.0016686 | 0.00039338 | 1.1233e-06 | -5.4072e-06 | 0.0025046 | 0.0025025 | 0.0025046 | 0.98809 | -0.23346 | 0.98881 | -0.21876 | 0.68806
3 | 0.00041215 | 0.00010103 | -0.00041213 | -0.0001027 | 1.889e-08 | -1.663e-06 | 0.00062011 | 0.00062069 | 0.00062069 | 0.98773 | -0.24069 | 0.98768 | -0.24166 | 0.17052
4 | 0.00061065 | 0.00013997 | -0.00061056 | -0.00014344 | 8.6804e-08 | -3.4744e-06 | 0.00091548 | 0.00091665 | 0.00091665 | 0.98773 | -0.24069 | 0.98758 | -0.24384 | 0.25183
5 | -0.0019529 | -0.00046462 | 0.001954 | 0.00046071 | 1.1696e-06 | -3.9167e-06 | 0.0029302 | 0.0029286 | 0.0029302 | 0.98881 | -0.21876 | 0.98946 | -0.20566 | 0.805
6 | 0.00019105 | 4.7286e-05 | -0.00019104 | -4.788e-05 | 1.4425e-09 | -5.9377e-07 | 0.00028762 | 0.00028783 | 0.00028783 | 0.98768 | -0.24166 | 0.98767 | -0.24182 | 0.079073
7 | 0.00042883 | 9.7895e-05 | -0.00042877 | -0.00010284 | 6.049e-08 | -4.9417e-06 | 0.00064288 | 0.00064454 | 0.00064454 | 0.98758 | -0.24384 | 0.98742 | -0.24695 | 0.17707
8 | -0.00026324 | -6.5975e-05 | 0.00026326 | 6.2841e-05 | 1.4341e-08 | -3.1339e-06 | 0.00039588 | 0.00039479 | 0.00039588 | 0.98946 | -0.20543 | 0.98952 | -0.20426 | 0.10876
9 | -0.00061665 | -0.00015141 | 0.00061674 | 0.00014769 | 9.4526e-08 | -3.72e-06 | 0.0009262 | 0.0009249 | 0.0009262 | 0.98952 | -0.20426 | 0.98968 | -0.20097 | 0.25445
10 | -0.001954 | -0.00046071 | 0.0019544 | 0.00045966 | 3.113e-07 | -1.0443e-06 | 0.0029286 | 0.0029282 | 0.0029286 | 0.98946 | -0.20566 | 0.98963 | -0.20217 | 0.80457
11 | 0.00042877 | 0.00010284 | -0.00042872 | -0.00010745 | 5.6737e-08 | -4.6101e-06 | 0.00064454 | 0.00064616 | 0.00064616 | 0.98742 | -0.24695 | 0.98728 | -0.24978 | 0.17752
12 | 0.0011303 | 0.00026311 | -0.0011299 | -0.00026745 | 3.8386e-07 | -4.339e-06 | 0.0016927 | 0.0016942 | 0.0016942 | 0.98963 | -0.20217 | 0.98926 | -0.20964 | 0.46543
13 | -0.0030847 | -0.00072277 | 0.0030872 | 0.00072035 | 2.5095e-06 | -2.4255e-06 | 0.0046209 | 0.0046195 | 0.0046209 | 0.98963 | -0.20217 | 0.99051 | -0.18422 | 1.2695
14 | 0.00082768 | 0.00019169 | -0.00082717 | -0.00020262 | 5.0679e-07 | -1.0926e-05 | 0.0012396 | 0.0012434 | 0.0012434 | 0.98926 | -0.20964 | 0.9886 | -0.22298 | 0.34159
15 | -0.0042128 | -0.00098304 | 0.0042192 | 0.00098161 | 6.3247e-06 | -1.4255e-06 | 0.0063039 | 0.0063021 | 0.0063039 | 0.99051 | -0.18422 | 0.99213 | -0.15104 | 1.7318
16 | 0.0011256 | 0.00026269 | -0.0011253 | -0.00026604 | 2.9228e-07 | -3.3455e-06 | 0.0016844 | 0.0016855 | 0.0016855 | 0.99051 | -0.18422 | 0.99023 | -0.18993 | 0.46306
17 | 0.00082717 | 0.00020262 | -0.00082701 | -0.00020602 | 1.587e-07 | -3.404e-06 | 0.0012434 | 0.0012446 | 0.0012446 | 0.9886 | -0.22298 | 0.98839 | -0.22705 | 0.34193
18 | -0.0053642 | -0.0012686 | 0.0053646 | 0.0012686 | 4.0044e-07 | 4.1833e-08 | 0.0080193 | 0.0080192 | 0.0080193 | 0.99213 | -0.15104 | 0.99221 | -0.1494 | 2.2031
19 | 0.00095258 | 0.00022274 | -0.00095252 | -0.00022366 | 5.6916e-08 | -9.2352e-07 | 0.001426 | 0.0014263 | 0.0014263 | 0.99023 | -0.18993 | 0.99016 | -0.19125 | 0.39183
20 | 0.0045309 | 0.0011344 | -0.0045303 | -0.0011344 | 5.714e-07 | -4.2729e-08 | 0.0068674 | 0.0068675 | 0.0068675 | 0.98168 | -0.35264 | 0.98155 | -0.35529 | 1.8867
21 | -0.0055301 | -0.0013848 | 0.0055315 | 0.001385 | 1.4037e-06 | 2.2455e-07 | 0.0083819 | 0.0083817 | 0.0083819 | 0.98168 | -0.35264 | 0.98195 | -0.34731 | 2.3027
22 | 0.0026895 | 0.00067305 | -0.0026892 | -0.00067345 | 2.8908e-07 | -4.0112e-07 | 0.0040768 | 0.0040771 | 0.0040771 | 0.98155 | -0.35529 | 0.98143 | -0.35755 | 1.1201
23 | -0.014973 | -0.0037513 | 0.014979 | 0.0037545 | 5.5002e-06 | 3.1596e-06 | 0.022689 | 0.022689 | 0.022689 | 0.98195 | -0.34731 | 0.98235 | -0.3396 | 6.2333
24 | 0.0010927 | 0.00027333 | -0.0010926 | -0.00027384 | 4.3664e-08 | -5.0818e-07 | 0.0016565 | 0.0016567 | 0.0016567 | 0.98143 | -0.35755 | 0.98139 | -0.35839 | 0.45514
25 | -0.017335 | -0.0043449 | 0.017359 | 0.0043596 | 2.4821e-05 | 1.4668e-05 | 0.026258 | 0.026257 | 0.026258 | 0.98235 | -0.3396 | 0.98388 | -0.30959 | 7.2137
26 | -0.017359 | -0.0043596 | 0.017473 | 0.0044269 | 0.00011391 | 6.7267e-05 | 0.026257 | 0.026255 | 0.026257 | 0.98388 | -0.30959 | 0.99094 | -0.17297 | 7.2136
27 | -0.017658 | -0.0044731 | 0.017711 | 0.0045046 | 5.3355e-05 | 3.1535e-05 | 0.026532 | 0.026531 | 0.026532 | 0.99094 | -0.17297 | 0.99421 | -0.11026 | 7.2891
28 | -0.017859 | -0.0045416 | 0.017891 | 0.004561 | 3.2687e-05 | 1.9337e-05 | 0.026752 | 0.026752 | 0.026752 | 0.99421 | -0.11026 | 0.99619 | -0.072338 | 7.3495
29 | 0.0021935 | 0.00054675 | -0.0021934 | -0.0005471 | 1.3358e-07 | -3.4675e-07 | 0.0032754 | 0.0032756 | 0.0032756 | 0.99619 | -0.072338 | 0.99613 | -0.073621 | 0.89989
30 | -0.020085 | -0.0051077 | 0.020155 | 0.0051499 | 7.0251e-05 | 4.2245e-05 | 0.030027 | 0.030026 | 0.030027 | 0.99619 | -0.072338 | 1 | 0 | 8.2492
31 | 0.081346 | 0.020726 | -0.081314 | -0.020706 | 3.1649e-05 | 1.9577e-05 | 0.12116 | 0.12116 | 0.12116 | 1 | 0 | 0.99958 | -0.008067 | 11.0956
32 | 0.080969 | 0.02062 | -0.080889 | -0.02057 | 7.9839e-05 | 4.9373e-05 | 0.12065 | 0.12065 | 0.12065 | 0.99958 | -0.008067 | 0.9985 | -0.028533 | 11.0486
33 | 0.080648 | 0.02051 | -0.080615 | -0.020489 | 3.3723e-05 | 2.0851e-05 | 0.12029 | 0.12029 | 0.12029 | 0.9985 | -0.028533 | 0.99804 | -0.037215 | 11.0157
34 | 0.0011087 | 0.00027647 | -0.0011086 | -0.00027767 | 1.0011e-07 | -1.2031e-06 | 0.0016557 | 0.0016562 | 0.0016562 | 0.99613 | -0.073621 | 0.99603 | -0.075521 | 0.45499
35 | 0.0010847 | 0.00027063 | -0.0010846 | -0.0002714 | 6.1803e-08 | -7.7786e-07 | 0.0016199 | 0.0016202 | 0.0016202 | 0.99613 | -0.073621 | 0.99607 | -0.07482 | 0.4451
36 | -0.0019973 | -0.00050056 | 0.0019973 | 0.00050035 | 7.2036e-08 | -2.1447e-07 | 0.0030402 | 0.0030401 | 0.0030402 | 0.97755 | -0.4327 | 0.97759 | -0.43194 | 0.83522
37 | -0.0032846 | -0.00082297 | 0.0032847 | 0.00082287 | 1.3837e-07 | -9.6537e-08 | 0.0049995 | 0.0049995 | 0.0049995 | 0.97759 | -0.43194 | 0.97763 | -0.43105 | 1.3735
38 | 0.080387 | 0.020432 | -0.080328 | -0.020395 | 5.9337e-05 | 3.6683e-05 | 0.11995 | 0.11995 | 0.11995 | 0.99804 | -0.037215 | 0.99724 | -0.052555 | 10.9847
39 | 0.0061596 | 0.0015434 | -0.0061594 | -0.0015433 | 1.0636e-07 | 2.7605e-08 | 0.0093749 | 0.0093749 | 0.0093749 | 0.97765 | -0.43069 | 0.97763 | -0.43105 | 2.5755
40 | -0.0075896 | -0.0019018 | 0.0075907 | 0.0019022 | 1.0768e-06 | 4.1926e-07 | 0.011551 | 0.011551 | 0.011551 | 0.97765 | -0.43069 | 0.9778 | -0.42771 | 3.1735
41 | -0.010461 | -0.0026214 | 0.010461 | 0.0026219 | 8.1802e-07 | 4.1555e-07 | 0.015919 | 0.015919 | 0.015919 | 0.9778 | -0.42771 | 0.97788 | -0.42607 | 4.3733
42 | -0.001187 | -0.00029749 | 0.001187 | 0.00029736 | 1.3572e-08 | -1.279e-07 | 0.0018147 | 0.0018147 | 0.0018147 | 0.97331 | -0.51622 | 0.97332 | -0.51598 | 0.49855
43 | 0.011083 | 0.0027702 | -0.011082 | -0.0027695 | 1.2238e-06 | 6.4192e-07 | 0.016941 | 0.016941 | 0.016941 | 0.97332 | -0.51598 | 0.9732 | -0.5183 | 4.6542
44 | -0.01227 | -0.0030676 | 0.012271 | 0.0030681 | 9.9633e-07 | 5.4377e-07 | 0.018756 | 0.018756 | 0.018756 | 0.97332 | -0.51598 | 0.9734 | -0.51427 | 5.1527
45 | 0.00045704 | 0.00011437 | -0.00045703 | -0.00011454 | 2.3283e-09 | -1.7186e-07 | 0.00068273 | 0.00068279 | 0.00068279 | 0.99603 | -0.075521 | 0.99602 | -0.075628 | 0.18758
46 | 0.00069053 | 0.00017263 | -0.00069053 | -0.00017285 | 6.6986e-09 | -2.1425e-07 | 0.0010314 | 0.0010315 | 0.0010315 | 0.99607 | -0.07482 | 0.99606 | -0.075024 | 0.28338
47 | 0.080073 | 0.020332 | -0.080054 | -0.02032 | 1.8718e-05 | 1.157e-05 | 0.11957 | 0.11957 | 0.11957 | 0.99724 | -0.052555 | 0.99698 | -0.057414 | 10.9499
48 | 0.013153 | 0.0032968 | -0.013152 | -0.0032963 | 7.9941e-07 | 4.4483e-07 | 0.020012 | 0.020012 | 0.020012 | 0.978 | -0.42382 | 0.97793 | -0.42509 | 5.4978
49 | 0.028157 | 0.0070873 | -0.0281 | -0.0070519 | 5.6845e-05 | 3.5347e-05 | 0.042852 | 0.042852 | 0.042852 | 0.978 | -0.42382 | 0.97584 | -0.46615 | 11.7726
50 | -0.04131 | -0.010384 | 0.041363 | 0.010418 | 5.3185e-05 | 3.3588e-05 | 0.062864 | 0.062864 | 0.062864 | 0.978 | -0.42382 | 0.97937 | -0.39689 | 17.2703
51 | 0.011585 | 0.0029036 | -0.011584 | -0.0029033 | 5.394e-07 | 2.8714e-07 | 0.017627 | 0.017627 | 0.017627 | 0.97793 | -0.42509 | 0.97788 | -0.42607 | 4.8427
52 | 0.025933 | 0.0065088 | -0.025925 | -0.0065039 | 7.9634e-06 | 4.927e-06 | 0.039548 | 0.039548 | 0.039548 | 0.97584 | -0.46615 | 0.97552 | -0.47259 | 10.8648
53 | -0.043772 | -0.011021 | 0.043803 | 0.01104 | 3.0644e-05 | 1.8682e-05 | 0.066524 | 0.066524 | 0.066524 | 0.97937 | -0.39689 | 0.98012 | -0.38226 | 9.1379
54 | 0.0088824 | 0.0022183 | -0.00888 | -0.0022172 | 2.3451e-06 | 1.0795e-06 | 0.013578 | 0.013578 | 0.013578 | 0.9732 | -0.5183 | 0.97292 | -0.52386 | 3.7303
55 | 0.0064152 | 0.0015995 | -0.0064134 | -0.0015989 | 1.8138e-06 | 5.3673e-07 | 0.0098086 | 0.0098089 | 0.0098089 | 0.97292 | -0.52386 | 0.97262 | -0.52982 | 2.6947
56 | -0.013876 | -0.0034704 | 0.013881 | 0.0034729 | 4.4593e-06 | 2.5252e-06 | 0.02121 | 0.02121 | 0.02121 | 0.9734 | -0.51427 | 0.97375 | -0.50752 | 5.8268
57 | -0.015506 | -0.0038802 | 0.015511 | 0.0038833 | 5.3396e-06 | 3.1017e-06 | 0.023693 | 0.023693 | 0.023693 | 0.97375 | -0.50752 | 0.97411 | -0.50028 | 6.509
58 | 0.00053701 | 0.00013437 | -0.000537 | -0.00013459 | 4.0006e-09 | -2.1322e-07 | 0.00080216 | 0.00080224 | 0.00080224 | 0.99606 | -0.075024 | 0.99605 | -0.07518 | 0.2204
59 | 0.00098774 | 0.00024704 | -0.00098773 | -0.00024719 | 9.7685e-09 | -1.4911e-07 | 0.0014763 | 0.0014764 | 0.0014764 | 0.99544 | -0.08701 | 0.99542 | -0.087218 | 0.4056
60 | -0.001254 | -0.00031378 | 0.0012541 | 0.00031337 | 4.4199e-08 | -4.0788e-07 | 0.0018744 | 0.0018742 | 0.0018744 | 0.99544 | -0.08701 | 0.99547 | -0.086269 | 0.51494
61 | 0.00069155 | 0.00017296 | -0.00069154 | -0.00017328 | 1.0113e-08 | -3.2162e-07 | 0.0010336 | 0.0010337 | 0.0010337 | 0.99542 | -0.087218 | 0.99541 | -0.087525 | 0.284
62 | 0.07485 | 0.018982 | -0.074736 | -0.018912 | 0.0001141 | 7.0189e-05 | 0.11196 | 0.11196 | 0.11196 | 0.99547 | -0.086269 | 0.99382 | -0.11803 | 10.2531
63 | -0.076104 | -0.019296 | 0.076209 | 0.019361 | 0.00010571 | 6.5102e-05 | 0.11384 | 0.11384 | 0.11384 | 0.99547 | -0.086269 | 0.99698 | -0.057414 | 10.4247
64 | 0.00021175 | 5.3034e-05 | -0.00021175 | -5.307e-05 | 1.0204e-10 | -3.5244e-08 | 0.00031653 | 0.00031654 | 0.00031654 | 0.99541 | -0.087525 | 0.99541 | -0.087535 | 0.086962
65 | 0.069967 | 0.017718 | -0.069925 | -0.017692 | 4.2268e-05 | 2.5856e-05 | 0.10483 | 0.10483 | 0.10483 | 0.99382 | -0.11803 | 0.99316 | -0.13062 | 9.5994
66 | 0.0047681 | 0.0011945 | -0.0047677 | -0.0011945 | 3.315e-07 | -1.2575e-08 | 0.0071389 | 0.007139 | 0.007139 | 0.99382 | -0.11803 | 0.99374 | -0.11949 | 1.9613
67 | 0.0038448 | 0.00095909 | -0.0038446 | -0.00095917 | 2.1022e-07 | -8.756e-08 | 0.0057368 | 0.0057369 | 0.0057369 | 0.99698 | -0.057414 | 0.99692 | -0.058566 | 1.5761
68 | 0.018805 | 0.0046253 | -0.018797 | -0.0046206 | 7.953e-06 | 4.7436e-06 | 0.028144 | 0.028144 | 0.028144 | 0.99316 | -0.13062 | 0.9927 | -0.13962 | 7.7319
69 | 0.05112 | 0.013067 | -0.050714 | -0.012828 | 0.00040674 | 0.00023902 | 0.076683 | 0.07669 | 0.07669 | 0.99316 | -0.13062 | 0.98453 | -0.29644 | 7.0229
70 | 0.0027396 | 0.00068616 | -0.0027394 | -0.00068638 | 1.5353e-07 | -2.1694e-07 | 0.004102 | 0.0041022 | 0.0041022 | 0.99374 | -0.11949 | 0.99368 | -0.12067 | 1.127
71 | 0.0035475 | 0.0008847 | -0.0035473 | -0.0008848 | 1.6251e-07 | -9.7637e-08 | 0.0052934 | 0.0052935 | 0.0052935 | 0.99692 | -0.058566 | 0.99687 | -0.059531 | 1.4543
72 | 0.013349 | 0.0032553 | -0.013348 | -0.0032546 | 1.2311e-06 | 6.8157e-07 | 0.019978 | 0.019978 | 0.019978 | 0.9927 | -0.13962 | 0.9926 | -0.1416 | 5.4885
73 | 0.00032981 | 7.8315e-05 | -0.00032978 | -8.2651e-05 | 3.1826e-08 | -4.3359e-06 | 0.00049697 | 0.00049848 | 0.00049848 | 0.98453 | -0.29644 | 0.98443 | -0.29851 | 0.13695
74 | 0.050384 | 0.012749 | -0.050381 | -0.012747 | 2.9281e-06 | 1.7201e-06 | 0.076193 | 0.076193 | 0.076193 | 0.98453 | -0.29644 | 0.98447 | -0.29765 | 6.9774
75 | 0.0079745 | 0.0019817 | -0.0079728 | -0.001981 | 1.7033e-06 | 6.8051e-07 | 0.01196 | 0.01196 | 0.01196 | 0.99168 | -0.15974 | 0.99145 | -0.16426 | 3.2857
76 | -0.0079745 | -0.0019817 | 0.0079784 | 0.0019833 | 3.9043e-06 | 1.5591e-06 | 0.01196 | 0.01196 | 0.01196 | 0.99168 | -0.15974 | 0.99221 | -0.1494 | 3.2857
77 | 0.0058178 | 0.0014415 | -0.0058132 | -0.0014406 | 4.6432e-06 | 8.7656e-07 | 0.0087259 | 0.0087266 | 0.0087266 | 0.99145 | -0.16426 | 0.99058 | -0.18116 | 2.3974
78 | 0.002155 | 0.00053949 | -0.0021548 | -0.00054004 | 2.1085e-07 | -5.5815e-07 | 0.0032341 | 0.0032344 | 0.0032344 | 0.99145 | -0.16426 | 0.99134 | -0.16631 | 0.88857
79 | -0.013343 | -0.0032519 | 0.013348 | 0.0032546 | 4.8604e-06 | 2.6911e-06 | 0.019978 | 0.019978 | 0.019978 | 0.99221 | -0.1494 | 0.9926 | -0.1416 | 5.4886
80 | 0.00064186 | 0.00016068 | -0.00064185 | -0.00016086 | 4.8999e-09 | -1.8009e-07 | 0.0009611 | 0.00096117 | 0.00096117 | 0.99368 | -0.12067 | 0.99367 | -0.12083 | 0.26406
81 | 0.0031966 | 0.00079691 | -0.0031964 | -0.00079707 | 1.8279e-07 | -1.623e-07 | 0.00477 | 0.0047701 | 0.0047701 | 0.99687 | -0.059531 | 0.99681 | -0.060736 | 1.3105
82 | -0.044818 | -0.011295 | 0.044838 | 0.011306 | 2.0106e-05 | 1.1554e-05 | 0.068065 | 0.068064 | 0.068065 | 0.98012 | -0.38226 | 0.9806 | -0.37289 | 6.2331
83 | 0.017707 | 0.0044341 | -0.017706 | -0.0044333 | 1.2999e-06 | 7.7292e-07 | 0.027045 | 0.027045 | 0.027045 | 0.97419 | -0.49874 | 0.97411 | -0.50028 | 7.4299
84 | -0.019319 | -0.0048382 | 0.019327 | 0.0048426 | 7.3862e-06 | 4.4454e-06 | 0.029508 | 0.029508 | 0.029508 | 0.97419 | -0.49874 | 0.9746 | -0.49071 | 8.1066
85 | -0.021131 | -0.0052949 | 0.021132 | 0.0052952 | 4.5194e-07 | 2.7481e-07 | 0.032263 | 0.032263 | 0.032263 | 0.9746 | -0.49071 | 0.97462 | -0.49026 | 8.8634
86 | 0.0044965 | 0.0011185 | -0.0044961 | -0.0011186 | 4.621e-07 | -2.766e-08 | 0.0068762 | 0.0068763 | 0.0068763 | 0.97262 | -0.52982 | 0.97251 | -0.53199 | 1.8891
87 | -0.044838 | -0.011306 | 0.044881 | 0.011331 | 4.267e-05 | 2.4517e-05 | 0.068064 | 0.068063 | 0.068064 | 0.9806 | -0.37289 | 0.98162 | -0.35302 | 6.233
88 | 0.0048703 | 0.0012187 | -0.0048699 | -0.0012187 | 3.1806e-07 | 6.8194e-09 | 0.007382 | 0.0073821 | 0.0073821 | 0.98162 | -0.35302 | 0.98155 | -0.35439 | 2.028
89 | -0.049751 | -0.012549 | 0.049883 | 0.012627 | 0.00013223 | 7.7561e-05 | 0.075446 | 0.075443 | 0.075446 | 0.98162 | -0.35302 | 0.98447 | -0.29765 | 6.9089
90 | 0.024833 | 0.00623 | -0.024823 | -0.0062242 | 9.449e-06 | 5.8282e-06 | 0.037881 | 0.037881 | 0.037881 | 0.97552 | -0.47259 | 0.97511 | -0.48057 | 10.4069
91 | 0.023815 | 0.0059716 | -0.023814 | -0.005971 | 1.025e-06 | 6.3021e-07 | 0.036343 | 0.036343 | 0.036343 | 0.97511 | -0.48057 | 0.97507 | -0.48148 | 9.9844
92 | 0.022953 | 0.0057551 | -0.022943 | -0.0057492 | 9.6089e-06 | 5.8893e-06 | 0.035029 | 0.035029 | 0.035029 | 0.97507 | -0.48148 | 0.97462 | -0.49026 | 9.6233
93 | 0.0035141 | 0.00087245 | -0.003514 | -0.00087252 | 1.2321e-07 | -6.2305e-08 | 0.0053739 | 0.0053739 | 0.0053739 | 0.97251 | -0.53199 | 0.97247 | -0.53273 | 1.4764
94 | -0.0010084 | -0.00025274 | 0.0010089 | 0.00024678 | 4.5024e-07 | -5.9563e-06 | 0.0015445 | 0.0015423 | 0.0015445 | 0.97154 | -0.55128 | 0.97202 | -0.54183 | 0.42432
95 | -0.0024218 | -0.00060089 | 0.0024228 | 0.00059905 | 1.0408e-06 | -1.8416e-06 | 0.0037052 | 0.0037043 | 0.0037052 | 0.97202 | -0.54183 | 0.97247 | -0.53273 | 1.0179
96 | -0.00049736 | -0.00012465 | 0.00049743 | 0.00012063 | 6.7607e-08 | -4.0189e-06 | 0.00075187 | 0.00075044 | 0.00075187 | 0.98433 | -0.30054 | 0.98447 | -0.29765 | 0.20656
97 | 0.0037926 | 0.00094869 | -0.0037919 | -0.00094898 | 7.7371e-07 | -2.9368e-07 | 0.0057489 | 0.0057492 | 0.0057492 | 0.98155 | -0.35439 | 0.98133 | -0.35868 | 1.5794
98 | 0.0030931 | 0.00077387 | -0.0030929 | -0.00077407 | 2.2457e-07 | -2.0025e-07 | 0.0046897 | 0.0046898 | 0.0046898 | 0.98133 | -0.35868 | 0.98126 | -0.36021 | 1.2884
99 | 0.0015679 | 0.00039186 | -0.0015678 | -0.00039268 | 1.5272e-07 | -8.1237e-07 | 0.0023773 | 0.0023776 | 0.0023776 | 0.98126 | -0.36021 | 0.98115 | -0.36226 | 0.65318
100 | 0.0007121 | 0.00017823 | -0.0007121 | -0.00017847 | 8.456e-09 | -2.3877e-07 | 0.0010799 | 0.00108 | 0.00108 | 0.98115 | -0.36226 | 0.98114 | -0.3625 | 0.2967
101 | 0.00098319 | 0.00024567 | -0.00098314 | -0.0002464 | 4.811e-08 | -7.2646e-07 | 0.0014767 | 0.0014769 | 0.0014769 | 0.99058 | -0.18116 | 0.99053 | -0.18219 | 0.40575
102 | 0.00483 | 0.001195 | -0.0048295 | -0.001195 | 4.9078e-07 | -6.3971e-09 | 0.00725 | 0.0072501 | 0.0072501 | 0.99058 | -0.18116 | 0.99047 | -0.18332 | 1.9918
103 | 0.0030267 | 0.00075454 | -0.0030263 | -0.000755 | 4.2707e-07 | -4.542e-07 | 0.0045168 | 0.0045171 | 0.0045171 | 0.99681 | -0.060736 | 0.99666 | -0.063709 | 1.241
104 | 0.0024664 | 0.00061467 | -0.0024661 | -0.00061516 | 2.5564e-07 | -4.9189e-07 | 0.0036811 | 0.0036813 | 0.0036813 | 0.99666 | -0.063709 | 0.99655 | -0.065894 | 1.0113
105 | 0.0019827 | 0.00049402 | -0.0019825 | -0.00049477 | 2.255e-07 | -7.4994e-07 | 0.0029596 | 0.0029599 | 0.0029599 | 0.99655 | -0.065894 | 0.99642 | -0.06829 | 0.81315
106 | 0.0011612 | 0.00028891 | -0.001161 | -0.00029021 | 1.1889e-07 | -1.298e-06 | 0.0017333 | 0.0017338 | 0.0017338 | 0.99642 | -0.06829 | 0.99631 | -0.070448 | 0.47631
107 | 0.00078876 | 0.00019691 | -0.00078873 | -0.00019767 | 3.139e-08 | -7.6554e-07 | 0.0011778 | 0.001178 | 0.001178 | 0.99631 | -0.070448 | 0.99627 | -0.071284 | 0.32364
108 | 0.00034939 | 8.6323e-05 | -0.00034938 | -8.7564e-05 | 1.0089e-08 | -1.2407e-06 | 0.00052557 | 0.00052601 | 0.00052601 | 0.98839 | -0.22705 | 0.98836 | -0.22766 | 0.14451
109 | -0.00061674 | -0.00014769 | 0.0006168 | 0.00014541 | 5.7632e-08 | -2.2739e-06 | 0.0009249 | 0.00092412 | 0.0009249 | 0.98968 | -0.20097 | 0.98978 | -0.19893 | 0.25409
110 | -0.00085158 | -0.00021343 | 0.00085175 | 0.00020995 | 1.7223e-07 | -3.4752e-06 | 0.0012821 | 0.0012808 | 0.0012821 | 0.98838 | -0.22467 | 0.98859 | -0.2204 | 0.35222
111 | -0.00085175 | -0.00020995 | 0.00085192 | 0.00020652 | 1.6984e-07 | -3.4353e-06 | 0.0012808 | 0.0012796 | 0.0012808 | 0.98859 | -0.2204 | 0.98881 | -0.21614 | 0.35187
112 | -0.00085192 | -0.00020652 | 0.00085193 | 0.00020641 | 5.1445e-09 | -1.0419e-07 | 0.0012796 | 0.0012795 | 0.0012796 | 0.98881 | -0.21614 | 0.98882 | -0.21601 | 0.35153
113 | -0.002084 | -0.0005152 | 0.002086 | 0.00050949 | 2.0023e-06 | -5.7065e-06 | 0.0031336 | 0.0031312 | 0.0031336 | 0.98882 | -0.21601 | 0.98985 | -0.19555 | 0.86088
114 | -0.0006168 | -0.00014541 | 0.00061683 | 0.00014434 | 2.7244e-08 | -1.0764e-06 | 0.00092412 | 0.00092376 | 0.00092412 | 0.98978 | -0.19893 | 0.98983 | -0.19796 | 0.25388
115 | 0.0042305 | 0.0010449 | -0.0042303 | -0.0010449 | 1.7523e-07 | -3.6987e-08 | 0.0063502 | 0.0063503 | 0.0063503 | 0.99047 | -0.18332 | 0.99043 | -0.18419 | 1.7446
116 | -0.0026317 | -0.00064626 | 0.0026323 | 0.00064533 | 5.9639e-07 | -9.2803e-07 | 0.0039515 | 0.0039511 | 0.0039515 | 0.98985 | -0.19555 | 0.9901 | -0.19072 | 1.0856
117 | -0.0031992 | -0.00078741 | 0.0031995 | 0.00078714 | 3.1813e-07 | -2.694e-07 | 0.0048031 | 0.0048029 | 0.0048031 | 0.9901 | -0.19072 | 0.9902 | -0.1886 | 1.3195
118 | 0.003607 | 0.00088868 | -0.0036063 | -0.00088908 | 7.4767e-07 | -3.967e-07 | 0.0054138 | 0.0054141 | 0.0054141 | 0.99043 | -0.18419 | 0.9902 | -0.1886 | 1.4874
119 | 0.00095252 | 0.00022366 | -0.00095241 | -0.00022551 | 1.1382e-07 | -1.8451e-06 | 0.0014263 | 0.0014269 | 0.0014269 | 0.99016 | -0.19125 | 0.99003 | -0.19387 | 0.39201
120 | 0.00095241 | 0.00022551 | -0.00095223 | -0.0002284 | 1.7864e-07 | -2.8915e-06 | 0.0014269 | 0.0014279 | 0.0014279 | 0.99003 | -0.19387 | 0.98983 | -0.19796 | 0.39229

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.10345 | 0.025952

## res_load
| p_mw | q_mvar
0 | 0.0004495 | 0.00011266
1 | 0.00019478 | 4.8816e-05
2 | 0.00028425 | 7.1239e-05
3 | 0.00022108 | 5.5409e-05
4 | 0.00018173 | 4.5545e-05
5 | 0.00026324 | 6.5975e-05
6 | 0.00035339 | 8.8568e-05
7 | 0.00019104 | 4.788e-05
8 | 0.00042872 | 0.00010745
9 | 0.00030226 | 7.5754e-05
10 | 0.001145 | 0.00028698
11 | 0.00017276 | 4.3298e-05
12 | 0.0009992 | 0.00025042
13 | 0.0018408 | 0.00046135
14 | 0.0094416 | 0.0023663
15 | 0.0015965 | 0.00040012
16 | 0.0023561 | 0.00059049
17 | 0.0010926 | 0.00027384
18 | 0.00018443 | 4.6223e-05
19 | 0.00014756 | 3.6983e-05
20 | 0.0003032 | 7.5988e-05
21 | 0.00034512 | 8.6495e-05
22 | 0.00024126 | 6.0465e-05
23 | 0.0019973 | 0.00050056
24 | 0.0012873 | 0.00032262
25 | 0.00022728 | 5.6962e-05
26 | 0.00143 | 0.0003584
27 | 0.0028747 | 0.00072047
28 | 0.0028698 | 0.00071925
29 | 0.001187 | 0.00029749
30 | 0.00065158 | 0.0001633
31 | 0.0003941 | 9.8771e-05
32 | 0.00025498 | 6.3903e-05
33 | 0.0015672 | 0.00039277
34 | 0.0021671 | 0.00054313
35 | 0.0024092 | 0.0006038
36 | 0.0011229 | 0.00028142
37 | 0.0021995 | 0.00055125
38 | 0.0024648 | 0.00061774
39 | 0.0016052 | 0.00040231
40 | 0.001625 | 0.00040727
41 | 0.00045703 | 0.00011454
42 | 0.00015352 | 3.8476e-05
43 | 0.00026629 | 6.6738e-05
44 | 0.00029619 | 7.4232e-05
45 | 0.00047979 | 0.00012025
46 | 0.00021175 | 5.307e-05
47 | 0.0020282 | 0.00050831
48 | 0.00029714 | 7.447e-05
49 | 0.0054477 | 0.0013653
50 | 0.0020976 | 0.0005257
51 | 0.0003507 | 8.7894e-05
52 | 0.0010152 | 0.00025444
53 | 0.0016125 | 0.00040413
54 | 0.0021945 | 0.00055
55 | 0.0018044 | 0.00045224
56 | 0.0019169 | 0.00048042
57 | 0.0010927 | 0.00027385
58 | 0.0010077 | 0.00025256
59 | 0.00086151 | 0.00021591
60 | 0.0018116 | 0.00045402
61 | 0.00098195 | 0.0002461
62 | 0.00064185 | 0.00016086
63 | 0.0010084 | 0.00025274
64 | 0.0014129 | 0.00035411
65 | 0.0010912 | 0.00027347
66 | 0.00049736 | 0.00012465
67 | 0.00032978 | 8.2651e-05
68 | 0.0010773 | 0.00027
69 | 0.00069871 | 0.00017511
70 | 0.001525 | 0.0003822
71 | 0.00085565 | 0.00021445
72 | 0.0007121 | 0.00017847
73 | 0.0021548 | 0.00054004
74 | 0.000537 | 0.00013459
75 | 0.00016968 | 4.2525e-05
76 | 0.00055993 | 0.00014033
77 | 0.00048336 | 0.00012114
78 | 0.00082137 | 0.00020586
79 | 0.00037227 | 9.33e-05
80 | 0.00078873 | 0.00019767
81 | 0.00047762 | 0.0001197
82 | 0.00034938 | 8.7564e-05
83 | 0.00085158 | 0.00021343
84 | 0.0012321 | 0.00030879
85 | 0.00098314 | 0.0002464
86 | 0.00059898 | 0.00015012
87 | 0.00054571 | 0.00013677
88 | 0.0005669 | 0.00014208
89 | 0.00062331 | 0.00015622
90 | 0.00040673 | 0.00010194
91 | 0.00033541 | 8.4061e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1