## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1301-18_1_3_node_4 | 0.4 | n |  | TRUE
1 | bus_LV_1301-18_1_3_node_5 | 0.4 | n |  | TRUE
2 | bus_LV_1301-18_1_3_node_6 | 0.4 | n |  | TRUE
3 | bus_LV_1301-18_1_3_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_1301-18_1_3_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_1301-18_1_3_node_99 | 0.4 | n |  | TRUE
6 | bus_LV_1301-18_1_3_node_87 | 0.4 | n |  | TRUE
7 | bus_LV_1301-18_1_3_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_1301-18_1_3_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_1301-18_1_3_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_1301-18_1_3_node_19 | 0.4 | n |  | TRUE
11 | bus_LV_1301-18_1_3_node_20 | 0.4 | n |  | TRUE
12 | bus_LV_1301-18_1_3_node_21 | 0.4 | n |  | TRUE
13 | bus_LV_1301-18_1_3_node_28 | 0.4 | n |  | TRUE
14 | bus_LV_1301-18_1_3_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_1301-18_1_3_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_1301-18_1_3_node_24 | 0.4 | n |  | TRUE
17 | bus_LV_1301-18_1_3_node_26 | 0.4 | n |  | TRUE
18 | bus_LV_1301-18_1_3_node_105 | 0.4 | n |  | TRUE
19 | bus_LV_1301-18_1_3_node_104 | 0.4 | n |  | TRUE
20 | bus_LV_1301-18_1_3_node_37 | 0.4 | n |  | TRUE
21 | bus_LV_1301-18_1_3_node_35 | 0.4 | n |  | TRUE
22 | bus_LV_1301-18_1_3_node_36 | 0.4 | n |  | TRUE
23 | bus_LV_1301-18_1_3_node_38 | 0.4 | n |  | TRUE
24 | bus_LV_1301-18_1_3_node_42 | 0.4 | n |  | TRUE
25 | bus_LV_1301-18_1_3_node_39 | 0.4 | n |  | TRUE
26 | bus_LV_1301-18_1_3_node_40 | 0.4 | n |  | TRUE
27 | bus_LV_1301-18_1_3_node_55 | 0.4 | n |  | TRUE
28 | bus_LV_1301-18_1_3_node_49 | 0.4 | n |  | TRUE
29 | bus_LV_1301-18_1_3_node_41 | 0.4 | n |  | TRUE
30 | bus_LV_1301-18_1_3_node_90 | 0.4 | n |  | TRUE
31 | bus_LV_1301-18_1_3_node_103 | 0.4 | n |  | TRUE
32 | bus_LV_1301-18_1_3_node_50 | 0.4 | n |  | TRUE
33 | bus_LV_1301-18_1_3_node_51 | 0.4 | n |  | TRUE
34 | bus_LV_1301-18_1_3_node_53 | 0.4 | n |  | TRUE
35 | bus_LV_1301-18_1_3_node_52 | 0.4 | n |  | TRUE
36 | bus_LV_1301-18_1_3_node_115 | 0.4 | n |  | TRUE
37 | bus_LV_1301-18_1_3_node_54 | 0.4 | n |  | TRUE
38 | bus_LV_1301-18_1_3_node_61 | 0.4 | n |  | TRUE
39 | bus_LV_1301-18_1_3_node_74 | 0.4 | n |  | TRUE
40 | bus_LV_1301-18_1_3_node_113 | 0.4 | n |  | TRUE
41 | bus_LV_1301-18_1_3_node_70 | 0.4 | n |  | TRUE
42 | bus_LV_1301-18_1_3_node_71 | 0.4 | n |  | TRUE
43 | bus_LV_1301-18_1_3_node_72 | 0.4 | n |  | TRUE
44 | bus_LV_1301-18_1_3_node_73 | 0.4 | n |  | TRUE
45 | bus_LV_1301-18_1_3_node_88 | 0.4 | n |  | TRUE
46 | bus_LV_1301-18_1_3_node_89 | 0.4 | n |  | TRUE
47 | bus_LV_1301-18_1_3_node_100 | 0.4 | n |  | TRUE
48 | bus_LV_1301-18_1_3_node_101 | 0.4 | n |  | TRUE
49 | bus_LV_1301-18_1_3_node_102 | 0.4 | n |  | TRUE
50 | bus_MV_17_0_node_23 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1301-18_1_3_load_4 | 0 | 0.003637 | 0.00091151 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1301-18_1_3_load_5 | 1 | 0.0065117 | 0.001632 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1301-18_1_3_load_8 | 4 | 0.00423 | 0.0010601 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1301-18_1_3_load_99 | 5 | 0.0035451 | 0.00088848 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1301-18_1_3_load_87 | 6 | 0.0018492 | 0.00046346 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1301-18_1_3_load_16 | 7 | 0.022544 | 0.00565 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1301-18_1_3_load_17 | 8 | 0.0016086 | 0.00040315 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1301-18_1_3_load_18 | 9 | 0.0044504 | 0.0011154 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1301-18_1_3_load_20 | 11 | 0.0044511 | 0.0011156 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1301-18_1_3_load_21 | 12 | 0.0015721 | 0.00039402 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1301-18_1_3_load_22 | 14 | 0.0013005 | 0.00032592 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1301-18_1_3_load_23 | 15 | 0.0004791 | 0.00012007 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1301-18_1_3_load_105 | 18 | 0.0095692 | 0.0023983 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1301-18_1_3_load_104 | 19 | 0.00057375 | 0.0001438 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1301-18_1_3_load_35 | 21 | 0.001218 | 0.00030525 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1301-18_1_3_load_36 | 22 | 0.00099004 | 0.00024813 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1301-18_1_3_load_38 | 23 | 0.0011611 | 0.000291 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1301-18_1_3_load_55 | 27 | 0.0025336 | 0.00063499 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1301-18_1_3_load_49 | 28 | 0.0066584 | 0.0016688 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1301-18_1_3_load_90 | 30 | 0.004578 | 0.0011474 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1301-18_1_3_load_103 | 31 | 0.00096073 | 0.00024078 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1301-18_1_3_load_115 | 36 | 0.020179 | 0.0050574 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1301-18_1_3_load_74 | 39 | 0.0036009 | 0.00090247 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1301-18_1_3_load_113 | 40 | 0.032998 | 0.00827 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1301-18_1_3_load_70 | 41 | 0.0030624 | 0.00076751 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1301-18_1_3_load_71 | 42 | 0.0065751 | 0.0016479 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1301-18_1_3_load_72 | 43 | 0.0070227 | 0.0017601 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1301-18_1_3_load_88 | 45 | 0.0033838 | 0.00084806 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1301-18_1_3_load_89 | 46 | 0.008062 | 0.0020205 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1301-18_1_3_load_100 | 47 | 0.0023718 | 0.00059442 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1301-18_1_3_load_101 | 48 | 0.00032028 | 8.027e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1301-18_1_3_load_102 | 49 | 0.0062802 | 0.001574 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1301-18_1_3_line_0 |  | 0 | 1 | 0.0086617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1301-18_1_3_line_1 |  | 0 | 2 | 0.030005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1301-18_1_3_line_2 |  | 2 | 3 | 0.015189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1301-18_1_3_line_3 |  | 2 | 4 | 0.039914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1301-18_1_3_line_4 |  | 3 | 5 | 0.018405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1301-18_1_3_line_5 |  | 4 | 6 | 0.031071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1301-18_1_3_line_6 |  | 6 | 33 | 0.0042258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1301-18_1_3_line_7 |  | 7 | 8 | 0.046493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1301-18_1_3_line_8 |  | 7 | 9 | 0.020398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1301-18_1_3_line_9 |  | 8 | 10 | 0.020238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1301-18_1_3_line_10 |  | 9 | 11 | 0.0085027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1301-18_1_3_line_11 |  | 10 | 12 | 0.017194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1301-18_1_3_line_12 |  | 11 | 13 | 0.016745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1301-18_1_3_line_13 |  | 13 | 20 | 0.096525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1301-18_1_3_line_14 |  | 14 | 15 | 0.012223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1301-18_1_3_line_15 |  | 14 | 16 | 0.2122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1301-18_1_3_line_16 |  | 16 | 17 | 0.13894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1301-18_1_3_line_17 |  | 17 | 18 | 0.049043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1301-18_1_3_line_18 |  | 17 | 19 | 0.015261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1301-18_1_3_line_19 |  | 18 | 25 | 0.037639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1301-18_1_3_line_20 |  | 20 | 24 | 0.21973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1301-18_1_3_line_21 |  | 20 | 21 | 0.065987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1301-18_1_3_line_22 |  | 21 | 22 | 0.026732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1301-18_1_3_line_23 |  | 22 | 23 | 0.0010434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1301-18_1_3_line_24 |  | 24 | 31 | 0.022493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1301-18_1_3_line_25 |  | 24 | 25 | 0.037434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1301-18_1_3_line_26 |  | 24 | 29 | 0.06327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1301-18_1_3_line_27 |  | 26 | 27 | 0.020672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_1301-18_1_3_line_28 |  | 26 | 28 | 0.0049418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_1301-18_1_3_line_29 |  | 27 | 29 | 0.014413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_1301-18_1_3_line_30 |  | 28 | 32 | 0.0042317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_1301-18_1_3_line_31 |  | 29 | 30 | 0.047011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_1301-18_1_3_line_32 |  | 30 | 46 | 0.059738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1301-18_1_3_line_33 |  | 31 | 48 | 0.035946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1301-18_1_3_line_34 |  | 32 | 33 | 0.035496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_1301-18_1_3_line_35 |  | 33 | 34 | 0.055535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_1301-18_1_3_line_36 |  | 34 | 35 | 0.099748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_1301-18_1_3_line_37 |  | 35 | 36 | 0.040566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1301-18_1_3_line_38 |  | 35 | 37 | 0.13234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1301-18_1_3_line_39 |  | 37 | 38 | 0.14635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1301-18_1_3_line_40 |  | 37 | 39 | 0.021467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1301-18_1_3_line_41 |  | 38 | 40 | 0.11138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1301-18_1_3_line_42 |  | 39 | 43 | 0.0086013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1301-18_1_3_line_43 |  | 41 | 42 | 0.018529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1301-18_1_3_line_44 |  | 41 | 43 | 0.0023465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1301-18_1_3_line_45 |  | 42 | 44 | 0.0085375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1301-18_1_3_line_46 |  | 44 | 45 | 0.012337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1301-18_1_3_line_47 |  | 47 | 48 | 0.0020539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1301-18_1_3_line_48 |  | 47 | 49 | 0.014016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1301-18_1_3_trafo_90 | 0.63 MVA 20/0.4 kV | 50 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2699149.1699 | 1221456.5213 | 2699150.6448 | 1221465.0565
1 | 2699144.0606 | 1221426.9549 | 2699149.1699 | 1221456.5213
2 | 2699144.0606 | 1221426.9549 | 2699129.1385 | 1221430.0086
3 | 2699144.0606 | 1221426.9549 | 2699138.9227 | 1221397.8819 | 2699136.9478 | 1221387.6813
4 | 2699129.1385 | 1221430.0086 | 2699111.1071 | 1221433.6982
5 | 2699136.9478 | 1221387.6813 | 2699131.0418 | 1221357.1764
6 | 2699130.2386 | 1221353.0276 | 2699131.0418 | 1221357.1764
7 | 2699305.0976 | 1221257.8084 | 2699280.8413 | 1221262.1158 | 2699280.0434 | 1221240.2734
8 | 2699325.1819 | 1221254.2419 | 2699305.0976 | 1221257.8084
9 | 2699279.3047 | 1221220.0491 | 2699280.0434 | 1221240.2734
10 | 2699333.5537 | 1221252.7552 | 2699325.1819 | 1221254.2419
11 | 2699279.3047 | 1221220.0491 | 2699278.6749 | 1221202.8668
12 | 2699350.0404 | 1221249.8275 | 2699333.5537 | 1221252.7552
13 | 2699390.4178 | 1221317.7608 | 2699379.3367 | 1221284.7857 | 2699377.823 | 1221280.4685 | 2699372.4058 | 1221246.3649 | 2699350.0404 | 1221249.8275
14 | 2699264.8775 | 1221220.0922 | 2699264.5765 | 1221207.8727
15 | 2699185.9265 | 1221065.9724 | 2699241.2248 | 1221061.9907 | 2699245.6881 | 1221062.3431 | 2699247.697 | 1221065.6456 | 2699248.6567 | 1221080.8947 | 2699251.9156 | 1221083.4063 | 2699257.7631 | 1221085.8388 | 2699260.9157 | 1221102.0029 | 2699264.5707 | 1221122.1559 | 2699264.4222 | 1221142.4346 | 2699263.7206 | 1221173.1336 | 2699264.5765 | 1221207.8727
16 | 2699185.9265 | 1221065.9724 | 2699187.924 | 1221090.9012 | 2699190.163 | 1221130.9337 | 2699191.7158 | 1221157.5007 | 2699193.3769 | 1221171.1937 | 2699195.3906 | 1221187.8613 | 2699197.3992 | 1221204.3843
17 | 2699197.3992 | 1221204.3843 | 2699199.3466 | 1221220.4727 | 2699201.3938 | 1221253.2457
18 | 2699197.3992 | 1221204.3843 | 2699212.6346 | 1221203.4974
19 | 2699203.7891 | 1221290.8079 | 2699203.2757 | 1221283.3718 | 2699201.3938 | 1221253.2457
20 | 2699217.1113 | 1221321.8519 | 2699212.3416 | 1221321.2276 | 2699210.6099 | 1221312.2257 | 2699222.5324 | 1221310.2562 | 2699262.5789 | 1221302.5513 | 2699284.5712 | 1221299.1488 | 2699379.3367 | 1221284.7857 | 2699390.4178 | 1221317.7608
21 | 2699390.4178 | 1221317.7608 | 2699324.8563 | 1221325.2459
22 | 2699324.8563 | 1221325.2459 | 2699298.2965 | 1221328.2783
23 | 2699297.2598 | 1221328.3966 | 2699298.2965 | 1221328.2783
24 | 2699217.1113 | 1221321.8519 | 2699221.5327 | 1221322.4371 | 2699239.429 | 1221320.2181
25 | 2699203.7891 | 1221290.8079 | 2699208.0552 | 1221294.7929 | 2699210.6099 | 1221312.2257 | 2699212.3416 | 1221321.2276 | 2699217.1113 | 1221321.8519
26 | 2699179.5518 | 1221297.3422 | 2699179.9002 | 1221306.9438 | 2699180.2347 | 1221316.0114 | 2699182.8892 | 1221315.622 | 2699205.4851 | 1221312.8741 | 2699210.6099 | 1221312.2257 | 2699212.3416 | 1221321.2276 | 2699217.1113 | 1221321.8519
27 | 2699154.0769 | 1221321.2351 | 2699163.7378 | 1221312.4675 | 2699169.759 | 1221307.788
28 | 2699154.0769 | 1221321.2351 | 2699149.2772 | 1221322.4116
29 | 2699179.5518 | 1221297.3422 | 2699173.7386 | 1221304.6951 | 2699169.759 | 1221307.788
30 | 2699145.2062 | 1221323.5669 | 2699149.2772 | 1221322.4116
31 | 2699179.5518 | 1221297.3422 | 2699179.4773 | 1221294.072 | 2699177.248 | 1221250.3887
32 | 2699171.8724 | 1221190.9436 | 2699174.2087 | 1221221.388 | 2699176.0499 | 1221232.0151 | 2699176.5201 | 1221236.1259 | 2699177.248 | 1221250.3887
33 | 2699259.1624 | 1221333.7477 | 2699259.2371 | 1221317.762 | 2699239.429 | 1221320.2181
34 | 2699145.2062 | 1221323.5669 | 2699135.5068 | 1221330.5549 | 2699134.3799 | 1221333.983 | 2699132.1398 | 1221336.8255 | 2699130.9683 | 1221347.0244 | 2699130.2386 | 1221353.0276
35 | 2699093.2371 | 1221339.6579 | 2699092.2532 | 1221332.6699 | 2699098.1525 | 1221331.5339 | 2699106.2716 | 1221332.87 | 2699116.1866 | 1221334.3471 | 2699119.1153 | 1221337.5426 | 2699123.1078 | 1221339.2769 | 2699126.7862 | 1221347.5663 | 2699130.2386 | 1221353.0276
36 | 2699093.2371 | 1221339.6579 | 2699092.2532 | 1221332.6699 | 2699098.1525 | 1221331.5339 | 2699093.7647 | 1221314.3487 | 2699104.7062 | 1221310.6837 | 2699095.4747 | 1221254.023
37 | 2699089.5329 | 1221213.9623 | 2699094.5808 | 1221240.7209 | 2699095.4747 | 1221254.023
38 | 2699092.1099 | 1221138.0177 | 2699107.5224 | 1221224.9472 | 2699112.2527 | 1221251.6338 | 2699095.4747 | 1221254.023
39 | 2699092.1099 | 1221138.0177 | 2699088.3222 | 1221117.1399 | 2699086.3344 | 1221104.8202 | 2699082.337 | 1221080.125 | 2699081.8902 | 1221077.3378 | 2699077.28 | 1221046.6059 | 2699099.4622 | 1221043.6951 | 2699101.1993 | 1221051.9299 | 2699110.6852 | 1221072.8248
40 | 2699092.1099 | 1221138.0177 | 2699082.547 | 1221139.9823 | 2699071.0287 | 1221142.0612
41 | 2699110.6852 | 1221072.8248 | 2699119.1716 | 1221092.2243 | 2699128.1739 | 1221101.603 | 2699136.2042 | 1221149.2929 | 2699137.9952 | 1221162.4876 | 2699138.9542 | 1221169.1417 | 2699139.1108 | 1221177.9617
42 | 2699071.0287 | 1221142.0612 | 2699062.5642 | 1221143.589
43 | 2699060.255 | 1221144.0058 | 2699042.0204 | 1221147.297
44 | 2699060.255 | 1221144.0058 | 2699062.5642 | 1221143.589
45 | 2699034.5385 | 1221143.6865 | 2699038.1211 | 1221145.8921 | 2699040.9779 | 1221147.4851 | 2699042.0204 | 1221147.297
46 | 2699034.5385 | 1221143.6865 | 2699036.4104 | 1221141.5383 | 2699035.9409 | 1221132.0621
47 | 2699259.1528 | 1221335.8017 | 2699259.1624 | 1221333.7477
48 | 2699258.9074 | 1221349.8127 | 2699259.1072 | 1221345.5686 | 2699259.1528 | 1221335.8017

## bus_geodata
| x | y | coords
0 | 2699149.1699 | 1221456.5213
1 | 2699150.6448 | 1221465.0565
2 | 2699144.0606 | 1221426.9549
3 | 2699129.1385 | 1221430.0087
4 | 2699136.9478 | 1221387.6813
5 | 2699111.1071 | 1221433.6982
6 | 2699131.0418 | 1221357.1764
7 | 2699305.0976 | 1221257.8084
8 | 2699280.0434 | 1221240.2734
9 | 2699325.1819 | 1221254.2419
10 | 2699279.3047 | 1221220.0491
11 | 2699333.5537 | 1221252.7552
12 | 2699278.6749 | 1221202.8668
13 | 2699350.0404 | 1221249.8275
14 | 2699264.5765 | 1221207.8727
15 | 2699264.8775 | 1221220.0922
16 | 2699185.9265 | 1221065.9724
17 | 2699197.3992 | 1221204.3843
18 | 2699201.3938 | 1221253.2457
19 | 2699212.6346 | 1221203.4974
20 | 2699390.4178 | 1221317.7608
21 | 2699324.8563 | 1221325.2459
22 | 2699298.2965 | 1221328.2783
23 | 2699297.2598 | 1221328.3966
24 | 2699217.1113 | 1221321.8519
25 | 2699203.7891 | 1221290.8079
26 | 2699154.0769 | 1221321.2351
27 | 2699169.759 | 1221307.788
28 | 2699149.2772 | 1221322.4116
29 | 2699179.5518 | 1221297.3422
30 | 2699177.248 | 1221250.3887
31 | 2699239.429 | 1221320.2181
32 | 2699145.2062 | 1221323.5669
33 | 2699130.2386 | 1221353.0276
34 | 2699093.2371 | 1221339.6579
35 | 2699095.4747 | 1221254.023
36 | 2699089.5329 | 1221213.9623
37 | 2699092.1099 | 1221138.0177
38 | 2699110.6852 | 1221072.8248
39 | 2699071.0287 | 1221142.0612
40 | 2699139.1108 | 1221177.9617
41 | 2699060.255 | 1221144.0058
42 | 2699042.0204 | 1221147.297
43 | 2699062.5642 | 1221143.589
44 | 2699034.5385 | 1221143.6865
45 | 2699035.9409 | 1221132.0621
46 | 2699171.8724 | 1221190.9436
47 | 2699259.1528 | 1221335.8017
48 | 2699259.1624 | 1221333.7477
49 | 2699258.9074 | 1221349.8127
50 | 2699179.5518 | 1221297.3422

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99134 | -0.16513 | 0.003637 | 0.00091151
1 | 0.99129 | -0.16613 | 0.0065117 | 0.001632
2 | 0.99162 | -0.15973 | 0 | 0
3 | 0.99157 | -0.16068 | 0 | 0
4 | 0.99212 | -0.15004 | 0.00423 | 0.0010601
5 | 0.99151 | -0.16184 | 0.0035451 | 0.00088848
6 | 0.99262 | -0.14018 | 0.0018492 | 0.00046346
7 | 0.98085 | -0.36855 | 0.022544 | 0.00565
8 | 0.98071 | -0.37123 | 0.0016086 | 0.00040315
9 | 0.98134 | -0.35904 | 0.0044504 | 0.0011154
10 | 0.98068 | -0.3718 | 0 | 0
11 | 0.98157 | -0.3544 | 0.0044511 | 0.0011156
12 | 0.98066 | -0.37229 | 0.0015721 | 0.00039402
13 | 0.98211 | -0.34392 | 0 | 0
14 | 0.99142 | -0.16392 | 0.0013005 | 0.00032592
15 | 0.99142 | -0.16402 | 0.0004791 | 0.00012007
16 | 0.99177 | -0.15721 | 0 | 0
17 | 0.99199 | -0.1528 | 0 | 0
18 | 0.9921 | -0.15075 | 0.0095692 | 0.0023983
19 | 0.99199 | -0.15296 | 0.00057375 | 0.0001438
20 | 0.9852 | -0.2837 | 0 | 0
21 | 0.98499 | -0.28769 | 0.001218 | 0.00030525
22 | 0.98494 | -0.28873 | 0.00099004 | 0.00024813
23 | 0.98494 | -0.28875 | 0.0011611 | 0.000291
24 | 0.99292 | -0.13489 | 0 | 0
25 | 0.99251 | -0.14279 | 0 | 0
26 | 0.99471 | -0.10032 | 0 | 0
27 | 0.9957 | -0.081534 | 0.0025336 | 0.00063499
28 | 0.99448 | -0.10482 | 0.0066584 | 0.0016688
29 | 0.9964 | -0.068136 | 0 | 0
30 | 1 | 0 | -0.17794 | -0.045158
31 | 0.99271 | -0.13884 | 0.00096073 | 0.00024078
32 | 0.99429 | -0.10842 | 0 | 0
33 | 0.9927 | -0.1387 | 0 | 0
34 | 0.99072 | -0.17652 | 0 | 0
35 | 0.98717 | -0.24482 | 0 | 0
36 | 0.98641 | -0.25947 | 0.020179 | 0.0050574
37 | 0.98019 | -0.37987 | 0 | 0
38 | 0.97569 | -0.4679 | 0 | 0
39 | 0.97972 | -0.38908 | 0.0036009 | 0.00090247
40 | 0.97226 | -0.53543 | 0.032998 | 0.00827
41 | 0.97953 | -0.39277 | 0.0030624 | 0.00076751
42 | 0.97936 | -0.39612 | 0.0065751 | 0.0016479
43 | 0.97956 | -0.39221 | 0.0070227 | 0.0017601
44 | 0.97934 | -0.39665 | 0 | 0
45 | 0.9793 | -0.39741 | 0.0033838 | 0.00084806
46 | 0.99956 | -0.0083989 | 0.008062 | 0.0020205
47 | 0.9924 | -0.14486 | 0.0023718 | 0.00059442
48 | 0.99242 | -0.14455 | 0.00032028 | 8.027e-05
49 | 0.99232 | -0.14642 | 0.0062802 | 0.001574
50 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.006512 | 0.0016321 | -0.0065117 | -0.001632 | 3.1034e-07 | 8.6949e-08 | 0.0097747 | 0.0097747 | 0.0097747 | 0.99134 | -0.16513 | 0.99129 | -0.16613 | 2.6854
1 | -0.010149 | -0.0025436 | 0.010152 | 0.0025449 | 2.6112e-06 | 1.2842e-06 | 0.015234 | 0.015234 | 0.015234 | 0.99134 | -0.16513 | 0.99162 | -0.15973 | 4.1851
2 | 0.0035454 | 0.00088828 | -0.0035453 | -0.00088837 | 1.6122e-07 | -9.2751e-08 | 0.0053202 | 0.0053203 | 0.0053203 | 0.99162 | -0.15973 | 0.99157 | -0.16068 | 1.4616
3 | -0.013697 | -0.0034331 | 0.013703 | 0.0034367 | 6.3232e-06 | 3.5317e-06 | 0.020554 | 0.020554 | 0.020554 | 0.99162 | -0.15973 | 0.99212 | -0.15004 | 5.6467
4 | 0.0035453 | 0.00088837 | -0.0035451 | -0.00088848 | 1.9536e-07 | -1.1236e-07 | 0.0053203 | 0.0053203 | 0.0053203 | 0.99157 | -0.16068 | 0.99151 | -0.16184 | 1.4616
5 | -0.017933 | -0.0044968 | 0.017942 | 0.0045018 | 8.43e-06 | 4.9938e-06 | 0.026898 | 0.026898 | 0.026898 | 0.99212 | -0.15004 | 0.99262 | -0.14018 | 7.3895
6 | -0.019791 | -0.0049653 | 0.019792 | 0.0049661 | 1.395e-06 | 8.3818e-07 | 0.02967 | 0.02967 | 0.02967 | 0.99262 | -0.14018 | 0.9927 | -0.1387 | 8.1511
7 | 0.0031812 | 0.00079642 | -0.0031808 | -0.00079675 | 4.0605e-07 | -3.2686e-07 | 0.0048258 | 0.004826 | 0.004826 | 0.98085 | -0.36855 | 0.98071 | -0.37123 | 1.3258
8 | -0.025725 | -0.0064465 | 0.025737 | 0.0064537 | 1.1651e-05 | 7.1987e-06 | 0.039026 | 0.039026 | 0.039026 | 0.98085 | -0.36855 | 0.98134 | -0.35904 | 10.7216
9 | 0.0015722 | 0.00039359 | -0.0015722 | -0.00039382 | 4.3183e-08 | -2.2772e-07 | 0.0023853 | 0.0023854 | 0.0023854 | 0.98071 | -0.37123 | 0.98068 | -0.3718 | 0.65534
10 | -0.030187 | -0.007569 | 0.030194 | 0.0075732 | 6.681e-06 | 4.1684e-06 | 0.045775 | 0.045775 | 0.045775 | 0.98134 | -0.35904 | 0.98157 | -0.3544 | 12.5754
11 | 0.0015722 | 0.00039382 | -0.0015721 | -0.00039402 | 3.669e-08 | -1.9345e-07 | 0.0023854 | 0.0023855 | 0.0023855 | 0.98068 | -0.3718 | 0.98066 | -0.37229 | 0.65536
12 | -0.034645 | -0.0086888 | 0.034662 | 0.0086996 | 1.7322e-05 | 1.0874e-05 | 0.052522 | 0.052522 | 0.052522 | 0.98157 | -0.3544 | 0.98211 | -0.34392 | 14.4292
13 | -0.034662 | -0.0086996 | 0.034762 | 0.0087623 | 9.9851e-05 | 6.2679e-05 | 0.052522 | 0.052522 | 0.052522 | 0.98211 | -0.34392 | 0.9852 | -0.2837 | 14.4292
14 | 0.0004791 | 0.00011992 | -0.0004791 | -0.00012007 | 2.3699e-09 | -1.561e-07 | 0.00071902 | 0.00071908 | 0.00071908 | 0.99142 | -0.16392 | 0.99142 | -0.16402 | 0.19755
15 | -0.0017796 | -0.00044584 | 0.0017801 | 0.00044347 | 5.6743e-07 | -2.3741e-06 | 0.0026709 | 0.0026699 | 0.0026709 | 0.99142 | -0.16392 | 0.99177 | -0.15721 | 0.73375
16 | -0.0017801 | -0.00044347 | 0.0017805 | 0.00044191 | 3.7132e-07 | -1.5557e-06 | 0.0026699 | 0.0026693 | 0.0026699 | 0.99177 | -0.15721 | 0.99199 | -0.1528 | 0.73349
17 | -0.0023542 | -0.00058551 | 0.0023545 | 0.00058503 | 2.2913e-07 | -4.8657e-07 | 0.0035298 | 0.0035296 | 0.0035298 | 0.99199 | -0.1528 | 0.9921 | -0.15075 | 0.96974
18 | 0.00057375 | 0.0001436 | -0.00057375 | -0.0001438 | 4.2387e-09 | -1.9431e-07 | 0.00086058 | 0.00086064 | 0.00086064 | 0.99199 | -0.1528 | 0.99199 | -0.15296 | 0.23644
19 | -0.011924 | -0.0029833 | 0.011928 | 0.0029857 | 4.5134e-06 | 2.4023e-06 | 0.017882 | 0.017882 | 0.017882 | 0.9921 | -0.15075 | 0.99251 | -0.14279 | 4.9127
20 | -0.038132 | -0.009606 | 0.038406 | 0.0097782 | 0.00027348 | 0.00017221 | 0.057611 | 0.05761 | 0.057611 | 0.9852 | -0.2837 | 0.99292 | -0.13489 | 15.8272
21 | 0.0033699 | 0.00084367 | -0.0033692 | -0.0008441 | 6.41e-07 | -4.2986e-07 | 0.0050894 | 0.0050897 | 0.0050897 | 0.9852 | -0.2837 | 0.98499 | -0.28769 | 1.3983
22 | 0.0021512 | 0.00053884 | -0.0021511 | -0.00053911 | 1.0587e-07 | -2.7249e-07 | 0.0032497 | 0.0032499 | 0.0032499 | 0.98499 | -0.28769 | 0.98494 | -0.28873 | 0.89282
23 | 0.0011611 | 0.00029099 | -0.0011611 | -0.000291 | 1.2041e-09 | -1.251e-08 | 0.0017541 | 0.0017542 | 0.0017542 | 0.98494 | -0.28873 | 0.98494 | -0.28875 | 0.48191
24 | 0.0099379 | 0.0024916 | -0.009936 | -0.0024907 | 1.871e-06 | 9.066e-07 | 0.014894 | 0.014894 | 0.014894 | 0.99292 | -0.13489 | 0.99271 | -0.13884 | 4.0917
25 | 0.011933 | 0.0029881 | -0.011928 | -0.0029857 | 4.4888e-06 | 2.3888e-06 | 0.017882 | 0.017882 | 0.017882 | 0.99292 | -0.13489 | 0.99251 | -0.14279 | 4.9126
26 | -0.060276 | -0.015258 | 0.06047 | 0.015381 | 0.00019383 | 0.00012323 | 0.090385 | 0.090385 | 0.090385 | 0.99292 | -0.13489 | 0.9964 | -0.068136 | 24.8311
27 | -0.1045 | -0.026662 | 0.10459 | 0.026722 | 9.4922e-05 | 6.0213e-05 | 0.15649 | 0.15649 | 0.15649 | 0.99471 | -0.10032 | 0.9957 | -0.081534 | 21.4961
28 | 0.1045 | 0.026662 | -0.10448 | -0.026648 | 2.2692e-05 | 1.4395e-05 | 0.15649 | 0.15649 | 0.15649 | 0.99471 | -0.10032 | 0.99448 | -0.10482 | 21.4961
29 | -0.10713 | -0.027357 | 0.1072 | 0.027401 | 6.9425e-05 | 4.4057e-05 | 0.16028 | 0.16028 | 0.16028 | 0.9957 | -0.081534 | 0.9964 | -0.068136 | 22.0162
30 | 0.097819 | 0.024979 | -0.097802 | -0.024968 | 1.7036e-05 | 1.0793e-05 | 0.14653 | 0.14653 | 0.14653 | 0.99448 | -0.10482 | 0.99429 | -0.10842 | 20.1276
31 | -0.16767 | -0.042782 | 0.16822 | 0.043136 | 0.00055384 | 0.00035323 | 0.25066 | 0.25066 | 0.25066 | 0.9964 | -0.068136 | 1 | 0 | 34.4317
32 | 0.0080653 | 0.0020218 | -0.008062 | -0.0020205 | 3.2267e-06 | 1.2817e-06 | 0.012001 | 0.012002 | 0.012002 | 1 | 0 | 0.99956 | -0.0083989 | 3.2972
33 | 0.0089753 | 0.0022499 | -0.0089728 | -0.0022488 | 2.4398e-06 | 1.0969e-06 | 0.013454 | 0.013454 | 0.013454 | 0.99271 | -0.13884 | 0.99242 | -0.14455 | 3.6961
34 | 0.097802 | 0.024968 | -0.097659 | -0.024878 | 0.0001429 | 9.0535e-05 | 0.14653 | 0.14653 | 0.14653 | 0.99429 | -0.10842 | 0.9927 | -0.1387 | 20.1276
35 | 0.077866 | 0.019911 | -0.077724 | -0.019822 | 0.0001422 | 8.9574e-05 | 0.11686 | 0.11686 | 0.11686 | 0.9927 | -0.1387 | 0.99072 | -0.17652 | 16.0522
36 | 0.077724 | 0.019822 | -0.077469 | -0.019661 | 0.00025541 | 0.0001609 | 0.11686 | 0.11686 | 0.11686 | 0.99072 | -0.17652 | 0.98717 | -0.24482 | 16.0523
37 | 0.020193 | 0.0050659 | -0.020179 | -0.0050574 | 1.4096e-05 | 8.5032e-06 | 0.03044 | 0.03044 | 0.03044 | 0.98717 | -0.24482 | 0.98641 | -0.25947 | 8.3628
38 | 0.057275 | 0.014595 | -0.056905 | -0.01436 | 0.00037064 | 0.00023553 | 0.086421 | 0.086421 | 0.086421 | 0.98717 | -0.24482 | 0.98019 | -0.37987 | 23.7422
39 | 0.033244 | 0.0084246 | -0.033104 | -0.0083368 | 0.00013997 | 8.7743e-05 | 0.050501 | 0.050502 | 0.050502 | 0.98019 | -0.37987 | 0.97569 | -0.4679 | 13.8741
40 | 0.02366 | 0.005935 | -0.02365 | -0.0059286 | 1.0387e-05 | 6.3772e-06 | 0.03592 | 0.035921 | 0.035921 | 0.98019 | -0.37987 | 0.97972 | -0.38908 | 9.8683
41 | 0.033104 | 0.0083368 | -0.032998 | -0.00827 | 0.00010652 | 6.6789e-05 | 0.050502 | 0.050502 | 0.050502 | 0.97569 | -0.4679 | 0.97226 | -0.53543 | 13.8742
42 | 0.020049 | 0.0050262 | -0.020046 | -0.0050244 | 2.991e-06 | 1.8059e-06 | 0.030451 | 0.030451 | 0.030451 | 0.97972 | -0.38908 | 0.97956 | -0.39221 | 8.3658
43 | 0.0099607 | 0.0024966 | -0.0099591 | -0.0024958 | 1.5909e-06 | 7.8499e-07 | 0.015131 | 0.015132 | 0.015132 | 0.97953 | -0.39277 | 0.97936 | -0.39612 | 4.157
44 | -0.013023 | -0.0032641 | 0.013023 | 0.0032643 | 3.444e-07 | 1.9088e-07 | 0.019784 | 0.019784 | 0.019784 | 0.97953 | -0.39277 | 0.97956 | -0.39221 | 5.435
45 | 0.003384 | 0.00084793 | -0.0033839 | -0.00084798 | 8.4633e-08 | -5.3262e-08 | 0.0051415 | 0.0051415 | 0.0051415 | 0.97936 | -0.39612 | 0.97934 | -0.39665 | 1.4125
46 | 0.0033839 | 0.00084798 | -0.0033838 | -0.00084806 | 1.223e-07 | -7.6956e-08 | 0.0051415 | 0.0051416 | 0.0051416 | 0.97934 | -0.39665 | 0.9793 | -0.39741 | 1.4125
47 | -0.0086524 | -0.0021685 | 0.0086526 | 0.0021686 | 1.2964e-07 | 5.643e-08 | 0.012974 | 0.012974 | 0.012974 | 0.9924 | -0.14486 | 0.99242 | -0.14455 | 3.5642
48 | 0.0062807 | 0.0015741 | -0.0062802 | -0.001574 | 4.6613e-07 | 1.1724e-07 | 0.0094173 | 0.0094173 | 0.0094173 | 0.9924 | -0.14486 | 0.99232 | -0.14642 | 2.5872

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.18251 | 0.046305

## res_load
| p_mw | q_mvar
0 | 0.003637 | 0.00091151
1 | 0.0065117 | 0.001632
2 | 0.00423 | 0.0010601
3 | 0.0035451 | 0.00088848
4 | 0.0018492 | 0.00046346
5 | 0.022544 | 0.00565
6 | 0.0016086 | 0.00040315
7 | 0.0044504 | 0.0011154
8 | 0.0044511 | 0.0011156
9 | 0.0015721 | 0.00039402
10 | 0.0013005 | 0.00032592
11 | 0.0004791 | 0.00012007
12 | 0.0095692 | 0.0023983
13 | 0.00057375 | 0.0001438
14 | 0.001218 | 0.00030525
15 | 0.00099004 | 0.00024813
16 | 0.0011611 | 0.000291
17 | 0.0025336 | 0.00063499
18 | 0.0066584 | 0.0016688
19 | 0.004578 | 0.0011474
20 | 0.00096073 | 0.00024078
21 | 0.020179 | 0.0050574
22 | 0.0036009 | 0.00090247
23 | 0.032998 | 0.00827
24 | 0.0030624 | 0.00076751
25 | 0.0065751 | 0.0016479
26 | 0.0070227 | 0.0017601
27 | 0.0033838 | 0.00084806
28 | 0.008062 | 0.0020205
29 | 0.0023718 | 0.00059442
30 | 0.00032028 | 8.027e-05
31 | 0.0062802 | 0.001574

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1