## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1301-34_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1301-34_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1301-34_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1301-34_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1301-34_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1301-34_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1301-34_0_4_node_53 | 0.4 | n |  | TRUE
7 | bus_LV_1301-34_0_4_node_38 | 0.4 | n |  | TRUE
8 | bus_LV_1301-34_0_4_node_36 | 0.4 | n |  | TRUE
9 | bus_LV_1301-34_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1301-34_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1301-34_0_4_node_39 | 0.4 | n |  | TRUE
12 | bus_LV_1301-34_0_4_node_84 | 0.4 | n |  | TRUE
13 | bus_LV_1301-34_0_4_node_83 | 0.4 | n |  | TRUE
14 | bus_LV_1301-34_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1301-34_0_4_node_56 | 0.4 | n |  | TRUE
16 | bus_LV_1301-34_0_4_node_63 | 0.4 | n |  | TRUE
17 | bus_LV_1301-34_0_4_node_37 | 0.4 | n |  | TRUE
18 | bus_LV_1301-34_0_4_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_1301-34_0_4_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_1301-34_0_4_node_113 | 0.4 | n |  | TRUE
21 | bus_LV_1301-34_0_4_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_1301-34_0_4_node_81 | 0.4 | n |  | TRUE
23 | bus_LV_1301-34_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1301-34_0_4_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_1301-34_0_4_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_1301-34_0_4_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_1301-34_0_4_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_1301-34_0_4_node_79 | 0.4 | n |  | TRUE
29 | bus_LV_1301-34_0_4_node_64 | 0.4 | n |  | TRUE
30 | bus_LV_1301-34_0_4_node_78 | 0.4 | n |  | TRUE
31 | bus_LV_1301-34_0_4_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_1301-34_0_4_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_1301-34_0_4_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_1301-34_0_4_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_1301-34_0_4_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_1301-34_0_4_node_69 | 0.4 | n |  | TRUE
37 | bus_LV_1301-34_0_4_node_67 | 0.4 | n |  | TRUE
38 | bus_LV_1301-34_0_4_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_1301-34_0_4_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_1301-34_0_4_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_1301-34_0_4_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_1301-34_0_4_node_41 | 0.4 | n |  | TRUE
43 | bus_LV_1301-34_0_4_node_57 | 0.4 | n |  | TRUE
44 | bus_LV_1301-34_0_4_node_42 | 0.4 | n |  | TRUE
45 | bus_LV_1301-34_0_4_node_43 | 0.4 | n |  | TRUE
46 | bus_LV_1301-34_0_4_node_44 | 0.4 | n |  | TRUE
47 | bus_LV_1301-34_0_4_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_1301-34_0_4_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_1301-34_0_4_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_1301-34_0_4_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_1301-34_0_4_node_30 | 0.4 | n |  | TRUE
52 | bus_LV_1301-34_0_4_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_1301-34_0_4_node_60 | 0.4 | n |  | TRUE
54 | bus_LV_1301-34_0_4_node_31 | 0.4 | n |  | TRUE
55 | bus_LV_1301-34_0_4_node_32 | 0.4 | n |  | TRUE
56 | bus_LV_1301-34_0_4_node_33 | 0.4 | n |  | TRUE
57 | bus_LV_1301-34_0_4_node_34 | 0.4 | n |  | TRUE
58 | bus_LV_1301-34_0_4_node_35 | 0.4 | n |  | TRUE
59 | bus_LV_1301-34_0_4_node_87 | 0.4 | n |  | TRUE
60 | bus_LV_1301-34_0_4_node_108 | 0.4 | n |  | TRUE
61 | bus_LV_1301-34_0_4_node_71 | 0.4 | n |  | TRUE
62 | bus_LV_1301-34_0_4_node_109 | 0.4 | n |  | TRUE
63 | bus_LV_1301-34_0_4_node_55 | 0.4 | n |  | TRUE
64 | bus_LV_1301-34_0_4_node_62 | 0.4 | n |  | TRUE
65 | bus_LV_1301-34_0_4_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_1301-34_0_4_node_48 | 0.4 | n |  | TRUE
67 | bus_LV_1301-34_0_4_node_45 | 0.4 | n |  | TRUE
68 | bus_LV_1301-34_0_4_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_1301-34_0_4_node_61 | 0.4 | n |  | TRUE
70 | bus_LV_1301-34_0_4_node_52 | 0.4 | n |  | TRUE
71 | bus_LV_1301-34_0_4_node_49 | 0.4 | n |  | TRUE
72 | bus_LV_1301-34_0_4_node_46 | 0.4 | n |  | TRUE
73 | bus_LV_1301-34_0_4_node_59 | 0.4 | n |  | TRUE
74 | bus_LV_1301-34_0_4_node_70 | 0.4 | n |  | TRUE
75 | bus_LV_1301-34_0_4_node_50 | 0.4 | n |  | TRUE
76 | bus_LV_1301-34_0_4_node_51 | 0.4 | n |  | TRUE
77 | bus_LV_1301-34_0_4_node_66 | 0.4 | n |  | TRUE
78 | bus_LV_1301-34_0_4_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_1301-34_0_4_node_54 | 0.4 | n |  | TRUE
80 | bus_LV_1301-34_0_4_node_86 | 0.4 | n |  | TRUE
81 | bus_LV_1301-34_0_4_node_85 | 0.4 | n |  | TRUE
82 | bus_LV_1301-34_0_4_node_72 | 0.4 | n |  | TRUE
83 | bus_LV_1301-34_0_4_node_73 | 0.4 | n |  | TRUE
84 | bus_LV_1301-34_0_4_node_74 | 0.4 | n |  | TRUE
85 | bus_LV_1301-34_0_4_node_75 | 0.4 | n |  | TRUE
86 | bus_LV_1301-34_0_4_node_76 | 0.4 | n |  | TRUE
87 | bus_LV_1301-34_0_4_node_77 | 0.4 | n |  | TRUE
88 | bus_LV_1301-34_0_4_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_1301-34_0_4_node_88 | 0.4 | n |  | TRUE
90 | bus_LV_1301-34_0_4_node_89 | 0.4 | n |  | TRUE
91 | bus_LV_1301-34_0_4_node_90 | 0.4 | n |  | TRUE
92 | bus_LV_1301-34_0_4_node_91 | 0.4 | n |  | TRUE
93 | bus_LV_1301-34_0_4_node_107 | 0.4 | n |  | TRUE
94 | bus_LV_1301-34_0_4_node_112 | 0.4 | n |  | TRUE
95 | bus_LV_1301-34_0_4_node_106 | 0.4 | n |  | TRUE
96 | bus_LV_1301-34_0_4_node_111 | 0.4 | n |  | TRUE
97 | bus_LV_1301-34_0_4_node_92 | 0.4 | n |  | TRUE
98 | bus_LV_1301-34_0_4_node_93 | 0.4 | n |  | TRUE
99 | bus_LV_1301-34_0_4_node_94 | 0.4 | n |  | TRUE
100 | bus_LV_1301-34_0_4_node_95 | 0.4 | n |  | TRUE
101 | bus_LV_1301-34_0_4_node_96 | 0.4 | n |  | TRUE
102 | bus_LV_1301-34_0_4_node_97 | 0.4 | n |  | TRUE
103 | bus_LV_1301-34_0_4_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_1301-34_0_4_node_99 | 0.4 | n |  | TRUE
105 | bus_LV_1301-34_0_4_node_100 | 0.4 | n |  | TRUE
106 | bus_LV_1301-34_0_4_node_101 | 0.4 | n |  | TRUE
107 | bus_LV_1301-34_0_4_node_102 | 0.4 | n |  | TRUE
108 | bus_LV_1301-34_0_4_node_103 | 0.4 | n |  | TRUE
109 | bus_LV_1301-34_0_4_node_104 | 0.4 | n |  | TRUE
110 | bus_LV_1301-34_0_4_node_105 | 0.4 | n |  | TRUE
111 | bus_LV_1301-34_0_4_node_110 | 0.4 | n |  | TRUE
112 | bus_MV_0_node_41 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1301-34_0_4_load_0 | 0 | 0.0049589 | 0.0012428 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1301-34_0_4_load_53 | 6 | 0.0012023 | 0.00030132 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1301-34_0_4_load_36 | 8 | 0.00075428 | 0.00018904 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1301-34_0_4_load_39 | 11 | 0.00056855 | 0.00014249 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1301-34_0_4_load_83 | 13 | 0.003252 | 0.00081503 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1301-34_0_4_load_11 | 14 | 0.0010977 | 0.00027511 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1301-34_0_4_load_63 | 16 | 0.00040164 | 0.00010066 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1301-34_0_4_load_37 | 17 | 0.00021823 | 5.4693e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1301-34_0_4_load_8 | 18 | 0.001051 | 0.00026342 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1301-34_0_4_load_9 | 19 | 0.0017377 | 0.00043551 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1301-34_0_4_load_113 | 20 | 0.0018624 | 0.00046676 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1301-34_0_4_load_81 | 22 | 0.0015121 | 0.00037897 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1301-34_0_4_load_12 | 23 | 0.0004871 | 0.00012208 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1301-34_0_4_load_13 | 24 | 0.001568 | 0.00039297 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1301-34_0_4_load_14 | 25 | 0.0012863 | 0.00032238 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1301-34_0_4_load_15 | 26 | 0.00090084 | 0.00022577 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1301-34_0_4_load_16 | 27 | 0.00050998 | 0.00012781 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1301-34_0_4_load_79 | 28 | 0.00081171 | 0.00020343 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1301-34_0_4_load_64 | 29 | 0.00090289 | 0.00022629 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1301-34_0_4_load_78 | 30 | 0.0004799 | 0.00012027 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1301-34_0_4_load_17 | 32 | 0.00028702 | 7.1934e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1301-34_0_4_load_18 | 33 | 0.00034773 | 8.7149e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1301-34_0_4_load_20 | 35 | 0.0010233 | 0.00025646 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1301-34_0_4_load_67 | 37 | 0.00052774 | 0.00013226 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1301-34_0_4_load_21 | 38 | 0.00038286 | 9.5953e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1301-34_0_4_load_22 | 39 | 0.00060293 | 0.00015111 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1301-34_0_4_load_23 | 40 | 0.0012516 | 0.00031368 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1301-34_0_4_load_24 | 41 | 0.00026107 | 6.5431e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1301-34_0_4_load_57 | 43 | 0.00056316 | 0.00014114 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1301-34_0_4_load_43 | 45 | 0.0011073 | 0.00027752 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1301-34_0_4_load_44 | 46 | 0.0023053 | 0.00057775 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1301-34_0_4_load_26 | 47 | 0.00020148 | 5.0495e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1301-34_0_4_load_27 | 48 | 0.00022274 | 5.5824e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1301-34_0_4_load_28 | 49 | 0.00024583 | 6.1611e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1301-34_0_4_load_29 | 50 | 0.00020606 | 5.1644e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1301-34_0_4_load_30 | 51 | 0.00057735 | 0.0001447 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1301-34_0_4_load_40 | 52 | 0.00016445 | 4.1216e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1301-34_0_4_load_60 | 53 | 0.0002926 | 7.3333e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1301-34_0_4_load_31 | 54 | 0.00076556 | 0.00019187 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1301-34_0_4_load_33 | 56 | 0.0011338 | 0.00028416 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1301-34_0_4_load_34 | 57 | 0.0013089 | 0.00032805 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1301-34_0_4_load_87 | 59 | 0.0003729 | 9.3458e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1301-34_0_4_load_108 | 60 | 0.00023144 | 5.8004e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1301-34_0_4_load_109 | 62 | 0.00026168 | 6.5584e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1301-34_0_4_load_62 | 64 | 0.00050179 | 0.00012576 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1301-34_0_4_load_47 | 65 | 0.00018244 | 4.5723e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1301-34_0_4_load_45 | 67 | 0.00022228 | 5.5709e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1301-34_0_4_load_58 | 68 | 0.00054291 | 0.00013607 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1301-34_0_4_load_61 | 69 | 0.00052368 | 0.00013125 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1301-34_0_4_load_52 | 70 | 0.00022471 | 5.6319e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1301-34_0_4_load_49 | 71 | 0.00029937 | 7.5029e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1301-34_0_4_load_46 | 72 | 0.00030918 | 7.7489e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1301-34_0_4_load_59 | 73 | 0.00057065 | 0.00014302 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1301-34_0_4_load_50 | 75 | 0.00056748 | 0.00014222 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1301-34_0_4_load_51 | 76 | 0.0003961 | 9.9271e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1301-34_0_4_load_66 | 77 | 0.00097296 | 0.00024385 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1301-34_0_4_load_65 | 78 | 0.00029353 | 7.3566e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1301-34_0_4_load_54 | 79 | 0.0011132 | 0.00027899 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1301-34_0_4_load_86 | 80 | 0.0005281 | 0.00013235 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1301-34_0_4_load_85 | 81 | 0.00090545 | 0.00022693 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1301-34_0_4_load_72 | 82 | 0.0010606 | 0.00026582 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1301-34_0_4_load_73 | 83 | 0.00055967 | 0.00014027 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1301-34_0_4_load_74 | 84 | 0.0022469 | 0.00056313 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1301-34_0_4_load_75 | 85 | 0.0011393 | 0.00028555 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1301-34_0_4_load_76 | 86 | 0.0014887 | 0.0003731 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1301-34_0_4_load_77 | 87 | 0.0012759 | 0.00031976 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1301-34_0_4_load_80 | 88 | 0.001393 | 0.00034913 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1301-34_0_4_load_88 | 89 | 0.00044411 | 0.0001113 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1301-34_0_4_load_90 | 91 | 0.00021386 | 5.3599e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1301-34_0_4_load_91 | 92 | 0.00019823 | 4.968e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1301-34_0_4_load_107 | 93 | 0.00038673 | 9.6923e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1301-34_0_4_load_112 | 94 | 0.00018765 | 4.7031e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1301-34_0_4_load_106 | 95 | 0.00022984 | 5.7604e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1301-34_0_4_load_111 | 96 | 0.00035873 | 8.9905e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1301-34_0_4_load_92 | 97 | 0.00057602 | 0.00014437 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1301-34_0_4_load_93 | 98 | 0.00022911 | 5.742e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1301-34_0_4_load_94 | 99 | 0.00058653 | 0.000147 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1301-34_0_4_load_95 | 100 | 0.00055646 | 0.00013946 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1301-34_0_4_load_96 | 101 | 0.00019429 | 4.8692e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1301-34_0_4_load_97 | 102 | 0.00021701 | 5.4389e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1301-34_0_4_load_98 | 103 | 0.0003528 | 8.8419e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1301-34_0_4_load_99 | 104 | 0.00027805 | 6.9687e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1301-34_0_4_load_100 | 105 | 0.00027913 | 6.9956e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1301-34_0_4_load_101 | 106 | 0.00022767 | 5.706e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1301-34_0_4_load_102 | 107 | 0.00041495 | 0.000104 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1301-34_0_4_load_103 | 108 | 0.00021204 | 5.3142e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1301-34_0_4_load_104 | 109 | 0.00018042 | 4.5217e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1301-34_0_4_load_105 | 110 | 0.00032654 | 8.1839e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1301-34_0_4_load_110 | 111 | 0.00045551 | 0.00011416 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1301-34_0_4_line_0 |  | 0 | 1 | 0.003102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1301-34_0_4_line_1 |  | 0 | 2 | 0.010744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1301-34_0_4_line_2 |  | 1 | 3 | 0.037618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1301-34_0_4_line_3 |  | 1 | 4 | 0.11691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1301-34_0_4_line_4 |  | 2 | 5 | 0.031498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1301-34_0_4_line_5 |  | 3 | 6 | 0.079173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1301-34_0_4_line_6 |  | 4 | 7 | 0.086633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1301-34_0_4_line_7 |  | 4 | 8 | 0.048224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1301-34_0_4_line_8 |  | 5 | 9 | 0.037227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1301-34_0_4_line_9 |  | 6 | 14 | 0.034605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1301-34_0_4_line_10 |  | 7 | 15 | 0.17202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1301-34_0_4_line_11 |  | 7 | 16 | 0.038804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1301-34_0_4_line_12 |  | 8 | 17 | 0.34002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1301-34_0_4_line_13 |  | 9 | 10 | 0.20762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1301-34_0_4_line_14 |  | 9 | 11 | 0.1091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1301-34_0_4_line_15 |  | 10 | 12 | 0.041216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1301-34_0_4_line_16 |  | 10 | 13 | 0.022201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1301-34_0_4_line_17 |  | 12 | 20 | 0.034244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1301-34_0_4_line_18 |  | 13 | 22 | 0.032309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1301-34_0_4_line_19 |  | 14 | 21 | 0.0024812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1301-34_0_4_line_20 |  | 15 | 63 | 0.073259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1301-34_0_4_line_21 |  | 16 | 64 | 0.017148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1301-34_0_4_line_22 |  | 17 | 35 | 0.27364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1301-34_0_4_line_23 |  | 18 | 19 | 0.0075571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1301-34_0_4_line_24 |  | 19 | 21 | 0.054672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1301-34_0_4_line_25 |  | 22 | 88 | 0.025265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1301-34_0_4_line_26 |  | 23 | 24 | 0.0082401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1301-34_0_4_line_27 |  | 23 | 25 | 0.0072933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1301-34_0_4_line_28 |  | 24 | 26 | 0.020227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1301-34_0_4_line_29 |  | 25 | 27 | 0.014692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1301-34_0_4_line_30 |  | 26 | 28 | 0.028256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1301-34_0_4_line_31 |  | 27 | 29 | 0.017475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1301-34_0_4_line_32 |  | 28 | 30 | 0.013724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1301-34_0_4_line_33 |  | 29 | 31 | 0.038912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1301-34_0_4_line_34 |  | 30 | 87 | 0.023337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1301-34_0_4_line_35 |  | 31 | 43 | 0.018148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1301-34_0_4_line_36 |  | 31 | 40 | 0.015863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1301-34_0_4_line_37 |  | 32 | 33 | 0.0090011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1301-34_0_4_line_38 |  | 32 | 34 | 0.10265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1301-34_0_4_line_39 |  | 34 | 35 | 0.16131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1301-34_0_4_line_40 |  | 35 | 36 | 0.62776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1301-34_0_4_line_41 |  | 36 | 37 | 0.055526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1301-34_0_4_line_42 |  | 38 | 39 | 0.0077721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1301-34_0_4_line_43 |  | 38 | 40 | 0.027787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1301-34_0_4_line_44 |  | 39 | 41 | 0.0099604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1301-34_0_4_line_45 |  | 41 | 42 | 0.078875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1301-34_0_4_line_46 |  | 42 | 44 | 0.3005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1301-34_0_4_line_47 |  | 42 | 45 | 0.20895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1301-34_0_4_line_48 |  | 42 | 46 | 0.10237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1301-34_0_4_line_49 |  | 44 | 66 | 0.20643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1301-34_0_4_line_50 |  | 44 | 67 | 0.10288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1301-34_0_4_line_51 |  | 45 | 68 | 0.013302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1301-34_0_4_line_52 |  | 46 | 69 | 0.021556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1301-34_0_4_line_53 |  | 47 | 48 | 0.0035773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1301-34_0_4_line_54 |  | 47 | 49 | 0.015467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1301-34_0_4_line_55 |  | 48 | 50 | 0.01947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1301-34_0_4_line_56 |  | 49 | 51 | 0.070658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1301-34_0_4_line_57 |  | 50 | 52 | 0.015185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1301-34_0_4_line_58 |  | 52 | 53 | 0.0032332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1301-34_0_4_line_59 |  | 53 | 65 | 0.0029805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1301-34_0_4_line_60 |  | 54 | 55 | 0.21699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1301-34_0_4_line_61 |  | 54 | 56 | 0.022308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1301-34_0_4_line_62 |  | 55 | 57 | 0.24754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1301-34_0_4_line_63 |  | 55 | 58 | 0.25857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1301-34_0_4_line_64 |  | 57 | 59 | 0.036925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1301-34_0_4_line_65 |  | 58 | 60 | 0.058604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1301-34_0_4_line_66 |  | 59 | 61 | 0.10295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1301-34_0_4_line_67 |  | 60 | 62 | 0.0003528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1301-34_0_4_line_68 |  | 61 | 80 | 0.053305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1301-34_0_4_line_69 |  | 61 | 74 | 0.27925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1301-34_0_4_line_70 |  | 62 | 111 | 0.022215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1301-34_0_4_line_71 |  | 63 | 79 | 0.11599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1301-34_0_4_line_72 |  | 64 | 69 | 0.0035426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1301-34_0_4_line_73 |  | 65 | 72 | 0.010465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1301-34_0_4_line_74 |  | 66 | 70 | 0.26472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1301-34_0_4_line_75 |  | 66 | 71 | 0.01921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1301-34_0_4_line_76 |  | 67 | 72 | 0.01482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1301-34_0_4_line_77 |  | 68 | 73 | 0.062093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1301-34_0_4_line_78 |  | 70 | 74 | 0.27485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1301-34_0_4_line_79 |  | 71 | 75 | 0.056581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1301-34_0_4_line_80 |  | 75 | 76 | 0.024879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1301-34_0_4_line_81 |  | 76 | 77 | 0.017894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1301-34_0_4_line_82 |  | 77 | 78 | 0.054362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1301-34_0_4_line_83 |  | 80 | 81 | 0.062248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1301-34_0_4_line_84 |  | 82 | 83 | 0.015081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1301-34_0_4_line_85 |  | 82 | 84 | 0.0067029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1301-34_0_4_line_86 |  | 83 | 85 | 0.013223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1301-34_0_4_line_87 |  | 85 | 86 | 0.013885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1301-34_0_4_line_88 |  | 86 | 87 | 0.040794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1301-34_0_4_line_89 |  | 89 | 90 | 0.18735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1301-34_0_4_line_90 |  | 90 | 91 | 0.029055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1301-34_0_4_line_91 |  | 90 | 92 | 0.012192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1301-34_0_4_line_92 |  | 91 | 93 | 0.010867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1301-34_0_4_line_93 |  | 92 | 94 | 0.0083492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1301-34_0_4_line_94 |  | 93 | 95 | 0.015309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1301-34_0_4_line_95 |  | 94 | 96 | 0.022419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1301-34_0_4_line_96 |  | 95 | 110 | 0.027994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1301-34_0_4_line_97 |  | 96 | 111 | 0.0082984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1301-34_0_4_line_98 |  | 97 | 98 | 0.016092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1301-34_0_4_line_99 |  | 97 | 99 | 0.021263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1301-34_0_4_line_100 |  | 98 | 100 | 0.0063516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1301-34_0_4_line_101 |  | 100 | 101 | 0.0071531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1301-34_0_4_line_102 |  | 101 | 102 | 0.021143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1301-34_0_4_line_103 |  | 102 | 103 | 0.0072812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1301-34_0_4_line_104 |  | 103 | 104 | 0.004817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1301-34_0_4_line_105 |  | 104 | 105 | 0.02164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1301-34_0_4_line_106 |  | 105 | 106 | 0.0083162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1301-34_0_4_line_107 |  | 106 | 107 | 0.020215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1301-34_0_4_line_108 |  | 107 | 108 | 0.009176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1301-34_0_4_line_109 |  | 108 | 109 | 0.001938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1301-34_0_4_line_110 |  | 109 | 110 | 0.033115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1301-34_0_4_trafo_41 | 0.63 MVA 20/0.4 kV | 112 | 42 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21
0 | 2702668.7232 | 1221816.4307 | 2702671.8234 | 1221816.5389
1 | 2702682.5612 | 1221816.914 | 2702671.8234 | 1221816.5389
2 | 2702649.4874 | 1221796.3512 | 2702650.2283 | 1221815.4222 | 2702654.9763 | 1221815.9489 | 2702668.7232 | 1221816.4307
3 | 2702654.0256 | 1221913.7255 | 2702652.6352 | 1221877.7755 | 2702650.9617 | 1221834.482 | 2702650.2283 | 1221815.4222 | 2702654.9763 | 1221815.9489 | 2702668.7232 | 1221816.4307
4 | 2702682.5612 | 1221816.914 | 2702687.8463 | 1221817.0942 | 2702695.9523 | 1221817.3564 | 2702702.8451 | 1221817.5754 | 2702714.0337 | 1221818.1465
5 | 2702649.4874 | 1221796.3512 | 2702646.4271 | 1221717.237
6 | 2702654.0256 | 1221913.7255 | 2702654.1041 | 1221915.7728 | 2702657.3729 | 1222000.2792
7 | 2702654.0256 | 1221913.7255 | 2702681.4657 | 1221914.2656 | 2702697.3123 | 1221927.7053
8 | 2702714.0337 | 1221818.1465 | 2702728.9548 | 1221817.8592 | 2702751.2363 | 1221818.8332
9 | 2702646.4271 | 1221717.237 | 2702645.4365 | 1221691.6278 | 2702645.0919 | 1221682.658
10 | 2702588.3012 | 1221881.9811 | 2702592.382 | 1221881.5955 | 2702627.7731 | 1221886.5534 | 2702642.3678 | 1221887.5834 | 2702645.0914 | 1221892.8675 | 2702648.1203 | 1221942.4667 | 2702649.723 | 1221995.1436 | 2702657.3729 | 1222000.2792
11 | 2702657.3729 | 1222000.2792 | 2702657.9412 | 1222014.8329 | 2702658.8374 | 1222038.0874 | 2702658.8748 | 1222039.0539
12 | 2702965.8427 | 1222126.6741 | 2702945.9031 | 1222104.858 | 2702904.4287 | 1222078.422 | 2702873.5313 | 1222065.0674 | 2702868.1157 | 1222061.4823 | 2702852.0826 | 1222037.9105 | 2702835.99 | 1222022.6104 | 2702831.0204 | 1222019.111 | 2702824.1535 | 1222007.3061 | 2702817.4837 | 1222000.7751 | 2702785.5415 | 1221978.0405 | 2702757.5645 | 1221962.9134 | 2702731.1234 | 1221951.5379 | 2702725.688 | 1221949.0868 | 2702710.4932 | 1221938.884 | 2702697.3123 | 1221927.7053
13 | 2702770.7223 | 1221699.1828 | 2702769.7636 | 1221738.8839 | 2702775.3773 | 1221752.5462 | 2702784.3928 | 1221768.2465 | 2702791.2719 | 1221776.727 | 2702802.7454 | 1221787.1659 | 2702824.8141 | 1221804.8486 | 2702824.7666 | 1221807.1605 | 2702818.6708 | 1221814.3828 | 2702814.0069 | 1221817.7714 | 2702773.4257 | 1221818.9829 | 2702751.2363 | 1221818.8332
14 | 2702751.2363 | 1221818.8332 | 2702739.888 | 1221739.6134 | 2702741.793 | 1221710.6036
15 | 2702770.7223 | 1221699.1828 | 2702782.8578 | 1221702.9283 | 2702797.7635 | 1221703.1079 | 2702810.9475 | 1221699.2994
16 | 2702770.7223 | 1221699.1828 | 2702771.9433 | 1221677.015
17 | 2702818.2755 | 1221732.7501 | 2702810.9475 | 1221699.2994
18 | 2702773.7203 | 1221644.7551 | 2702771.9433 | 1221677.015
19 | 2702644.9966 | 1221680.1786 | 2702645.0919 | 1221682.658
20 | 2702517.8551 | 1221896.5897 | 2702525.7158 | 1221891.7103 | 2702534.9157 | 1221887.9215 | 2702541.2129 | 1221884.8388 | 2702552.1154 | 1221883.5145 | 2702558.2932 | 1221883.3986 | 2702585.8945 | 1221882.5178 | 2702588.3012 | 1221881.9811
21 | 2702658.8748 | 1222039.0539 | 2702659.5378 | 1222056.1889
22 | 2703172.656 | 1222252.8262 | 2703170.6844 | 1222235.0759 | 2703161.995 | 1222229.9883 | 2703135.3429 | 1222232.2171 | 2703132.3568 | 1222232.0431 | 2703126.3153 | 1222225.189 | 2703109.0014 | 1222213.8921 | 2703102.6303 | 1222208.5446 | 2703097.7882 | 1222198.1421 | 2703094.2086 | 1222193.688 | 2703061.355 | 1222179.4535 | 2703044.9292 | 1222174.2432 | 2703036.7912 | 1222174.1023 | 2703026.4279 | 1222178.9265 | 2703021.1297 | 1222181.7146 | 2703015.3739 | 1222180.2585 | 2703011.3279 | 1222172.0714 | 2703003.7122 | 1222163.6669 | 2703000.1957 | 1222151.6196 | 2702993.8719 | 1222143.0929 | 2702965.8427 | 1222126.6741 | 2702965.8427 | 1222126.6741
23 | 2702677.6145 | 1221732.9235 | 2702673.351 | 1221726.6839
24 | 2702644.9966 | 1221680.1786 | 2702657.1949 | 1221696.5674 | 2702668.5269 | 1221719.6239 | 2702673.351 | 1221726.6839
25 | 2702775.1098 | 1221619.5285 | 2702773.7203 | 1221644.7551
26 | 2702454.6378 | 1222132.1913 | 2702446.5867 | 1222133.9461 | 2702446.5867 | 1222133.9461
27 | 2702454.6378 | 1222132.1913 | 2702461.7638 | 1222130.6381
28 | 2702429.6669 | 1222144.9572 | 2702431.5418 | 1222143.2385 | 2702446.5867 | 1222133.9461
29 | 2702461.7638 | 1222130.6381 | 2702461.7638 | 1222130.6381 | 2702476.3576 | 1222132.3352
30 | 2702408.8383 | 1222164.0507 | 2702429.6669 | 1222144.9572
31 | 2702476.3576 | 1222132.3352 | 2702493.7158 | 1222134.3536
32 | 2702408.8383 | 1222164.0507 | 2702398.7214 | 1222173.3248
33 | 2702532.3676 | 1222138.8482 | 2702493.7158 | 1222134.3536
34 | 2702381.2366 | 1222188.7072 | 2702383.0959 | 1222187.6486 | 2702398.7214 | 1222173.3248
35 | 2702532.3676 | 1222138.8482 | 2702533.2664 | 1222120.7226
36 | 2702532.3676 | 1222138.8482 | 2702544.501 | 1222141.7926 | 2702547.4997 | 1222143.3466
37 | 2703286.0446 | 1222370.5963 | 2703285.4733 | 1222379.5792
38 | 2703200.5056 | 1222411.4429 | 2703235.8044 | 1222409.7091 | 2703276.0348 | 1222402.2679 | 2703281.9496 | 1222398.4789 | 2703284.8551 | 1222389.3004 | 2703285.4733 | 1222379.5792
39 | 2703200.5056 | 1222411.4429 | 2703187.9189 | 1222359.4426 | 2703180.3895 | 1222322.4741 | 2703175.9013 | 1222282.0448 | 2703172.656 | 1222252.8262
40 | 2703172.656 | 1222252.8262 | 2703491.1343 | 1221711.8562
41 | 2703491.1343 | 1221711.8562 | 2703459.174 | 1221683.2245 | 2703447.7815 | 1221677.8028
42 | 2702576.7699 | 1222163.3674 | 2702570.5239 | 1222158.7421
43 | 2702547.4997 | 1222143.3466 | 2702555.9305 | 1222147.7159 | 2702562.6987 | 1222152.9474 | 2702570.5239 | 1222158.7421
44 | 2702584.7745 | 1222169.295 | 2702576.7699 | 1222163.3674
45 | 2702662.2449 | 1222183.5848 | 2702626.9639 | 1222176.7496 | 2702600.432 | 1222172.8896 | 2702591.7898 | 1222171.6287 | 2702584.7745 | 1222169.295
46 | 2702595.3593 | 1222472.8195 | 2702611.6306 | 1222452.2072 | 2702623.0052 | 1222425.6506 | 2702632.153 | 1222377.7735 | 2702651.1593 | 1222272.9585 | 2702653.4941 | 1222256.3534 | 2702659.2367 | 1222215.4783 | 2702659.9293 | 1222210.5089 | 2702662.2449 | 1222183.5848
47 | 2702662.2449 | 1222183.5848 | 2702670.3962 | 1222188.2287 | 2702678.0425 | 1222197.0781 | 2702682.9211 | 1222214.1968 | 2702687.001 | 1222226.1648 | 2702694.1763 | 1222235.9289 | 2702702.3385 | 1222242.1297 | 2702727.1636 | 1222254.3112 | 2702755.1689 | 1222277.3889 | 2702776.0611 | 1222290.6146 | 2702809.2882 | 1222302.9971 | 2702816.238 | 1222305.5967 | 2702819.7144 | 1222306.084
48 | 2702662.2449 | 1222183.5848 | 2702662.5479 | 1222179.6539 | 2702662.8874 | 1222163.9372 | 2702661.5659 | 1222108.6077 | 2702660.5081 | 1222081.2689
49 | 2702465.2295 | 1222625.0337 | 2702468.2996 | 1222610.1869 | 2702473.8463 | 1222592.047 | 2702487.9373 | 1222565.4035 | 2702504.4656 | 1222544.8064 | 2702538.0531 | 1222516.4085 | 2702595.3593 | 1222472.8195
50 | 2702595.3593 | 1222472.8195 | 2702603.3947 | 1222475.8046 | 2702635.2498 | 1222463.0109 | 2702642.8887 | 1222462.1531 | 2702648.7476 | 1222465.9791 | 2702650.2375 | 1222473.2767 | 2702646.537 | 1222486.8228 | 2702640.7116 | 1222504.3684 | 2702640.2088 | 1222509.6573
51 | 2702819.7144 | 1222306.084 | 2702832.8878 | 1222307.9304
52 | 2702659.6747 | 1222059.7288 | 2702660.5081 | 1222081.2689
53 | 2702686.342 | 1222493.7371 | 2702689.295 | 1222491.718
54 | 2702702.0632 | 1222482.9879 | 2702689.295 | 1222491.718
55 | 2702686.342 | 1222493.7371 | 2702673.4314 | 1222502.5645 | 2702670.9668 | 1222505.4964
56 | 2702764.9983 | 1222468.1772 | 2702753.68 | 1222462.8977 | 2702750.0528 | 1222461.2006 | 2702737.9833 | 1222461.1923 | 2702721.5725 | 1222469.6487 | 2702702.0632 | 1222482.9879
57 | 2702661.196 | 1222517.1199 | 2702670.9668 | 1222505.4964
58 | 2702661.196 | 1222517.1199 | 2702659.1155 | 1222519.5949
59 | 2702659.1155 | 1222519.5949 | 2702657.1977 | 1222521.8764
60 | 2703015.8196 | 1222731.1884 | 2703018.9607 | 1222704.8681 | 2703028.1229 | 1222672.1028 | 2703035.1732 | 1222652.6551 | 2703045.0222 | 1222636.7473 | 2703058.0355 | 1222621.6616 | 2703068.6672 | 1222598.2397 | 2703078.2654 | 1222560.0336 | 2703089.3609 | 1222529.994
61 | 2703098.9036 | 1222509.8878 | 2703092.2342 | 1222522.2146 | 2703089.3609 | 1222529.994
62 | 2703015.8196 | 1222731.1884 | 2702866.7913 | 1222807.7566 | 2702798.7389 | 1222794.6051 | 2702789.1372 | 1222799.282
63 | 2703015.8196 | 1222731.1884 | 2703031.1269 | 1222727.306 | 2703053.1808 | 1222724.5746 | 2703094.3735 | 1222721.8745 | 2703113.0192 | 1222714.8923 | 2703121.2973 | 1222710.8438 | 2703146.2848 | 1222698.6233 | 2703164.3525 | 1222688.6735 | 2703197.5837 | 1222694.5203 | 2703217.3793 | 1222701.2905 | 2703238.0817 | 1222713.9475 | 2703255.7656 | 1222728.309
64 | 2702755.9412 | 1222815.4514 | 2702789.1372 | 1222799.282
65 | 2703255.7656 | 1222728.309 | 2703281.8928 | 1222775.8634 | 2703283.7526 | 1222779.7898
66 | 2702695.2399 | 1222894.2915 | 2702714.6117 | 1222870.6752 | 2702736.2603 | 1222825.0378 | 2702755.9412 | 1222815.4514
67 | 2703283.7526 | 1222779.7898 | 2703283.9036 | 1222780.1087
68 | 2702695.2399 | 1222894.2915 | 2702699.3906 | 1222947.4345
69 | 2702695.2399 | 1222894.2915 | 2702627.327 | 1222963.2485 | 2702622.7101 | 1222969.251 | 2702619.9008 | 1222974.2396 | 2702617.844 | 1222980.4642 | 2702615.4507 | 1222989.0403 | 2702612.0449 | 1223005.7493 | 2702610.3915 | 1223018.0519 | 2702609.607 | 1223053.8644 | 2702609.2368 | 1223056.8602 | 2702608.4648 | 1223059.838 | 2702607.0967 | 1223063.5171 | 2702605.6512 | 1223065.9606 | 2702593.8099 | 1223080.9452 | 2702589.3373 | 1223085.1823 | 2702584.7542 | 1223088.3501 | 2702579.6663 | 1223090.8754 | 2702573.7191 | 1223092.652 | 2702540.7883 | 1223096.3208
70 | 2703283.9036 | 1222780.1087 | 2703293.4131 | 1222800.1855
71 | 2702517.8551 | 1221896.5897 | 2702506.0005 | 1221891.9711 | 2702498.487 | 1221886.3822 | 2702478.0559 | 1221870.9306 | 2702477.3435 | 1221867.8049 | 2702478.9398 | 1221863.6627 | 2702498.9046 | 1221835.7083 | 2702505.0331 | 1221833.6123 | 2702509.7183 | 1221835.1385 | 2702522.4594 | 1221842.8405
72 | 2702659.6747 | 1222059.7288 | 2702659.5378 | 1222056.1889
73 | 2702647.2789 | 1222521.2216 | 2702650.1245 | 1222522.9219 | 2702657.1977 | 1222521.8764 | 2702657.1977 | 1222521.8764
74 | 2702465.2295 | 1222625.0337 | 2702463.4125 | 1222633.6309 | 2702461.9582 | 1222640.5553 | 2702455.4873 | 1222671.3997 | 2702454.8 | 1222703.8225 | 2702457.0982 | 1222724.1101 | 2702465.4817 | 1222755.3214 | 2702477.067 | 1222776.803 | 2702492.0308 | 1222798.5541 | 2702538.4804 | 1222856.1067 | 2702543.0201 | 1222861.9629
75 | 2702465.2295 | 1222625.0337 | 2702474.7459 | 1222631.4354 | 2702477.9983 | 1222638.46
76 | 2702640.2088 | 1222509.6573 | 2702639.9053 | 1222512.8495 | 2702642.766 | 1222518.5252 | 2702647.2789 | 1222521.2216
77 | 2702880.9076 | 1222268.5646 | 2702832.8878 | 1222307.9304
78 | 2702540.7883 | 1223096.3208 | 2702538.8288 | 1223090.3049 | 2702505.707 | 1223029.3348 | 2702501.6361 | 1223017.3004 | 2702500.1104 | 1223003.7087 | 2702502.8634 | 1222989.6459 | 2702508.4533 | 1222978.6786 | 2702541.4709 | 1222951.0827 | 2702555.7234 | 1222936.1618 | 2702562.1235 | 1222923.0847 | 2702565.7288 | 1222907.5578 | 2702563.9486 | 1222896.419 | 2702557.3067 | 1222880.393 | 2702543.0201 | 1222861.9629
79 | 2702477.9983 | 1222638.46 | 2702484.1443 | 1222651.7341 | 2702490.8797 | 1222658.833 | 2702513.0263 | 1222682.1631
80 | 2702513.0263 | 1222682.1631 | 2702521.301 | 1222690.8799 | 2702530.0806 | 1222700.2775
81 | 2702530.0806 | 1222700.2775 | 2702542.2962 | 1222713.3529
82 | 2702578.1001 | 1222707.4034 | 2702575.115 | 1222710.2652 | 2702572.9684 | 1222717.7336 | 2702570.1679 | 1222724.4124 | 2702565.2161 | 1222727.8296 | 2702559.6238 | 1222728.8007 | 2702554.4319 | 1222726.3428 | 2702542.2962 | 1222713.3529
83 | 2702664.5021 | 1222982.676 | 2702674.9447 | 1222983.7287 | 2702688.4903 | 1222980.7824 | 2702697.7316 | 1222972.747 | 2702700.415 | 1222960.5511 | 2702699.3906 | 1222947.4345
84 | 2702349.0858 | 1222239.9137 | 2702343.5497 | 1222225.8854 | 2702343.5497 | 1222225.8854
85 | 2702351.5463 | 1222246.1486 | 2702349.0858 | 1222239.9137
86 | 2702343.5497 | 1222225.8854 | 2702340.5937 | 1222212.997
87 | 2702340.5937 | 1222212.997 | 2702340.2469 | 1222211.4849 | 2702341.7355 | 1222200.358 | 2702342.5378 | 1222199.595
88 | 2702342.5378 | 1222199.595 | 2702344.3656 | 1222197.8569 | 2702375.7408 | 1222191.8363 | 2702381.2366 | 1222188.7072
89 | 2703312.4239 | 1222847.6231 | 2703291.026 | 1222878.1296 | 2703257.8171 | 1222897.7234 | 2703220.4705 | 1222936.771 | 2703203.6775 | 1222991.7619
90 | 2703312.4239 | 1222847.6231 | 2703320.525 | 1222875.5257
91 | 2703312.4239 | 1222847.6231 | 2703309.0151 | 1222835.9174
92 | 2703323.5551 | 1222885.9621 | 2703320.525 | 1222875.5257
93 | 2703309.0151 | 1222835.9174 | 2703306.9044 | 1222828.6691 | 2703306.562 | 1222827.9462
94 | 2703323.5551 | 1222885.9621 | 2703327.8235 | 1222900.6639
95 | 2703296.9653 | 1222807.6852 | 2703306.562 | 1222827.9462
96 | 2703334.117 | 1222927.6926 | 2703334.4908 | 1222923.628 | 2703327.8235 | 1222900.6639
97 | 2703293.4131 | 1222800.1855 | 2703296.9653 | 1222807.6852
98 | 2703305.7223 | 1223080.9348 | 2703311.6343 | 1223065.9682
99 | 2703297.9105 | 1223100.7111 | 2703305.7223 | 1223080.9348
100 | 2703313.9677 | 1223060.0608 | 2703311.6343 | 1223065.9682
101 | 2703313.9677 | 1223060.0608 | 2703316.5957 | 1223053.4079
102 | 2703316.5957 | 1223053.4079 | 2703324.3633 | 1223033.7435 | 2703324.3633 | 1223033.7435
103 | 2703325.0301 | 1223026.4929 | 2703324.3633 | 1223033.7435
104 | 2703325.0301 | 1223026.4929 | 2703325.4713 | 1223021.6962
105 | 2703327.4532 | 1223000.1471 | 2703325.4713 | 1223021.6962
106 | 2703327.4532 | 1223000.1471 | 2703328.2148 | 1222991.8658
107 | 2703330.0663 | 1222971.7354 | 2703328.2148 | 1222991.8658
108 | 2703330.0663 | 1222971.7354 | 2703330.9067 | 1222962.598
109 | 2703331.0841 | 1222960.6681 | 2703330.9067 | 1222962.598
110 | 2703331.0841 | 1222960.6681 | 2703334.117 | 1222927.6926

## bus_geodata
| x | y | coords
0 | 2702671.8234 | 1221816.5389
1 | 2702668.7232 | 1221816.4307
2 | 2702682.5612 | 1221816.914
3 | 2702649.4874 | 1221796.3512
4 | 2702654.0256 | 1221913.7255
5 | 2702714.0337 | 1221818.1465
6 | 2702646.4271 | 1221717.237
7 | 2702657.3729 | 1222000.2792
8 | 2702697.3123 | 1221927.7053
9 | 2702751.2363 | 1221818.8332
10 | 2702770.7223 | 1221699.1828
11 | 2702741.793 | 1221710.6036
12 | 2702810.9475 | 1221699.2994
13 | 2702771.9433 | 1221677.015
14 | 2702645.0919 | 1221682.658
15 | 2702588.3012 | 1221881.9811
16 | 2702658.8748 | 1222039.0539
17 | 2702965.8427 | 1222126.6741
18 | 2702677.6145 | 1221732.9235
19 | 2702673.351 | 1221726.6839
20 | 2702818.2755 | 1221732.7501
21 | 2702644.9966 | 1221680.1786
22 | 2702773.7203 | 1221644.7551
23 | 2702454.6378 | 1222132.1913
24 | 2702446.5867 | 1222133.9461
25 | 2702461.7638 | 1222130.6381
26 | 2702429.6669 | 1222144.9572
27 | 2702476.3576 | 1222132.3352
28 | 2702408.8383 | 1222164.0507
29 | 2702493.7158 | 1222134.3536
30 | 2702398.7214 | 1222173.3248
31 | 2702532.3676 | 1222138.8482
32 | 2703285.4733 | 1222379.5792
33 | 2703286.0446 | 1222370.5963
34 | 2703200.5056 | 1222411.4429
35 | 2703172.656 | 1222252.8262
36 | 2703491.1343 | 1221711.8562
37 | 2703447.7815 | 1221677.8028
38 | 2702570.5239 | 1222158.7421
39 | 2702576.7699 | 1222163.3674
40 | 2702547.4997 | 1222143.3466
41 | 2702584.7745 | 1222169.295
42 | 2702662.2449 | 1222183.5848
43 | 2702533.2664 | 1222120.7226
44 | 2702595.3593 | 1222472.8195
45 | 2702819.7144 | 1222306.084
46 | 2702660.5081 | 1222081.2689
47 | 2702689.295 | 1222491.718
48 | 2702686.342 | 1222493.7371
49 | 2702702.0632 | 1222482.9879
50 | 2702670.9668 | 1222505.4964
51 | 2702764.9983 | 1222468.1772
52 | 2702661.196 | 1222517.1199
53 | 2702659.1155 | 1222519.5949
54 | 2703089.3609 | 1222529.994
55 | 2703015.8196 | 1222731.1884
56 | 2703098.9036 | 1222509.8878
57 | 2702789.1372 | 1222799.282
58 | 2703255.7656 | 1222728.309
59 | 2702755.9412 | 1222815.4514
60 | 2703283.7526 | 1222779.7898
61 | 2702695.2399 | 1222894.2915
62 | 2703283.9036 | 1222780.1087
63 | 2702517.8551 | 1221896.5897
64 | 2702659.5378 | 1222056.1889
65 | 2702657.1977 | 1222521.8764
66 | 2702465.2295 | 1222625.0337
67 | 2702640.2088 | 1222509.6573
68 | 2702832.8878 | 1222307.9304
69 | 2702659.6747 | 1222059.7288
70 | 2702543.0201 | 1222861.9629
71 | 2702477.9983 | 1222638.46
72 | 2702647.2789 | 1222521.2216
73 | 2702880.9076 | 1222268.5646
74 | 2702540.7883 | 1223096.3208
75 | 2702513.0263 | 1222682.1631
76 | 2702530.0806 | 1222700.2775
77 | 2702542.2962 | 1222713.3529
78 | 2702578.1001 | 1222707.4034
79 | 2702522.4594 | 1221842.8405
80 | 2702699.3906 | 1222947.4345
81 | 2702664.5021 | 1222982.676
82 | 2702349.0858 | 1222239.9137
83 | 2702343.5497 | 1222225.8854
84 | 2702351.5463 | 1222246.1486
85 | 2702340.5937 | 1222212.997
86 | 2702342.5378 | 1222199.595
87 | 2702381.2366 | 1222188.7073
88 | 2702775.1098 | 1221619.5285
89 | 2703203.6775 | 1222991.7619
90 | 2703312.4239 | 1222847.6231
91 | 2703320.525 | 1222875.5257
92 | 2703309.0151 | 1222835.9174
93 | 2703323.5551 | 1222885.9621
94 | 2703306.562 | 1222827.9462
95 | 2703327.8235 | 1222900.6639
96 | 2703296.9653 | 1222807.6852
97 | 2703305.7223 | 1223080.9348
98 | 2703311.6343 | 1223065.9682
99 | 2703297.9105 | 1223100.7111
100 | 2703313.9677 | 1223060.0608
101 | 2703316.5957 | 1223053.4079
102 | 2703324.3633 | 1223033.7435
103 | 2703325.0301 | 1223026.4929
104 | 2703325.4713 | 1223021.6962
105 | 2703327.4532 | 1223000.1471
106 | 2703328.2148 | 1222991.8658
107 | 2703330.0663 | 1222971.7354
108 | 2703330.9067 | 1222962.598
109 | 2703331.0841 | 1222960.6681
110 | 2703334.117 | 1222927.6926
111 | 2703293.4131 | 1222800.1855
112 | 2702662.2449 | 1222183.5848

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99202 | -0.15395 | 0.0049589 | 0.0012428
1 | 0.99205 | -0.15321 | 0 | 0
2 | 0.99193 | -0.15559 | 0 | 0
3 | 0.99188 | -0.1566 | 0 | 0
4 | 0.99405 | -0.11464 | 0 | 0
5 | 0.99168 | -0.16039 | 0 | 0
6 | 0.99151 | -0.16375 | 0.0012023 | 0.00030132
7 | 0.99577 | -0.081269 | 0 | 0
8 | 0.99391 | -0.11738 | 0.00075428 | 0.00018904
9 | 0.99139 | -0.16607 | 0 | 0
10 | 0.98987 | -0.19567 | 0 | 0
11 | 0.99133 | -0.16717 | 0.00056855 | 0.00014249
12 | 0.9898 | -0.19704 | 0 | 0
13 | 0.98974 | -0.19811 | 0.003252 | 0.00081503
14 | 0.99139 | -0.16614 | 0.0010977 | 0.00027511
15 | 0.9956 | -0.084664 | 0 | 0
16 | 0.99659 | -0.06559 | 0.00040164 | 0.00010066
17 | 0.99317 | -0.13209 | 0.00021823 | 5.4693e-05
18 | 0.99123 | -0.1691 | 0.001051 | 0.00026342
19 | 0.99124 | -0.16896 | 0.0017377 | 0.00043551
20 | 0.98974 | -0.19818 | 0.0018624 | 0.00046676
21 | 0.99138 | -0.16626 | 0 | 0
22 | 0.98965 | -0.19978 | 0.0015121 | 0.00037897
23 | 0.99681 | -0.061366 | 0.0004871 | 0.00012208
24 | 0.99672 | -0.063034 | 0.001568 | 0.00039297
25 | 0.99689 | -0.059828 | 0.0012863 | 0.00032238
26 | 0.99654 | -0.066572 | 0.00090084 | 0.00022577
27 | 0.99707 | -0.056398 | 0.00050998 | 0.00012781
28 | 0.99631 | -0.07107 | 0.00081171 | 0.00020343
29 | 0.99729 | -0.052164 | 0.00090289 | 0.00022629
30 | 0.9962 | -0.073059 | 0.0004799 | 0.00012027
31 | 0.99781 | -0.042128 | 0 | 0
32 | 0.99247 | -0.14582 | 0.00028702 | 7.1934e-05
33 | 0.99247 | -0.14588 | 0.00034773 | 8.7149e-05
34 | 0.99253 | -0.14467 | 0 | 0
35 | 0.99262 | -0.14284 | 0.0010233 | 0.00025646
36 | 0.99232 | -0.14884 | 0 | 0
37 | 0.99229 | -0.14936 | 0.00052774 | 0.00013226
38 | 0.99845 | -0.029842 | 0.00038286 | 9.5953e-05
39 | 0.99857 | -0.027543 | 0.00060293 | 0.00015111
40 | 0.99803 | -0.037883 | 0.0012516 | 0.00031368
41 | 0.99872 | -0.024491 | 0.00026107 | 6.5431e-05
42 | 1 | 0 | -0.066831 | -0.016457
43 | 0.9978 | -0.042307 | 0.00056316 | 0.00014114
44 | 0.99501 | -0.095255 | 0 | 0
45 | 0.99958 | -0.0081134 | 0.0011073 | 0.00027752
46 | 0.99751 | -0.047832 | 0.0023053 | 0.00057775
47 | 0.99465 | -0.10211 | 0.00020148 | 5.0495e-05
48 | 0.99466 | -0.10205 | 0.00022274 | 5.5824e-05
49 | 0.99464 | -0.10234 | 0.00024583 | 6.1611e-05
50 | 0.99468 | -0.10162 | 0.00020606 | 5.1644e-05
51 | 0.9946 | -0.10306 | 0.00057735 | 0.0001447
52 | 0.9947 | -0.10123 | 0.00016445 | 4.1216e-05
53 | 0.9947 | -0.10114 | 0.0002926 | 7.3333e-05
54 | 0.97844 | -0.4168 | 0.00076556 | 0.00019187
55 | 0.97882 | -0.40928 | 0 | 0
56 | 0.97841 | -0.41726 | 0.0011338 | 0.00028416
57 | 0.981 | -0.36643 | 0.0013089 | 0.00032805
58 | 0.97699 | -0.4452 | 0 | 0
59 | 0.98137 | -0.35918 | 0.0003729 | 9.3458e-05
60 | 0.97658 | -0.45336 | 0.00023144 | 5.8004e-05
61 | 0.98244 | -0.33829 | 0 | 0
62 | 0.97658 | -0.4534 | 0.00026168 | 6.5584e-05
63 | 0.99553 | -0.086104 | 0 | 0
64 | 0.99695 | -0.058549 | 0.00050179 | 0.00012576
65 | 0.99471 | -0.10104 | 0.00018244 | 4.5723e-05
66 | 0.99207 | -0.15159 | 0 | 0
67 | 0.99476 | -0.10002 | 0.00022228 | 5.5709e-05
68 | 0.99957 | -0.0083724 | 0.00054291 | 0.00013607
69 | 0.99703 | -0.057063 | 0.00052368 | 0.00013125
70 | 0.98892 | -0.21231 | 0.00022471 | 5.6319e-05
71 | 0.99203 | -0.15245 | 0.00029937 | 7.5029e-05
72 | 0.99473 | -0.10065 | 0.00030918 | 7.7489e-05
73 | 0.99953 | -0.0089916 | 0.00057065 | 0.00014302
74 | 0.98571 | -0.27461 | 0 | 0
75 | 0.99191 | -0.15469 | 0.00056748 | 0.00014222
76 | 0.99187 | -0.15542 | 0.0003961 | 9.9271e-05
77 | 0.99185 | -0.15582 | 0.00097296 | 0.00024385
78 | 0.99184 | -0.15611 | 0.00029353 | 7.3566e-05
79 | 0.99541 | -0.088379 | 0.0011132 | 0.00027899
80 | 0.98237 | -0.33967 | 0.0005281 | 0.00013235
81 | 0.98232 | -0.34069 | 0.00090545 | 0.00022693
82 | 0.99564 | -0.083903 | 0.0010606 | 0.00026582
83 | 0.99569 | -0.083026 | 0.00055967 | 0.00014027
84 | 0.99563 | -0.084168 | 0.0022469 | 0.00056313
85 | 0.99573 | -0.082126 | 0.0011393 | 0.00028555
86 | 0.9958 | -0.080904 | 0.0014887 | 0.0003731
87 | 0.99604 | -0.076246 | 0.0012759 | 0.00031976
88 | 0.98962 | -0.2004 | 0.001393 | 0.00034913
89 | 0.97606 | -0.46368 | 0.00044411 | 0.0001113
90 | 0.97614 | -0.46215 | 0 | 0
91 | 0.97599 | -0.46505 | 0.00021386 | 5.3599e-05
92 | 0.9762 | -0.46083 | 0.00019823 | 4.968e-05
93 | 0.97594 | -0.4661 | 0.00038673 | 9.6923e-05
94 | 0.97625 | -0.45989 | 0.00018765 | 4.7031e-05
95 | 0.97587 | -0.46746 | 0.00022984 | 5.7604e-05
96 | 0.97638 | -0.45731 | 0.00035873 | 8.9905e-05
97 | 0.97531 | -0.47838 | 0.00057602 | 0.00014437
98 | 0.97533 | -0.47804 | 0.00022911 | 5.742e-05
99 | 0.9753 | -0.47861 | 0.00058653 | 0.000147
100 | 0.97534 | -0.47788 | 0.00055646 | 0.00013946
101 | 0.97535 | -0.47762 | 0.00019429 | 4.8692e-05
102 | 0.97539 | -0.47679 | 0.00021701 | 5.4389e-05
103 | 0.97541 | -0.47648 | 0.0003528 | 8.8419e-05
104 | 0.97542 | -0.47624 | 0.00027805 | 6.9687e-05
105 | 0.97548 | -0.47505 | 0.00027913 | 6.9956e-05
106 | 0.97551 | -0.47455 | 0.00022767 | 5.706e-05
107 | 0.97557 | -0.47326 | 0.00041495 | 0.000104
108 | 0.97561 | -0.4726 | 0.00021204 | 5.3142e-05
109 | 0.97561 | -0.47245 | 0.00018042 | 4.5217e-05
110 | 0.97575 | -0.46984 | 0.00032654 | 8.1839e-05
111 | 0.97643 | -0.4563 | 0.00045551 | 0.00011416
112 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.013564 | -0.0033993 | 0.013565 | 0.0033996 | 4.8157e-07 | 2.6815e-07 | 0.020347 | 0.020347 | 0.020347 | 0.99202 | -0.15395 | 0.99205 | -0.15321 | 5.5897
1 | 0.0086056 | 0.0021565 | -0.008605 | -0.0021562 | 6.7135e-07 | 2.9096e-07 | 0.012908 | 0.012908 | 0.012908 | 0.99202 | -0.15395 | 0.99193 | -0.15559 | 3.5462
2 | 0.0050921 | 0.0012747 | -0.0050913 | -0.0012747 | 8.2285e-07 | 4.0999e-08 | 0.0076373 | 0.0076375 | 0.0076375 | 0.99205 | -0.15321 | 0.99188 | -0.1566 | 2.0982
3 | -0.018657 | -0.0046743 | 0.018691 | 0.0046948 | 3.4331e-05 | 2.0459e-05 | 0.027984 | 0.027983 | 0.027984 | 0.99205 | -0.15321 | 0.99405 | -0.11464 | 7.6879
4 | 0.008605 | 0.0021562 | -0.008603 | -0.0021554 | 1.9681e-06 | 8.5313e-07 | 0.012908 | 0.012908 | 0.012908 | 0.99193 | -0.15559 | 0.99168 | -0.16039 | 3.5463
5 | 0.0050913 | 0.0012747 | -0.0050896 | -0.0012746 | 1.7319e-06 | 8.6928e-08 | 0.0076375 | 0.0076379 | 0.0076379 | 0.99188 | -0.1566 | 0.99151 | -0.16375 | 2.0983
6 | -0.021853 | -0.0054676 | 0.021888 | 0.0054887 | 3.4758e-05 | 2.112e-05 | 0.032709 | 0.032709 | 0.032709 | 0.99405 | -0.11464 | 0.99577 | -0.081269 | 8.986
7 | 0.0031617 | 0.00077279 | -0.0031613 | -0.00077316 | 4.0392e-07 | -3.6656e-07 | 0.0047259 | 0.0047262 | 0.0047262 | 0.99405 | -0.11464 | 0.99391 | -0.11738 | 1.2984
8 | 0.008603 | 0.0021554 | -0.0086007 | -0.0021543 | 2.3262e-06 | 1.0086e-06 | 0.012908 | 0.012909 | 0.012909 | 0.99168 | -0.16039 | 0.99139 | -0.16607 | 3.5463
9 | 0.0038873 | 0.00097329 | -0.0038868 | -0.00097345 | 4.4161e-07 | -1.6363e-07 | 0.0058335 | 0.0058337 | 0.0058337 | 0.99151 | -0.16375 | 0.99139 | -0.16614 | 1.6027
10 | 0.0011136 | 0.00027454 | -0.0011134 | -0.00027666 | 1.7837e-07 | -2.1232e-06 | 0.0016625 | 0.0016632 | 0.0016632 | 0.99577 | -0.081269 | 0.9956 | -0.084664 | 0.45693
11 | -0.023001 | -0.0057632 | 0.023019 | 0.0057737 | 1.7191e-05 | 1.0497e-05 | 0.034371 | 0.034371 | 0.034371 | 0.99577 | -0.081269 | 0.99659 | -0.06559 | 9.4426
12 | 0.002407 | 0.00058411 | -0.0024053 | -0.00058746 | 1.6504e-06 | -3.3471e-06 | 0.0035969 | 0.0035984 | 0.0035984 | 0.99391 | -0.11738 | 0.99317 | -0.13209 | 0.98858
13 | 0.0080321 | 0.0020132 | -0.0080208 | -0.0020087 | 1.1317e-05 | 4.5696e-06 | 0.012056 | 0.012057 | 0.012057 | 0.99139 | -0.16607 | 0.98987 | -0.19567 | 3.3123
14 | 0.00056858 | 0.0001411 | -0.00056855 | -0.00014249 | 2.9779e-08 | -1.3876e-06 | 0.0008529 | 0.0008534 | 0.0008534 | 0.99139 | -0.16607 | 0.99133 | -0.16717 | 0.23445
15 | 0.0018626 | 0.00046594 | -0.0018625 | -0.00046639 | 1.2116e-07 | -4.5224e-07 | 0.0027997 | 0.0027999 | 0.0027999 | 0.98987 | -0.19567 | 0.9898 | -0.19704 | 0.7692
16 | 0.0061581 | 0.0015427 | -0.0061574 | -0.0015426 | 7.1344e-07 | 1.7124e-07 | 0.009257 | 0.0092571 | 0.0092571 | 0.98987 | -0.19567 | 0.98974 | -0.19811 | 2.5432
17 | 0.0018625 | 0.00046639 | -0.0018624 | -0.00046676 | 1.0067e-07 | -3.7568e-07 | 0.0027999 | 0.0028 | 0.0028 | 0.9898 | -0.19704 | 0.98974 | -0.19818 | 0.76924
18 | 0.0029054 | 0.00072753 | -0.0029052 | -0.0007278 | 2.3116e-07 | -2.6724e-07 | 0.0043679 | 0.0043681 | 0.0043681 | 0.98974 | -0.19811 | 0.98965 | -0.19978 | 1.2
19 | 0.0027891 | 0.00069834 | -0.0027891 | -0.00069836 | 1.6305e-08 | -2.1558e-08 | 0.0041861 | 0.0041861 | 0.0041861 | 0.99139 | -0.16614 | 0.99138 | -0.16626 | 1.15
20 | 0.0011134 | 0.00027666 | -0.0011133 | -0.00027756 | 7.6013e-08 | -9.0395e-07 | 0.0016632 | 0.0016636 | 0.0016636 | 0.9956 | -0.084664 | 0.99553 | -0.086104 | 0.45703
21 | -0.02342 | -0.0058744 | 0.023428 | 0.0058792 | 7.8641e-06 | 4.8095e-06 | 0.034971 | 0.034971 | 0.034971 | 0.99659 | -0.06559 | 0.99695 | -0.058549 | 9.6074
22 | 0.0021871 | 0.00053277 | -0.002186 | -0.0005356 | 1.0986e-06 | -2.8359e-06 | 0.0032715 | 0.0032727 | 0.0032727 | 0.99317 | -0.13209 | 0.99262 | -0.14284 | 0.89909
23 | -0.001051 | -0.00026342 | 0.001051 | 0.00026332 | 7.0547e-09 | -9.2899e-08 | 0.0015778 | 0.0015778 | 0.0015778 | 0.99123 | -0.1691 | 0.99124 | -0.16896 | 0.43346
24 | -0.0027888 | -0.00069884 | 0.0027891 | 0.00069836 | 3.5929e-07 | -4.749e-07 | 0.0041864 | 0.0041861 | 0.0041864 | 0.99124 | -0.16896 | 0.99138 | -0.16626 | 1.1501
25 | 0.0013931 | 0.00034883 | -0.001393 | -0.00034913 | 4.1565e-08 | -2.9802e-07 | 0.0020945 | 0.0020946 | 0.0020946 | 0.98965 | -0.19978 | 0.98962 | -0.2004 | 0.57544
26 | 0.01154 | 0.0028932 | -0.011539 | -0.0028927 | 9.1705e-07 | 4.7951e-07 | 0.017227 | 0.017227 | 0.017227 | 0.99681 | -0.061366 | 0.99672 | -0.063034 | 4.7328
27 | -0.012027 | -0.0030153 | 0.012028 | 0.0030157 | 8.8164e-07 | 4.6917e-07 | 0.017954 | 0.017954 | 0.017954 | 0.99681 | -0.061366 | 0.99689 | -0.059828 | 4.9325
28 | 0.0099712 | 0.0024997 | -0.0099695 | -0.0024989 | 1.6809e-06 | 8.1219e-07 | 0.014886 | 0.014886 | 0.014886 | 0.99672 | -0.063034 | 0.99654 | -0.066572 | 4.0897
29 | -0.013314 | -0.0033381 | 0.013317 | 0.0033393 | 2.1762e-06 | 1.2012e-06 | 0.019874 | 0.019874 | 0.019874 | 0.99689 | -0.059828 | 0.99707 | -0.056398 | 5.46
30 | 0.0090687 | 0.0022731 | -0.0090668 | -0.0022723 | 1.943e-06 | 8.7546e-07 | 0.013541 | 0.013541 | 0.013541 | 0.99654 | -0.066572 | 0.99631 | -0.07107 | 3.7202
31 | -0.013827 | -0.0034671 | 0.013829 | 0.0034687 | 2.7905e-06 | 1.5579e-06 | 0.020635 | 0.020635 | 0.020635 | 0.99707 | -0.056398 | 0.99729 | -0.052164 | 5.6691
32 | 0.008255 | 0.0020688 | -0.0082543 | -0.0020685 | 7.8234e-07 | 3.2199e-07 | 0.012329 | 0.012329 | 0.012329 | 0.99631 | -0.07107 | 0.9962 | -0.073059 | 3.3872
33 | -0.014732 | -0.003695 | 0.014739 | 0.003699 | 7.0512e-06 | 4.0048e-06 | 0.021982 | 0.021982 | 0.021982 | 0.99729 | -0.052164 | 0.99781 | -0.042128 | 6.0391
34 | 0.0077744 | 0.0019482 | -0.0077732 | -0.0019478 | 1.1801e-06 | 4.5148e-07 | 0.011612 | 0.011613 | 0.011613 | 0.9962 | -0.073059 | 0.99604 | -0.076246 | 3.1903
35 | 0.00056317 | 0.00014091 | -0.00056316 | -0.00014114 | 4.7997e-09 | -2.3397e-07 | 0.00083976 | 0.00083984 | 0.00083984 | 0.99781 | -0.042128 | 0.9978 | -0.042307 | 0.23073
36 | -0.015302 | -0.0038399 | 0.015306 | 0.0038416 | 3.0983e-06 | 1.7757e-06 | 0.022822 | 0.022822 | 0.022822 | 0.99781 | -0.042128 | 0.99803 | -0.037883 | 6.2698
37 | 0.00034773 | 8.7033e-05 | -0.00034773 | -8.7149e-05 | 9.174e-10 | -1.1573e-07 | 0.00052131 | 0.00052135 | 0.00052135 | 0.99247 | -0.14582 | 0.99247 | -0.14588 | 0.14323
38 | -0.00063475 | -0.00015897 | 0.00063478 | 0.00015766 | 3.4843e-08 | -1.3042e-06 | 0.00095164 | 0.00095118 | 0.00095164 | 0.99247 | -0.14582 | 0.99253 | -0.14467 | 0.26144
39 | -0.00063478 | -0.00015766 | 0.00063484 | 0.00015561 | 5.4685e-08 | -2.0499e-06 | 0.00095118 | 0.00095045 | 0.00095118 | 0.99253 | -0.14467 | 0.99262 | -0.14284 | 0.26131
40 | 0.0005279 | 0.00012354 | -0.00052775 | -0.00013155 | 1.4682e-07 | -8.0182e-06 | 0.00078836 | 0.00079113 | 0.00079113 | 0.99262 | -0.14284 | 0.99232 | -0.14884 | 0.21734
41 | 0.00052775 | 0.00013155 | -0.00052774 | -0.00013226 | 1.3037e-08 | -7.0896e-07 | 0.00079113 | 0.00079138 | 0.00079138 | 0.99232 | -0.14884 | 0.99229 | -0.14936 | 0.21741
42 | -0.016946 | -0.004255 | 0.016948 | 0.0042561 | 1.8595e-06 | 1.0884e-06 | 0.025258 | 0.025258 | 0.025258 | 0.99845 | -0.029842 | 0.99857 | -0.027543 | 6.9391
43 | 0.016564 | 0.004159 | -0.016557 | -0.0041553 | 6.3511e-06 | 3.7014e-06 | 0.024688 | 0.024688 | 0.024688 | 0.99845 | -0.029842 | 0.99803 | -0.037883 | 6.7824
44 | -0.017551 | -0.0044072 | 0.017554 | 0.0044087 | 2.5555e-06 | 1.5052e-06 | 0.026157 | 0.026157 | 0.026157 | 0.99857 | -0.027543 | 0.99872 | -0.024491 | 7.186
45 | -0.017815 | -0.0044741 | 0.017836 | 0.0044864 | 2.0843e-05 | 1.2306e-05 | 0.026546 | 0.026545 | 0.026546 | 0.99872 | -0.024491 | 1 | 0 | 7.2928
46 | 0.018291 | 0.0046578 | -0.018207 | -0.0046082 | 8.3637e-05 | 4.9605e-05 | 0.027243 | 0.027244 | 0.027244 | 1 | 0 | 0.99501 | -0.095255 | 7.4847
47 | 0.0022217 | 0.00055344 | -0.0022209 | -0.00055563 | 8.5603e-07 | -2.1922e-06 | 0.0033048 | 0.0033058 | 0.0033058 | 1 | 0 | 0.99958 | -0.0081134 | 0.90818
48 | 0.026833 | 0.0067594 | -0.026771 | -0.0067216 | 6.1235e-05 | 3.7851e-05 | 0.039939 | 0.03994 | 0.03994 | 1 | 0 | 0.99751 | -0.047832 | 10.9725
49 | 0.015582 | 0.0039533 | -0.01554 | -0.003929 | 4.2097e-05 | 2.4269e-05 | 0.023319 | 0.02332 | 0.02332 | 0.99501 | -0.095255 | 0.99207 | -0.15159 | 6.4067
50 | 0.0026252 | 0.0006549 | -0.0026246 | -0.00065585 | 5.9437e-07 | -9.5548e-07 | 0.0039249 | 0.0039254 | 0.0039254 | 0.99501 | -0.095255 | 0.99476 | -0.10002 | 1.0784
51 | 0.0011136 | 0.00027812 | -0.0011136 | -0.00027828 | 1.3703e-08 | -1.656e-07 | 0.0016574 | 0.0016575 | 0.0016575 | 0.99958 | -0.0081134 | 0.99957 | -0.0083724 | 0.45535
52 | 0.024466 | 0.0061438 | -0.024455 | -0.0061372 | 1.077e-05 | 6.6116e-06 | 0.036501 | 0.036501 | 0.036501 | 0.99751 | -0.047832 | 0.99703 | -0.057063 | 10.0278
53 | -0.0010247 | -0.00025571 | 0.0010247 | 0.00025566 | 3.1508e-09 | -4.4415e-08 | 0.0015326 | 0.0015325 | 0.0015326 | 0.99465 | -0.10211 | 0.99466 | -0.10205 | 0.42103
54 | 0.00082321 | 0.00020521 | -0.0008232 | -0.00020541 | 8.7922e-09 | -1.9513e-07 | 0.0012311 | 0.0012312 | 0.0012312 | 0.99465 | -0.10211 | 0.99464 | -0.10234 | 0.33825
55 | -0.0012474 | -0.00031148 | 0.0012475 | 0.00031125 | 2.5415e-08 | -2.3645e-07 | 0.0018658 | 0.0018657 | 0.0018658 | 0.99466 | -0.10205 | 0.99468 | -0.10162 | 0.51257
56 | 0.00057737 | 0.00014379 | -0.00057735 | -0.0001447 | 1.9762e-08 | -9.044e-07 | 0.00086345 | 0.00086377 | 0.00086377 | 0.99464 | -0.10234 | 0.9946 | -0.10306 | 0.2373
57 | -0.0014535 | -0.00036289 | 0.0014535 | 0.00036271 | 2.691e-08 | -1.7988e-07 | 0.0021739 | 0.0021739 | 0.0021739 | 0.99468 | -0.10162 | 0.9947 | -0.10123 | 0.59724
58 | -0.001618 | -0.00040393 | 0.001618 | 0.00040389 | 7.1e-09 | -3.7425e-08 | 0.0024199 | 0.0024199 | 0.0024199 | 0.9947 | -0.10123 | 0.9947 | -0.10114 | 0.6648
59 | -0.0019106 | -0.00047722 | 0.0019106 | 0.00047719 | 9.1268e-09 | -3.2848e-08 | 0.0028576 | 0.0028576 | 0.0028576 | 0.9947 | -0.10114 | 0.99471 | -0.10104 | 0.78505
60 | -0.0018994 | -0.00047577 | 0.0019001 | 0.00047347 | 6.7869e-07 | -2.292e-06 | 0.0028885 | 0.0028876 | 0.0028885 | 0.97844 | -0.4168 | 0.97882 | -0.40928 | 0.79355
61 | 0.0011338 | 0.0002839 | -0.0011338 | -0.00028416 | 2.4873e-08 | -2.6426e-07 | 0.0017243 | 0.0017244 | 0.0017244 | 0.97844 | -0.4168 | 0.97841 | -0.41726 | 0.47373
62 | -0.0095208 | -0.0023814 | 0.0095403 | 0.0023908 | 1.944e-05 | 9.3233e-06 | 0.014472 | 0.014471 | 0.014472 | 0.97882 | -0.40928 | 0.981 | -0.36643 | 3.9758
63 | 0.0076207 | 0.001908 | -0.0076077 | -0.0019029 | 1.3014e-05 | 5.0848e-06 | 0.011584 | 0.011586 | 0.011586 | 0.97882 | -0.40928 | 0.97699 | -0.4452 | 3.1829
64 | -0.010849 | -0.0027188 | 0.010853 | 0.0027208 | 3.7498e-06 | 1.9335e-06 | 0.016456 | 0.016456 | 0.016456 | 0.981 | -0.36643 | 0.98137 | -0.35918 | 4.521
65 | 0.0076077 | 0.0019029 | -0.0076048 | -0.0019017 | 2.9499e-06 | 1.1544e-06 | 0.011586 | 0.011586 | 0.011586 | 0.97699 | -0.4452 | 0.97658 | -0.45336 | 3.1829
66 | -0.011226 | -0.0028142 | 0.011237 | 0.0028201 | 1.1185e-05 | 5.8563e-06 | 0.017022 | 0.017021 | 0.017022 | 0.98137 | -0.35918 | 0.98244 | -0.33829 | 4.6763
67 | 0.0073733 | 0.0018437 | -0.0073733 | -0.0018437 | 1.6694e-08 | 6.2705e-09 | 0.011233 | 0.011233 | 0.011233 | 0.97658 | -0.45336 | 0.97658 | -0.4534 | 3.0861
68 | 0.0014337 | 0.00035791 | -0.0014336 | -0.00035852 | 9.4223e-08 | -6.1463e-07 | 0.002171 | 0.0021712 | 0.0021712 | 0.98244 | -0.33829 | 0.98237 | -0.33967 | 0.59649
69 | -0.012671 | -0.003178 | 0.012709 | 0.0031991 | 3.8569e-05 | 2.1136e-05 | 0.019192 | 0.019191 | 0.019192 | 0.98244 | -0.33829 | 0.98571 | -0.27461 | 5.2726
70 | 0.0071116 | 0.0017781 | -0.0071107 | -0.0017778 | 9.7792e-07 | 3.4795e-07 | 0.010835 | 0.010835 | 0.010835 | 0.97658 | -0.4534 | 0.97643 | -0.4563 | 2.9765
71 | 0.0011133 | 0.00027756 | -0.0011132 | -0.00027899 | 1.2042e-07 | -1.4309e-06 | 0.0016636 | 0.0016641 | 0.0016641 | 0.99553 | -0.086104 | 0.99541 | -0.088379 | 0.45717
72 | -0.02393 | -0.0060049 | 0.023932 | 0.006006 | 1.695e-06 | 1.0386e-06 | 0.03572 | 0.03572 | 0.03572 | 0.99695 | -0.058549 | 0.99703 | -0.057063 | 9.8131
73 | -0.0020931 | -0.00052291 | 0.0020931 | 0.0005228 | 3.8458e-08 | -1.1123e-07 | 0.0031305 | 0.0031304 | 0.0031305 | 0.99471 | -0.10104 | 0.99473 | -0.10065 | 0.86002
74 | 0.01301 | 0.003297 | -0.012972 | -0.0032762 | 3.7852e-05 | 2.0818e-05 | 0.019526 | 0.019528 | 0.019528 | 0.99207 | -0.15159 | 0.98892 | -0.21231 | 5.3648
75 | 0.0025299 | 0.00063198 | -0.0025298 | -0.00063216 | 1.0369e-07 | -1.8167e-07 | 0.0037938 | 0.0037939 | 0.0037939 | 0.99207 | -0.15159 | 0.99203 | -0.15245 | 1.0423
76 | 0.0024024 | 0.00060015 | -0.0024023 | -0.00060029 | 7.174e-08 | -1.4647e-07 | 0.0035929 | 0.0035929 | 0.0035929 | 0.99476 | -0.10002 | 0.99473 | -0.10065 | 0.98707
77 | 0.00057066 | 0.00014221 | -0.00057065 | -0.00014302 | 1.6799e-08 | -8.0313e-07 | 0.00084924 | 0.00084953 | 0.00084953 | 0.99957 | -0.0083724 | 0.99953 | -0.0089916 | 0.23339
78 | 0.012747 | 0.0032199 | -0.012709 | -0.0031991 | 3.7956e-05 | 2.0777e-05 | 0.01919 | 0.019191 | 0.019191 | 0.98892 | -0.21231 | 0.98571 | -0.27461 | 5.2722
79 | 0.0022304 | 0.00055713 | -0.0022302 | -0.00055771 | 2.3741e-07 | -5.7849e-07 | 0.0033449 | 0.0033451 | 0.0033451 | 0.99203 | -0.15245 | 0.99191 | -0.15469 | 0.91899
80 | 0.0016627 | 0.00041549 | -0.0016626 | -0.00041577 | 5.8027e-08 | -2.8399e-07 | 0.0024938 | 0.002494 | 0.002494 | 0.99191 | -0.15469 | 0.99187 | -0.15542 | 0.68515
81 | 0.0012665 | 0.0003165 | -0.0012665 | -0.00031672 | 2.4218e-08 | -2.1545e-07 | 0.0018997 | 0.0018998 | 0.0018998 | 0.99187 | -0.15542 | 0.99185 | -0.15582 | 0.52192
82 | 0.00029354 | 7.2867e-05 | -0.00029353 | -7.3566e-05 | 3.9512e-09 | -6.9908e-07 | 0.00044013 | 0.00044038 | 0.00044038 | 0.99185 | -0.15582 | 0.99184 | -0.15611 | 0.12098
83 | 0.0009055 | 0.00022617 | -0.00090545 | -0.00022693 | 4.3905e-08 | -7.5997e-07 | 0.0013713 | 0.0013716 | 0.0013716 | 0.98237 | -0.33967 | 0.98232 | -0.34069 | 0.37681
84 | -0.0033076 | -0.00082889 | 0.0033077 | 0.00082878 | 1.3819e-07 | -1.077e-07 | 0.0049433 | 0.0049432 | 0.0049433 | 0.99564 | -0.083903 | 0.99569 | -0.083026 | 1.358
85 | 0.002247 | 0.00056306 | -0.0022469 | -0.00056313 | 2.8346e-08 | -6.9029e-08 | 0.0033581 | 0.0033582 | 0.0033582 | 0.99564 | -0.083903 | 0.99563 | -0.084168 | 0.92257
86 | -0.0038674 | -0.00096904 | 0.0038676 | 0.00096898 | 1.6564e-07 | -6.5984e-08 | 0.0057796 | 0.0057796 | 0.0057796 | 0.99569 | -0.083026 | 0.99573 | -0.082126 | 1.5878
87 | -0.0050069 | -0.0012545 | 0.0050072 | 0.0012545 | 2.9149e-07 | 5.9347e-09 | 0.0074822 | 0.0074821 | 0.0074822 | 0.99573 | -0.082126 | 0.9958 | -0.080904 | 2.0555
88 | -0.0064959 | -0.0016276 | 0.0064973 | 0.001628 | 1.4413e-06 | 3.9161e-07 | 0.0097066 | 0.0097065 | 0.0097066 | 0.9958 | -0.080904 | 0.99604 | -0.076246 | 2.6667
89 | -0.00044411 | -0.0001113 | 0.00044414 | 0.00010898 | 3.2166e-08 | -2.3212e-06 | 0.00067705 | 0.00067622 | 0.00067705 | 0.97606 | -0.46368 | 0.97614 | -0.46215 | 0.186
90 | 0.0054647 | 0.0013676 | -0.0054639 | -0.0013674 | 7.5597e-07 | 1.2067e-07 | 0.0083296 | 0.0083297 | 0.0083297 | 0.97614 | -0.46215 | 0.97599 | -0.46505 | 2.2884
91 | -0.0059088 | -0.0014765 | 0.0059092 | 0.0014766 | 3.708e-07 | 8.4898e-08 | 0.0090058 | 0.0090057 | 0.0090058 | 0.97614 | -0.46215 | 0.9762 | -0.46083 | 2.4741
92 | 0.00525 | 0.0013138 | -0.0052498 | -0.0013138 | 2.6106e-07 | 3.1276e-08 | 0.0080036 | 0.0080037 | 0.0080037 | 0.97599 | -0.46505 | 0.97594 | -0.4661 | 2.1988
93 | -0.0061074 | -0.0015263 | 0.0061077 | 0.0015264 | 2.7126e-07 | 6.9214e-08 | 0.0093079 | 0.0093079 | 0.0093079 | 0.9762 | -0.46083 | 0.97625 | -0.45989 | 2.5571
94 | 0.0048631 | 0.0012169 | -0.0048627 | -0.0012169 | 3.1556e-07 | 1.0684e-08 | 0.007414 | 0.0074141 | 0.0074141 | 0.97594 | -0.4661 | 0.97587 | -0.46746 | 2.0368
95 | -0.0062953 | -0.0015734 | 0.0062961 | 0.0015736 | 7.738e-07 | 2.1488e-07 | 0.0095939 | 0.0095938 | 0.0095939 | 0.97625 | -0.45989 | 0.97638 | -0.45731 | 2.6357
96 | 0.0046329 | 0.0011593 | -0.0046324 | -0.0011593 | 5.238e-07 | -1.4476e-08 | 0.0070637 | 0.0070638 | 0.0070638 | 0.97587 | -0.46746 | 0.97575 | -0.46984 | 1.9406
97 | -0.0066548 | -0.0016635 | 0.0066551 | 0.0016636 | 3.1999e-07 | 1.01e-07 | 0.01014 | 0.01014 | 0.01014 | 0.97638 | -0.45731 | 0.97643 | -0.4563 | 2.7858
98 | -0.0011626 | -0.0002911 | 0.0011626 | 0.00029091 | 1.8982e-08 | -1.8868e-07 | 0.0017736 | 0.0017735 | 0.0017736 | 0.97531 | -0.47838 | 0.97533 | -0.47804 | 0.48725
99 | 0.00058653 | 0.00014674 | -0.00058653 | -0.000147 | 6.3845e-09 | -2.6127e-07 | 0.00089477 | 0.00089486 | 0.00089486 | 0.97531 | -0.47838 | 0.9753 | -0.47861 | 0.24584
100 | -0.0013917 | -0.00034833 | 0.0013917 | 0.00034826 | 1.0736e-08 | -7.2397e-08 | 0.0021231 | 0.002123 | 0.0021231 | 0.97533 | -0.47804 | 0.97534 | -0.47788 | 0.58326
101 | -0.0019482 | -0.00048772 | 0.0019482 | 0.00048765 | 2.3693e-08 | -7.411e-08 | 0.002972 | 0.002972 | 0.002972 | 0.97534 | -0.47788 | 0.97535 | -0.47762 | 0.81648
102 | -0.0021425 | -0.00053634 | 0.0021425 | 0.00053613 | 8.4692e-08 | -2.0968e-07 | 0.0032684 | 0.0032683 | 0.0032684 | 0.97535 | -0.47762 | 0.97539 | -0.47679 | 0.8979
103 | -0.0023596 | -0.00059052 | 0.0023596 | 0.00059045 | 3.5373e-08 | -6.8244e-08 | 0.0035993 | 0.0035993 | 0.0035993 | 0.97539 | -0.47679 | 0.97541 | -0.47648 | 0.98883
104 | -0.0027124 | -0.00067887 | 0.0027124 | 0.00067883 | 3.0923e-08 | -4.0336e-08 | 0.0041375 | 0.0041375 | 0.0041375 | 0.97541 | -0.47648 | 0.97542 | -0.47624 | 1.1367
105 | -0.0029905 | -0.00074852 | 0.0029906 | 0.00074835 | 1.6886e-07 | -1.6206e-07 | 0.0045617 | 0.0045616 | 0.0045617 | 0.97542 | -0.47624 | 0.97548 | -0.47505 | 1.2532
106 | -0.0032698 | -0.00081831 | 0.0032699 | 0.00081826 | 7.757e-08 | -5.4176e-08 | 0.0049873 | 0.0049873 | 0.0049873 | 0.97548 | -0.47505 | 0.97551 | -0.47455 | 1.3702
107 | -0.0034975 | -0.00087532 | 0.0034977 | 0.0008752 | 2.1573e-07 | -1.1433e-07 | 0.0053346 | 0.0053345 | 0.0053346 | 0.97551 | -0.47455 | 0.97557 | -0.47326 | 1.4655
108 | -0.0039127 | -0.0009792 | 0.0039128 | 0.00097916 | 1.2253e-07 | -3.6156e-08 | 0.0059674 | 0.0059674 | 0.0059674 | 0.97557 | -0.47326 | 0.97561 | -0.4726 | 1.6394
109 | -0.0041248 | -0.0010323 | 0.0041249 | 0.0010323 | 2.876e-08 | -5.7934e-09 | 0.0062908 | 0.0062908 | 0.0062908 | 0.97561 | -0.4726 | 0.97561 | -0.47245 | 1.7282
110 | -0.0043053 | -0.0010775 | 0.0043058 | 0.0010774 | 5.3535e-07 | -7.0943e-08 | 0.0065659 | 0.0065658 | 0.0065659 | 0.97561 | -0.47245 | 0.97575 | -0.46984 | 1.8038

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.066831 | 0.016457

## res_load
| p_mw | q_mvar
0 | 0.0049589 | 0.0012428
1 | 0.0012023 | 0.00030132
2 | 0.00075428 | 0.00018904
3 | 0.00056855 | 0.00014249
4 | 0.003252 | 0.00081503
5 | 0.0010977 | 0.00027511
6 | 0.00040164 | 0.00010066
7 | 0.00021823 | 5.4693e-05
8 | 0.001051 | 0.00026342
9 | 0.0017377 | 0.00043551
10 | 0.0018624 | 0.00046676
11 | 0.0015121 | 0.00037897
12 | 0.0004871 | 0.00012208
13 | 0.001568 | 0.00039297
14 | 0.0012863 | 0.00032238
15 | 0.00090084 | 0.00022577
16 | 0.00050998 | 0.00012781
17 | 0.00081171 | 0.00020343
18 | 0.00090289 | 0.00022629
19 | 0.0004799 | 0.00012027
20 | 0.00028702 | 7.1934e-05
21 | 0.00034773 | 8.7149e-05
22 | 0.0010233 | 0.00025646
23 | 0.00052774 | 0.00013226
24 | 0.00038286 | 9.5953e-05
25 | 0.00060293 | 0.00015111
26 | 0.0012516 | 0.00031368
27 | 0.00026107 | 6.5431e-05
28 | 0.00056316 | 0.00014114
29 | 0.0011073 | 0.00027752
30 | 0.0023053 | 0.00057775
31 | 0.00020148 | 5.0495e-05
32 | 0.00022274 | 5.5824e-05
33 | 0.00024583 | 6.1611e-05
34 | 0.00020606 | 5.1644e-05
35 | 0.00057735 | 0.0001447
36 | 0.00016445 | 4.1216e-05
37 | 0.0002926 | 7.3333e-05
38 | 0.00076556 | 0.00019187
39 | 0.0011338 | 0.00028416
40 | 0.0013089 | 0.00032805
41 | 0.0003729 | 9.3458e-05
42 | 0.00023144 | 5.8004e-05
43 | 0.00026168 | 6.5584e-05
44 | 0.00050179 | 0.00012576
45 | 0.00018244 | 4.5723e-05
46 | 0.00022228 | 5.5709e-05
47 | 0.00054291 | 0.00013607
48 | 0.00052368 | 0.00013125
49 | 0.00022471 | 5.6319e-05
50 | 0.00029937 | 7.5029e-05
51 | 0.00030918 | 7.7489e-05
52 | 0.00057065 | 0.00014302
53 | 0.00056748 | 0.00014222
54 | 0.0003961 | 9.9271e-05
55 | 0.00097296 | 0.00024385
56 | 0.00029353 | 7.3566e-05
57 | 0.0011132 | 0.00027899
58 | 0.0005281 | 0.00013235
59 | 0.00090545 | 0.00022693
60 | 0.0010606 | 0.00026582
61 | 0.00055967 | 0.00014027
62 | 0.0022469 | 0.00056313
63 | 0.0011393 | 0.00028555
64 | 0.0014887 | 0.0003731
65 | 0.0012759 | 0.00031976
66 | 0.001393 | 0.00034913
67 | 0.00044411 | 0.0001113
68 | 0.00021386 | 5.3599e-05
69 | 0.00019823 | 4.968e-05
70 | 0.00038673 | 9.6923e-05
71 | 0.00018765 | 4.7031e-05
72 | 0.00022984 | 5.7604e-05
73 | 0.00035873 | 8.9905e-05
74 | 0.00057602 | 0.00014437
75 | 0.00022911 | 5.742e-05
76 | 0.00058653 | 0.000147
77 | 0.00055646 | 0.00013946
78 | 0.00019429 | 4.8692e-05
79 | 0.00021701 | 5.4389e-05
80 | 0.0003528 | 8.8419e-05
81 | 0.00027805 | 6.9687e-05
82 | 0.00027913 | 6.9956e-05
83 | 0.00022767 | 5.706e-05
84 | 0.00041495 | 0.000104
85 | 0.00021204 | 5.3142e-05
86 | 0.00018042 | 4.5217e-05
87 | 0.00032654 | 8.1839e-05
88 | 0.00045551 | 0.00011416

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1