## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1301-35_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1301-35_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1301-35_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1301-35_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1301-35_0_5_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1301-35_0_5_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_1301-35_0_5_node_58 | 0.4 | n |  | TRUE
7 | bus_LV_1301-35_0_5_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1301-35_0_5_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_1301-35_0_5_node_32 | 0.4 | n |  | TRUE
10 | bus_LV_1301-35_0_5_node_60 | 0.4 | n |  | TRUE
11 | bus_LV_1301-35_0_5_node_76 | 0.4 | n |  | TRUE
12 | bus_LV_1301-35_0_5_node_59 | 0.4 | n |  | TRUE
13 | bus_LV_1301-35_0_5_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_1301-35_0_5_node_38 | 0.4 | n |  | TRUE
15 | bus_LV_1301-35_0_5_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_1301-35_0_5_node_70 | 0.4 | n |  | TRUE
17 | bus_LV_1301-35_0_5_node_40 | 0.4 | n |  | TRUE
18 | bus_LV_1301-35_0_5_node_71 | 0.4 | n |  | TRUE
19 | bus_LV_1301-35_0_5_node_57 | 0.4 | n |  | TRUE
20 | bus_LV_1301-35_0_5_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1301-35_0_5_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_1301-35_0_5_node_39 | 0.4 | n |  | TRUE
23 | bus_LV_1301-35_0_5_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_1301-35_0_5_node_6 | 0.4 | n |  | TRUE
25 | bus_LV_1301-35_0_5_node_7 | 0.4 | n |  | TRUE
26 | bus_LV_1301-35_0_5_node_8 | 0.4 | n |  | TRUE
27 | bus_LV_1301-35_0_5_node_10 | 0.4 | n |  | TRUE
28 | bus_LV_1301-35_0_5_node_11 | 0.4 | n |  | TRUE
29 | bus_LV_1301-35_0_5_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_1301-35_0_5_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_1301-35_0_5_node_13 | 0.4 | n |  | TRUE
32 | bus_LV_1301-35_0_5_node_12 | 0.4 | n |  | TRUE
33 | bus_LV_1301-35_0_5_node_69 | 0.4 | n |  | TRUE
34 | bus_LV_1301-35_0_5_node_68 | 0.4 | n |  | TRUE
35 | bus_LV_1301-35_0_5_node_66 | 0.4 | n |  | TRUE
36 | bus_LV_1301-35_0_5_node_67 | 0.4 | n |  | TRUE
37 | bus_LV_1301-35_0_5_node_64 | 0.4 | n |  | TRUE
38 | bus_LV_1301-35_0_5_node_83 | 0.4 | n |  | TRUE
39 | bus_LV_1301-35_0_5_node_52 | 0.4 | n |  | TRUE
40 | bus_LV_1301-35_0_5_node_24 | 0.4 | n |  | TRUE
41 | bus_LV_1301-35_0_5_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_1301-35_0_5_node_20 | 0.4 | n |  | TRUE
43 | bus_LV_1301-35_0_5_node_21 | 0.4 | n |  | TRUE
44 | bus_LV_1301-35_0_5_node_22 | 0.4 | n |  | TRUE
45 | bus_LV_1301-35_0_5_node_25 | 0.4 | n |  | TRUE
46 | bus_LV_1301-35_0_5_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_1301-35_0_5_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_1301-35_0_5_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_1301-35_0_5_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_1301-35_0_5_node_54 | 0.4 | n |  | TRUE
51 | bus_LV_1301-35_0_5_node_56 | 0.4 | n |  | TRUE
52 | bus_LV_1301-35_0_5_node_85 | 0.4 | n |  | TRUE
53 | bus_LV_1301-35_0_5_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_1301-35_0_5_node_28 | 0.4 | n |  | TRUE
55 | bus_LV_1301-35_0_5_node_29 | 0.4 | n |  | TRUE
56 | bus_LV_1301-35_0_5_node_37 | 0.4 | n |  | TRUE
57 | bus_LV_1301-35_0_5_node_53 | 0.4 | n |  | TRUE
58 | bus_LV_1301-35_0_5_node_55 | 0.4 | n |  | TRUE
59 | bus_LV_1301-35_0_5_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_1301-35_0_5_node_41 | 0.4 | n |  | TRUE
61 | bus_LV_1301-35_0_5_node_42 | 0.4 | n |  | TRUE
62 | bus_LV_1301-35_0_5_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_1301-35_0_5_node_44 | 0.4 | n |  | TRUE
64 | bus_LV_1301-35_0_5_node_45 | 0.4 | n |  | TRUE
65 | bus_LV_1301-35_0_5_node_46 | 0.4 | n |  | TRUE
66 | bus_LV_1301-35_0_5_node_47 | 0.4 | n |  | TRUE
67 | bus_LV_1301-35_0_5_node_48 | 0.4 | n |  | TRUE
68 | bus_LV_1301-35_0_5_node_49 | 0.4 | n |  | TRUE
69 | bus_LV_1301-35_0_5_node_51 | 0.4 | n |  | TRUE
70 | bus_LV_1301-35_0_5_node_80 | 0.4 | n |  | TRUE
71 | bus_LV_1301-35_0_5_node_81 | 0.4 | n |  | TRUE
72 | bus_LV_1301-35_0_5_node_77 | 0.4 | n |  | TRUE
73 | bus_LV_1301-35_0_5_node_61 | 0.4 | n |  | TRUE
74 | bus_LV_1301-35_0_5_node_65 | 0.4 | n |  | TRUE
75 | bus_LV_1301-35_0_5_node_84 | 0.4 | n |  | TRUE
76 | bus_LV_1301-35_0_5_node_82 | 0.4 | n |  | TRUE
77 | bus_LV_1301-35_0_5_node_72 | 0.4 | n |  | TRUE
78 | bus_LV_1301-35_0_5_node_73 | 0.4 | n |  | TRUE
79 | bus_LV_1301-35_0_5_node_74 | 0.4 | n |  | TRUE
80 | bus_LV_1301-35_0_5_node_75 | 0.4 | n |  | TRUE
81 | bus_LV_1301-35_0_5_node_79 | 0.4 | n |  | TRUE
82 | bus_LV_1301-35_0_5_node_78 | 0.4 | n |  | TRUE
83 | bus_MV_17_0_node_152 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1301-35_0_5_load_0 | 0 | 0.010762 | 0.0026971 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1301-35_0_5_load_1 | 1 | 0.0082106 | 0.0020578 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1301-35_0_5_load_4 | 7 | 0.0041331 | 0.0010359 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1301-35_0_5_load_32 | 9 | 0.0059604 | 0.0014938 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1301-35_0_5_load_76 | 11 | 0.0010219 | 0.0002561 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1301-35_0_5_load_38 | 14 | 0.0047443 | 0.001189 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1301-35_0_5_load_70 | 16 | 0.0045743 | 0.0011464 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1301-35_0_5_load_71 | 18 | 0.01336 | 0.0033483 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1301-35_0_5_load_57 | 19 | 0.0078803 | 0.001975 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1301-35_0_5_load_14 | 20 | 0.013097 | 0.0032824 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1301-35_0_5_load_26 | 21 | 0.0063345 | 0.0015876 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1301-35_0_5_load_39 | 22 | 0.0046775 | 0.0011723 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1301-35_0_5_load_30 | 23 | 0.0038069 | 0.0009541 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1301-35_0_5_load_6 | 24 | 0.011004 | 0.0027577 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1301-35_0_5_load_7 | 25 | 0.0028775 | 0.00072116 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1301-35_0_5_load_11 | 28 | 0.013361 | 0.0033487 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1301-35_0_5_load_16 | 29 | 0.012723 | 0.0031886 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1301-35_0_5_load_13 | 31 | 0.01126 | 0.002822 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1301-35_0_5_load_68 | 34 | 0.014901 | 0.0037345 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1301-35_0_5_load_66 | 35 | 0.004004 | 0.0010035 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1301-35_0_5_load_67 | 36 | 0.0025991 | 0.0006514 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1301-35_0_5_load_64 | 37 | 0.00042472 | 0.00010644 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1301-35_0_5_load_83 | 38 | 0.0070595 | 0.0017693 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1301-35_0_5_load_52 | 39 | 0.0038501 | 0.00096493 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1301-35_0_5_load_24 | 40 | 0.01205 | 0.0030199 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1301-35_0_5_load_23 | 41 | 0.012266 | 0.0030741 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1301-35_0_5_load_20 | 42 | 0.093962 | 0.023549 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1301-35_0_5_load_21 | 43 | 0.067022 | 0.016797 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1301-35_0_5_load_22 | 44 | 0.017813 | 0.0044643 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1301-35_0_5_load_25 | 45 | 0.025971 | 0.0065088 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1301-35_0_5_load_35 | 47 | 0.0014564 | 0.000365 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1301-35_0_5_load_33 | 49 | 0.0088808 | 0.0022257 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1301-35_0_5_load_54 | 50 | 0.0013566 | 0.00034 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1301-35_0_5_load_85 | 52 | 0.0040513 | 0.0010154 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1301-35_0_5_load_28 | 54 | 0.0044946 | 0.0011265 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1301-35_0_5_load_29 | 55 | 0.004991 | 0.0012509 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1301-35_0_5_load_37 | 56 | 0.0067865 | 0.0017009 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1301-35_0_5_load_53 | 57 | 0.0011766 | 0.00029487 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1301-35_0_5_load_55 | 58 | 0.0050048 | 0.0012543 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1301-35_0_5_load_50 | 59 | 0.0019073 | 0.00047802 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1301-35_0_5_load_41 | 60 | 0.0014714 | 0.00036877 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1301-35_0_5_load_42 | 61 | 0.0024428 | 0.00061223 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1301-35_0_5_load_43 | 62 | 0.0023487 | 0.00058864 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1301-35_0_5_load_44 | 63 | 0.0014515 | 0.00036378 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1301-35_0_5_load_45 | 64 | 0.001386 | 0.00034736 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1301-35_0_5_load_46 | 65 | 0.0011369 | 0.00028494 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1301-35_0_5_load_47 | 66 | 0.0030149 | 0.0007556 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1301-35_0_5_load_48 | 67 | 0.0029736 | 0.00074525 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1301-35_0_5_load_51 | 69 | 0.0042084 | 0.0010547 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1301-35_0_5_load_80 | 70 | 0.0043632 | 0.0010935 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1301-35_0_5_load_81 | 71 | 0.0012999 | 0.00032579 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1301-35_0_5_load_77 | 72 | 0.00097465 | 0.00024427 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1301-35_0_5_load_61 | 73 | 0.00077895 | 0.00019522 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1301-35_0_5_load_84 | 75 | 0.00085008 | 0.00021305 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1301-35_0_5_load_82 | 76 | 0.0043498 | 0.0010902 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1301-35_0_5_load_72 | 77 | 0.0010444 | 0.00026176 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1301-35_0_5_load_73 | 78 | 0.00086331 | 0.00021637 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1301-35_0_5_load_74 | 79 | 0.00098752 | 0.0002475 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1301-35_0_5_load_75 | 80 | 0.0011183 | 0.00028026 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1301-35_0_5_load_78 | 82 | 0.0011009 | 0.0002759 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1301-35_0_5_line_0 |  | 0 | 1 | 0.020713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_1301-35_0_5_line_1 |  | 0 | 2 | 0.010778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_1301-35_0_5_line_2 |  | 1 | 3 | 0.018305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_1301-35_0_5_line_3 |  | 2 | 4 | 0.006671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1301-35_0_5_line_4 |  | 3 | 5 | 0.032172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1301-35_0_5_line_5 |  | 3 | 6 | 0.003756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1301-35_0_5_line_6 |  | 4 | 8 | 0.051245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1301-35_0_5_line_7 |  | 4 | 9 | 0.021863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1301-35_0_5_line_8 |  | 5 | 13 | 0.0264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1301-35_0_5_line_9 |  | 6 | 12 | 0.007904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1301-35_0_5_line_10 |  | 6 | 7 | 0.018387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1301-35_0_5_line_11 |  | 8 | 21 | 0.01057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1301-35_0_5_line_12 |  | 8 | 22 | 0.020303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1301-35_0_5_line_13 |  | 9 | 23 | 8.154e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1301-35_0_5_line_14 |  | 10 | 11 | 0.10486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1301-35_0_5_line_15 |  | 10 | 12 | 0.054389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1301-35_0_5_line_16 |  | 11 | 72 | 0.0095032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1301-35_0_5_line_17 |  | 12 | 14 | 0.025082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1301-35_0_5_line_18 |  | 13 | 20 | 0.019627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1301-35_0_5_line_19 |  | 13 | 15 | 0.037176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1301-35_0_5_line_20 |  | 15 | 16 | 0.018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1301-35_0_5_line_21 |  | 17 | 18 | 0.009339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1301-35_0_5_line_22 |  | 17 | 19 | 0.021852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1301-35_0_5_line_23 |  | 19 | 59 | 0.013662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1301-35_0_5_line_24 |  | 20 | 31 | 0.031593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1301-35_0_5_line_25 |  | 21 | 40 | 0.029073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1301-35_0_5_line_26 |  | 22 | 41 | 0.0012358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_1301-35_0_5_line_27 |  | 23 | 54 | 0.013654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1301-35_0_5_line_28 |  | 24 | 25 | 0.028648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1301-35_0_5_line_29 |  | 24 | 26 | 0.01273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1301-35_0_5_line_30 |  | 26 | 27 | 0.019414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1301-35_0_5_line_31 |  | 26 | 28 | 0.0082036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1301-35_0_5_line_32 |  | 27 | 29 | 0.020618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1301-35_0_5_line_33 |  | 27 | 30 | 0.030761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1301-35_0_5_line_34 |  | 27 | 31 | 0.014237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1301-35_0_5_line_35 |  | 28 | 32 | 0.028853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1301-35_0_5_line_36 |  | 30 | 33 | 0.044578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1301-35_0_5_line_37 |  | 30 | 34 | 0.0091077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1301-35_0_5_line_38 |  | 32 | 35 | 0.083588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1301-35_0_5_line_39 |  | 33 | 38 | 0.017769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1301-35_0_5_line_40 |  | 33 | 39 | 0.030095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1301-35_0_5_line_41 |  | 35 | 36 | 0.0013677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1301-35_0_5_line_42 |  | 35 | 37 | 0.034013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1301-35_0_5_line_43 |  | 37 | 74 | 0.055724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1301-35_0_5_line_44 |  | 38 | 75 | 0.024958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1301-35_0_5_line_45 |  | 39 | 68 | 0.019003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1301-35_0_5_line_46 |  | 40 | 45 | 0.013052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1301-35_0_5_line_47 |  | 41 | 44 | 0.0022699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_1301-35_0_5_line_48 |  | 42 | 43 | 0.00022919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1301-35_0_5_line_49 |  | 42 | 44 | 0.023122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_1301-35_0_5_line_50 |  | 45 | 46 | 0.011764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1301-35_0_5_line_51 |  | 46 | 47 | 0.03266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1301-35_0_5_line_52 |  | 46 | 48 | 0.012377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1301-35_0_5_line_53 |  | 46 | 49 | 0.014518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1301-35_0_5_line_54 |  | 47 | 50 | 0.021251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1301-35_0_5_line_55 |  | 48 | 51 | 0.024586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1301-35_0_5_line_56 |  | 48 | 52 | 0.005162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1301-35_0_5_line_57 |  | 49 | 53 | 0.016701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1301-35_0_5_line_58 |  | 50 | 57 | 0.00068067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1301-35_0_5_line_59 |  | 51 | 58 | 0.038085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1301-35_0_5_line_60 |  | 53 | 56 | 0.0017923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1301-35_0_5_line_61 |  | 54 | 55 | 0.016387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1301-35_0_5_line_62 |  | 57 | 64 | 0.017673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1301-35_0_5_line_63 |  | 59 | 67 | 0.021551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1301-35_0_5_line_64 |  | 60 | 61 | 0.001498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1301-35_0_5_line_65 |  | 60 | 62 | 0.018871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1301-35_0_5_line_66 |  | 61 | 63 | 0.017448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1301-35_0_5_line_67 |  | 62 | 64 | 0.0039601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1301-35_0_5_line_68 |  | 63 | 65 | 0.00011275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1301-35_0_5_line_69 |  | 66 | 67 | 0.02877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1301-35_0_5_line_70 |  | 66 | 68 | 0.024877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1301-35_0_5_line_71 |  | 68 | 69 | 0.013583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1301-35_0_5_line_72 |  | 69 | 70 | 0.035103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1301-35_0_5_line_73 |  | 70 | 71 | 0.013953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1301-35_0_5_line_74 |  | 71 | 76 | 0.019847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1301-35_0_5_line_75 |  | 72 | 82 | 0.01031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1301-35_0_5_line_76 |  | 73 | 74 | 0.032789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1301-35_0_5_line_77 |  | 77 | 78 | 0.017575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1301-35_0_5_line_78 |  | 77 | 79 | 0.0089847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1301-35_0_5_line_79 |  | 78 | 80 | 0.0052301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1301-35_0_5_line_80 |  | 80 | 81 | 0.0182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1301-35_0_5_line_81 |  | 81 | 82 | 0.026162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1301-35_0_5_trafo_19 | 0.63 MVA 20/0.4 kV | 83 | 8 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2698899.867 | 1220546.2 | 2698904.017 | 1220543.0128 | 2698916.5733 | 1220533.9595
1 | 2698897.2267 | 1220553.4297 | 2698894.5932 | 1220550.2504 | 2698899.867 | 1220546.2
2 | 2698931.6805 | 1220523.6251 | 2698918.9402 | 1220532.2529 | 2698916.5733 | 1220533.9595
3 | 2698897.2267 | 1220553.4297 | 2698891.8341 | 1220557.3763
4 | 2698931.6805 | 1220523.6251 | 2698928.0942 | 1220518.8732 | 2698914.4205 | 1220505.1253 | 2698908.2719 | 1220502.0432
5 | 2698931.6805 | 1220523.6251 | 2698933.9528 | 1220526.6205
6 | 2698851.2846 | 1220588.7033 | 2698867.8864 | 1220575.5583 | 2698887.4631 | 1220560.5726 | 2698891.8341 | 1220557.3763
7 | 2698891.8341 | 1220557.3763 | 2698905.9715 | 1220574.0528
8 | 2698908.2719 | 1220502.0432 | 2698903.1489 | 1220505.7386 | 2698889.1987 | 1220515.9364 | 2698887.664 | 1220518.3349
9 | 2698933.9528 | 1220526.6205 | 2698940.3516 | 1220521.9568
10 | 2698933.9528 | 1220526.6205 | 2698919.0885 | 1220537.4428
11 | 2698851.2846 | 1220588.7033 | 2698847.6638 | 1220591.5118 | 2698842.9455 | 1220595.1985
12 | 2698851.2846 | 1220588.7033 | 2698864.5773 | 1220604.0494
13 | 2698906.0242 | 1220574.115 | 2698905.9715 | 1220574.0528
14 | 2698982.237 | 1220516.6711 | 2698983.1647 | 1220522.4906 | 2699000.9862 | 1220619.8351
15 | 2698940.3516 | 1220521.9568 | 2698949.2007 | 1220515.5103 | 2698965.2358 | 1220506.3479 | 2698968.2955 | 1220510.8242 | 2698973.2131 | 1220509.4382 | 2698975.0433 | 1220511.181 | 2698976.8372 | 1220517.393 | 2698982.237 | 1220516.6711
16 | 2699000.9862 | 1220619.8351 | 2699002.6976 | 1220629.1829
17 | 2698940.3516 | 1220521.9568 | 2698946.1779 | 1220534.8405 | 2698947.9804 | 1220545.6327
18 | 2698887.664 | 1220518.3349 | 2698882.1454 | 1220511.5829 | 2698876.2968 | 1220504.1472 | 2698875.2795 | 1220503.1187
19 | 2698887.664 | 1220518.3349 | 2698886.5964 | 1220520.0183 | 2698884.563 | 1220525.0215 | 2698875.1252 | 1220533.1039 | 2698865.4024 | 1220541.4484 | 2698862.2776 | 1220538.1498
20 | 2698862.2776 | 1220538.1498 | 2698875.7526 | 1220526.2159
21 | 2698824.5997 | 1220573.4052 | 2698831.3844 | 1220566.9687
22 | 2698831.3844 | 1220566.9687 | 2698819.8989 | 1220561.2741 | 2698812.3515 | 1220556.3123
23 | 2698800.9358 | 1220548.8074 | 2698812.3515 | 1220556.3123
24 | 2698853.8193 | 1220480.6678 | 2698857.2177 | 1220483.6716 | 2698858.8695 | 1220487.9353 | 2698863.4932 | 1220493.2825 | 2698870.0799 | 1220497.8618 | 2698875.2795 | 1220503.1187
25 | 2698842.9455 | 1220595.1985 | 2698820.0365 | 1220613.0984
26 | 2698864.5773 | 1220604.0494 | 2698865.3863 | 1220604.9835
27 | 2698906.0242 | 1220574.115 | 2698914.8538 | 1220584.5304
28 | 2698857.3281 | 1220464.9043 | 2698857.8576 | 1220465.7028 | 2698860.1998 | 1220469.978 | 2698862.3238 | 1220473.6825 | 2698864.5902 | 1220475.666 | 2698870.7947 | 1220478.1263 | 2698876.999 | 1220484.4497
29 | 2698849.7691 | 1220454.6829 | 2698853.7118 | 1220459.4517 | 2698857.3281 | 1220464.9043
30 | 2698849.7691 | 1220454.6829 | 2698845.0746 | 1220460.4536 | 2698843.3865 | 1220465.2289 | 2698842.4682 | 1220472.0852
31 | 2698849.7691 | 1220454.6829 | 2698855.4333 | 1220448.7486
32 | 2698842.4682 | 1220472.0852 | 2698839.8017 | 1220466.7817 | 2698837.5235 | 1220462.7632 | 2698834.7401 | 1220460.382 | 2698832.1551 | 1220460.2168 | 2698830.3386 | 1220463.5891
33 | 2698842.4682 | 1220472.0852 | 2698831.0444 | 1220482.3252 | 2698826.5263 | 1220486.1529 | 2698819.2451 | 1220492.3254
34 | 2698842.4682 | 1220472.0852 | 2698852.4612 | 1220479.4674 | 2698853.8193 | 1220480.6678
35 | 2698870.483 | 1220424.7054 | 2698866.0448 | 1220436.5179 | 2698863.2148 | 1220440.5961 | 2698855.4333 | 1220448.7486
36 | 2698819.2451 | 1220492.3254 | 2698793.1614 | 1220466.8302 | 2698785.9635 | 1220462.9525
37 | 2698819.2451 | 1220492.3254 | 2698825.4695 | 1220498.9743
38 | 2698870.483 | 1220424.7054 | 2698813.629 | 1220363.4314
39 | 2698785.9635 | 1220462.9525 | 2698773.4816 | 1220450.3057
40 | 2698785.9635 | 1220462.9525 | 2698765.7448 | 1220477.75 | 2698762.2014 | 1220481.3344
41 | 2698813.629 | 1220363.4314 | 2698814.5806 | 1220362.449
42 | 2698813.629 | 1220363.4314 | 2698779.6487 | 1220361.9313
43 | 2698736.3762 | 1220326.8227 | 2698779.6487 | 1220361.9313
44 | 2698753.6797 | 1220443.8593 | 2698759.0424 | 1220439.8898 | 2698765.1115 | 1220441.8251 | 2698773.4816 | 1220450.3057
45 | 2698748.8422 | 1220494.8486 | 2698762.2014 | 1220481.3344
46 | 2698809.7517 | 1220621.1345 | 2698820.0365 | 1220613.0984
47 | 2698866.8725 | 1220606.6992 | 2698865.3863 | 1220604.9835
48 | 2698880.8897 | 1220625.356 | 2698880.7555 | 1220625.1702
49 | 2698866.8725 | 1220606.6992 | 2698870.1147 | 1220610.4423 | 2698880.7555 | 1220625.1702
50 | 2698800.4818 | 1220628.3775 | 2698809.7517 | 1220621.1345
51 | 2698800.4818 | 1220628.3775 | 2698797.7758 | 1220626.3645 | 2698793.9303 | 1220623.5098 | 2698778.05 | 1220604.8552
52 | 2698790.7029 | 1220635.9985 | 2698800.4818 | 1220628.3775
53 | 2698800.4818 | 1220628.3775 | 2698806.7646 | 1220641.4653
54 | 2698778.05 | 1220604.8552 | 2698765.6457 | 1220590.2838 | 2698764.3023 | 1220588.6505
55 | 2698771.2907 | 1220651.154 | 2698790.7029 | 1220635.9985
56 | 2698787.6302 | 1220631.8446 | 2698790.7029 | 1220635.9985
57 | 2698813.9923 | 1220656.5216 | 2698806.7646 | 1220641.4653
58 | 2698763.8699 | 1220588.1248 | 2698764.3023 | 1220588.6505
59 | 2698771.2907 | 1220651.154 | 2698760.4739 | 1220639.0105 | 2698761.0884 | 1220631.2485 | 2698760.9382 | 1220625.6642 | 2698754.9182 | 1220619.7347
60 | 2698813.9923 | 1220656.5216 | 2698814.9844 | 1220658.0143
61 | 2698925.4502 | 1220597.03 | 2698914.8538 | 1220584.5304
62 | 2698752.6429 | 1220574.4756 | 2698763.8699 | 1220588.1248
63 | 2698800.9358 | 1220548.8074 | 2698796.6136 | 1220545.9659 | 2698786.1622 | 1220536.4858 | 2698784.6448 | 1220534.8004
64 | 2698738.1393 | 1220556.8426 | 2698737.1876 | 1220555.6857
65 | 2698738.1393 | 1220556.8426 | 2698750.1273 | 1220571.4172
66 | 2698726.104 | 1220542.2107 | 2698737.1876 | 1220555.6857
67 | 2698752.6429 | 1220574.4756 | 2698750.1273 | 1220571.4172
68 | 2698726.0324 | 1220542.1236 | 2698726.104 | 1220542.2107
69 | 2698765.3941 | 1220513.4193 | 2698784.6448 | 1220534.8004
70 | 2698748.8422 | 1220494.8486 | 2698757.5943 | 1220504.7563 | 2698765.3941 | 1220513.4193
71 | 2698748.8422 | 1220494.8486 | 2698739.9632 | 1220484.57
72 | 2698716.4109 | 1220458.5594 | 2698726.498 | 1220468.9821 | 2698739.9632 | 1220484.57
73 | 2698716.4109 | 1220458.5594 | 2698706.7076 | 1220448.5332
74 | 2698706.7076 | 1220448.5332 | 2698692.9049 | 1220434.2711
75 | 2699004.5202 | 1220639.3304 | 2699003.7282 | 1220634.8122 | 2699002.6976 | 1220629.1829
76 | 2698769.0494 | 1220329.5772 | 2698736.3762 | 1220326.8227
77 | 2699016.0524 | 1220705.5003 | 2699013.0466 | 1220688.1839
78 | 2699016.0524 | 1220705.5003 | 2699017.589 | 1220714.3526
79 | 2699012.1521 | 1220683.0309 | 2699013.0466 | 1220688.1839
80 | 2699009.0371 | 1220665.0998 | 2699009.3628 | 1220666.9621 | 2699012.1521 | 1220683.0309
81 | 2699009.0371 | 1220665.0998 | 2699004.5202 | 1220639.3304

## bus_geodata
| x | y | coords
0 | 2698899.867 | 1220546.2
1 | 2698916.5733 | 1220533.9595
2 | 2698897.2267 | 1220553.4297
3 | 2698931.6805 | 1220523.6251
4 | 2698891.8341 | 1220557.3763
5 | 2698908.2719 | 1220502.0432
6 | 2698933.9528 | 1220526.6205
7 | 2698919.0885 | 1220537.4428
8 | 2698851.2846 | 1220588.7033
9 | 2698905.9715 | 1220574.0528
10 | 2698982.237 | 1220516.6711
11 | 2699000.9862 | 1220619.8351
12 | 2698940.3516 | 1220521.9568
13 | 2698887.664 | 1220518.3349
14 | 2698947.9804 | 1220545.6327
15 | 2698862.2776 | 1220538.1498
16 | 2698875.7526 | 1220526.2159
17 | 2698831.3844 | 1220566.9687
18 | 2698824.5997 | 1220573.4052
19 | 2698812.3515 | 1220556.3123
20 | 2698875.2795 | 1220503.1187
21 | 2698842.9455 | 1220595.1985
22 | 2698864.5773 | 1220604.0494
23 | 2698906.0242 | 1220574.115
24 | 2698857.3281 | 1220464.9043
25 | 2698876.999 | 1220484.4497
26 | 2698849.7691 | 1220454.6829
27 | 2698842.4682 | 1220472.0852
28 | 2698855.4333 | 1220448.7486
29 | 2698830.3386 | 1220463.5891
30 | 2698819.2451 | 1220492.3254
31 | 2698853.8193 | 1220480.6678
32 | 2698870.483 | 1220424.7054
33 | 2698785.9635 | 1220462.9525
34 | 2698825.4695 | 1220498.9743
35 | 2698813.629 | 1220363.4314
36 | 2698814.5806 | 1220362.449
37 | 2698779.6487 | 1220361.9313
38 | 2698773.4816 | 1220450.3057
39 | 2698762.2014 | 1220481.3344
40 | 2698820.0365 | 1220613.0984
41 | 2698865.3863 | 1220604.9835
42 | 2698880.7555 | 1220625.1702
43 | 2698880.8897 | 1220625.356
44 | 2698866.8725 | 1220606.6992
45 | 2698809.7517 | 1220621.1345
46 | 2698800.4818 | 1220628.3775
47 | 2698778.05 | 1220604.8552
48 | 2698790.7029 | 1220635.9985
49 | 2698806.7646 | 1220641.4653
50 | 2698764.3023 | 1220588.6505
51 | 2698771.2907 | 1220651.154
52 | 2698787.6302 | 1220631.8446
53 | 2698813.9923 | 1220656.5216
54 | 2698914.8538 | 1220584.5304
55 | 2698925.4502 | 1220597.03
56 | 2698814.9844 | 1220658.0143
57 | 2698763.8699 | 1220588.1248
58 | 2698754.9182 | 1220619.7347
59 | 2698800.9358 | 1220548.8074
60 | 2698738.1393 | 1220556.8426
61 | 2698737.1876 | 1220555.6857
62 | 2698750.1273 | 1220571.4172
63 | 2698726.104 | 1220542.2107
64 | 2698752.6429 | 1220574.4756
65 | 2698726.0324 | 1220542.1236
66 | 2698765.3941 | 1220513.4193
67 | 2698784.6448 | 1220534.8004
68 | 2698748.8422 | 1220494.8486
69 | 2698739.9632 | 1220484.57
70 | 2698716.4109 | 1220458.5594
71 | 2698706.7076 | 1220448.5332
72 | 2699002.6976 | 1220629.1829
73 | 2698769.0494 | 1220329.5772
74 | 2698736.3762 | 1220326.8227
75 | 2698753.6797 | 1220443.8593
76 | 2698692.9049 | 1220434.2711
77 | 2699016.0524 | 1220705.5003
78 | 2699013.0466 | 1220688.1839
79 | 2699017.589 | 1220714.3526
80 | 2699012.1521 | 1220683.0309
81 | 2699009.0371 | 1220665.0998
82 | 2699004.5202 | 1220639.3304
83 | 2698867.8864 | 1220575.5583

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99377 | -0.11812 | 0.010762 | 0.0026971
1 | 0.99213 | -0.14942 | 0.0082106 | 0.0020578
2 | 0.99468 | -0.10086 | 0 | 0
3 | 0.99075 | -0.17584 | 0 | 0
4 | 0.99524 | -0.090185 | 0 | 0
5 | 0.98856 | -0.21785 | 0 | 0
6 | 0.99069 | -0.1769 | 0 | 0
7 | 0.99062 | -0.17825 | 0.0041331 | 0.0010359
8 | 1 | 0 | -0.48596 | -0.12304
9 | 0.99485 | -0.097595 | 0.0059604 | 0.0014938
10 | 0.99025 | -0.18545 | 0 | 0
11 | 0.98957 | -0.19872 | 0.0010219 | 0.0002561
12 | 0.99061 | -0.17857 | 0 | 0
13 | 0.98676 | -0.25246 | 0 | 0
14 | 0.9905 | -0.18068 | 0.0047443 | 0.001189
15 | 0.9866 | -0.2555 | 0 | 0
16 | 0.98653 | -0.25698 | 0.0045743 | 0.0011464
17 | 0.97134 | -0.55367 | 0 | 0
18 | 0.97123 | -0.55597 | 0.01336 | 0.0033483
19 | 0.97161 | -0.54827 | 0.0078803 | 0.001975
20 | 0.98546 | -0.27746 | 0.013097 | 0.0032824
21 | 0.9992 | -0.015362 | 0.0063345 | 0.0015876
22 | 0.99819 | -0.034696 | 0.0046775 | 0.0011723
23 | 0.99485 | -0.097614 | 0.0038069 | 0.0009541
24 | 0.97932 | -0.39688 | 0.011004 | 0.0027577
25 | 0.97925 | -0.39838 | 0.0028775 | 0.00072116
26 | 0.97949 | -0.39367 | 0 | 0
27 | 0.98012 | -0.38132 | 0 | 0
28 | 0.97933 | -0.39683 | 0.013361 | 0.0033487
29 | 0.97988 | -0.38608 | 0.012723 | 0.0031886
30 | 0.97811 | -0.42048 | 0 | 0
31 | 0.98168 | -0.35093 | 0.01126 | 0.002822
32 | 0.97912 | -0.40093 | 0 | 0
33 | 0.97582 | -0.46536 | 0 | 0
34 | 0.97799 | -0.42295 | 0.014901 | 0.0037345
35 | 0.97851 | -0.41281 | 0.004004 | 0.0010035
36 | 0.97851 | -0.41287 | 0.0025991 | 0.0006514
37 | 0.97848 | -0.41355 | 0.00042472 | 0.00010644
38 | 0.97569 | -0.46793 | 0.0070595 | 0.0017693
39 | 0.9745 | -0.4914 | 0.0038501 | 0.00096493
40 | 0.99716 | -0.054511 | 0.01205 | 0.0030199
41 | 0.99808 | -0.036761 | 0.012266 | 0.0030741
42 | 0.99621 | -0.072943 | 0.093962 | 0.023549
43 | 0.99619 | -0.073212 | 0.067022 | 0.016797
44 | 0.9979 | -0.040312 | 0.017813 | 0.0044643
45 | 0.99639 | -0.069378 | 0.025971 | 0.0065088
46 | 0.99597 | -0.077427 | 0 | 0
47 | 0.99555 | -0.085596 | 0.0014564 | 0.000365
48 | 0.99587 | -0.079397 | 0 | 0
49 | 0.99577 | -0.081424 | 0.0088808 | 0.0022257
50 | 0.9953 | -0.090371 | 0.0013566 | 0.00034
51 | 0.99576 | -0.081561 | 0 | 0
52 | 0.99585 | -0.079765 | 0.0040513 | 0.0010154
53 | 0.99566 | -0.083417 | 0 | 0
54 | 0.99473 | -0.099895 | 0.0044946 | 0.0011265
55 | 0.99466 | -0.10134 | 0.004991 | 0.0012509
56 | 0.99565 | -0.083631 | 0.0067865 | 0.0017009
57 | 0.99529 | -0.090508 | 0.0011766 | 0.00029487
58 | 0.99558 | -0.084912 | 0.0050048 | 0.0012543
59 | 0.97188 | -0.54292 | 0.0019073 | 0.00047802
60 | 0.99499 | -0.09647 | 0.0014714 | 0.00036877
61 | 0.99498 | -0.096602 | 0.0024428 | 0.00061223
62 | 0.9951 | -0.094309 | 0.0023487 | 0.00058864
63 | 0.99494 | -0.097398 | 0.0014515 | 0.00036378
64 | 0.99513 | -0.093692 | 0.001386 | 0.00034736
65 | 0.99494 | -0.0974 | 0.0011369 | 0.00028494
66 | 0.97305 | -0.51987 | 0.0030149 | 0.0007556
67 | 0.97235 | -0.53372 | 0.0029736 | 0.00074525
68 | 0.97373 | -0.50654 | 0 | 0
69 | 0.97355 | -0.51009 | 0.0042084 | 0.0010547
70 | 0.97322 | -0.51656 | 0.0043632 | 0.0010935
71 | 0.97315 | -0.51801 | 0.0012999 | 0.00032579
72 | 0.98952 | -0.19975 | 0.00097465 | 0.00024427
73 | 0.97841 | -0.41481 | 0.00077895 | 0.00019522
74 | 0.97844 | -0.41435 | 0 | 0
75 | 0.97567 | -0.46832 | 0.00085008 | 0.00021305
76 | 0.97307 | -0.5196 | 0.0043498 | 0.0010902
77 | 0.98926 | -0.20477 | 0.0010444 | 0.00026176
78 | 0.98929 | -0.20413 | 0.00086331 | 0.00021637
79 | 0.98925 | -0.20492 | 0.00098752 | 0.0002475
80 | 0.98931 | -0.20386 | 0.0011183 | 0.00028026
81 | 0.98937 | -0.20256 | 0 | 0
82 | 0.98947 | -0.20069 | 0.0011009 | 0.0002759
83 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.17319 | 0.044275 | -0.17293 | -0.044108 | 0.00026181 | 0.00016702 | 0.25964 | 0.25964 | 0.25964 | 0.99377 | -0.11812 | 0.99213 | -0.14942 | 35.6651
1 | -0.18396 | -0.046972 | 0.18411 | 0.047071 | 0.00015367 | 9.8069e-05 | 0.27576 | 0.27576 | 0.27576 | 0.99377 | -0.11812 | 0.99468 | -0.10086 | 37.8785
2 | 0.16472 | 0.042051 | -0.16451 | -0.041917 | 0.00020995 | 0.00013389 | 0.24733 | 0.24733 | 0.24733 | 0.99213 | -0.14942 | 0.99075 | -0.17584 | 33.9736
3 | -0.18411 | -0.047071 | 0.1842 | 0.047131 | 9.5113e-05 | 6.0699e-05 | 0.27576 | 0.27576 | 0.27576 | 0.99468 | -0.10086 | 0.99524 | -0.090185 | 37.8785
4 | 0.14851 | 0.037907 | -0.14821 | -0.037715 | 0.00030078 | 0.00019167 | 0.2233 | 0.2233 | 0.2233 | 0.99075 | -0.17584 | 0.98856 | -0.21785 | 30.673
5 | 0.015999 | 0.0040098 | -0.015998 | -0.0040093 | 8.1325e-07 | 4.7212e-07 | 0.024029 | 0.024029 | 0.024029 | 0.99075 | -0.17584 | 0.99069 | -0.1769 | 6.6014
6 | -0.20347 | -0.051961 | 0.20436 | 0.05253 | 0.0008912 | 0.00056903 | 0.30455 | 0.30455 | 0.30455 | 0.99524 | -0.090185 | 1 | 0 | 41.8343
7 | 0.019261 | 0.0048298 | -0.019254 | -0.0048257 | 6.7996e-06 | 4.0678e-06 | 0.028799 | 0.028799 | 0.028799 | 0.99524 | -0.090185 | 0.99485 | -0.097595 | 7.9118
8 | 0.14821 | 0.037715 | -0.14797 | -0.037558 | 0.00024682 | 0.00015729 | 0.2233 | 0.2233 | 0.2233 | 0.98856 | -0.21785 | 0.98676 | -0.25246 | 30.673
9 | 0.011865 | 0.0029735 | -0.011864 | -0.002973 | 9.4129e-07 | 5.0066e-07 | 0.017821 | 0.017821 | 0.017821 | 0.99069 | -0.1769 | 0.99061 | -0.17857 | 4.8958
10 | 0.0041334 | 0.0010358 | -0.0041331 | -0.0010359 | 2.6576e-07 | -6.6649e-08 | 0.0062083 | 0.0062084 | 0.0062084 | 0.99069 | -0.1769 | 0.99062 | -0.17825 | 1.7056
11 | 0.083589 | 0.021056 | -0.083527 | -0.021017 | 6.136e-05 | 3.9132e-05 | 0.12442 | 0.12442 | 0.12442 | 1 | 0 | 0.9992 | -0.015362 | 34.181
12 | 0.19637 | 0.049456 | -0.19604 | -0.049249 | 0.00032521 | 0.0002076 | 0.29228 | 0.29228 | 0.29228 | 1 | 0 | 0.99819 | -0.034696 | 40.1486
13 | 0.013294 | 0.0033319 | -0.013294 | -0.0033319 | 1.2088e-08 | 6.6786e-09 | 0.019884 | 0.019884 | 0.019884 | 0.99485 | -0.097595 | 0.99485 | -0.097614 | 5.4626
14 | 0.0071166 | 0.0017832 | -0.0071121 | -0.0017817 | 4.4968e-06 | 1.5299e-06 | 0.010694 | 0.010694 | 0.010694 | 0.99025 | -0.18545 | 0.98957 | -0.19872 | 2.938
15 | -0.0071166 | -0.0017832 | 0.0071189 | 0.001784 | 2.3323e-06 | 7.9274e-07 | 0.010694 | 0.010694 | 0.010694 | 0.99025 | -0.18545 | 0.99061 | -0.17857 | 2.9378
16 | 0.0060903 | 0.0015256 | -0.00609 | -0.0015255 | 2.9886e-07 | 6.9191e-08 | 0.0091577 | 0.0091577 | 0.0091577 | 0.98957 | -0.19872 | 0.98952 | -0.19975 | 2.5159
17 | 0.0047447 | 0.001189 | -0.0047443 | -0.001189 | 4.7777e-07 | -1.7088e-08 | 0.0071271 | 0.0071273 | 0.0071273 | 0.99061 | -0.17857 | 0.9905 | -0.18068 | 1.958
18 | 0.14339 | 0.036411 | -0.14322 | -0.036302 | 0.00017234 | 0.00010979 | 0.2164 | 0.2164 | 0.2164 | 0.98676 | -0.25246 | 0.98546 | -0.27746 | 29.7253
19 | 0.0045753 | 0.0011464 | -0.0045747 | -0.0011464 | 6.6363e-07 | -5.0092e-08 | 0.0068994 | 0.0068996 | 0.0068996 | 0.98676 | -0.25246 | 0.9866 | -0.2555 | 1.8955
20 | 0.0045747 | 0.0011464 | -0.0045743 | -0.0011464 | 3.2133e-07 | -2.4192e-08 | 0.0068996 | 0.0068997 | 0.0068997 | 0.9866 | -0.2555 | 0.98653 | -0.25698 | 1.8955
21 | 0.013361 | 0.0033492 | -0.01336 | -0.0033483 | 1.4673e-06 | 8.2349e-07 | 0.020469 | 0.020469 | 0.020469 | 0.97134 | -0.55367 | 0.97123 | -0.55597 | 5.6233
22 | -0.013361 | -0.0033492 | 0.013365 | 0.0033511 | 3.4333e-06 | 1.9267e-06 | 0.020469 | 0.020469 | 0.020469 | 0.97134 | -0.55367 | 0.97161 | -0.54827 | 5.6233
23 | -0.021245 | -0.0053261 | 0.021251 | 0.0053294 | 5.4237e-06 | 3.3019e-06 | 0.032537 | 0.032537 | 0.032537 | 0.97161 | -0.54827 | 0.97188 | -0.54292 | 8.9388
24 | 0.13012 | 0.033019 | -0.12966 | -0.032727 | 0.00045804 | 0.00029274 | 0.19662 | 0.19662 | 0.19662 | 0.98546 | -0.27746 | 0.98168 | -0.35093 | 54.0177
25 | 0.077193 | 0.019429 | -0.077049 | -0.019337 | 0.00014415 | 9.1874e-05 | 0.11499 | 0.11499 | 0.11499 | 0.9992 | -0.015362 | 0.99716 | -0.054511 | 31.5894
26 | 0.19136 | 0.048077 | -0.19134 | -0.048065 | 1.8861e-05 | 1.2039e-05 | 0.28531 | 0.28531 | 0.28531 | 0.99819 | -0.034696 | 0.99808 | -0.036761 | 39.1908
27 | 0.009487 | 0.0023778 | -0.0094859 | -0.0023773 | 1.031e-06 | 4.8256e-07 | 0.01419 | 0.01419 | 0.01419 | 0.99485 | -0.097614 | 0.99473 | -0.099895 | 3.8983
28 | 0.0028777 | 0.00072094 | -0.0028775 | -0.00072116 | 2.0539e-07 | -2.2899e-07 | 0.0043723 | 0.0043725 | 0.0043725 | 0.97932 | -0.39688 | 0.97925 | -0.39838 | 1.2012
29 | -0.013881 | -0.0034787 | 0.013883 | 0.0034799 | 2.1237e-06 | 1.1989e-06 | 0.021091 | 0.021091 | 0.021091 | 0.97932 | -0.39688 | 0.97949 | -0.39367 | 5.7943
30 | -0.035061 | -0.008788 | 0.035081 | 0.0088009 | 2.0654e-05 | 1.2974e-05 | 0.053264 | 0.053264 | 0.053264 | 0.97949 | -0.39367 | 0.98012 | -0.38132 | 14.6329
31 | 0.021178 | 0.0053081 | -0.021174 | -0.0053062 | 3.1843e-06 | 1.9347e-06 | 0.032173 | 0.032173 | 0.032173 | 0.97949 | -0.39367 | 0.97933 | -0.39683 | 8.8386
32 | 0.012726 | 0.0031902 | -0.012723 | -0.0031886 | 2.8861e-06 | 1.5873e-06 | 0.01932 | 0.01932 | 0.01932 | 0.98012 | -0.38132 | 0.97988 | -0.38608 | 5.3078
33 | 0.070424 | 0.017803 | -0.070292 | -0.017719 | 0.000132 | 8.4095e-05 | 0.10697 | 0.10697 | 0.10697 | 0.98012 | -0.38132 | 0.97811 | -0.42048 | 29.3883
34 | -0.11823 | -0.029795 | 0.1184 | 0.029905 | 0.00017212 | 0.00010998 | 0.17956 | 0.17956 | 0.17956 | 0.98012 | -0.38132 | 0.98168 | -0.35093 | 49.3289
35 | 0.0078129 | 0.0019575 | -0.0078114 | -0.0019569 | 1.5247e-06 | 6.1286e-07 | 0.011871 | 0.011871 | 0.011871 | 0.97933 | -0.39683 | 0.97912 | -0.40093 | 3.2613
36 | 0.05539 | 0.013984 | -0.055271 | -0.013908 | 0.0001188 | 7.5476e-05 | 0.084302 | 0.084302 | 0.084302 | 0.97811 | -0.42048 | 0.97582 | -0.46536 | 23.1599
37 | 0.014902 | 0.0037355 | -0.014901 | -0.0037345 | 1.7555e-06 | 1.0092e-06 | 0.022672 | 0.022672 | 0.022672 | 0.97811 | -0.42048 | 0.97799 | -0.42295 | 6.2285
38 | 0.0078114 | 0.0019569 | -0.0078069 | -0.0019551 | 4.4174e-06 | 1.7765e-06 | 0.011871 | 0.011871 | 0.011871 | 0.97912 | -0.40093 | 0.97851 | -0.41281 | 3.2614
39 | 0.0079106 | 0.0019824 | -0.0079096 | -0.001982 | 9.6958e-07 | 3.9858e-07 | 0.012063 | 0.012063 | 0.012063 | 0.97582 | -0.46536 | 0.97569 | -0.46793 | 3.3139
40 | 0.04736 | 0.011926 | -0.047301 | -0.011889 | 5.8895e-05 | 3.7317e-05 | 0.072239 | 0.07224 | 0.07224 | 0.97582 | -0.46536 | 0.9745 | -0.4914 | 19.846
41 | 0.0025991 | 0.00065139 | -0.0025991 | -0.0006514 | 8.0127e-09 | -1.2053e-08 | 0.0039525 | 0.0039525 | 0.0039525 | 0.97851 | -0.41281 | 0.97851 | -0.41287 | 1.0858
42 | 0.0012038 | 0.00030018 | -0.0012037 | -0.00030058 | 4.2719e-08 | -3.9991e-07 | 0.00183 | 0.0018301 | 0.0018301 | 0.97851 | -0.41281 | 0.97848 | -0.41355 | 0.50279
43 | 0.00077899 | 0.00019414 | -0.00077896 | -0.00019482 | 2.9313e-08 | -6.8113e-07 | 0.0011843 | 0.0011845 | 0.0011845 | 0.97848 | -0.41355 | 0.97844 | -0.41435 | 0.32541
44 | 0.0008501 | 0.00021275 | -0.00085008 | -0.00021305 | 1.573e-08 | -3.0163e-07 | 0.0012964 | 0.0012965 | 0.0012965 | 0.97569 | -0.46793 | 0.97567 | -0.46832 | 0.35617
45 | 0.043451 | 0.010924 | -0.04342 | -0.010904 | 3.1381e-05 | 1.9847e-05 | 0.066361 | 0.066361 | 0.066361 | 0.9745 | -0.4914 | 0.97373 | -0.50654 | 18.2309
46 | 0.064999 | 0.016317 | -0.064953 | -0.016288 | 4.6057e-05 | 2.9306e-05 | 0.097004 | 0.097005 | 0.097005 | 0.99716 | -0.054511 | 0.99639 | -0.069378 | 26.6496
47 | 0.17908 | 0.04499 | -0.17905 | -0.044971 | 3.0346e-05 | 1.9362e-05 | 0.26702 | 0.26702 | 0.26702 | 0.99808 | -0.036761 | 0.9979 | -0.040312 | 36.6789
48 | 0.067023 | 0.016798 | -0.067022 | -0.016797 | 8.6136e-07 | 5.4829e-07 | 0.10011 | 0.10011 | 0.10011 | 0.99621 | -0.072943 | 0.99619 | -0.073212 | 27.503
49 | -0.16098 | -0.040347 | 0.16124 | 0.040507 | 0.00025067 | 0.00015983 | 0.24046 | 0.24046 | 0.24046 | 0.99621 | -0.072943 | 0.9979 | -0.040312 | 33.0303
50 | 0.038982 | 0.0097793 | -0.038967 | -0.0097698 | 1.4953e-05 | 9.4168e-06 | 0.05822 | 0.05822 | 0.05822 | 0.99639 | -0.069378 | 0.99597 | -0.077427 | 15.9945
51 | 0.014238 | 0.0035712 | -0.014232 | -0.0035681 | 5.5426e-06 | 3.1224e-06 | 0.021273 | 0.021273 | 0.021273 | 0.99597 | -0.077427 | 0.99555 | -0.085596 | 5.8443
52 | 0.0090584 | 0.0022701 | -0.0090576 | -0.0022697 | 8.501e-07 | 3.8301e-07 | 0.013534 | 0.013534 | 0.013534 | 0.99597 | -0.077427 | 0.99587 | -0.079397 | 3.718
53 | 0.015671 | 0.0039285 | -0.015668 | -0.0039268 | 2.9844e-06 | 1.7211e-06 | 0.023413 | 0.023413 | 0.023413 | 0.99597 | -0.077427 | 0.99577 | -0.081424 | 6.4323
54 | 0.012776 | 0.0032031 | -0.012773 | -0.0032015 | 2.9061e-06 | 1.5837e-06 | 0.019096 | 0.019096 | 0.019096 | 0.99555 | -0.085596 | 0.9953 | -0.090371 | 5.2463
55 | 0.0050062 | 0.0012544 | -0.0050056 | -0.0012543 | 5.1586e-07 | 1.0295e-08 | 0.00748 | 0.0074801 | 0.0074801 | 0.99587 | -0.079397 | 0.99576 | -0.081561 | 2.055
56 | 0.0040514 | 0.0010153 | -0.0040513 | -0.0010154 | 7.0937e-08 | -2.1763e-08 | 0.0060535 | 0.0060536 | 0.0060536 | 0.99587 | -0.079397 | 0.99585 | -0.079765 | 1.6631
57 | 0.0067872 | 0.0017011 | -0.0067866 | -0.0017009 | 6.4428e-07 | 1.951e-07 | 0.010142 | 0.010143 | 0.010143 | 0.99577 | -0.081424 | 0.99566 | -0.083417 | 2.7864
58 | 0.011417 | 0.0028615 | -0.011416 | -0.0028615 | 7.4361e-08 | 3.8745e-08 | 0.017068 | 0.017068 | 0.017068 | 0.9953 | -0.090371 | 0.99529 | -0.090508 | 4.6891
59 | 0.0050056 | 0.0012543 | -0.0050048 | -0.0012543 | 7.9912e-07 | 1.6109e-08 | 0.0074801 | 0.0074803 | 0.0074803 | 0.99576 | -0.081561 | 0.99558 | -0.084912 | 2.055
60 | 0.0067866 | 0.0017009 | -0.0067865 | -0.0017009 | 6.9143e-08 | 2.0941e-08 | 0.010143 | 0.010143 | 0.010143 | 0.99566 | -0.083417 | 0.99565 | -0.083631 | 2.7864
61 | 0.0049913 | 0.0012509 | -0.004991 | -0.0012509 | 3.4257e-07 | 6.5383e-09 | 0.0074664 | 0.0074665 | 0.0074665 | 0.99473 | -0.099895 | 0.99466 | -0.10134 | 2.0512
62 | 0.01024 | 0.0025666 | -0.010238 | -0.0025658 | 1.5533e-06 | 7.6448e-07 | 0.015309 | 0.015309 | 0.015309 | 0.99529 | -0.090508 | 0.99513 | -0.093692 | 4.2059
63 | -0.023158 | -0.0058074 | 0.023168 | 0.0058136 | 1.016e-05 | 6.2355e-06 | 0.035458 | 0.035457 | 0.035458 | 0.97188 | -0.54292 | 0.97235 | -0.53372 | 9.7411
64 | 0.0050314 | 0.0012608 | -0.0050313 | -0.0012608 | 3.1805e-08 | 8.9881e-10 | 0.0075244 | 0.0075244 | 0.0075244 | 0.99499 | -0.09647 | 0.99498 | -0.096602 | 2.0671
65 | -0.0065028 | -0.0016296 | 0.0065034 | 0.0016297 | 6.6927e-07 | 1.832e-07 | 0.0097249 | 0.0097248 | 0.0097249 | 0.99499 | -0.09647 | 0.9951 | -0.094309 | 2.6717
66 | 0.0025885 | 0.00064855 | -0.0025884 | -0.00064871 | 9.805e-08 | -1.6385e-07 | 0.0038711 | 0.0038712 | 0.0038712 | 0.99498 | -0.096602 | 0.99494 | -0.097398 | 1.0635
67 | -0.0088522 | -0.0022184 | 0.0088524 | 0.0022185 | 2.6021e-07 | 1.1508e-07 | 0.013237 | 0.013237 | 0.013237 | 0.9951 | -0.094309 | 0.99513 | -0.093692 | 3.6365
68 | 0.0011369 | 0.00028494 | -0.0011369 | -0.00028494 | 1.2156e-10 | -1.3859e-09 | 0.0017004 | 0.0017004 | 0.0017004 | 0.99494 | -0.097398 | 0.99494 | -0.0974 | 0.46713
69 | 0.026159 | 0.0065696 | -0.026142 | -0.0065589 | 1.7269e-05 | 1.0695e-05 | 0.040008 | 0.040008 | 0.040008 | 0.97305 | -0.51987 | 0.97235 | -0.53372 | 10.9912
70 | -0.029174 | -0.0073252 | 0.029192 | 0.0073368 | 1.8572e-05 | 1.1577e-05 | 0.044618 | 0.044618 | 0.044618 | 0.97305 | -0.51987 | 0.97373 | -0.50654 | 12.2578
71 | 0.014227 | 0.0035671 | -0.014225 | -0.0035658 | 2.4078e-06 | 1.3721e-06 | 0.021742 | 0.021742 | 0.021742 | 0.97373 | -0.50654 | 0.97355 | -0.51009 | 5.9732
72 | 0.010017 | 0.002511 | -0.010014 | -0.0025095 | 3.0856e-06 | 1.5384e-06 | 0.01531 | 0.01531 | 0.01531 | 0.97355 | -0.51009 | 0.97322 | -0.51656 | 4.2061
73 | 0.0056504 | 0.001416 | -0.00565 | -0.0014159 | 3.9051e-07 | 7.6565e-08 | 0.0086392 | 0.0086392 | 0.0086392 | 0.97322 | -0.51656 | 0.97315 | -0.51801 | 2.3734
74 | 0.0043501 | 0.0010901 | -0.0043498 | -0.0010902 | 3.293e-07 | -3.5817e-08 | 0.0066516 | 0.0066517 | 0.0066517 | 0.97315 | -0.51801 | 0.97307 | -0.5196 | 1.8274
75 | 0.0051153 | 0.0012813 | -0.0051151 | -0.0012813 | 2.2876e-07 | 1.3972e-08 | 0.007692 | 0.0076921 | 0.0076921 | 0.98952 | -0.19975 | 0.98947 | -0.20069 | 2.1132
76 | -0.00077895 | -0.00019522 | 0.00077896 | 0.00019482 | 1.7254e-08 | -4.0076e-07 | 0.0011847 | 0.0011845 | 0.0011847 | 0.97841 | -0.41481 | 0.97844 | -0.41435 | 0.32546
77 | -0.002032 | -0.00050914 | 0.002032 | 0.00050896 | 6.1565e-08 | -1.8625e-07 | 0.0030564 | 0.0030563 | 0.0030564 | 0.98926 | -0.20477 | 0.98929 | -0.20413 | 0.83966
78 | 0.00098753 | 0.00024739 | -0.00098752 | -0.0002475 | 7.4339e-09 | -1.106e-07 | 0.0014854 | 0.0014854 | 0.0014854 | 0.98926 | -0.20477 | 0.98925 | -0.20492 | 0.40808
79 | -0.0028953 | -0.00072532 | 0.0028954 | 0.00072528 | 3.7195e-08 | -4.335e-08 | 0.0043548 | 0.0043548 | 0.0043548 | 0.98929 | -0.20413 | 0.98931 | -0.20386 | 1.1964
80 | -0.0040136 | -0.0010055 | 0.0040139 | 0.0010055 | 2.4871e-07 | -7.4527e-08 | 0.0060368 | 0.0060367 | 0.0060368 | 0.98931 | -0.20386 | 0.98937 | -0.20256 | 1.6585
81 | -0.0040139 | -0.0010055 | 0.0040142 | 0.0010054 | 3.5752e-07 | -1.072e-07 | 0.0060367 | 0.0060366 | 0.0060367 | 0.98937 | -0.20256 | 0.98947 | -0.20069 | 1.6584

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48596 | 0.12304

## res_load
| p_mw | q_mvar
0 | 0.010762 | 0.0026971
1 | 0.0082106 | 0.0020578
2 | 0.0041331 | 0.0010359
3 | 0.0059604 | 0.0014938
4 | 0.0010219 | 0.0002561
5 | 0.0047443 | 0.001189
6 | 0.0045743 | 0.0011464
7 | 0.01336 | 0.0033483
8 | 0.0078803 | 0.001975
9 | 0.013097 | 0.0032824
10 | 0.0063345 | 0.0015876
11 | 0.0046775 | 0.0011723
12 | 0.0038069 | 0.0009541
13 | 0.011004 | 0.0027577
14 | 0.0028775 | 0.00072116
15 | 0.013361 | 0.0033487
16 | 0.012723 | 0.0031886
17 | 0.01126 | 0.002822
18 | 0.014901 | 0.0037345
19 | 0.004004 | 0.0010035
20 | 0.0025991 | 0.0006514
21 | 0.00042472 | 0.00010644
22 | 0.0070595 | 0.0017693
23 | 0.0038501 | 0.00096493
24 | 0.01205 | 0.0030199
25 | 0.012266 | 0.0030741
26 | 0.093962 | 0.023549
27 | 0.067022 | 0.016797
28 | 0.017813 | 0.0044643
29 | 0.025971 | 0.0065088
30 | 0.0014564 | 0.000365
31 | 0.0088808 | 0.0022257
32 | 0.0013566 | 0.00034
33 | 0.0040513 | 0.0010154
34 | 0.0044946 | 0.0011265
35 | 0.004991 | 0.0012509
36 | 0.0067865 | 0.0017009
37 | 0.0011766 | 0.00029487
38 | 0.0050048 | 0.0012543
39 | 0.0019073 | 0.00047802
40 | 0.0014714 | 0.00036877
41 | 0.0024428 | 0.00061223
42 | 0.0023487 | 0.00058864
43 | 0.0014515 | 0.00036378
44 | 0.001386 | 0.00034736
45 | 0.0011369 | 0.00028494
46 | 0.0030149 | 0.0007556
47 | 0.0029736 | 0.00074525
48 | 0.0042084 | 0.0010547
49 | 0.0043632 | 0.0010935
50 | 0.0012999 | 0.00032579
51 | 0.00097465 | 0.00024427
52 | 0.00077895 | 0.00019522
53 | 0.00085008 | 0.00021305
54 | 0.0043498 | 0.0010902
55 | 0.0010444 | 0.00026176
56 | 0.00086331 | 0.00021637
57 | 0.00098752 | 0.0002475
58 | 0.0011183 | 0.00028026
59 | 0.0011009 | 0.0002759

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1