## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1301-49_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1301-49_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1301-49_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1301-49_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1301-49_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1301-49_0_3_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_1301-49_0_3_node_35 | 0.4 | n |  | TRUE
7 | bus_LV_1301-49_0_3_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_1301-49_0_3_node_36 | 0.4 | n |  | TRUE
9 | bus_LV_1301-49_0_3_node_32 | 0.4 | n |  | TRUE
10 | bus_LV_1301-49_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1301-49_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1301-49_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1301-49_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1301-49_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1301-49_0_3_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1301-49_0_3_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_1301-49_0_3_node_31 | 0.4 | n |  | TRUE
18 | bus_LV_1301-49_0_3_node_30 | 0.4 | n |  | TRUE
19 | bus_LV_1301-49_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1301-49_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1301-49_0_3_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_1301-49_0_3_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_1301-49_0_3_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1301-49_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1301-49_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1301-49_0_3_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1301-49_0_3_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1301-49_0_3_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_1301-49_0_3_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_1301-49_0_3_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_1301-49_0_3_node_34 | 0.4 | n |  | TRUE
32 | bus_LV_1301-49_0_3_node_37 | 0.4 | n |  | TRUE
33 | bus_LV_1301-49_0_3_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_1301-49_0_3_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_1301-49_0_3_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_1301-49_0_3_node_27 | 0.4 | n |  | TRUE
37 | bus_MV_17_0_node_96 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1301-49_0_3_load_0 | 0 | 0.0032719 | 0.00082002 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1301-49_0_3_load_1 | 1 | 0.028338 | 0.0071022 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1301-49_0_3_load_2 | 2 | 0.037038 | 0.0092826 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1301-49_0_3_load_3 | 3 | 0.0029443 | 0.00073791 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1301-49_0_3_load_4 | 4 | 0.026257 | 0.0065806 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1301-49_0_3_load_13 | 5 | 0.0044107 | 0.0011054 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1301-49_0_3_load_11 | 7 | 0.0016428 | 0.00041172 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1301-49_0_3_load_36 | 8 | 0.05853 | 0.014669 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1301-49_0_3_load_5 | 10 | 0.0022937 | 0.00057484 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1301-49_0_3_load_6 | 11 | 0.0017374 | 0.00043543 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1301-49_0_3_load_8 | 13 | 0.0012229 | 0.00030648 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1301-49_0_3_load_9 | 14 | 0.0037692 | 0.00094465 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1301-49_0_3_load_23 | 16 | 0.0048281 | 0.00121 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1301-49_0_3_load_31 | 17 | 0.026335 | 0.0066001 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1301-49_0_3_load_30 | 18 | 0.020399 | 0.0051125 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1301-49_0_3_load_12 | 19 | 0.0040319 | 0.0010105 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1301-49_0_3_load_14 | 20 | 0.0084456 | 0.0021167 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1301-49_0_3_load_25 | 21 | 0.0030342 | 0.00076043 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1301-49_0_3_load_26 | 22 | 0.0042886 | 0.0010748 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1301-49_0_3_load_15 | 23 | 0.0030755 | 0.00077079 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1301-49_0_3_load_16 | 24 | 0.0047518 | 0.0011909 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1301-49_0_3_load_18 | 25 | 0.0011862 | 0.00029728 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1301-49_0_3_load_21 | 29 | 0.0020534 | 0.00051463 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1301-49_0_3_load_29 | 30 | 0.0038069 | 0.00095409 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1301-49_0_3_load_37 | 32 | 0.0028449 | 0.000713 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1301-49_0_3_load_22 | 33 | 0.0018112 | 0.00045393 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1301-49_0_3_load_28 | 34 | 0.0026245 | 0.00065777 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1301-49_0_3_load_33 | 35 | 0.025101 | 0.006291 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1301-49_0_3_load_27 | 36 | 0.0061858 | 0.0015503 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1301-49_0_3_line_0 |  | 0 | 1 | 0.005001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1301-49_0_3_line_1 |  | 0 | 2 | 0.016922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1301-49_0_3_line_2 |  | 1 | 3 | 0.00041214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1301-49_0_3_line_3 |  | 2 | 4 | 0.0080878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1301-49_0_3_line_4 |  | 3 | 5 | 0.015734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1301-49_0_3_line_5 |  | 4 | 6 | 0.009106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1301-49_0_3_line_6 |  | 5 | 7 | 0.0014501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1301-49_0_3_line_7 |  | 6 | 8 | 0.001402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1301-49_0_3_line_8 |  | 6 | 9 | 0.001323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1301-49_0_3_line_9 |  | 7 | 19 | 0.013913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1301-49_0_3_line_10 |  | 9 | 17 | 0.016649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1301-49_0_3_line_11 |  | 9 | 14 | 0.019889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1301-49_0_3_line_12 |  | 10 | 11 | 0.01244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1301-49_0_3_line_13 |  | 10 | 12 | 0.012343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1301-49_0_3_line_14 |  | 11 | 13 | 0.011984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1301-49_0_3_line_15 |  | 12 | 14 | 0.016381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1301-49_0_3_line_16 |  | 13 | 15 | 0.015156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1301-49_0_3_line_17 |  | 15 | 16 | 0.00082989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1301-49_0_3_line_18 |  | 16 | 33 | 0.01032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1301-49_0_3_line_19 |  | 17 | 18 | 0.014564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1301-49_0_3_line_20 |  | 19 | 20 | 0.00064765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1301-49_0_3_line_21 |  | 20 | 21 | 0.00049843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1301-49_0_3_line_22 |  | 21 | 22 | 0.0089414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1301-49_0_3_line_23 |  | 22 | 36 | 0.0023805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1301-49_0_3_line_24 |  | 23 | 24 | 0.0064574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1301-49_0_3_line_25 |  | 24 | 25 | 0.0090575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1301-49_0_3_line_26 |  | 25 | 29 | 0.0037429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1301-49_0_3_line_27 |  | 26 | 27 | 0.057384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1301-49_0_3_line_28 |  | 26 | 28 | 0.067451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1301-49_0_3_line_29 |  | 27 | 30 | 0.061108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1301-49_0_3_line_30 |  | 27 | 31 | 0.13605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1301-49_0_3_line_31 |  | 28 | 32 | 0.04219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1301-49_0_3_line_32 |  | 29 | 33 | 0.0062893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1301-49_0_3_line_33 |  | 30 | 34 | 0.0018078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1301-49_0_3_line_34 |  | 31 | 35 | 0.02408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1301-49_0_3_line_35 |  | 34 | 36 | 0.0082564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1301-49_0_3_trafo_2 | 0.63 MVA 20/0.4 kV | 37 | 2 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2699011.2351 | 1220174.6415 | 2699012.865 | 1220179.3695
1 | 2699011.2351 | 1220174.6415 | 2699005.7201 | 1220158.6439
2 | 2699012.865 | 1220179.3695 | 2699012.9993 | 1220179.7591
3 | 2699005.7201 | 1220158.6439 | 2699003.0842 | 1220150.9978
4 | 2699017.9952 | 1220194.678 | 2699015.9507 | 1220188.3204 | 2699012.9993 | 1220179.7591
5 | 2699000.1099 | 1220142.3912 | 2699000.8921 | 1220144.6391 | 2699003.0842 | 1220150.9978
6 | 2699017.9952 | 1220194.678 | 2699018.4392 | 1220196.0585
7 | 2698998.7317 | 1220142.6685 | 2699000.1099 | 1220142.3912
8 | 2698999.6524 | 1220141.1493 | 2699000.1099 | 1220142.3912
9 | 2699022.6985 | 1220209.303 | 2699018.4392 | 1220196.0585
10 | 2698999.6524 | 1220141.1493 | 2698993.7584 | 1220125.5789
11 | 2698999.6524 | 1220141.1493 | 2699018.2431 | 1220134.0809
12 | 2699038.1725 | 1220139.7059 | 2699042.8265 | 1220151.242
13 | 2699033.5545 | 1220128.2592 | 2699038.1725 | 1220139.7059
14 | 2699047.3101 | 1220162.3556 | 2699042.8265 | 1220151.242
15 | 2699033.5545 | 1220128.2592 | 2699018.2431 | 1220134.0809
16 | 2699054.7842 | 1220175.5013 | 2699048.4666 | 1220165.2223 | 2699047.3101 | 1220162.3556
17 | 2699055.2189 | 1220176.2082 | 2699054.7842 | 1220175.5013
18 | 2699060.6253 | 1220184.9985 | 2699055.2189 | 1220176.2082
19 | 2698988.6026 | 1220111.9584 | 2698993.7584 | 1220125.5789
20 | 2699022.6985 | 1220209.303 | 2699022.8968 | 1220209.9196
21 | 2699022.8968 | 1220209.9196 | 2699023.0494 | 1220210.3941
22 | 2699025.7867 | 1220218.9061 | 2699023.0494 | 1220210.3941
23 | 2699025.7867 | 1220218.9061 | 2699026.5155 | 1220221.1723
24 | 2699072.8089 | 1220207.3902 | 2699070.1947 | 1220201.4857
25 | 2699070.1947 | 1220201.4857 | 2699068.7273 | 1220198.1715 | 2699065.8811 | 1220193.5438
26 | 2699063.9202 | 1220190.3557 | 2699065.8811 | 1220193.5438
27 | 2699048.4506 | 1220288.8765 | 2699049.0683 | 1220290.5213 | 2699056.8552 | 1220285.4583 | 2699075.4398 | 1220275.905 | 2699097.6466 | 1220263.4878
28 | 2699097.6466 | 1220263.4878 | 2699105.403 | 1220262.5384 | 2699106.2045 | 1220257.7038 | 2699147.4795 | 1220221.754
29 | 2699048.4506 | 1220288.8765 | 2699047.2953 | 1220285.7885 | 2699029.5966 | 1220230.7532
30 | 2698939.0858 | 1220232.3968 | 2698949.9899 | 1220240.6838 | 2698985.8322 | 1220267.6095 | 2698996.5483 | 1220277.1499 | 2699014.5857 | 1220293.1944 | 2699020.6502 | 1220299.9778 | 2699048.4506 | 1220288.8765
31 | 2699121.8196 | 1220197.7099 | 2699128.6924 | 1220193.3211 | 2699147.4795 | 1220221.754
32 | 2699060.6253 | 1220184.9985 | 2699063.9202 | 1220190.3557
33 | 2699029.5966 | 1220230.7532 | 2699029.0432 | 1220229.0323
34 | 2698939.0858 | 1220232.3968 | 2698942.702 | 1220227.5979 | 2698954.1583 | 1220213.6227
35 | 2699029.0432 | 1220229.0323 | 2699026.5155 | 1220221.1723

## bus_geodata
| x | y | coords
0 | 2699011.2351 | 1220174.6415
1 | 2699012.865 | 1220179.3695
2 | 2699005.7201 | 1220158.6439
3 | 2699012.9993 | 1220179.7591
4 | 2699003.0842 | 1220150.9978
5 | 2699017.9952 | 1220194.678
6 | 2699000.1099 | 1220142.3912
7 | 2699018.4392 | 1220196.0585
8 | 2698998.7317 | 1220142.6685
9 | 2698999.6524 | 1220141.1493
10 | 2699038.1725 | 1220139.7059
11 | 2699042.8265 | 1220151.242
12 | 2699033.5545 | 1220128.2592
13 | 2699047.3101 | 1220162.3556
14 | 2699018.2431 | 1220134.0809
15 | 2699054.7842 | 1220175.5013
16 | 2699055.2189 | 1220176.2082
17 | 2698993.7584 | 1220125.5789
18 | 2698988.6026 | 1220111.9584
19 | 2699022.6985 | 1220209.303
20 | 2699022.8968 | 1220209.9196
21 | 2699023.0494 | 1220210.3941
22 | 2699025.7867 | 1220218.9061
23 | 2699072.8089 | 1220207.3902
24 | 2699070.1947 | 1220201.4857
25 | 2699065.8811 | 1220193.5438
26 | 2699097.6466 | 1220263.4878
27 | 2699048.4506 | 1220288.8765
28 | 2699147.4795 | 1220221.754
29 | 2699063.9202 | 1220190.3557
30 | 2699029.5966 | 1220230.7532
31 | 2698939.0858 | 1220232.3968
32 | 2699121.8196 | 1220197.7099
33 | 2699060.6253 | 1220184.9985
34 | 2699029.0432 | 1220229.0323
35 | 2698954.1583 | 1220213.6227
36 | 2699026.5155 | 1220221.1723
37 | 2699000.1099 | 1220142.3912

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99844 | -0.029831 | 0.0032719 | 0.00082002
1 | 0.998 | -0.038378 | 0.028338 | 0.0071022
2 | 1 | 0 | -0.26162 | -0.06544
3 | 0.99797 | -0.038879 | 0.0029443 | 0.00073791
4 | 0.99942 | -0.011161 | 0.026257 | 0.0065806
5 | 0.99702 | -0.057188 | 0.0044107 | 0.0011054
6 | 0.99833 | -0.032158 | 0 | 0
7 | 0.99694 | -0.058765 | 0.0016428 | 0.00041172
8 | 0.99825 | -0.033593 | 0.05853 | 0.014669
9 | 0.99824 | -0.033858 | 0 | 0
10 | 0.99715 | -0.054717 | 0.0022937 | 0.00057484
11 | 0.99692 | -0.059225 | 0.0017374 | 0.00043543
12 | 0.99741 | -0.04975 | 0 | 0
13 | 0.99671 | -0.063205 | 0.0012229 | 0.00030648
14 | 0.99775 | -0.043162 | 0.0037692 | 0.00094465
15 | 0.99647 | -0.067914 | 0 | 0
16 | 0.99646 | -0.068172 | 0.0048281 | 0.00121
17 | 0.99753 | -0.047477 | 0.026335 | 0.0066001
18 | 0.99726 | -0.052682 | 0.020399 | 0.0051125
19 | 0.99617 | -0.073507 | 0.0040319 | 0.0010105
20 | 0.99614 | -0.074148 | 0.0084456 | 0.0021167
21 | 0.99611 | -0.074568 | 0.0030342 | 0.00076043
22 | 0.99575 | -0.081617 | 0.0042886 | 0.0010748
23 | 0.99616 | -0.073914 | 0.0030755 | 0.00077079
24 | 0.99618 | -0.073566 | 0.0047518 | 0.0011909
25 | 0.99624 | -0.07232 | 0.0011862 | 0.00029728
26 | 0.99363 | -0.12231 | 0 | 0
27 | 0.99378 | -0.11942 | 0 | 0
28 | 0.99346 | -0.1257 | 0 | 0
29 | 0.99627 | -0.071728 | 0.0020534 | 0.00051463
30 | 0.99535 | -0.089319 | 0.0038069 | 0.00095409
31 | 0.99066 | -0.17989 | 0 | 0
32 | 0.99335 | -0.12782 | 0.0028449 | 0.000713
33 | 0.99634 | -0.070506 | 0.0018112 | 0.00045393
34 | 0.9954 | -0.088308 | 0.0026245 | 0.00065777
35 | 0.9901 | -0.19063 | 0.025101 | 0.006291
36 | 0.99566 | -0.083315 | 0.0061858 | 0.0015503
37 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.098005 | 0.024675 | -0.097965 | -0.02465 | 4.003e-05 | 2.5554e-05 | 0.1461 | 0.1461 | 0.1461 | 0.99844 | -0.029831 | 0.998 | -0.038378 | 40.1373
1 | -0.10128 | -0.025495 | 0.10142 | 0.025588 | 0.00014464 | 9.2348e-05 | 0.15098 | 0.15098 | 0.15098 | 0.99844 | -0.029831 | 1 | 0 | 41.4769
2 | 0.069627 | 0.017548 | -0.069625 | -0.017547 | 1.6668e-06 | 1.0613e-06 | 0.10385 | 0.10385 | 0.10385 | 0.998 | -0.038378 | 0.99797 | -0.038879 | 28.5296
3 | 0.15855 | 0.039852 | -0.15847 | -0.039798 | 8.4437e-05 | 5.3828e-05 | 0.23597 | 0.23597 | 0.23597 | 1 | 0 | 0.99942 | -0.011161 | 32.4132
4 | 0.066681 | 0.016809 | -0.066622 | -0.016772 | 5.8364e-05 | 3.7148e-05 | 0.099458 | 0.099458 | 0.099458 | 0.99797 | -0.038879 | 0.99702 | -0.057188 | 27.3235
5 | 0.13221 | 0.033217 | -0.13208 | -0.033133 | 0.00013235 | 8.4588e-05 | 0.19687 | 0.19687 | 0.19687 | 0.99942 | -0.011161 | 0.99833 | -0.032158 | 54.0864
6 | 0.062212 | 0.015666 | -0.062207 | -0.015663 | 4.6906e-06 | 2.9831e-06 | 0.092875 | 0.092875 | 0.092875 | 0.99702 | -0.057188 | 0.99694 | -0.058765 | 25.5151
7 | 0.058534 | 0.014671 | -0.05853 | -0.014669 | 4.0019e-06 | 2.5429e-06 | 0.087246 | 0.087246 | 0.087246 | 0.99833 | -0.032158 | 0.99825 | -0.033593 | 23.9686
8 | 0.073544 | 0.018461 | -0.073538 | -0.018458 | 5.9627e-06 | 3.7988e-06 | 0.10963 | 0.10963 | 0.10963 | 0.99833 | -0.032158 | 0.99824 | -0.033858 | 30.1178
9 | 0.060564 | 0.015251 | -0.060521 | -0.015224 | 4.2658e-05 | 2.712e-05 | 0.090423 | 0.090423 | 0.090423 | 0.99694 | -0.058765 | 0.99617 | -0.073507 | 24.8415
10 | 0.046769 | 0.011735 | -0.046739 | -0.011716 | 3.0349e-05 | 1.9206e-05 | 0.069721 | 0.069721 | 0.069721 | 0.99824 | -0.033858 | 0.99753 | -0.047477 | 19.1541
11 | 0.026769 | 0.0067227 | -0.026757 | -0.0067154 | 1.1878e-05 | 7.3423e-06 | 0.039908 | 0.039908 | 0.039908 | 0.99824 | -0.033858 | 0.99775 | -0.043162 | 10.9637
12 | 0.020681 | 0.0051881 | -0.020677 | -0.0051855 | 4.4437e-06 | 2.6817e-06 | 0.030864 | 0.030864 | 0.030864 | 0.99715 | -0.054717 | 0.99692 | -0.059225 | 8.4791
13 | -0.022975 | -0.005763 | 0.022981 | 0.0057663 | 5.4413e-06 | 3.3214e-06 | 0.034287 | 0.034287 | 0.034287 | 0.99715 | -0.054717 | 0.99741 | -0.04975 | 9.4194
14 | 0.01894 | 0.00475 | -0.018936 | -0.0047479 | 3.5917e-06 | 2.1425e-06 | 0.028271 | 0.028271 | 0.028271 | 0.99692 | -0.059225 | 0.99671 | -0.063205 | 7.7667
15 | -0.022981 | -0.0057663 | 0.022988 | 0.0057707 | 7.2213e-06 | 4.4078e-06 | 0.034287 | 0.034287 | 0.034287 | 0.99741 | -0.04975 | 0.99775 | -0.043162 | 9.4194
16 | 0.017713 | 0.0044414 | -0.017709 | -0.0044391 | 3.9748e-06 | 2.3464e-06 | 0.026445 | 0.026445 | 0.026445 | 0.99671 | -0.063205 | 0.99647 | -0.067914 | 7.2652
17 | 0.017709 | 0.0044391 | -0.017709 | -0.0044389 | 2.1764e-07 | 1.2848e-07 | 0.026445 | 0.026445 | 0.026445 | 0.99647 | -0.067914 | 0.99646 | -0.068172 | 7.2652
18 | 0.012881 | 0.0032289 | -0.012879 | -0.0032281 | 1.4319e-06 | 7.8198e-07 | 0.019235 | 0.019235 | 0.019235 | 0.99646 | -0.068172 | 0.99634 | -0.070506 | 5.2845
19 | 0.020404 | 0.0051156 | -0.020399 | -0.0051125 | 5.0597e-06 | 3.0481e-06 | 0.030438 | 0.030438 | 0.030438 | 0.99753 | -0.047477 | 0.99726 | -0.052682 | 8.362
20 | 0.05649 | 0.014214 | -0.056488 | -0.014213 | 1.7301e-06 | 1.0988e-06 | 0.0844 | 0.0844 | 0.0844 | 0.99617 | -0.073507 | 0.99614 | -0.074148 | 23.1869
21 | 0.048042 | 0.012096 | -0.048041 | -0.012095 | 9.6316e-07 | 6.0993e-07 | 0.071785 | 0.071785 | 0.071785 | 0.99614 | -0.074148 | 0.99611 | -0.074568 | 19.721
22 | 0.045007 | 0.011335 | -0.044992 | -0.011325 | 1.5165e-05 | 9.5893e-06 | 0.067252 | 0.067252 | 0.067252 | 0.99611 | -0.074568 | 0.99575 | -0.081617 | 18.4759
23 | 0.040703 | 0.010251 | -0.0407 | -0.010248 | 3.3046e-06 | 2.084e-06 | 0.060843 | 0.060843 | 0.060843 | 0.99575 | -0.081617 | 0.99566 | -0.083315 | 16.7152
24 | -0.0030755 | -0.00077079 | 0.0030755 | 0.00077074 | 5.1106e-08 | -5.136e-08 | 0.004594 | 0.004594 | 0.004594 | 0.99616 | -0.073914 | 0.99618 | -0.073566 | 1.2621
25 | -0.0078273 | -0.0019617 | 0.0078278 | 0.0019618 | 4.6431e-07 | 1.7923e-07 | 0.011692 | 0.011692 | 0.011692 | 0.99618 | -0.073566 | 0.99624 | -0.07232 | 3.2121
26 | -0.009014 | -0.0022591 | 0.0090142 | 0.0022592 | 2.5442e-07 | 1.1409e-07 | 0.013464 | 0.013464 | 0.013464 | 0.99624 | -0.07232 | 0.99627 | -0.071728 | 3.6988
27 | -0.0028457 | -0.00071206 | 0.0028461 | 0.00071157 | 3.907e-07 | -4.9335e-07 | 0.0042611 | 0.0042609 | 0.0042611 | 0.99363 | -0.12231 | 0.99378 | -0.11942 | 1.1706
28 | 0.0028457 | 0.00071206 | -0.0028452 | -0.00071264 | 4.593e-07 | -5.7957e-07 | 0.0042611 | 0.0042614 | 0.0042614 | 0.99363 | -0.12231 | 0.99346 | -0.1257 | 1.1707
29 | -0.028033 | -0.0070551 | 0.028073 | 0.0070802 | 4.0393e-05 | 2.5058e-05 | 0.041985 | 0.041984 | 0.041985 | 0.99378 | -0.11942 | 0.99535 | -0.089319 | 11.5342
30 | 0.025187 | 0.0063436 | -0.025114 | -0.0062989 | 7.2603e-05 | 4.4709e-05 | 0.037724 | 0.037724 | 0.037724 | 0.99378 | -0.11942 | 0.99066 | -0.17989 | 10.3638
31 | 0.0028452 | 0.00071264 | -0.0028449 | -0.000713 | 2.8732e-07 | -3.6234e-07 | 0.0042614 | 0.0042616 | 0.0042616 | 0.99346 | -0.1257 | 0.99335 | -0.12782 | 1.1708
32 | -0.011068 | -0.0027739 | 0.011068 | 0.0027742 | 6.4447e-07 | 3.3056e-07 | 0.01653 | 0.01653 | 0.01653 | 0.99627 | -0.071728 | 0.99634 | -0.070506 | 4.5413
33 | -0.03188 | -0.0080343 | 0.031882 | 0.0080353 | 1.5408e-06 | 9.6264e-07 | 0.047675 | 0.047675 | 0.047675 | 0.99535 | -0.089319 | 0.9954 | -0.088308 | 13.0976
34 | 0.025114 | 0.0062989 | -0.025101 | -0.006291 | 1.2851e-05 | 7.9145e-06 | 0.037724 | 0.037724 | 0.037724 | 0.99066 | -0.17989 | 0.9901 | -0.19063 | 10.3638
35 | -0.034506 | -0.008693 | 0.034514 | 0.0086982 | 8.2433e-06 | 5.1683e-06 | 0.051599 | 0.051599 | 0.051599 | 0.9954 | -0.088308 | 0.99566 | -0.083315 | 14.1755

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.29866 | 0.074722

## res_load
| p_mw | q_mvar
0 | 0.0032719 | 0.00082002
1 | 0.028338 | 0.0071022
2 | 0.037038 | 0.0092826
3 | 0.0029443 | 0.00073791
4 | 0.026257 | 0.0065806
5 | 0.0044107 | 0.0011054
6 | 0.0016428 | 0.00041172
7 | 0.05853 | 0.014669
8 | 0.0022937 | 0.00057484
9 | 0.0017374 | 0.00043543
10 | 0.0012229 | 0.00030648
11 | 0.0037692 | 0.00094465
12 | 0.0048281 | 0.00121
13 | 0.026335 | 0.0066001
14 | 0.020399 | 0.0051125
15 | 0.0040319 | 0.0010105
16 | 0.0084456 | 0.0021167
17 | 0.0030342 | 0.00076043
18 | 0.0042886 | 0.0010748
19 | 0.0030755 | 0.00077079
20 | 0.0047518 | 0.0011909
21 | 0.0011862 | 0.00029728
22 | 0.0020534 | 0.00051463
23 | 0.0038069 | 0.00095409
24 | 0.0028449 | 0.000713
25 | 0.0018112 | 0.00045393
26 | 0.0026245 | 0.00065777
27 | 0.025101 | 0.006291
28 | 0.0061858 | 0.0015503

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1