## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1301-51_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1301-51_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1301-51_0_4_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_1301-51_0_4_node_62 | 0.4 | n |  | TRUE
4 | bus_LV_1301-51_0_4_node_63 | 0.4 | n |  | TRUE
5 | bus_LV_1301-51_0_4_node_46 | 0.4 | n |  | TRUE
6 | bus_LV_1301-51_0_4_node_48 | 0.4 | n |  | TRUE
7 | bus_LV_1301-51_0_4_node_52 | 0.4 | n |  | TRUE
8 | bus_LV_1301-51_0_4_node_57 | 0.4 | n |  | TRUE
9 | bus_LV_1301-51_0_4_node_45 | 0.4 | n |  | TRUE
10 | bus_LV_1301-51_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1301-51_0_4_node_3 | 0.4 | n |  | TRUE
12 | bus_LV_1301-51_0_4_node_131 | 0.4 | n |  | TRUE
13 | bus_LV_1301-51_0_4_node_130 | 0.4 | n |  | TRUE
14 | bus_LV_1301-51_0_4_node_47 | 0.4 | n |  | TRUE
15 | bus_LV_1301-51_0_4_node_133 | 0.4 | n |  | TRUE
16 | bus_LV_1301-51_0_4_node_6 | 0.4 | n |  | TRUE
17 | bus_LV_1301-51_0_4_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_1301-51_0_4_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_1301-51_0_4_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_1301-51_0_4_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_1301-51_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1301-51_0_4_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_1301-51_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1301-51_0_4_node_98 | 0.4 | n |  | TRUE
25 | bus_LV_1301-51_0_4_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_1301-51_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_1301-51_0_4_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_1301-51_0_4_node_37 | 0.4 | n |  | TRUE
29 | bus_LV_1301-51_0_4_node_103 | 0.4 | n |  | TRUE
30 | bus_LV_1301-51_0_4_node_99 | 0.4 | n |  | TRUE
31 | bus_LV_1301-51_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_1301-51_0_4_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_1301-51_0_4_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_1301-51_0_4_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_1301-51_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1301-51_0_4_node_41 | 0.4 | n |  | TRUE
37 | bus_LV_1301-51_0_4_node_107 | 0.4 | n |  | TRUE
38 | bus_LV_1301-51_0_4_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_1301-51_0_4_node_106 | 0.4 | n |  | TRUE
40 | bus_LV_1301-51_0_4_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_1301-51_0_4_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_1301-51_0_4_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_1301-51_0_4_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_1301-51_0_4_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_1301-51_0_4_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_1301-51_0_4_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_1301-51_0_4_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_1301-51_0_4_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_1301-51_0_4_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_1301-51_0_4_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_1301-51_0_4_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_1301-51_0_4_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_1301-51_0_4_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_1301-51_0_4_node_35 | 0.4 | n |  | TRUE
55 | bus_LV_1301-51_0_4_node_101 | 0.4 | n |  | TRUE
56 | bus_LV_1301-51_0_4_node_109 | 0.4 | n |  | TRUE
57 | bus_LV_1301-51_0_4_node_102 | 0.4 | n |  | TRUE
58 | bus_LV_1301-51_0_4_node_108 | 0.4 | n |  | TRUE
59 | bus_LV_1301-51_0_4_node_104 | 0.4 | n |  | TRUE
60 | bus_LV_1301-51_0_4_node_38 | 0.4 | n |  | TRUE
61 | bus_LV_1301-51_0_4_node_43 | 0.4 | n |  | TRUE
62 | bus_LV_1301-51_0_4_node_44 | 0.4 | n |  | TRUE
63 | bus_LV_1301-51_0_4_node_61 | 0.4 | n |  | TRUE
64 | bus_LV_1301-51_0_4_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_1301-51_0_4_node_132 | 0.4 | n |  | TRUE
66 | bus_LV_1301-51_0_4_node_129 | 0.4 | n |  | TRUE
67 | bus_LV_1301-51_0_4_node_60 | 0.4 | n |  | TRUE
68 | bus_LV_1301-51_0_4_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_1301-51_0_4_node_119 | 0.4 | n |  | TRUE
70 | bus_LV_1301-51_0_4_node_50 | 0.4 | n |  | TRUE
71 | bus_LV_1301-51_0_4_node_56 | 0.4 | n |  | TRUE
72 | bus_LV_1301-51_0_4_node_49 | 0.4 | n |  | TRUE
73 | bus_LV_1301-51_0_4_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_1301-51_0_4_node_58 | 0.4 | n |  | TRUE
75 | bus_LV_1301-51_0_4_node_59 | 0.4 | n |  | TRUE
76 | bus_LV_1301-51_0_4_node_54 | 0.4 | n |  | TRUE
77 | bus_LV_1301-51_0_4_node_122 | 0.4 | n |  | TRUE
78 | bus_LV_1301-51_0_4_node_121 | 0.4 | n |  | TRUE
79 | bus_LV_1301-51_0_4_node_123 | 0.4 | n |  | TRUE
80 | bus_LV_1301-51_0_4_node_120 | 0.4 | n |  | TRUE
81 | bus_LV_1301-51_0_4_node_64 | 0.4 | n |  | TRUE
82 | bus_LV_1301-51_0_4_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_1301-51_0_4_node_66 | 0.4 | n |  | TRUE
84 | bus_LV_1301-51_0_4_node_67 | 0.4 | n |  | TRUE
85 | bus_LV_1301-51_0_4_node_68 | 0.4 | n |  | TRUE
86 | bus_LV_1301-51_0_4_node_70 | 0.4 | n |  | TRUE
87 | bus_LV_1301-51_0_4_node_71 | 0.4 | n |  | TRUE
88 | bus_LV_1301-51_0_4_node_85 | 0.4 | n |  | TRUE
89 | bus_LV_1301-51_0_4_node_83 | 0.4 | n |  | TRUE
90 | bus_LV_1301-51_0_4_node_72 | 0.4 | n |  | TRUE
91 | bus_LV_1301-51_0_4_node_81 | 0.4 | n |  | TRUE
92 | bus_LV_1301-51_0_4_node_82 | 0.4 | n |  | TRUE
93 | bus_LV_1301-51_0_4_node_73 | 0.4 | n |  | TRUE
94 | bus_LV_1301-51_0_4_node_74 | 0.4 | n |  | TRUE
95 | bus_LV_1301-51_0_4_node_75 | 0.4 | n |  | TRUE
96 | bus_LV_1301-51_0_4_node_76 | 0.4 | n |  | TRUE
97 | bus_LV_1301-51_0_4_node_77 | 0.4 | n |  | TRUE
98 | bus_LV_1301-51_0_4_node_78 | 0.4 | n |  | TRUE
99 | bus_LV_1301-51_0_4_node_79 | 0.4 | n |  | TRUE
100 | bus_LV_1301-51_0_4_node_115 | 0.4 | n |  | TRUE
101 | bus_LV_1301-51_0_4_node_116 | 0.4 | n |  | TRUE
102 | bus_LV_1301-51_0_4_node_80 | 0.4 | n |  | TRUE
103 | bus_LV_1301-51_0_4_node_114 | 0.4 | n |  | TRUE
104 | bus_LV_1301-51_0_4_node_117 | 0.4 | n |  | TRUE
105 | bus_LV_1301-51_0_4_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_1301-51_0_4_node_92 | 0.4 | n |  | TRUE
107 | bus_LV_1301-51_0_4_node_84 | 0.4 | n |  | TRUE
108 | bus_LV_1301-51_0_4_node_88 | 0.4 | n |  | TRUE
109 | bus_LV_1301-51_0_4_node_86 | 0.4 | n |  | TRUE
110 | bus_LV_1301-51_0_4_node_87 | 0.4 | n |  | TRUE
111 | bus_LV_1301-51_0_4_node_89 | 0.4 | n |  | TRUE
112 | bus_LV_1301-51_0_4_node_91 | 0.4 | n |  | TRUE
113 | bus_LV_1301-51_0_4_node_93 | 0.4 | n |  | TRUE
114 | bus_LV_1301-51_0_4_node_95 | 0.4 | n |  | TRUE
115 | bus_LV_1301-51_0_4_node_110 | 0.4 | n |  | TRUE
116 | bus_LV_1301-51_0_4_node_94 | 0.4 | n |  | TRUE
117 | bus_LV_1301-51_0_4_node_96 | 0.4 | n |  | TRUE
118 | bus_LV_1301-51_0_4_node_97 | 0.4 | n |  | TRUE
119 | bus_LV_1301-51_0_4_node_100 | 0.4 | n |  | TRUE
120 | bus_LV_1301-51_0_4_node_127 | 0.4 | n |  | TRUE
121 | bus_LV_1301-51_0_4_node_125 | 0.4 | n |  | TRUE
122 | bus_LV_1301-51_0_4_node_105 | 0.4 | n |  | TRUE
123 | bus_LV_1301-51_0_4_node_111 | 0.4 | n |  | TRUE
124 | bus_LV_1301-51_0_4_node_112 | 0.4 | n |  | TRUE
125 | bus_LV_1301-51_0_4_node_113 | 0.4 | n |  | TRUE
126 | bus_LV_1301-51_0_4_node_118 | 0.4 | n |  | TRUE
127 | bus_LV_1301-51_0_4_node_124 | 0.4 | n |  | TRUE
128 | bus_LV_1301-51_0_4_node_126 | 0.4 | n |  | TRUE
129 | bus_LV_1301-51_0_4_node_128 | 0.4 | n |  | TRUE
130 | bus_MV_135_0_node_49 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1301-51_0_4_load_0 | 0 | 0.0021164 | 0.00053042 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1301-51_0_4_load_4 | 2 | 0.0009724 | 0.00024371 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1301-51_0_4_load_62 | 3 | 0.00016872 | 4.2284e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1301-51_0_4_load_63 | 4 | 0.00033994 | 8.5198e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1301-51_0_4_load_46 | 5 | 0.0012188 | 0.00030545 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1301-51_0_4_load_48 | 6 | 0.00092698 | 0.00023232 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1301-51_0_4_load_52 | 7 | 0.00074307 | 0.00018623 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1301-51_0_4_load_57 | 8 | 0.00041499 | 0.00010401 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1301-51_0_4_load_45 | 9 | 0.00039076 | 9.7934e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1301-51_0_4_load_5 | 10 | 0.0022502 | 0.00056395 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1301-51_0_4_load_3 | 11 | 0.00039184 | 9.8204e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1301-51_0_4_load_131 | 12 | 8.5324e-05 | 2.1384e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1301-51_0_4_load_47 | 14 | 0.0013904 | 0.00034846 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1301-51_0_4_load_133 | 15 | 0.0010712 | 0.00026846 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1301-51_0_4_load_6 | 16 | 0.016407 | 0.004112 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1301-51_0_4_load_7 | 17 | 0.012768 | 0.0032001 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1301-51_0_4_load_8 | 18 | 0.017139 | 0.0042954 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1301-51_0_4_load_10 | 20 | 0.015596 | 0.0039086 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1301-51_0_4_load_14 | 21 | 0.0032919 | 0.00082504 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1301-51_0_4_load_11 | 22 | 0.058606 | 0.014688 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1301-51_0_4_load_15 | 23 | 0.003955 | 0.00099122 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1301-51_0_4_load_98 | 24 | 0.0021357 | 0.00053525 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1301-51_0_4_load_12 | 25 | 0.015205 | 0.0038106 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1301-51_0_4_load_16 | 26 | 0.00087903 | 0.00022031 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1301-51_0_4_load_13 | 27 | 0.014436 | 0.0036179 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1301-51_0_4_load_37 | 28 | 0.028809 | 0.0072201 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1301-51_0_4_load_103 | 29 | 0.0016581 | 0.00041557 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1301-51_0_4_load_99 | 30 | 0.0020915 | 0.00052419 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1301-51_0_4_load_18 | 31 | 0.00095782 | 0.00024005 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1301-51_0_4_load_19 | 32 | 0.0007339 | 0.00018393 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1301-51_0_4_load_20 | 33 | 0.0017043 | 0.00042713 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1301-51_0_4_load_22 | 35 | 0.00078348 | 0.00019636 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1301-51_0_4_load_41 | 36 | 0.00092228 | 0.00023115 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1301-51_0_4_load_107 | 37 | 0.00061408 | 0.0001539 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1301-51_0_4_load_39 | 38 | 0.0024717 | 0.00061946 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1301-51_0_4_load_106 | 39 | 0.00044824 | 0.00011234 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1301-51_0_4_load_23 | 40 | 0.00030353 | 7.6071e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1301-51_0_4_load_24 | 41 | 0.00022368 | 5.6059e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1301-51_0_4_load_25 | 42 | 0.00026881 | 6.7371e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1301-51_0_4_load_26 | 43 | 0.0012724 | 0.00031888 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1301-51_0_4_load_36 | 44 | 0.00037517 | 9.4026e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1301-51_0_4_load_27 | 45 | 0.00031191 | 7.8172e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1301-51_0_4_load_28 | 46 | 0.00046624 | 0.00011685 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1301-51_0_4_load_40 | 49 | 0.0019895 | 0.00049861 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1301-51_0_4_load_31 | 50 | 0.00783 | 0.0019624 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1301-51_0_4_load_32 | 51 | 0.026323 | 0.0065971 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1301-51_0_4_load_33 | 52 | 0.0266 | 0.0066666 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1301-51_0_4_load_34 | 53 | 0.016093 | 0.0040333 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1301-51_0_4_load_35 | 54 | 0.0020094 | 0.00050361 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1301-51_0_4_load_101 | 55 | 0.021255 | 0.005327 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1301-51_0_4_load_109 | 56 | 0.001241 | 0.00031102 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1301-51_0_4_load_102 | 57 | 0.002117 | 0.00053057 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1301-51_0_4_load_108 | 58 | 0.0032769 | 0.00082127 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1301-51_0_4_load_104 | 59 | 0.0007379 | 0.00018494 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1301-51_0_4_load_38 | 60 | 0.0011583 | 0.00029029 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1301-51_0_4_load_43 | 61 | 0.00014118 | 3.5383e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1301-51_0_4_load_44 | 62 | 5.6856e-05 | 1.425e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1301-51_0_4_load_61 | 63 | 0.00030573 | 7.6623e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1301-51_0_4_load_55 | 64 | 0.00016576 | 4.1543e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1301-51_0_4_load_132 | 65 | 6.7149e-05 | 1.6829e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1301-51_0_4_load_129 | 66 | 0.00017604 | 4.4119e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1301-51_0_4_load_60 | 67 | 0.00021611 | 5.4161e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1301-51_0_4_load_53 | 68 | 0.00046381 | 0.00011624 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1301-51_0_4_load_119 | 69 | 0.0013853 | 0.00034718 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1301-51_0_4_load_50 | 70 | 0.0023117 | 0.00057936 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1301-51_0_4_load_56 | 71 | 0.00011364 | 2.848e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1301-51_0_4_load_49 | 72 | 0.0016193 | 0.00040583 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1301-51_0_4_load_51 | 73 | 0.0013905 | 0.00034849 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1301-51_0_4_load_58 | 74 | 0.00045242 | 0.00011339 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1301-51_0_4_load_122 | 77 | 0.0019556 | 0.00049012 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1301-51_0_4_load_123 | 79 | 0.004093 | 0.0010258 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1301-51_0_4_load_120 | 80 | 0.0011653 | 0.00029205 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1301-51_0_4_load_64 | 81 | 0.0065697 | 0.0016465 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1301-51_0_4_load_66 | 83 | 0.0027001 | 0.0006767 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1301-51_0_4_load_67 | 84 | 0.0019807 | 0.00049641 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1301-51_0_4_load_70 | 86 | 0.0034744 | 0.00087078 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1301-51_0_4_load_85 | 88 | 0.0034565 | 0.00086627 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1301-51_0_4_load_83 | 89 | 0.0043023 | 0.0010782 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1301-51_0_4_load_81 | 91 | 0.004259 | 0.0010674 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1301-51_0_4_load_73 | 93 | 0.0037502 | 0.0009399 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1301-51_0_4_load_74 | 94 | 0.0027464 | 0.00068832 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1301-51_0_4_load_76 | 96 | 0.0030996 | 0.00077683 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1301-51_0_4_load_77 | 97 | 0.0033601 | 0.00084213 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1301-51_0_4_load_78 | 98 | 0.0042704 | 0.0010703 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1301-51_0_4_load_79 | 99 | 0.0034219 | 0.00085762 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1301-51_0_4_load_115 | 100 | 0.0073693 | 0.0018469 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1301-51_0_4_load_116 | 101 | 0.001044 | 0.00026165 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1301-51_0_4_load_80 | 102 | 0.0014395 | 0.00036077 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1301-51_0_4_load_114 | 103 | 0.0027426 | 0.00068737 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1301-51_0_4_load_117 | 104 | 0.0021826 | 0.00054702 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1301-51_0_4_load_92 | 106 | 0.0023841 | 0.00059751 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1301-51_0_4_load_84 | 107 | 0.0072937 | 0.001828 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1301-51_0_4_load_86 | 109 | 0.0010427 | 0.00026132 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1301-51_0_4_load_87 | 110 | 0.0035594 | 0.00089208 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1301-51_0_4_load_89 | 111 | 0.0013103 | 0.00032838 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1301-51_0_4_load_91 | 112 | 0.0044799 | 0.0011228 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1301-51_0_4_load_93 | 113 | 0.0025154 | 0.00063041 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1301-51_0_4_load_95 | 114 | 0.0081507 | 0.0020428 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1301-51_0_4_load_110 | 115 | 0.001057 | 0.00026492 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1301-51_0_4_load_94 | 116 | 0.0039538 | 0.00099091 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1301-51_0_4_load_96 | 117 | 0.0010001 | 0.00025066 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1301-51_0_4_load_97 | 118 | 0.0027862 | 0.00069829 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1301-51_0_4_load_100 | 119 | 0.0020546 | 0.00051493 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1301-51_0_4_load_127 | 120 | 0.0018806 | 0.00047132 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1301-51_0_4_load_125 | 121 | 0.0018835 | 0.00047204 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1301-51_0_4_load_105 | 122 | 0.00073098 | 0.0001832 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1301-51_0_4_load_111 | 123 | 0.0022546 | 0.00056504 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1301-51_0_4_load_112 | 124 | 0.00086232 | 0.00021612 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1301-51_0_4_load_113 | 125 | 0.0047105 | 0.0011806 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1301-51_0_4_load_118 | 126 | 0.0015835 | 0.00039686 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1301-51_0_4_load_124 | 127 | 0.002011 | 0.00050401 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1301-51_0_4_load_126 | 128 | 0.0021913 | 0.0005492 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1301-51_0_4_load_128 | 129 | 0.0023441 | 0.00058748 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 54 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1301-51_0_4_line_0 |  | 0 | 1 | 0.062926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1301-51_0_4_line_1 |  | 1 | 2 | 0.025532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1301-51_0_4_line_2 |  | 2 | 10 | 0.26205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1301-51_0_4_line_3 |  | 3 | 4 | 0.024469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1301-51_0_4_line_4 |  | 3 | 5 | 0.29394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1301-51_0_4_line_5 |  | 4 | 11 | 0.63069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1301-51_0_4_line_6 |  | 5 | 9 | 0.26785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1301-51_0_4_line_7 |  | 5 | 10 | 0.30531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1301-51_0_4_line_8 |  | 6 | 7 | 0.21724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1301-51_0_4_line_9 |  | 6 | 8 | 0.24222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1301-51_0_4_line_10 |  | 6 | 9 | 0.27961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1301-51_0_4_line_11 |  | 7 | 70 | 0.0064925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1301-51_0_4_line_12 |  | 8 | 71 | 0.01592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1301-51_0_4_line_13 |  | 12 | 13 | 0.023885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1301-51_0_4_line_14 |  | 13 | 65 | 0.067329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1301-51_0_4_line_15 |  | 14 | 15 | 0.26553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1301-51_0_4_line_16 |  | 15 | 69 | 0.10389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1301-51_0_4_line_17 |  | 16 | 17 | 0.026031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1301-51_0_4_line_18 |  | 16 | 18 | 0.023523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1301-51_0_4_line_19 |  | 17 | 19 | 0.0048319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1301-51_0_4_line_20 |  | 18 | 20 | 0.023567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1301-51_0_4_line_21 |  | 19 | 21 | 0.030582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_1301-51_0_4_line_22 |  | 19 | 22 | 0.0092645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_1301-51_0_4_line_23 |  | 20 | 23 | 0.027127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1301-51_0_4_line_24 |  | 21 | 24 | 0.00043722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_1301-51_0_4_line_25 |  | 22 | 25 | 0.025779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_1301-51_0_4_line_26 |  | 23 | 26 | 0.041199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1301-51_0_4_line_27 |  | 24 | 30 | 0.0045684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_1301-51_0_4_line_28 |  | 25 | 27 | 0.036004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1301-51_0_4_line_29 |  | 27 | 28 | 0.00052234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1301-51_0_4_line_30 |  | 28 | 29 | 0.022631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1301-51_0_4_line_31 |  | 29 | 59 | 0.012615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1301-51_0_4_line_32 |  | 30 | 119 | 0.00064045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1301-51_0_4_line_33 |  | 31 | 32 | 0.030785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1301-51_0_4_line_34 |  | 31 | 33 | 0.0022851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1301-51_0_4_line_35 |  | 32 | 34 | 0.010895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1301-51_0_4_line_36 |  | 33 | 35 | 0.018418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1301-51_0_4_line_37 |  | 34 | 36 | 0.015926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1301-51_0_4_line_38 |  | 34 | 37 | 0.028511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1301-51_0_4_line_39 |  | 36 | 38 | 0.023507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1301-51_0_4_line_40 |  | 37 | 39 | 0.012738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1301-51_0_4_line_41 |  | 38 | 60 | 0.0026461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1301-51_0_4_line_42 |  | 39 | 122 | 0.0068006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1301-51_0_4_line_43 |  | 40 | 41 | 0.0016321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1301-51_0_4_line_44 |  | 40 | 42 | 0.044261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1301-51_0_4_line_45 |  | 41 | 43 | 0.024369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1301-51_0_4_line_46 |  | 43 | 44 | 0.022915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1301-51_0_4_line_47 |  | 43 | 45 | 0.049783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1301-51_0_4_line_48 |  | 44 | 47 | 0.0691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1301-51_0_4_line_49 |  | 45 | 46 | 0.019963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1301-51_0_4_line_50 |  | 47 | 48 | 0.025857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1301-51_0_4_line_51 |  | 48 | 49 | 0.06954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1301-51_0_4_line_52 |  | 49 | 60 | 0.017655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1301-51_0_4_line_53 |  | 50 | 51 | 0.014632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1301-51_0_4_line_54 |  | 50 | 52 | 0.011577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1301-51_0_4_line_55 |  | 51 | 53 | 4.3935e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1301-51_0_4_line_56 |  | 52 | 54 | 0.023562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1301-51_0_4_line_57 |  | 53 | 55 | 0.011905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1301-51_0_4_line_58 |  | 54 | 56 | 0.023665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_1301-51_0_4_line_59 |  | 55 | 57 | 0.021879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1301-51_0_4_line_60 |  | 56 | 58 | 0.02193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_1301-51_0_4_line_61 |  | 57 | 120 | 0.016193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1301-51_0_4_line_62 |  | 58 | 115 | 0.033492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_1301-51_0_4_line_63 |  | 59 | 122 | 0.0060522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1301-51_0_4_line_64 |  | 61 | 62 | 0.045861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1301-51_0_4_line_65 |  | 61 | 63 | 0.19467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1301-51_0_4_line_66 |  | 62 | 64 | 0.19166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1301-51_0_4_line_67 |  | 63 | 65 | 0.22608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1301-51_0_4_line_68 |  | 64 | 66 | 0.18666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1301-51_0_4_line_69 |  | 64 | 67 | 0.075927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1301-51_0_4_line_70 |  | 64 | 68 | 0.11797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1301-51_0_4_line_71 |  | 68 | 76 | 0.014167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1301-51_0_4_line_72 |  | 69 | 80 | 0.014959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_1301-51_0_4_line_73 |  | 69 | 126 | 0.017484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_1301-51_0_4_line_74 |  | 70 | 72 | 0.034062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1301-51_0_4_line_75 |  | 71 | 76 | 0.03694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1301-51_0_4_line_76 |  | 72 | 73 | 0.075842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1301-51_0_4_line_77 |  | 73 | 74 | 0.079436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
78 | LV_1301-51_0_4_line_78 |  | 74 | 75 | 0.022227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_1301-51_0_4_line_79 |  | 75 | 77 | 0.023547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1301-51_0_4_line_80 |  | 75 | 78 | 0.008702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_1301-51_0_4_line_81 |  | 77 | 79 | 0.01622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1301-51_0_4_line_82 |  | 78 | 80 | 0.019782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_1301-51_0_4_line_83 |  | 81 | 82 | 0.008581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1301-51_0_4_line_84 |  | 82 | 83 | 0.017716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1301-51_0_4_line_85 |  | 83 | 84 | 0.016943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1301-51_0_4_line_86 |  | 84 | 85 | 0.014044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1301-51_0_4_line_87 |  | 85 | 86 | 0.015267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1301-51_0_4_line_88 |  | 86 | 87 | 0.019248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1301-51_0_4_line_89 |  | 87 | 90 | 0.016488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1301-51_0_4_line_90 |  | 88 | 89 | 0.023854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1301-51_0_4_line_91 |  | 89 | 90 | 0.063944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1301-51_0_4_line_92 |  | 90 | 91 | 0.0053583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1301-51_0_4_line_93 |  | 91 | 92 | 0.027069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1301-51_0_4_line_94 |  | 92 | 107 | 0.0023861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1301-51_0_4_line_95 |  | 93 | 94 | 0.011323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_1301-51_0_4_line_96 |  | 93 | 95 | 0.0066837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_1301-51_0_4_line_97 |  | 94 | 96 | 0.030785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_1301-51_0_4_line_98 |  | 95 | 97 | 0.034604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1301-51_0_4_line_99 |  | 95 | 98 | 0.025467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_1301-51_0_4_line_100 |  | 96 | 99 | 0.015312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_1301-51_0_4_line_101 |  | 97 | 100 | 0.0119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1301-51_0_4_line_102 |  | 98 | 101 | 0.045044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_1301-51_0_4_line_103 |  | 99 | 102 | 0.025621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_1301-51_0_4_line_104 |  | 100 | 103 | 0.018616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1301-51_0_4_line_105 |  | 101 | 104 | 0.0023116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_1301-51_0_4_line_106 |  | 102 | 105 | 0.029467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_1301-51_0_4_line_107 |  | 103 | 125 | 0.029535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1301-51_0_4_line_108 |  | 104 | 126 | 0.022228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_1301-51_0_4_line_109 |  | 105 | 106 | 0.03616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_1301-51_0_4_line_110 |  | 105 | 107 | 0.022323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1301-51_0_4_line_111 |  | 105 | 108 | 0.015746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
112 | LV_1301-51_0_4_line_112 |  | 106 | 115 | 0.020387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_1301-51_0_4_line_113 |  | 108 | 112 | 0.020861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
114 | LV_1301-51_0_4_line_114 |  | 108 | 109 | 0.042048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1301-51_0_4_line_115 |  | 109 | 110 | 0.0077492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1301-51_0_4_line_116 |  | 110 | 111 | 0.023207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1301-51_0_4_line_117 |  | 111 | 113 | 0.03765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1301-51_0_4_line_118 |  | 112 | 114 | 0.020995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_1301-51_0_4_line_119 |  | 114 | 116 | 0.0039379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
120 | LV_1301-51_0_4_line_120 |  | 116 | 117 | 0.00065824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_1301-51_0_4_line_121 |  | 117 | 118 | 0.0029108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
122 | LV_1301-51_0_4_line_122 |  | 118 | 119 | 0.014741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_1301-51_0_4_line_123 |  | 120 | 121 | 0.013908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1301-51_0_4_line_124 |  | 121 | 127 | 0.03188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1301-51_0_4_line_125 |  | 123 | 124 | 0.017272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1301-51_0_4_line_126 |  | 123 | 125 | 0.0018948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1301-51_0_4_line_127 |  | 127 | 128 | 0.0031902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1301-51_0_4_line_128 |  | 128 | 129 | 0.0028598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1301-51_0_4_trafo_35 | 0.63 MVA 20/0.4 kV | 130 | 54 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2704327.6369 | 1218390.6328 | 2704337.1278 | 1218395.3135 | 2704372.1794 | 1218434.1887
1 | 2704327.6369 | 1218390.6328 | 2704320.5332 | 1218382.725 | 2704317.9137 | 1218373.6503 | 2704316.6739 | 1218368.3363
2 | 2704316.6739 | 1218368.3363 | 2704176.5196 | 1218146.9179
3 | 2704697.8275 | 1218211.4741 | 2704686.8105 | 1218208.1003 | 2704676.0717 | 1218200.8683
4 | 2704450.5644 | 1218012.3261 | 2704676.0717 | 1218200.8683
5 | 2704697.8275 | 1218211.4741 | 2704970.0273 | 1218780.3966
6 | 2704278.282 | 1217807.2336 | 2704450.5644 | 1218012.3261
7 | 2704450.5644 | 1218012.3261 | 2704176.5196 | 1218146.9179
8 | 2704456.7683 | 1217460.5884 | 2704520.8576 | 1217668.1646
9 | 2704750.0524 | 1217589.8108 | 2704520.8576 | 1217668.1646
10 | 2704520.8576 | 1217668.1646 | 2704278.282 | 1217807.2336
11 | 2704456.7683 | 1217460.5884 | 2704456.0982 | 1217454.1306
12 | 2704750.0524 | 1217589.8108 | 2704762.7746 | 1217599.3809
13 | 2705210.942 | 1218092.6144 | 2705213.715 | 1218100.2355 | 2705217.3917 | 1218115.5782
14 | 2705210.942 | 1218092.6144 | 2705165.9951 | 1218042.4848
15 | 2704229.8658 | 1217441.1715 | 2704052.0842 | 1217638.4067
16 | 2704267.7214 | 1217344.4276 | 2704229.8658 | 1217441.1715
17 | 2704440.2897 | 1217119.5418 | 2704436.098 | 1217123.3644 | 2704431.4697 | 1217127.4974 | 2704420.2798 | 1217136.1622
18 | 2704457.6705 | 1217103.6915 | 2704440.2897 | 1217119.5418
19 | 2704416.4594 | 1217139.1205 | 2704420.2798 | 1217136.1622
20 | 2704475.0841 | 1217087.8112 | 2704457.6705 | 1217103.6915
21 | 2704416.4594 | 1217139.1205 | 2704404.9775 | 1217142.6552 | 2704390.7942 | 1217146.087 | 2704386.9421 | 1217147.07
22 | 2704416.4594 | 1217139.1205 | 2704425.0851 | 1217142.501
23 | 2704475.0841 | 1217087.8112 | 2704495.128 | 1217069.5322
24 | 2704386.9421 | 1217147.07 | 2704386.5184 | 1217147.1781
25 | 2704449.0871 | 1217151.9077 | 2704425.0851 | 1217142.501
26 | 2704525.3488 | 1217041.5382 | 2704523.6079 | 1217043.352 | 2704507.9934 | 1217057.7997 | 2704495.128 | 1217069.5322
27 | 2704386.5184 | 1217147.1781 | 2704382.0919 | 1217148.3077
28 | 2704449.0871 | 1217151.9077 | 2704457.9211 | 1217155.3698 | 2704484.0615 | 1217159.8184
29 | 2704484.0615 | 1217159.8184 | 2704484.5765 | 1217159.9061
30 | 2704484.5765 | 1217159.9061 | 2704506.8868 | 1217163.7028
31 | 2704519.3232 | 1217165.8193 | 2704506.8868 | 1217163.7028
32 | 2704382.0919 | 1217148.3077 | 2704381.4713 | 1217148.466
33 | 2704582.4554 | 1217134.3832 | 2704575.2195 | 1217164.306
34 | 2704582.4554 | 1217134.3832 | 2704582.9926 | 1217132.162
35 | 2704572.6586 | 1217174.8959 | 2704575.2195 | 1217164.306
36 | 2704596.9871 | 1217124.015 | 2704587.101 | 1217125.1469 | 2704583.9575 | 1217128.1717 | 2704582.9926 | 1217132.162
37 | 2704572.6586 | 1217174.8959 | 2704588.3588 | 1217177.5686
38 | 2704572.6586 | 1217174.8959 | 2704544.5518 | 1217170.1127
39 | 2704588.3588 | 1217177.5686 | 2704601.0628 | 1217179.7312 | 2704611.5326 | 1217181.5138
40 | 2704531.9939 | 1217167.9756 | 2704544.5518 | 1217170.1127
41 | 2704614.1412 | 1217181.958 | 2704611.5326 | 1217181.5138
42 | 2704531.9939 | 1217167.9756 | 2704525.2897 | 1217166.8346
43 | 2704708.1912 | 1217330.047 | 2704708.0182 | 1217331.6699
44 | 2704723.29 | 1217369.6722 | 2704723.4638 | 1217369.2171 | 2704722.9884 | 1217363.4379 | 2704716.7491 | 1217356.8458 | 2704709.5027 | 1217349.6688 | 2704706.7197 | 1217343.8491 | 2704708.0182 | 1217331.6699
45 | 2704708.1912 | 1217330.047 | 2704708.62 | 1217326.0252 | 2704711.2405 | 1217305.87
46 | 2704711.2405 | 1217305.87 | 2704712.4394 | 1217296.6489 | 2704714.1948 | 1217283.1462
47 | 2704711.2405 | 1217305.87 | 2704757.9013 | 1217323.2225
48 | 2704704.4067 | 1217216.2832 | 2704704.955 | 1217222.2416 | 2704712.424 | 1217240.953 | 2704716.2647 | 1217252.6845 | 2704716.6364 | 1217264.3661 | 2704714.1948 | 1217283.1462
49 | 2704772.3181 | 1217336.5098 | 2704763.685 | 1217331.1076 | 2704757.9013 | 1217323.2225 | 2704757.9013 | 1217323.2225
50 | 2704700.0984 | 1217196.5934 | 2704706.9873 | 1217197.7708 | 2704706.2417 | 1217200.4485 | 2704705.5852 | 1217202.8054 | 2704703.9785 | 1217211.7058 | 2704704.4067 | 1217216.2832
51 | 2704700.0984 | 1217196.5934 | 2704631.5453 | 1217184.9213
52 | 2704614.1412 | 1217181.958 | 2704631.5453 | 1217184.9213
53 | 2704447.7979 | 1217215.2302 | 2704460.9773 | 1217208.875
54 | 2704447.7979 | 1217215.2302 | 2704437.3703 | 1217220.2584
55 | 2704460.9773 | 1217208.875 | 2704461.0169 | 1217208.8559
56 | 2704414.7385 | 1217226.4531 | 2704414.7385 | 1217226.4531 | 2704433.1024 | 1217222.3164 | 2704437.3703 | 1217220.2584
57 | 2704471.7567 | 1217203.722 | 2704471.0159 | 1217204.0343 | 2704461.0169 | 1217208.8559
58 | 2704414.7385 | 1217226.4531 | 2704411.2785 | 1217226.7483 | 2704405.9397 | 1217227.2329 | 2704391.1843 | 1217228.7334
59 | 2704491.917 | 1217195.2218 | 2704471.7567 | 1217203.722
60 | 2704369.837 | 1217225.83 | 2704382.717 | 1217229.5945 | 2704391.1843 | 1217228.7334
61 | 2704507.2688 | 1217190.3632 | 2704500.3597 | 1217191.6621 | 2704491.917 | 1217195.2218
62 | 2704369.837 | 1217225.83 | 2704360.1751 | 1217223.0061 | 2704340.1686 | 1217210.8203
63 | 2704519.3232 | 1217165.8193 | 2704525.2897 | 1217166.8346
64 | 2705126.214 | 1217742.0641 | 2705123.7335 | 1217736.5402 | 2705117.6515 | 1217726.2477 | 2705109.8879 | 1217718.3162 | 2705097.9375 | 1217712.7236 | 2705094.5238 | 1217711.7236
65 | 2705126.214 | 1217742.0641 | 2704999.3427 | 1217889.7134
66 | 2704919.5538 | 1217633.4899 | 2705094.5238 | 1217711.7236
67 | 2704999.3427 | 1217889.7134 | 2705165.9951 | 1218042.4848
68 | 2704919.5538 | 1217633.4899 | 2705005.2506 | 1217467.6685
69 | 2704919.5538 | 1217633.4899 | 2704893.1204 | 1217704.6666
70 | 2704805.328 | 1217603.9921 | 2704919.5538 | 1217633.4899
71 | 2704795.2695 | 1217613.3997 | 2704799.2772 | 1217611.7357 | 2704805.328 | 1217603.9921
72 | 2704281.6939 | 1217349.648 | 2704275.513 | 1217347.9363 | 2704267.7214 | 1217344.4276
73 | 2704251.779 | 1217337.2484 | 2704267.7214 | 1217344.4276
74 | 2704442.1075 | 1217424.9533 | 2704442.1075 | 1217424.9533 | 2704454.4742 | 1217438.4798 | 2704456.0982 | 1217454.1306
75 | 2704795.2695 | 1217613.3997 | 2704791.3382 | 1217615.0318 | 2704769.3639 | 1217604.3377 | 2704762.7746 | 1217599.3809
76 | 2704442.1075 | 1217424.9533 | 2704440.3799 | 1217406.999 | 2704437.3061 | 1217381.8159 | 2704413.0721 | 1217368.2704 | 2704409.2346 | 1217365.6046
77 | 2704330.4363 | 1217355.5561 | 2704409.2346 | 1217365.6046
78 | 2704309.1681 | 1217357.2542 | 2704317.714 | 1217359.6277 | 2704330.4363 | 1217355.5561
79 | 2704309.1681 | 1217357.2542 | 2704306.291 | 1217333.884
80 | 2704300.7581 | 1217354.9275 | 2704309.1681 | 1217357.2542
81 | 2704304.309 | 1217317.7852 | 2704306.291 | 1217333.884
82 | 2704300.7581 | 1217354.9275 | 2704281.6939 | 1217349.648
83 | 2704149.674 | 1217192.7021 | 2704141.3568 | 1217194.8133
84 | 2704149.674 | 1217192.7021 | 2704166.2548 | 1217188.4889 | 2704166.8404 | 1217188.3242
85 | 2704166.8404 | 1217188.3242 | 2704183.1506 | 1217183.7381
86 | 2704196.6701 | 1217179.9366 | 2704183.1506 | 1217183.7381
87 | 2704196.6701 | 1217179.9366 | 2704211.7486 | 1217177.5446
88 | 2704230.7587 | 1217174.5288 | 2704211.7486 | 1217177.5446
89 | 2704247.279 | 1217173.7839 | 2704242.294 | 1217174.0079 | 2704230.7587 | 1217174.5288
90 | 2704229.2502 | 1217098.4589 | 2704236.6516 | 1217098.9998 | 2704243.1355 | 1217114.0992
91 | 2704247.279 | 1217173.7839 | 2704254.9962 | 1217132.4225 | 2704244.1662 | 1217116.4994 | 2704243.1355 | 1217114.0992
92 | 2704247.279 | 1217173.7839 | 2704252.632 | 1217173.5461
93 | 2704279.6735 | 1217172.3273 | 2704252.6666 | 1217173.5446 | 2704252.632 | 1217173.5461
94 | 2704279.6735 | 1217172.3273 | 2704282.0215 | 1217171.9024
95 | 2704236.8906 | 1217254.1953 | 2704243.0767 | 1217244.7119
96 | 2704233.2676 | 1217259.8117 | 2704234.3533 | 1217258.085 | 2704236.8906 | 1217254.1953
97 | 2704243.0767 | 1217244.7119 | 2704249.6925 | 1217234.5698 | 2704260.8881 | 1217219.6215 | 2704260.8881 | 1217219.6215
98 | 2704233.2676 | 1217259.8117 | 2704240.6521 | 1217266.5124 | 2704246.9697 | 1217271.2707 | 2704256.6714 | 1217270.9513 | 2704263.5603 | 1217269.6203
99 | 2704233.2676 | 1217259.8117 | 2704228.1449 | 1217272.2533 | 2704224.6942 | 1217283.7593
100 | 2704260.8881 | 1217219.6215 | 2704270.3828 | 1217213.7834 | 2704273.6434 | 1217211.19
101 | 2704263.5603 | 1217269.6203 | 2704275.2441 | 1217267.3628
102 | 2704224.6942 | 1217283.7593 | 2704219.7025 | 1217300.4037 | 2704221.9 | 1217312.3729 | 2704231.4276 | 1217324.5965
103 | 2704292.9882 | 1217194.4181 | 2704282.3104 | 1217204.2964 | 2704273.6434 | 1217211.19
104 | 2704293.5623 | 1217264.0987 | 2704290.1783 | 1217264.4773 | 2704275.2441 | 1217267.3628
105 | 2704231.4276 | 1217324.5965 | 2704232.8487 | 1217326.4196
106 | 2704303.9875 | 1217167.9274 | 2704303.3347 | 1217177.4561 | 2704299.8283 | 1217184.2997 | 2704293.3395 | 1217194.0932 | 2704292.9882 | 1217194.4181
107 | 2704293.5623 | 1217264.0987 | 2704310.2858 | 1217262.2276 | 2704322.9708 | 1217262.9838
108 | 2704232.8487 | 1217326.4196 | 2704235.616 | 1217329.9699 | 2704251.779 | 1217337.2484
109 | 2704303.9875 | 1217167.9274 | 2704312.3166 | 1217182.6949 | 2704325.802 | 1217196.3702
110 | 2704303.9875 | 1217167.9274 | 2704282.0215 | 1217171.9024
111 | 2704319.3583 | 1217164.316 | 2704309.5914 | 1217166.6134 | 2704303.9875 | 1217167.9274
112 | 2704340.1686 | 1217210.8203 | 2704339.8755 | 1217210.6418 | 2704325.802 | 1217196.3702
113 | 2704319.3583 | 1217164.316 | 2704339.5714 | 1217159.1581
114 | 2704319.3583 | 1217164.316 | 2704304.5492 | 1217124.9624
115 | 2704304.5492 | 1217124.9624 | 2704301.82 | 1217117.7097
116 | 2704293.7485 | 1217095.9556 | 2704294.095 | 1217097.1812 | 2704301.82 | 1217117.7097
117 | 2704293.7485 | 1217095.9556 | 2704290.5127 | 1217084.5094 | 2704294.4779 | 1217076.6176 | 2704305.2607 | 1217066.6102 | 2704306.8341 | 1217065.0554
118 | 2704359.9141 | 1217153.967 | 2704339.5714 | 1217159.1581
119 | 2704363.7298 | 1217152.9933 | 2704359.9141 | 1217153.967
120 | 2704364.3676 | 1217152.8306 | 2704363.7298 | 1217152.9933
121 | 2704364.3676 | 1217152.8306 | 2704367.1879 | 1217152.1109
122 | 2704367.1879 | 1217152.1109 | 2704381.4713 | 1217148.466
123 | 2704521.0723 | 1217189.256 | 2704513.2344 | 1217189.2417 | 2704507.2688 | 1217190.3632
124 | 2704552.928 | 1217190.2541 | 2704533.75 | 1217189.2793 | 2704521.0723 | 1217189.256
125 | 2704324.8622 | 1217263.0966 | 2704342.1033 | 1217264.1244
126 | 2704324.8622 | 1217263.0966 | 2704322.9708 | 1217262.9838
127 | 2704552.928 | 1217190.2541 | 2704556.1141 | 1217190.416
128 | 2704556.1141 | 1217190.416 | 2704558.9702 | 1217190.5612

## bus_geodata
| x | y | coords
0 | 2704372.1794 | 1218434.1887
1 | 2704327.6369 | 1218390.6328
2 | 2704316.6739 | 1218368.3363
3 | 2704676.0717 | 1218200.8683
4 | 2704697.8275 | 1218211.4741
5 | 2704450.5643 | 1218012.3261
6 | 2704520.8576 | 1217668.1646
7 | 2704456.7683 | 1217460.5884
8 | 2704750.0524 | 1217589.8108
9 | 2704278.282 | 1217807.2336
10 | 2704176.5196 | 1218146.9179
11 | 2704970.0273 | 1218780.3966
12 | 2705217.3917 | 1218115.5782
13 | 2705210.942 | 1218092.6144
14 | 2704052.0842 | 1217638.4067
15 | 2704229.8658 | 1217441.1715
16 | 2704440.2897 | 1217119.5418
17 | 2704420.2798 | 1217136.1622
18 | 2704457.6705 | 1217103.6915
19 | 2704416.4594 | 1217139.1205
20 | 2704475.0841 | 1217087.8112
21 | 2704386.9421 | 1217147.07
22 | 2704425.0851 | 1217142.501
23 | 2704495.128 | 1217069.5322
24 | 2704386.5184 | 1217147.1781
25 | 2704449.0871 | 1217151.9077
26 | 2704525.3488 | 1217041.5382
27 | 2704484.0615 | 1217159.8184
28 | 2704484.5765 | 1217159.9061
29 | 2704506.8868 | 1217163.7028
30 | 2704382.0919 | 1217148.3077
31 | 2704582.4554 | 1217134.3832
32 | 2704575.2195 | 1217164.306
33 | 2704582.9925 | 1217132.162
34 | 2704572.6586 | 1217174.8959
35 | 2704596.9871 | 1217124.015
36 | 2704588.3588 | 1217177.5686
37 | 2704544.5518 | 1217170.1127
38 | 2704611.5326 | 1217181.5138
39 | 2704531.9939 | 1217167.9756
40 | 2704708.0182 | 1217331.6699
41 | 2704708.1912 | 1217330.047
42 | 2704723.29 | 1217369.6722
43 | 2704711.2405 | 1217305.87
44 | 2704714.1948 | 1217283.1462
45 | 2704757.9013 | 1217323.2225
46 | 2704772.3181 | 1217336.5098
47 | 2704704.4067 | 1217216.2832
48 | 2704700.0984 | 1217196.5934
49 | 2704631.5453 | 1217184.9213
50 | 2704447.7979 | 1217215.2302
51 | 2704460.9773 | 1217208.875
52 | 2704437.3703 | 1217220.2584
53 | 2704461.0169 | 1217208.8559
54 | 2704414.7385 | 1217226.4531
55 | 2704471.7567 | 1217203.722
56 | 2704391.1843 | 1217228.7334
57 | 2704491.917 | 1217195.2218
58 | 2704369.837 | 1217225.83
59 | 2704519.3232 | 1217165.8193
60 | 2704614.1412 | 1217181.958
61 | 2705126.214 | 1217742.0641
62 | 2705094.5238 | 1217711.7236
63 | 2704999.3427 | 1217889.7134
64 | 2704919.5538 | 1217633.4899
65 | 2705165.9951 | 1218042.4848
66 | 2705005.2506 | 1217467.6685
67 | 2704893.1204 | 1217704.6666
68 | 2704805.328 | 1217603.9921
69 | 2704267.7214 | 1217344.4276
70 | 2704456.0982 | 1217454.1306
71 | 2704762.7746 | 1217599.3809
72 | 2704442.1075 | 1217424.9533
73 | 2704409.2346 | 1217365.6046
74 | 2704330.4363 | 1217355.5561
75 | 2704309.1681 | 1217357.2542
76 | 2704795.2695 | 1217613.3997
77 | 2704306.291 | 1217333.884
78 | 2704300.7581 | 1217354.9275
79 | 2704304.309 | 1217317.7852
80 | 2704281.6939 | 1217349.648
81 | 2704141.3568 | 1217194.8133
82 | 2704149.674 | 1217192.7021
83 | 2704166.8404 | 1217188.3242
84 | 2704183.1506 | 1217183.7381
85 | 2704196.6701 | 1217179.9366
86 | 2704211.7486 | 1217177.5446
87 | 2704230.7587 | 1217174.5288
88 | 2704229.2502 | 1217098.4589
89 | 2704243.1355 | 1217114.0992
90 | 2704247.279 | 1217173.7839
91 | 2704252.632 | 1217173.5461
92 | 2704279.6735 | 1217172.3273
93 | 2704236.8906 | 1217254.1953
94 | 2704243.0767 | 1217244.7119
95 | 2704233.2676 | 1217259.8117
96 | 2704260.8881 | 1217219.6215
97 | 2704263.5603 | 1217269.6203
98 | 2704224.6942 | 1217283.7593
99 | 2704273.6434 | 1217211.19
100 | 2704275.2441 | 1217267.3628
101 | 2704231.4276 | 1217324.5965
102 | 2704292.9882 | 1217194.4181
103 | 2704293.5623 | 1217264.0987
104 | 2704232.8487 | 1217326.4196
105 | 2704303.9875 | 1217167.9274
106 | 2704325.802 | 1217196.3702
107 | 2704282.0215 | 1217171.9024
108 | 2704319.3583 | 1217164.316
109 | 2704304.5492 | 1217124.9624
110 | 2704301.82 | 1217117.7097
111 | 2704293.7485 | 1217095.9556
112 | 2704339.5714 | 1217159.1581
113 | 2704306.8341 | 1217065.0554
114 | 2704359.9141 | 1217153.967
115 | 2704340.1686 | 1217210.8203
116 | 2704363.7298 | 1217152.9933
117 | 2704364.3676 | 1217152.8306
118 | 2704367.1879 | 1217152.1109
119 | 2704381.4713 | 1217148.466
120 | 2704507.2688 | 1217190.3632
121 | 2704521.0723 | 1217189.256
122 | 2704525.2897 | 1217166.8346
123 | 2704324.8622 | 1217263.0966
124 | 2704342.1033 | 1217264.1244
125 | 2704322.9708 | 1217262.9838
126 | 2704251.779 | 1217337.2484
127 | 2704552.928 | 1217190.2541
128 | 2704556.1141 | 1217190.416
129 | 2704558.9702 | 1217190.5612
130 | 2704303.9875 | 1217167.9274

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97031 | -0.57588 | 0.0021164 | 0.00053042
1 | 0.97043 | -0.57342 | 0 | 0
2 | 0.97048 | -0.57242 | 0.0009724 | 0.00024371
3 | 0.97251 | -0.53227 | 0.00016872 | 4.2284e-05
4 | 0.9725 | -0.53261 | 0.00033994 | 8.5198e-05
5 | 0.97276 | -0.52725 | 0.0012188 | 0.00030545
6 | 0.97667 | -0.44974 | 0.00092698 | 0.00023232
7 | 0.97889 | -0.40578 | 0.00074307 | 0.00018623
8 | 0.97617 | -0.4597 | 0.00041499 | 0.00010401
9 | 0.97462 | -0.49026 | 0.00039076 | 9.7934e-05
10 | 0.97124 | -0.55742 | 0.0022502 | 0.00056395
11 | 0.97227 | -0.53728 | 0.00039184 | 9.8204e-05
12 | 0.97567 | -0.46991 | 8.5324e-05 | 2.1384e-05
13 | 0.97567 | -0.46987 | 0 | 0
14 | 0.981 | -0.3642 | 0.0013904 | 0.00034846
15 | 0.98134 | -0.3575 | 0.0010712 | 0.00026846
16 | 0.97477 | -0.4855 | 0.016407 | 0.004112
17 | 0.97607 | -0.45976 | 0.012768 | 0.0032001
18 | 0.97394 | -0.50173 | 0.017139 | 0.0042954
19 | 0.97637 | -0.45386 | 0 | 0
20 | 0.97349 | -0.51058 | 0.015596 | 0.0039086
21 | 0.97925 | -0.39757 | 0.0032919 | 0.00082504
22 | 0.97579 | -0.46532 | 0.058606 | 0.014688
23 | 0.97337 | -0.51299 | 0.003955 | 0.00099122
24 | 0.97928 | -0.39703 | 0.0021357 | 0.00053525
25 | 0.97487 | -0.48341 | 0.015205 | 0.0038106
26 | 0.97334 | -0.51366 | 0.00087903 | 0.00022031
27 | 0.97281 | -0.52404 | 0.014436 | 0.0036179
28 | 0.97279 | -0.52449 | 0.028809 | 0.0072201
29 | 0.9724 | -0.53206 | 0.0016581 | 0.00041557
30 | 0.97957 | -0.39129 | 0.0020915 | 0.00052419
31 | 0.97134 | -0.55311 | 0.00095782 | 0.00024005
32 | 0.97144 | -0.55115 | 0.0007339 | 0.00018393
33 | 0.97134 | -0.55321 | 0.0017043 | 0.00042713
34 | 0.97148 | -0.55031 | 0 | 0
35 | 0.97132 | -0.55348 | 0.00078348 | 0.00019636
36 | 0.97134 | -0.55318 | 0.00092228 | 0.00023115
37 | 0.97185 | -0.54296 | 0.00061408 | 0.0001539
38 | 0.97114 | -0.55703 | 0.0024717 | 0.00061946
39 | 0.97203 | -0.53953 | 0.00044824 | 0.00011234
40 | 0.97047 | -0.57045 | 0.00030353 | 7.6071e-05
41 | 0.97047 | -0.57044 | 0.00022368 | 5.6059e-05
42 | 0.97046 | -0.57067 | 0.00026881 | 6.7371e-05
43 | 0.97049 | -0.57008 | 0.0012724 | 0.00031888
44 | 0.97055 | -0.56887 | 0.00037517 | 9.4026e-05
45 | 0.97045 | -0.57079 | 0.00031191 | 7.8172e-05
46 | 0.97044 | -0.57097 | 0.00046624 | 0.00011685
47 | 0.97075 | -0.56474 | 0 | 0
48 | 0.97083 | -0.5632 | 0 | 0
49 | 0.97104 | -0.55904 | 0.0019895 | 0.00049861
50 | 0.99674 | -0.062532 | 0.00783 | 0.0019624
51 | 0.99573 | -0.082086 | 0.026323 | 0.0065971
52 | 0.99763 | -0.045501 | 0.0266 | 0.0066666
53 | 0.99573 | -0.082125 | 0.016093 | 0.0040333
54 | 1 | 0 | -0.47574 | -0.12179
55 | 0.99536 | -0.089177 | 0.021255 | 0.005327
56 | 0.99739 | -0.049064 | 0.001241 | 0.00031102
57 | 0.99512 | -0.093962 | 0.002117 | 0.00053057
58 | 0.99498 | -0.094601 | 0.0032769 | 0.00082127
59 | 0.97221 | -0.53589 | 0.0007379 | 0.00018494
60 | 0.97113 | -0.55734 | 0.0011583 | 0.00029029
61 | 0.97579 | -0.46742 | 0.00014118 | 3.5383e-05
62 | 0.97582 | -0.46691 | 5.6856e-05 | 1.425e-05
63 | 0.97571 | -0.46911 | 0.00030573 | 7.6623e-05
64 | 0.97593 | -0.46453 | 0.00016576 | 4.1543e-05
65 | 0.97568 | -0.46976 | 6.7149e-05 | 1.6829e-05
66 | 0.9759 | -0.46514 | 0.00017604 | 4.4119e-05
67 | 0.97592 | -0.46483 | 0.00021611 | 5.4161e-05
68 | 0.97607 | -0.46184 | 0.00046381 | 0.00011624
69 | 0.98158 | -0.35285 | 0.0013853 | 0.00034718
70 | 0.97896 | -0.40438 | 0.0023117 | 0.00057936
71 | 0.97615 | -0.46023 | 0.00011364 | 2.848e-05
72 | 0.9794 | -0.39561 | 0.0016193 | 0.00040583
73 | 0.9805 | -0.37389 | 0.0013905 | 0.00034849
74 | 0.98113 | -0.36153 | 0.00045242 | 0.00011339
75 | 0.98125 | -0.35916 | 0 | 0
76 | 0.97609 | -0.46139 | 0 | 0
77 | 0.98112 | -0.36174 | 0.0019556 | 0.00049012
78 | 0.98132 | -0.35792 | 0 | 0
79 | 0.98106 | -0.36294 | 0.004093 | 0.0010258
80 | 0.98146 | -0.35509 | 0.0011653 | 0.00029205
81 | 0.98261 | -0.33264 | 0.0065697 | 0.0016465
82 | 0.98266 | -0.33163 | 0 | 0
83 | 0.98277 | -0.32953 | 0.0027001 | 0.0006767
84 | 0.98291 | -0.32669 | 0.0019807 | 0.00049641
85 | 0.98306 | -0.32384 | 0 | 0
86 | 0.98322 | -0.32074 | 0.0034744 | 0.00087078
87 | 0.98348 | -0.31563 | 0 | 0
88 | 0.98317 | -0.32169 | 0.0034565 | 0.00086627
89 | 0.98324 | -0.3202 | 0.0043023 | 0.0010782
90 | 0.9837 | -0.31126 | 0 | 0
91 | 0.98381 | -0.30909 | 0.004259 | 0.0010674
92 | 0.98448 | -0.29606 | 0 | 0
93 | 0.98284 | -0.32805 | 0.0037502 | 0.0009399
94 | 0.98306 | -0.32377 | 0.0027464 | 0.00068832
95 | 0.98272 | -0.33043 | 0 | 0
96 | 0.98368 | -0.31164 | 0.0030996 | 0.00077683
97 | 0.98204 | -0.34374 | 0.0033601 | 0.00084213
98 | 0.98242 | -0.33622 | 0.0042704 | 0.0010703
99 | 0.984 | -0.30532 | 0.0034219 | 0.00085762
100 | 0.98184 | -0.3476 | 0.0073693 | 0.0018469
101 | 0.98196 | -0.34531 | 0.001044 | 0.00026165
102 | 0.98457 | -0.29424 | 0.0014395 | 0.00036077
103 | 0.98166 | -0.35116 | 0.0027426 | 0.00068737
104 | 0.98194 | -0.34577 | 0.0021826 | 0.00054702
105 | 0.98524 | -0.28125 | 0 | 0
106 | 0.98913 | -0.20624 | 0.0023841 | 0.00059751
107 | 0.98454 | -0.29491 | 0.0072937 | 0.001828
108 | 0.98407 | -0.30393 | 0 | 0
109 | 0.98374 | -0.31031 | 0.0010427 | 0.00026132
110 | 0.98369 | -0.31135 | 0.0035594 | 0.00089208
111 | 0.9836 | -0.31295 | 0.0013103 | 0.00032838
112 | 0.98257 | -0.333 | 0.0044799 | 0.0011228
113 | 0.98352 | -0.31465 | 0.0025154 | 0.00063041
114 | 0.98108 | -0.36178 | 0.0081507 | 0.0020428
115 | 0.99134 | -0.16392 | 0.001057 | 0.00026492
116 | 0.98082 | -0.36699 | 0.0039538 | 0.00099091
117 | 0.98077 | -0.36785 | 0.0010001 | 0.00025066
118 | 0.98058 | -0.37162 | 0.0027862 | 0.00069829
119 | 0.97961 | -0.39048 | 0.0020546 | 0.00051493
120 | 0.99496 | -0.096902 | 0.0018806 | 0.00047132
121 | 0.99486 | -0.098967 | 0.0018835 | 0.00047204
122 | 0.97212 | -0.53765 | 0.00073098 | 0.0001832
123 | 0.98144 | -0.35545 | 0.0022546 | 0.00056504
124 | 0.98143 | -0.35572 | 0.00086232 | 0.00021612
125 | 0.98145 | -0.35534 | 0.0047105 | 0.0011806
126 | 0.98173 | -0.34982 | 0.0015835 | 0.00039686
127 | 0.99467 | -0.10264 | 0.002011 | 0.00050401
128 | 0.99465 | -0.1029 | 0.0021913 | 0.0005492
129 | 0.99465 | -0.10302 | 0.0023441 | 0.00058748
130 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0021164 | -0.00053042 | 0.0021166 | 0.0005298 | 2.4855e-07 | -6.1828e-07 | 0.0032456 | 0.0032453 | 0.0032456 | 0.97031 | -0.57588 | 0.97043 | -0.57342 | 0.89164
1 | -0.0021166 | -0.0005298 | 0.0021167 | 0.00052955 | 1.0083e-07 | -2.5093e-07 | 0.0032453 | 0.0032452 | 0.0032453 | 0.97043 | -0.57342 | 0.97048 | -0.57242 | 0.89157
2 | -0.0030891 | -0.00077325 | 0.0030913 | 0.00077142 | 2.2037e-06 | -1.8301e-06 | 0.0047362 | 0.004735 | 0.0047362 | 0.97048 | -0.57242 | 0.97124 | -0.55742 | 1.3011
3 | 0.00073188 | 0.00017534 | -0.00073187 | -0.00017563 | 1.1449e-08 | -2.9628e-07 | 0.001117 | 0.0011171 | 0.0011171 | 0.97251 | -0.53227 | 0.9725 | -0.53261 | 0.30689
4 | -0.00090059 | -0.00021762 | 0.0009008 | 0.00021411 | 2.0824e-07 | -3.5149e-06 | 0.0013751 | 0.0013738 | 0.0013751 | 0.97251 | -0.53227 | 0.97276 | -0.52725 | 0.37778
5 | 0.00039192 | 9.0434e-05 | -0.00039184 | -9.8204e-05 | 8.4662e-08 | -7.7693e-06 | 0.00059697 | 0.00059969 | 0.00059969 | 0.9725 | -0.53261 | 0.97227 | -0.53728 | 0.16475
6 | -0.0074688 | -0.0018561 | 0.0074819 | 0.0018611 | 1.3096e-05 | 5.0501e-06 | 0.011419 | 0.011418 | 0.011419 | 0.97276 | -0.52725 | 0.97462 | -0.49026 | 3.1371
7 | 0.0053492 | 0.0013365 | -0.0053415 | -0.0013354 | 7.6643e-06 | 1.1209e-06 | 0.0081811 | 0.0081825 | 0.0081825 | 0.97276 | -0.52725 | 0.97124 | -0.55742 | 2.2479
8 | -0.011023 | -0.0027335 | 0.011046 | 0.0027455 | 2.2947e-05 | 1.1961e-05 | 0.016784 | 0.016783 | 0.016784 | 0.97667 | -0.44974 | 0.97889 | -0.40578 | 4.6109
9 | 0.0022081 | 0.00053598 | -0.002207 | -0.00053836 | 1.0245e-06 | -2.3739e-06 | 0.003358 | 0.003359 | 0.003359 | 0.97667 | -0.44974 | 0.97617 | -0.4597 | 0.92281
10 | 0.0078878 | 0.0019652 | -0.0078726 | -0.001959 | 1.5134e-05 | 6.1941e-06 | 0.012013 | 0.012015 | 0.012015 | 0.97667 | -0.44974 | 0.97462 | -0.49026 | 3.3007
11 | -0.011789 | -0.0029317 | 0.01179 | 0.0029321 | 7.8115e-07 | 4.1832e-07 | 0.017912 | 0.017912 | 0.017912 | 0.97889 | -0.40578 | 0.97896 | -0.40438 | 4.9209
12 | 0.001792 | 0.00043435 | -0.001792 | -0.00043452 | 4.4379e-08 | -1.7061e-07 | 0.0027264 | 0.0027265 | 0.0027265 | 0.97617 | -0.4597 | 0.97615 | -0.46023 | 0.74904
13 | -8.5324e-05 | -2.1384e-05 | 8.5324e-05 | 2.1086e-05 | 1.5154e-10 | -2.982e-07 | 0.00013013 | 0.00013002 | 0.00013013 | 0.97567 | -0.46991 | 0.97567 | -0.46987 | 0.03575
14 | -8.5324e-05 | -2.1086e-05 | 8.5324e-05 | 2.0245e-05 | 4.2588e-10 | -8.4059e-07 | 0.00013002 | 0.00012973 | 0.00013002 | 0.97567 | -0.46987 | 0.97568 | -0.46976 | 0.03572
15 | -0.0013904 | -0.00034846 | 0.0013908 | 0.00034538 | 4.4262e-07 | -3.0704e-06 | 0.0021089 | 0.0021077 | 0.0021089 | 0.981 | -0.3642 | 0.98134 | -0.3575 | 0.57938
16 | -0.002462 | -0.00061385 | 0.0024625 | 0.00061288 | 5.4252e-07 | -9.6563e-07 | 0.003732 | 0.0037315 | 0.003732 | 0.98134 | -0.3575 | 0.98158 | -0.35285 | 1.0253
17 | -0.054014 | -0.013551 | 0.05408 | 0.013593 | 6.6373e-05 | 4.2154e-05 | 0.082459 | 0.082459 | 0.082459 | 0.97477 | -0.4855 | 0.97607 | -0.45976 | 22.6537
18 | 0.037607 | 0.0094386 | -0.037578 | -0.0094203 | 2.9077e-05 | 1.8316e-05 | 0.057413 | 0.057413 | 0.057413 | 0.97477 | -0.4855 | 0.97394 | -0.50173 | 15.7729
19 | -0.066849 | -0.016793 | 0.066868 | 0.016805 | 1.8824e-05 | 1.1987e-05 | 0.10192 | 0.10192 | 0.10192 | 0.97607 | -0.45976 | 0.97637 | -0.45386 | 28.0012
20 | 0.020439 | 0.0051249 | -0.02043 | -0.0051197 | 8.6184e-06 | 5.2226e-06 | 0.031228 | 0.031228 | 0.031228 | 0.97394 | -0.50173 | 0.97349 | -0.51058 | 8.5791
21 | -0.20234 | -0.050861 | 0.20289 | 0.051209 | 0.00054546 | 0.00034833 | 0.30843 | 0.30843 | 0.30843 | 0.97637 | -0.45386 | 0.97925 | -0.39757 | 42.3662
22 | 0.13547 | 0.034056 | -0.1354 | -0.034009 | 7.4074e-05 | 4.7176e-05 | 0.2065 | 0.2065 | 0.2065 | 0.97637 | -0.45386 | 0.97579 | -0.46532 | 28.3656
23 | 0.0048346 | 0.001211 | -0.0048341 | -0.001211 | 5.555e-07 | 1.8292e-08 | 0.0073896 | 0.0073897 | 0.0073897 | 0.97349 | -0.51058 | 0.97337 | -0.51299 | 2.0302
24 | -0.20618 | -0.052034 | 0.20618 | 0.052038 | 5.369e-06 | 3.4196e-06 | 0.31343 | 0.31343 | 0.31343 | 0.97925 | -0.39757 | 0.97928 | -0.39703 | 28.7022
25 | 0.076793 | 0.019321 | -0.076726 | -0.019279 | 6.6316e-05 | 4.1799e-05 | 0.11713 | 0.11713 | 0.11713 | 0.97579 | -0.46532 | 0.97487 | -0.48341 | 16.0894
26 | 0.00087906 | 0.00021981 | -0.00087903 | -0.00022031 | 2.7897e-08 | -4.9423e-07 | 0.0013437 | 0.0013438 | 0.0013438 | 0.97337 | -0.51299 | 0.97334 | -0.51366 | 0.36919
27 | -0.20832 | -0.052573 | 0.20838 | 0.052609 | 5.7266e-05 | 3.6477e-05 | 0.31667 | 0.31667 | 0.31667 | 0.97928 | -0.39703 | 0.97957 | -0.39129 | 28.9993
28 | 0.061522 | 0.015468 | -0.061403 | -0.015392 | 0.00011911 | 7.578e-05 | 0.093923 | 0.093923 | 0.093923 | 0.97487 | -0.48341 | 0.97281 | -0.52404 | 25.8031
29 | 0.046967 | 0.011775 | -0.046966 | -0.011774 | 1.011e-06 | 6.4055e-07 | 0.071842 | 0.071842 | 0.071842 | 0.97281 | -0.52404 | 0.97279 | -0.52449 | 19.7369
30 | 0.018157 | 0.0045538 | -0.018151 | -0.0045499 | 6.5472e-06 | 3.9094e-06 | 0.027775 | 0.027775 | 0.027775 | 0.97279 | -0.52449 | 0.9724 | -0.53206 | 7.6306
31 | 0.016493 | 0.0041343 | -0.01649 | -0.0041326 | 3.0133e-06 | 1.7721e-06 | 0.025238 | 0.025238 | 0.025238 | 0.9724 | -0.53206 | 0.97221 | -0.53589 | 6.9336
32 | -0.21047 | -0.053134 | 0.21048 | 0.053139 | 8.1901e-06 | 5.2175e-06 | 0.31985 | 0.31985 | 0.31985 | 0.97957 | -0.39129 | 0.97961 | -0.39048 | 29.2903
33 | -0.0034456 | -0.0008633 | 0.0034459 | 0.00086313 | 3.2162e-07 | -1.7526e-07 | 0.0052783 | 0.0052782 | 0.0052783 | 0.97134 | -0.55311 | 0.97144 | -0.55115 | 1.4501
34 | 0.0024878 | 0.00062325 | -0.0024878 | -0.00062327 | 1.2446e-08 | -2.032e-08 | 0.003811 | 0.003811 | 0.003811 | 0.97134 | -0.55311 | 0.97134 | -0.55321 | 1.047
35 | -0.0041798 | -0.0010471 | 0.00418 | 0.001047 | 1.6747e-07 | -2.7714e-08 | 0.0064023 | 0.0064023 | 0.0064023 | 0.97144 | -0.55115 | 0.97148 | -0.55031 | 1.7589
36 | 0.00078349 | 0.00019614 | -0.00078348 | -0.00019636 | 9.9494e-09 | -2.2161e-07 | 0.0012002 | 0.0012002 | 0.0012002 | 0.97134 | -0.55321 | 0.97132 | -0.55348 | 0.32974
37 | 0.0097686 | 0.0024455 | -0.0097672 | -0.0024448 | 1.3369e-06 | 6.5843e-07 | 0.014961 | 0.014962 | 0.014962 | 0.97148 | -0.55031 | 0.97134 | -0.55318 | 4.1103
38 | -0.013949 | -0.0034925 | 0.013953 | 0.0034953 | 4.8797e-06 | 2.7699e-06 | 0.021364 | 0.021364 | 0.021364 | 0.97148 | -0.55031 | 0.97185 | -0.54296 | 5.8692
39 | 0.0088449 | 0.0022137 | -0.0088433 | -0.0022129 | 1.6182e-06 | 7.4473e-07 | 0.013549 | 0.013549 | 0.013549 | 0.97134 | -0.55318 | 0.97114 | -0.55703 | 3.7222
40 | -0.014567 | -0.0036492 | 0.01457 | 0.0036505 | 2.3763e-06 | 1.363e-06 | 0.022304 | 0.022304 | 0.022304 | 0.97185 | -0.54296 | 0.97203 | -0.53953 | 6.1274
41 | 0.0063716 | 0.0015935 | -0.0063715 | -0.0015934 | 9.4555e-08 | 2.7775e-08 | 0.0097616 | 0.0097616 | 0.0097616 | 0.97114 | -0.55703 | 0.97113 | -0.55734 | 2.6818
42 | -0.015018 | -0.0037629 | 0.015019 | 0.0037636 | 1.3479e-06 | 7.7834e-07 | 0.02299 | 0.02299 | 0.02299 | 0.97203 | -0.53953 | 0.97212 | -0.53765 | 6.3159
43 | -0.00057234 | -0.0001429 | 0.00057234 | 0.00014288 | 4.7117e-10 | -1.9865e-08 | 0.00087738 | 0.00087737 | 0.00087738 | 0.97047 | -0.57045 | 0.97047 | -0.57044 | 0.24104
44 | 0.00026882 | 6.6826e-05 | -0.00026881 | -6.7371e-05 | 2.8184e-09 | -5.4507e-07 | 0.00041198 | 0.00041218 | 0.00041218 | 0.97047 | -0.57045 | 0.97046 | -0.57067 | 0.11324
45 | -0.00079602 | -0.00019894 | 0.00079603 | 0.00019864 | 1.3608e-08 | -2.924e-07 | 0.0012203 | 0.0012202 | 0.0012203 | 0.97047 | -0.57044 | 0.97049 | -0.57008 | 0.33526
46 | -0.0028466 | -0.0007117 | 0.0028467 | 0.00071153 | 1.6364e-07 | -1.7843e-07 | 0.0043639 | 0.0043638 | 0.0043639 | 0.97049 | -0.57008 | 0.97055 | -0.56887 | 1.1989
47 | 0.00077818 | 0.00019418 | -0.00077815 | -0.00019478 | 2.6568e-08 | -5.9811e-07 | 0.0011928 | 0.0011931 | 0.0011931 | 0.97049 | -0.57008 | 0.97045 | -0.57079 | 0.32777
48 | -0.0032219 | -0.00080555 | 0.0032225 | 0.0008051 | 6.3207e-07 | -4.4959e-07 | 0.004939 | 0.0049387 | 0.004939 | 0.97055 | -0.56887 | 0.97075 | -0.56474 | 1.3569
49 | 0.00046624 | 0.00011661 | -0.00046624 | -0.00011685 | 3.8255e-09 | -2.442e-07 | 0.00071481 | 0.0007149 | 0.0007149 | 0.97045 | -0.57079 | 0.97044 | -0.57097 | 0.1964
50 | -0.0032225 | -0.0008051 | 0.0032228 | 0.00080493 | 2.365e-07 | -1.6834e-07 | 0.0049387 | 0.0049386 | 0.0049387 | 0.97075 | -0.56474 | 0.97083 | -0.5632 | 1.3568
51 | -0.0032228 | -0.00080493 | 0.0032234 | 0.00080448 | 6.3598e-07 | -4.5302e-07 | 0.0049386 | 0.0049383 | 0.0049386 | 0.97083 | -0.5632 | 0.97104 | -0.55904 | 1.3568
52 | -0.0052129 | -0.0013031 | 0.0052133 | 0.0013031 | 4.2233e-07 | 5.1872e-08 | 0.0079869 | 0.0079869 | 0.0079869 | 0.97104 | -0.55904 | 0.97113 | -0.55734 | 2.1942
53 | 0.076187 | 0.019127 | -0.076116 | -0.019082 | 7.0994e-05 | 4.5245e-05 | 0.11375 | 0.11375 | 0.11375 | 0.99674 | -0.062532 | 0.99573 | -0.082086 | 31.2497
54 | -0.084017 | -0.02109 | 0.084085 | 0.021133 | 6.8308e-05 | 4.3566e-05 | 0.12544 | 0.12544 | 0.12544 | 0.99674 | -0.062532 | 0.99763 | -0.045501 | 34.461
55 | 0.049793 | 0.012485 | -0.049793 | -0.012485 | 9.1227e-08 | 5.7817e-08 | 0.074412 | 0.074412 | 0.074412 | 0.99573 | -0.082086 | 0.99573 | -0.082125 | 20.443
56 | -0.11068 | -0.0278 | 0.11093 | 0.027954 | 0.00024089 | 0.00015386 | 0.16511 | 0.16511 | 0.16511 | 0.99763 | -0.045501 | 1 | 0 | 45.3608
57 | 0.0337 | 0.0084516 | -0.033689 | -0.0084445 | 1.1323e-05 | 7.0922e-06 | 0.050363 | 0.050363 | 0.050363 | 0.99573 | -0.082125 | 0.99536 | -0.089177 | 13.836
58 | 0.36316 | 0.093833 | -0.3623 | -0.093279 | 0.00086705 | 0.00055398 | 0.5414 | 0.5414 | 0.5414 | 1 | 0 | 0.99739 | -0.049064 | 49.5785
59 | 0.012434 | 0.0031175 | -0.012431 | -0.003116 | 2.835e-06 | 1.5301e-06 | 0.018588 | 0.018588 | 0.018588 | 0.99536 | -0.089177 | 0.99512 | -0.093962 | 5.1067
60 | 0.36106 | 0.092968 | -0.36026 | -0.092458 | 0.000798 | 0.00050986 | 0.53955 | 0.53955 | 0.53955 | 0.99739 | -0.049064 | 0.99498 | -0.094601 | 49.409
61 | 0.010314 | 0.0025854 | -0.010313 | -0.0025847 | 1.4444e-06 | 7.1407e-07 | 0.015423 | 0.015423 | 0.015423 | 0.99512 | -0.093962 | 0.99496 | -0.096902 | 4.2371
62 | 0.35698 | 0.091637 | -0.35579 | -0.090872 | 0.0011967 | 0.00076458 | 0.53465 | 0.53465 | 0.53465 | 0.99498 | -0.094601 | 0.99134 | -0.16392 | 48.9603
63 | 0.015752 | 0.0039476 | -0.01575 | -0.0039468 | 1.3192e-06 | 7.6922e-07 | 0.024109 | 0.024109 | 0.024109 | 0.97221 | -0.53589 | 0.97212 | -0.53765 | 6.6233
64 | -0.00059942 | -0.00014385 | 0.00059943 | 0.00014329 | 1.4296e-08 | -5.6375e-07 | 0.00091183 | 0.00091163 | 0.00091183 | 0.97579 | -0.46742 | 0.97582 | -0.46691 | 0.2505
65 | 0.00045824 | 0.00010847 | -0.00045821 | -0.00011088 | 3.5462e-08 | -2.4089e-06 | 0.00069655 | 0.00069739 | 0.00069739 | 0.97579 | -0.46742 | 0.97571 | -0.46911 | 0.19159
66 | -0.00065629 | -0.00015754 | 0.00065636 | 0.00015519 | 7.1574e-08 | -2.3488e-06 | 0.00099832 | 0.0009975 | 0.00099832 | 0.97582 | -0.46691 | 0.97593 | -0.46453 | 0.27426
67 | 0.00015248 | 3.4254e-05 | -0.00015247 | -3.7075e-05 | 4.5494e-09 | -2.8207e-06 | 0.00023118 | 0.00023213 | 0.00023213 | 0.97571 | -0.46911 | 0.97568 | -0.46976 | 0.063773
68 | 0.00017604 | 4.179e-05 | -0.00017604 | -4.4119e-05 | 5.0274e-09 | -2.3291e-06 | 0.0002676 | 0.00026842 | 0.00026842 | 0.97593 | -0.46453 | 0.9759 | -0.46514 | 0.07374
69 | 0.00021611 | 5.3215e-05 | -0.00021611 | -5.4161e-05 | 3.0881e-09 | -9.4674e-07 | 0.00032917 | 0.0003295 | 0.0003295 | 0.97593 | -0.46453 | 0.97592 | -0.46483 | 0.090523
70 | -0.0012143 | -0.00029173 | 0.0012144 | 0.00029036 | 1.5087e-07 | -1.3778e-06 | 0.001847 | 0.0018465 | 0.001847 | 0.97593 | -0.46453 | 0.97607 | -0.46184 | 0.50741
71 | -0.0016782 | -0.0004066 | 0.0016783 | 0.00040644 | 3.4639e-08 | -1.549e-07 | 0.0025535 | 0.0025535 | 0.0025535 | 0.97607 | -0.46184 | 0.97609 | -0.46139 | 0.70152
72 | 0.02482 | 0.0062079 | -0.024817 | -0.0062068 | 2.6465e-06 | 1.1266e-06 | 0.037621 | 0.037621 | 0.037621 | 0.98158 | -0.35285 | 0.98146 | -0.35509 | 3.4452
73 | -0.028668 | -0.007168 | 0.028672 | 0.00717 | 4.1265e-06 | 1.9779e-06 | 0.043452 | 0.043452 | 0.043452 | 0.98158 | -0.35285 | 0.98173 | -0.34982 | 3.9792
74 | -0.014101 | -0.0035115 | 0.014107 | 0.0035148 | 5.8638e-06 | 3.3244e-06 | 0.021426 | 0.021426 | 0.021426 | 0.97896 | -0.40438 | 0.9794 | -0.39561 | 5.8862
75 | 0.0016784 | 0.00040604 | -0.0016783 | -0.00040644 | 9.0316e-08 | -4.0396e-07 | 0.0025533 | 0.0025535 | 0.0025535 | 0.97615 | -0.46023 | 0.97609 | -0.46139 | 0.7015
76 | -0.015726 | -0.0039207 | 0.015743 | 0.0039301 | 1.6226e-05 | 9.4294e-06 | 0.023886 | 0.023886 | 0.023886 | 0.9794 | -0.39561 | 0.9805 | -0.37389 | 6.5621
77 | -0.017133 | -0.0042786 | 0.017143 | 0.004283 | 1.0065e-05 | 4.4365e-06 | 0.025996 | 0.025995 | 0.025996 | 0.9805 | -0.37389 | 0.98113 | -0.36153 | 3.5709
78 | -0.017596 | -0.0043964 | 0.017598 | 0.0043968 | 1.9779e-06 | 4.2363e-07 | 0.026681 | 0.026681 | 0.026681 | 0.98113 | -0.36153 | 0.98125 | -0.35916 | 2.4433
79 | 0.0060496 | 0.0015161 | -0.0060489 | -0.0015159 | 7.4314e-07 | 1.7821e-07 | 0.0091739 | 0.009174 | 0.009174 | 0.98125 | -0.35916 | 0.98112 | -0.36174 | 2.5203
80 | -0.023647 | -0.0059129 | 0.023649 | 0.0059135 | 1.3984e-06 | 5.6516e-07 | 0.035855 | 0.035855 | 0.035855 | 0.98125 | -0.35916 | 0.98132 | -0.35792 | 3.2834
81 | 0.0040933 | 0.0010258 | -0.004093 | -0.0010258 | 2.3443e-07 | -5.4797e-08 | 0.006208 | 0.0062081 | 0.0062081 | 0.98112 | -0.36174 | 0.98106 | -0.36294 | 1.7055
82 | -0.023649 | -0.0059135 | 0.023652 | 0.0059147 | 3.1788e-06 | 1.2846e-06 | 0.035855 | 0.035854 | 0.035855 | 0.98132 | -0.35792 | 0.98146 | -0.35509 | 3.2834
83 | -0.0065697 | -0.0016465 | 0.0065701 | 0.0016466 | 3.185e-07 | 9.5143e-08 | 0.0099489 | 0.0099489 | 0.0099489 | 0.98261 | -0.33264 | 0.98266 | -0.33163 | 2.7332
84 | -0.0065701 | -0.0016466 | 0.0065707 | 0.0016468 | 6.5757e-07 | 1.9639e-07 | 0.0099489 | 0.0099488 | 0.0099489 | 0.98266 | -0.33163 | 0.98277 | -0.32953 | 2.7332
85 | -0.0092708 | -0.0023235 | 0.009272 | 0.0023241 | 1.2519e-06 | 5.8648e-07 | 0.014037 | 0.014037 | 0.014037 | 0.98277 | -0.32953 | 0.98291 | -0.32669 | 3.8563
86 | -0.011253 | -0.0028205 | 0.011254 | 0.0028213 | 1.5283e-06 | 8.0011e-07 | 0.017035 | 0.017035 | 0.017035 | 0.98291 | -0.32669 | 0.98306 | -0.32384 | 4.6801
87 | -0.011254 | -0.0028213 | 0.011256 | 0.0028222 | 1.6615e-06 | 8.6974e-07 | 0.017035 | 0.017035 | 0.017035 | 0.98306 | -0.32384 | 0.98322 | -0.32074 | 4.68
88 | -0.01473 | -0.003693 | 0.014734 | 0.003695 | 3.5873e-06 | 2.0517e-06 | 0.022294 | 0.022294 | 0.022294 | 0.98322 | -0.32074 | 0.98348 | -0.31563 | 6.1246
89 | -0.014734 | -0.003695 | 0.014737 | 0.0036968 | 3.0729e-06 | 1.7574e-06 | 0.022294 | 0.022293 | 0.022294 | 0.98348 | -0.31563 | 0.9837 | -0.31126 | 6.1246
90 | -0.0034565 | -0.00086627 | 0.0034567 | 0.00086612 | 2.4479e-07 | -1.4585e-07 | 0.0052313 | 0.0052312 | 0.0052313 | 0.98317 | -0.32169 | 0.98324 | -0.3202 | 1.4372
91 | -0.007759 | -0.0019444 | 0.0077623 | 0.0019457 | 3.3061e-06 | 1.3045e-06 | 0.011742 | 0.011742 | 0.011742 | 0.98324 | -0.3202 | 0.9837 | -0.31126 | 3.2259
92 | -0.022499 | -0.0056425 | 0.022502 | 0.0056439 | 2.3276e-06 | 1.4217e-06 | 0.034035 | 0.034035 | 0.034035 | 0.9837 | -0.31126 | 0.98381 | -0.30909 | 9.3504
93 | -0.026761 | -0.0067113 | 0.026777 | 0.0067216 | 1.6631e-05 | 1.03e-05 | 0.040477 | 0.040477 | 0.040477 | 0.98381 | -0.30909 | 0.98448 | -0.29606 | 11.1201
94 | -0.026777 | -0.0067216 | 0.026779 | 0.0067225 | 1.466e-06 | 9.079e-07 | 0.040477 | 0.040477 | 0.040477 | 0.98448 | -0.29606 | 0.98454 | -0.29491 | 11.12
95 | -0.06286 | -0.015756 | 0.062873 | 0.015764 | 1.2819e-05 | 7.7737e-06 | 0.09517 | 0.09517 | 0.09517 | 0.98284 | -0.32805 | 0.98306 | -0.32377 | 8.7152
96 | 0.05911 | 0.014816 | -0.059103 | -0.014812 | 6.6912e-06 | 4.0283e-06 | 0.089493 | 0.089493 | 0.089493 | 0.98284 | -0.32805 | 0.98272 | -0.33043 | 8.1953
97 | -0.065619 | -0.016452 | 0.065657 | 0.016475 | 3.7965e-05 | 2.3126e-05 | 0.099327 | 0.099327 | 0.099327 | 0.98306 | -0.32377 | 0.98368 | -0.31164 | 9.0959
98 | 0.02132 | 0.0053496 | -0.021306 | -0.0053414 | 1.3525e-05 | 8.2178e-06 | 0.032284 | 0.032284 | 0.032284 | 0.98272 | -0.33043 | 0.98204 | -0.34374 | 8.8693
99 | 0.037784 | 0.0094623 | -0.037773 | -0.0094566 | 1.0419e-05 | 5.7003e-06 | 0.057209 | 0.057209 | 0.057209 | 0.98272 | -0.33043 | 0.98242 | -0.33622 | 5.2389
100 | -0.068757 | -0.017252 | 0.068778 | 0.017265 | 2.0708e-05 | 1.267e-05 | 0.10402 | 0.10402 | 0.10402 | 0.98368 | -0.31164 | 0.984 | -0.30532 | 9.5253
101 | 0.017946 | 0.0044993 | -0.017943 | -0.0044973 | 3.2998e-06 | 1.9613e-06 | 0.027193 | 0.027193 | 0.027193 | 0.98204 | -0.34374 | 0.98184 | -0.3476 | 7.4706
102 | 0.033503 | 0.0083863 | -0.033488 | -0.0083787 | 1.4497e-05 | 7.5677e-06 | 0.050741 | 0.050742 | 0.050742 | 0.98242 | -0.33622 | 0.98196 | -0.34531 | 4.6467
103 | -0.0722 | -0.018122 | 0.072238 | 0.018146 | 3.8183e-05 | 2.346e-05 | 0.10919 | 0.10919 | 0.10919 | 0.984 | -0.30532 | 0.98457 | -0.29424 | 9.9991
104 | 0.010573 | 0.0026504 | -0.010572 | -0.0026495 | 1.7926e-06 | 9.1187e-07 | 0.016025 | 0.016025 | 0.016025 | 0.98184 | -0.3476 | 0.98166 | -0.35116 | 4.4024
105 | 0.032444 | 0.0081171 | -0.032444 | -0.0081167 | 6.9828e-07 | 3.5918e-07 | 0.04916 | 0.04916 | 0.04916 | 0.98196 | -0.34531 | 0.98194 | -0.34577 | 4.5018
106 | -0.073677 | -0.018506 | 0.073723 | 0.018534 | 4.5682e-05 | 2.8112e-05 | 0.11137 | 0.11137 | 0.11137 | 0.98457 | -0.29424 | 0.98524 | -0.28125 | 10.1983
107 | 0.007829 | 0.0019621 | -0.0078274 | -0.0019615 | 1.5598e-06 | 6.2498e-07 | 0.011867 | 0.011867 | 0.011867 | 0.98166 | -0.35116 | 0.98145 | -0.35534 | 3.2603
108 | 0.030261 | 0.0075697 | -0.030255 | -0.0075668 | 5.8415e-06 | 2.8952e-06 | 0.045852 | 0.045852 | 0.045852 | 0.98194 | -0.34577 | 0.98173 | -0.34982 | 4.1989
109 | -0.35035 | -0.088737 | 0.35162 | 0.089547 | 0.0012672 | 0.0008096 | 0.52947 | 0.52947 | 0.52947 | 0.98524 | -0.28125 | 0.98913 | -0.20624 | 48.4866
110 | 0.034095 | 0.0085644 | -0.034072 | -0.0085505 | 2.2202e-05 | 1.3925e-05 | 0.0515 | 0.0515 | 0.0515 | 0.98524 | -0.28125 | 0.98454 | -0.29491 | 14.1485
111 | 0.24254 | 0.061639 | -0.24227 | -0.06147 | 0.00026454 | 0.0001687 | 0.36661 | 0.36661 | 0.36661 | 0.98524 | -0.28125 | 0.98407 | -0.30393 | 33.5723
112 | -0.354 | -0.090145 | 0.35473 | 0.090607 | 0.00072411 | 0.00046265 | 0.53306 | 0.53306 | 0.53306 | 0.98913 | -0.20624 | 0.99134 | -0.16392 | 48.815
113 | 0.23384 | 0.059357 | -0.23351 | -0.059149 | 0.00032652 | 0.00020818 | 0.35386 | 0.35386 | 0.35386 | 0.98407 | -0.30393 | 0.98257 | -0.333 | 32.4048
114 | 0.0084312 | 0.002113 | -0.0084286 | -0.0021119 | 2.5628e-06 | 1.1062e-06 | 0.012749 | 0.012749 | 0.012749 | 0.98407 | -0.30393 | 0.98374 | -0.31031 | 3.5025
115 | 0.0073859 | 0.0018506 | -0.0073856 | -0.0018504 | 3.6269e-07 | 1.3374e-07 | 0.011172 | 0.011172 | 0.011172 | 0.98374 | -0.31031 | 0.98369 | -0.31135 | 3.0692
116 | 0.0038261 | 0.00095834 | -0.0038258 | -0.00095845 | 2.9151e-07 | -1.0802e-07 | 0.0057876 | 0.0057877 | 0.0057877 | 0.98369 | -0.31135 | 0.9836 | -0.31295 | 1.59
117 | 0.0025156 | 0.00063007 | -0.0025154 | -0.00063041 | 2.0447e-07 | -3.4697e-07 | 0.0038055 | 0.0038056 | 0.0038056 | 0.9836 | -0.31295 | 0.98352 | -0.31465 | 1.0455
118 | 0.22903 | 0.058026 | -0.22872 | -0.057824 | 0.00031613 | 0.00020153 | 0.34708 | 0.34708 | 0.34708 | 0.98257 | -0.333 | 0.98108 | -0.36178 | 31.7836
119 | 0.22057 | 0.055782 | -0.22051 | -0.055747 | 5.5147e-05 | 3.5145e-05 | 0.33471 | 0.33471 | 0.33471 | 0.98108 | -0.36178 | 0.98082 | -0.36699 | 30.6515
120 | 0.21656 | 0.054756 | -0.21655 | -0.05475 | 8.8907e-06 | 5.6651e-06 | 0.32872 | 0.32872 | 0.32872 | 0.98082 | -0.36699 | 0.98077 | -0.36785 | 30.1022
121 | 0.21555 | 0.054499 | -0.21551 | -0.054474 | 3.8953e-05 | 2.482e-05 | 0.3272 | 0.3272 | 0.3272 | 0.98077 | -0.36785 | 0.98058 | -0.37162 | 29.9632
122 | 0.21272 | 0.053776 | -0.21253 | -0.053654 | 0.00019221 | 0.00012245 | 0.32297 | 0.32297 | 0.32297 | 0.98058 | -0.37162 | 0.97961 | -0.39048 | 29.5761
123 | 0.0084319 | 0.0021134 | -0.0084311 | -0.002113 | 8.2939e-07 | 3.502e-07 | 0.01261 | 0.01261 | 0.01261 | 0.99496 | -0.096902 | 0.99486 | -0.098967 | 3.4644
124 | 0.0065476 | 0.001641 | -0.0065465 | -0.0016407 | 1.1466e-06 | 3.1997e-07 | 0.0097933 | 0.0097935 | 0.0097935 | 0.99486 | -0.098967 | 0.99467 | -0.10264 | 2.6905
125 | 0.00086233 | 0.00021591 | -0.00086232 | -0.00021612 | 1.1071e-08 | -2.1117e-07 | 0.0013074 | 0.0013074 | 0.0013074 | 0.98144 | -0.35545 | 0.98143 | -0.35572 | 0.35918
126 | -0.0031169 | -0.00078095 | 0.0031169 | 0.00078094 | 1.5868e-08 | -1.379e-08 | 0.0047256 | 0.0047256 | 0.0047256 | 0.98144 | -0.35545 | 0.98145 | -0.35534 | 1.2982
127 | 0.0045355 | 0.0011366 | -0.0045354 | -0.0011366 | 5.5075e-08 | -6.1594e-09 | 0.006785 | 0.006785 | 0.006785 | 0.99467 | -0.10264 | 0.99465 | -0.1029 | 1.864
128 | 0.0023441 | 0.00058745 | -0.0023441 | -0.00058748 | 1.3188e-08 | -2.8678e-08 | 0.0035068 | 0.0035068 | 0.0035068 | 0.99465 | -0.1029 | 0.99465 | -0.10302 | 0.9634

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47775 | 0.12229

## res_load
| p_mw | q_mvar
0 | 0.0021164 | 0.00053042
1 | 0.0009724 | 0.00024371
2 | 0.00016872 | 4.2284e-05
3 | 0.00033994 | 8.5198e-05
4 | 0.0012188 | 0.00030545
5 | 0.00092698 | 0.00023232
6 | 0.00074307 | 0.00018623
7 | 0.00041499 | 0.00010401
8 | 0.00039076 | 9.7934e-05
9 | 0.0022502 | 0.00056395
10 | 0.00039184 | 9.8204e-05
11 | 8.5324e-05 | 2.1384e-05
12 | 0.0013904 | 0.00034846
13 | 0.0010712 | 0.00026846
14 | 0.016407 | 0.004112
15 | 0.012768 | 0.0032001
16 | 0.017139 | 0.0042954
17 | 0.015596 | 0.0039086
18 | 0.0032919 | 0.00082504
19 | 0.058606 | 0.014688
20 | 0.003955 | 0.00099122
21 | 0.0021357 | 0.00053525
22 | 0.015205 | 0.0038106
23 | 0.00087903 | 0.00022031
24 | 0.014436 | 0.0036179
25 | 0.028809 | 0.0072201
26 | 0.0016581 | 0.00041557
27 | 0.0020915 | 0.00052419
28 | 0.00095782 | 0.00024005
29 | 0.0007339 | 0.00018393
30 | 0.0017043 | 0.00042713
31 | 0.00078348 | 0.00019636
32 | 0.00092228 | 0.00023115
33 | 0.00061408 | 0.0001539
34 | 0.0024717 | 0.00061946
35 | 0.00044824 | 0.00011234
36 | 0.00030353 | 7.6071e-05
37 | 0.00022368 | 5.6059e-05
38 | 0.00026881 | 6.7371e-05
39 | 0.0012724 | 0.00031888
40 | 0.00037517 | 9.4026e-05
41 | 0.00031191 | 7.8172e-05
42 | 0.00046624 | 0.00011685
43 | 0.0019895 | 0.00049861
44 | 0.00783 | 0.0019624
45 | 0.026323 | 0.0065971
46 | 0.0266 | 0.0066666
47 | 0.016093 | 0.0040333
48 | 0.0020094 | 0.00050361
49 | 0.021255 | 0.005327
50 | 0.001241 | 0.00031102
51 | 0.002117 | 0.00053057
52 | 0.0032769 | 0.00082127
53 | 0.0007379 | 0.00018494
54 | 0.0011583 | 0.00029029
55 | 0.00014118 | 3.5383e-05
56 | 5.6856e-05 | 1.425e-05
57 | 0.00030573 | 7.6623e-05
58 | 0.00016576 | 4.1543e-05
59 | 6.7149e-05 | 1.6829e-05
60 | 0.00017604 | 4.4119e-05
61 | 0.00021611 | 5.4161e-05
62 | 0.00046381 | 0.00011624
63 | 0.0013853 | 0.00034718
64 | 0.0023117 | 0.00057936
65 | 0.00011364 | 2.848e-05
66 | 0.0016193 | 0.00040583
67 | 0.0013905 | 0.00034849
68 | 0.00045242 | 0.00011339
69 | 0.0019556 | 0.00049012
70 | 0.004093 | 0.0010258
71 | 0.0011653 | 0.00029205
72 | 0.0065697 | 0.0016465
73 | 0.0027001 | 0.0006767
74 | 0.0019807 | 0.00049641
75 | 0.0034744 | 0.00087078
76 | 0.0034565 | 0.00086627
77 | 0.0043023 | 0.0010782
78 | 0.004259 | 0.0010674
79 | 0.0037502 | 0.0009399
80 | 0.0027464 | 0.00068832
81 | 0.0030996 | 0.00077683
82 | 0.0033601 | 0.00084213
83 | 0.0042704 | 0.0010703
84 | 0.0034219 | 0.00085762
85 | 0.0073693 | 0.0018469
86 | 0.001044 | 0.00026165
87 | 0.0014395 | 0.00036077
88 | 0.0027426 | 0.00068737
89 | 0.0021826 | 0.00054702
90 | 0.0023841 | 0.00059751
91 | 0.0072937 | 0.001828
92 | 0.0010427 | 0.00026132
93 | 0.0035594 | 0.00089208
94 | 0.0013103 | 0.00032838
95 | 0.0044799 | 0.0011228
96 | 0.0025154 | 0.00063041
97 | 0.0081507 | 0.0020428
98 | 0.001057 | 0.00026492
99 | 0.0039538 | 0.00099091
100 | 0.0010001 | 0.00025066
101 | 0.0027862 | 0.00069829
102 | 0.0020546 | 0.00051493
103 | 0.0018806 | 0.00047132
104 | 0.0018835 | 0.00047204
105 | 0.00073098 | 0.0001832
106 | 0.0022546 | 0.00056504
107 | 0.00086232 | 0.00021612
108 | 0.0047105 | 0.0011806
109 | 0.0015835 | 0.00039686
110 | 0.002011 | 0.00050401
111 | 0.0021913 | 0.0005492
112 | 0.0023441 | 0.00058748

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1