## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1301-54_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1301-54_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1301-54_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1301-54_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1301-54_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1301-54_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1301-54_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1301-54_0_3_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_1301-54_0_3_node_36 | 0.4 | n |  | TRUE
9 | bus_LV_1301-54_0_3_node_35 | 0.4 | n |  | TRUE
10 | bus_LV_1301-54_0_3_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_1301-54_0_3_node_37 | 0.4 | n |  | TRUE
12 | bus_LV_1301-54_0_3_node_34 | 0.4 | n |  | TRUE
13 | bus_LV_1301-54_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1301-54_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1301-54_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1301-54_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1301-54_0_3_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1301-54_0_3_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1301-54_0_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1301-54_0_3_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1301-54_0_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1301-54_0_3_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_1301-54_0_3_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_1301-54_0_3_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_1301-54_0_3_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1301-54_0_3_node_94 | 0.4 | n |  | TRUE
27 | bus_LV_1301-54_0_3_node_73 | 0.4 | n |  | TRUE
28 | bus_LV_1301-54_0_3_node_61 | 0.4 | n |  | TRUE
29 | bus_LV_1301-54_0_3_node_62 | 0.4 | n |  | TRUE
30 | bus_LV_1301-54_0_3_node_63 | 0.4 | n |  | TRUE
31 | bus_LV_1301-54_0_3_node_64 | 0.4 | n |  | TRUE
32 | bus_LV_1301-54_0_3_node_65 | 0.4 | n |  | TRUE
33 | bus_LV_1301-54_0_3_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_1301-54_0_3_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_1301-54_0_3_node_99 | 0.4 | n |  | TRUE
36 | bus_LV_1301-54_0_3_node_100 | 0.4 | n |  | TRUE
37 | bus_LV_1301-54_0_3_node_101 | 0.4 | n |  | TRUE
38 | bus_LV_1301-54_0_3_node_102 | 0.4 | n |  | TRUE
39 | bus_LV_1301-54_0_3_node_118 | 0.4 | n |  | TRUE
40 | bus_LV_1301-54_0_3_node_117 | 0.4 | n |  | TRUE
41 | bus_LV_1301-54_0_3_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_1301-54_0_3_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_1301-54_0_3_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_1301-54_0_3_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_1301-54_0_3_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_1301-54_0_3_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_1301-54_0_3_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_1301-54_0_3_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_1301-54_0_3_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_1301-54_0_3_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_1301-54_0_3_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_1301-54_0_3_node_38 | 0.4 | n |  | TRUE
53 | bus_LV_1301-54_0_3_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_1301-54_0_3_node_114 | 0.4 | n |  | TRUE
55 | bus_LV_1301-54_0_3_node_115 | 0.4 | n |  | TRUE
56 | bus_LV_1301-54_0_3_node_116 | 0.4 | n |  | TRUE
57 | bus_LV_1301-54_0_3_node_119 | 0.4 | n |  | TRUE
58 | bus_LV_1301-54_0_3_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_1301-54_0_3_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_1301-54_0_3_node_43 | 0.4 | n |  | TRUE
61 | bus_LV_1301-54_0_3_node_44 | 0.4 | n |  | TRUE
62 | bus_LV_1301-54_0_3_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_1301-54_0_3_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_1301-54_0_3_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_1301-54_0_3_node_48 | 0.4 | n |  | TRUE
66 | bus_LV_1301-54_0_3_node_140 | 0.4 | n |  | TRUE
67 | bus_LV_1301-54_0_3_node_71 | 0.4 | n |  | TRUE
68 | bus_LV_1301-54_0_3_node_68 | 0.4 | n |  | TRUE
69 | bus_LV_1301-54_0_3_node_69 | 0.4 | n |  | TRUE
70 | bus_LV_1301-54_0_3_node_49 | 0.4 | n |  | TRUE
71 | bus_LV_1301-54_0_3_node_50 | 0.4 | n |  | TRUE
72 | bus_LV_1301-54_0_3_node_51 | 0.4 | n |  | TRUE
73 | bus_LV_1301-54_0_3_node_52 | 0.4 | n |  | TRUE
74 | bus_LV_1301-54_0_3_node_53 | 0.4 | n |  | TRUE
75 | bus_LV_1301-54_0_3_node_54 | 0.4 | n |  | TRUE
76 | bus_LV_1301-54_0_3_node_55 | 0.4 | n |  | TRUE
77 | bus_LV_1301-54_0_3_node_56 | 0.4 | n |  | TRUE
78 | bus_LV_1301-54_0_3_node_59 | 0.4 | n |  | TRUE
79 | bus_LV_1301-54_0_3_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_1301-54_0_3_node_57 | 0.4 | n |  | TRUE
81 | bus_LV_1301-54_0_3_node_87 | 0.4 | n |  | TRUE
82 | bus_LV_1301-54_0_3_node_97 | 0.4 | n |  | TRUE
83 | bus_LV_1301-54_0_3_node_95 | 0.4 | n |  | TRUE
84 | bus_LV_1301-54_0_3_node_58 | 0.4 | n |  | TRUE
85 | bus_LV_1301-54_0_3_node_86 | 0.4 | n |  | TRUE
86 | bus_LV_1301-54_0_3_node_98 | 0.4 | n |  | TRUE
87 | bus_LV_1301-54_0_3_node_96 | 0.4 | n |  | TRUE
88 | bus_LV_1301-54_0_3_node_74 | 0.4 | n |  | TRUE
89 | bus_LV_1301-54_0_3_node_75 | 0.4 | n |  | TRUE
90 | bus_LV_1301-54_0_3_node_67 | 0.4 | n |  | TRUE
91 | bus_LV_1301-54_0_3_node_66 | 0.4 | n |  | TRUE
92 | bus_LV_1301-54_0_3_node_70 | 0.4 | n |  | TRUE
93 | bus_LV_1301-54_0_3_node_72 | 0.4 | n |  | TRUE
94 | bus_LV_1301-54_0_3_node_83 | 0.4 | n |  | TRUE
95 | bus_LV_1301-54_0_3_node_77 | 0.4 | n |  | TRUE
96 | bus_LV_1301-54_0_3_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_1301-54_0_3_node_85 | 0.4 | n |  | TRUE
98 | bus_LV_1301-54_0_3_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_1301-54_0_3_node_76 | 0.4 | n |  | TRUE
100 | bus_LV_1301-54_0_3_node_78 | 0.4 | n |  | TRUE
101 | bus_LV_1301-54_0_3_node_80 | 0.4 | n |  | TRUE
102 | bus_LV_1301-54_0_3_node_81 | 0.4 | n |  | TRUE
103 | bus_LV_1301-54_0_3_node_82 | 0.4 | n |  | TRUE
104 | bus_LV_1301-54_0_3_node_89 | 0.4 | n |  | TRUE
105 | bus_LV_1301-54_0_3_node_91 | 0.4 | n |  | TRUE
106 | bus_LV_1301-54_0_3_node_88 | 0.4 | n |  | TRUE
107 | bus_LV_1301-54_0_3_node_90 | 0.4 | n |  | TRUE
108 | bus_LV_1301-54_0_3_node_92 | 0.4 | n |  | TRUE
109 | bus_LV_1301-54_0_3_node_93 | 0.4 | n |  | TRUE
110 | bus_LV_1301-54_0_3_node_103 | 0.4 | n |  | TRUE
111 | bus_LV_1301-54_0_3_node_104 | 0.4 | n |  | TRUE
112 | bus_LV_1301-54_0_3_node_108 | 0.4 | n |  | TRUE
113 | bus_LV_1301-54_0_3_node_109 | 0.4 | n |  | TRUE
114 | bus_LV_1301-54_0_3_node_107 | 0.4 | n |  | TRUE
115 | bus_LV_1301-54_0_3_node_129 | 0.4 | n |  | TRUE
116 | bus_LV_1301-54_0_3_node_127 | 0.4 | n |  | TRUE
117 | bus_LV_1301-54_0_3_node_105 | 0.4 | n |  | TRUE
118 | bus_LV_1301-54_0_3_node_110 | 0.4 | n |  | TRUE
119 | bus_LV_1301-54_0_3_node_133 | 0.4 | n |  | TRUE
120 | bus_LV_1301-54_0_3_node_132 | 0.4 | n |  | TRUE
121 | bus_LV_1301-54_0_3_node_106 | 0.4 | n |  | TRUE
122 | bus_LV_1301-54_0_3_node_111 | 0.4 | n |  | TRUE
123 | bus_LV_1301-54_0_3_node_112 | 0.4 | n |  | TRUE
124 | bus_LV_1301-54_0_3_node_134 | 0.4 | n |  | TRUE
125 | bus_LV_1301-54_0_3_node_131 | 0.4 | n |  | TRUE
126 | bus_LV_1301-54_0_3_node_113 | 0.4 | n |  | TRUE
127 | bus_LV_1301-54_0_3_node_121 | 0.4 | n |  | TRUE
128 | bus_LV_1301-54_0_3_node_122 | 0.4 | n |  | TRUE
129 | bus_LV_1301-54_0_3_node_137 | 0.4 | n |  | TRUE
130 | bus_LV_1301-54_0_3_node_139 | 0.4 | n |  | TRUE
131 | bus_LV_1301-54_0_3_node_138 | 0.4 | n |  | TRUE
132 | bus_LV_1301-54_0_3_node_136 | 0.4 | n |  | TRUE
133 | bus_LV_1301-54_0_3_node_123 | 0.4 | n |  | TRUE
134 | bus_LV_1301-54_0_3_node_124 | 0.4 | n |  | TRUE
135 | bus_LV_1301-54_0_3_node_125 | 0.4 | n |  | TRUE
136 | bus_LV_1301-54_0_3_node_135 | 0.4 | n |  | TRUE
137 | bus_LV_1301-54_0_3_node_126 | 0.4 | n |  | TRUE
138 | bus_LV_1301-54_0_3_node_128 | 0.4 | n |  | TRUE
139 | bus_LV_1301-54_0_3_node_130 | 0.4 | n |  | TRUE
140 | bus_MV_17_0_node_151 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1301-54_0_3_load_0 | 0 | 0.0269 | 0.0067418 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1301-54_0_3_load_1 | 1 | 0.0033952 | 0.00085092 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1301-54_0_3_load_2 | 2 | 0.0034398 | 0.0008621 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1301-54_0_3_load_3 | 3 | 0.0016687 | 0.00041821 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1301-54_0_3_load_4 | 4 | 0.001694 | 0.00042456 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1301-54_0_3_load_5 | 5 | 0.0023446 | 0.00058761 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1301-54_0_3_load_19 | 7 | 0.0017779 | 0.00044559 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1301-54_0_3_load_36 | 8 | 0.0023322 | 0.0005845 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1301-54_0_3_load_35 | 9 | 0.0021768 | 0.00054556 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1301-54_0_3_load_37 | 11 | 0.0011887 | 0.00029792 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1301-54_0_3_load_34 | 12 | 0.0025307 | 0.00063425 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1301-54_0_3_load_7 | 13 | 0.00083758 | 0.00020992 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1301-54_0_3_load_8 | 14 | 0.00051695 | 0.00012956 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1301-54_0_3_load_9 | 15 | 0.0011045 | 0.00027681 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1301-54_0_3_load_10 | 16 | 0.0033797 | 0.00084704 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1301-54_0_3_load_11 | 17 | 0.0017983 | 0.00045071 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1301-54_0_3_load_12 | 18 | 0.0018655 | 0.00046753 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1301-54_0_3_load_16 | 19 | 0.00034425 | 8.6278e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1301-54_0_3_load_17 | 20 | 0.00057028 | 0.00014292 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1301-54_0_3_load_18 | 21 | 0.0003617 | 9.0652e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1301-54_0_3_load_33 | 22 | 0.00018284 | 4.5825e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1301-54_0_3_load_15 | 25 | 0.0017025 | 0.00042669 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1301-54_0_3_load_94 | 26 | 0.0015534 | 0.00038931 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1301-54_0_3_load_73 | 27 | 0.0019029 | 0.00047692 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1301-54_0_3_load_61 | 28 | 0.003506 | 0.00087867 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1301-54_0_3_load_62 | 29 | 0.0017187 | 0.00043075 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1301-54_0_3_load_65 | 32 | 0.0030783 | 0.0007715 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1301-54_0_3_load_99 | 35 | 0.011009 | 0.0027591 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1301-54_0_3_load_100 | 36 | 0.010286 | 0.0025779 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1301-54_0_3_load_101 | 37 | 0.010002 | 0.0025068 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1301-54_0_3_load_102 | 38 | 0.0067105 | 0.0016818 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1301-54_0_3_load_118 | 39 | 0.0039127 | 0.00098063 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1301-54_0_3_load_22 | 41 | 0.00036045 | 9.0337e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1301-54_0_3_load_23 | 42 | 0.00051699 | 0.00012957 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1301-54_0_3_load_24 | 43 | 0.001999 | 0.00050101 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1301-54_0_3_load_25 | 44 | 0.00050091 | 0.00012554 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1301-54_0_3_load_26 | 45 | 0.0023155 | 0.00058032 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1301-54_0_3_load_29 | 46 | 0.00047957 | 0.00012019 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1301-54_0_3_load_28 | 47 | 0.00034076 | 8.5404e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1301-54_0_3_load_31 | 49 | 0.0026671 | 0.00066845 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1301-54_0_3_load_32 | 50 | 0.00035217 | 8.8262e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1301-54_0_3_load_40 | 51 | 0.00057943 | 0.00014522 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1301-54_0_3_load_38 | 52 | 0.00034524 | 8.6526e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1301-54_0_3_load_39 | 53 | 0.0017718 | 0.00044405 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1301-54_0_3_load_114 | 54 | 0.0013233 | 0.00033165 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1301-54_0_3_load_115 | 55 | 0.00052414 | 0.00013136 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1301-54_0_3_load_116 | 56 | 0.0011119 | 0.00027866 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1301-54_0_3_load_119 | 57 | 0.001727 | 0.00043283 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1301-54_0_3_load_41 | 58 | 0.0027568 | 0.00069092 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1301-54_0_3_load_45 | 62 | 0.0017912 | 0.00044891 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1301-54_0_3_load_46 | 63 | 0.0021617 | 0.00054177 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1301-54_0_3_load_47 | 64 | 0.0027709 | 0.00069445 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1301-54_0_3_load_140 | 66 | 0.0022389 | 0.00056112 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1301-54_0_3_load_71 | 67 | 0.0019467 | 0.00048788 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1301-54_0_3_load_68 | 68 | 0.0036755 | 0.00092116 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1301-54_0_3_load_69 | 69 | 0.0014629 | 0.00036663 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1301-54_0_3_load_49 | 70 | 0.0050909 | 0.0012759 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1301-54_0_3_load_50 | 71 | 0.007656 | 0.0019188 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1301-54_0_3_load_51 | 72 | 0.010813 | 0.0027099 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1301-54_0_3_load_53 | 74 | 0.00069592 | 0.00017441 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1301-54_0_3_load_54 | 75 | 0.0022632 | 0.00056721 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1301-54_0_3_load_55 | 76 | 0.0019232 | 0.000482 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1301-54_0_3_load_59 | 78 | 0.016559 | 0.00415 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1301-54_0_3_load_57 | 80 | 0.0014088 | 0.00035308 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1301-54_0_3_load_87 | 81 | 0.0061076 | 0.0015307 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1301-54_0_3_load_97 | 82 | 0.0074274 | 0.0018615 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1301-54_0_3_load_95 | 83 | 0.0055883 | 0.0014006 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1301-54_0_3_load_58 | 84 | 0.0011331 | 0.00028397 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1301-54_0_3_load_86 | 85 | 0.0045332 | 0.0011361 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1301-54_0_3_load_98 | 86 | 0.0046551 | 0.0011667 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1301-54_0_3_load_96 | 87 | 0.007267 | 0.0018213 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1301-54_0_3_load_74 | 88 | 0.0034955 | 0.00087606 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1301-54_0_3_load_75 | 89 | 0.0040316 | 0.0010104 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1301-54_0_3_load_67 | 90 | 0.00203 | 0.00050877 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1301-54_0_3_load_66 | 91 | 0.0023853 | 0.00059781 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1301-54_0_3_load_70 | 92 | 0.00062479 | 0.00015659 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1301-54_0_3_load_84 | 96 | 0.014932 | 0.0037423 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1301-54_0_3_load_85 | 97 | 0.013274 | 0.0033268 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1301-54_0_3_load_79 | 98 | 0.0018209 | 0.00045637 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1301-54_0_3_load_78 | 100 | 0.0025908 | 0.00064932 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1301-54_0_3_load_80 | 101 | 0.0013567 | 0.00034003 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1301-54_0_3_load_81 | 102 | 0.00084637 | 0.00021212 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1301-54_0_3_load_82 | 103 | 0.0071024 | 0.00178 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1301-54_0_3_load_91 | 105 | 0.0018304 | 0.00045875 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1301-54_0_3_load_90 | 107 | 0.014815 | 0.0037129 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1301-54_0_3_load_92 | 108 | 0.015354 | 0.003848 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1301-54_0_3_load_93 | 109 | 0.03148 | 0.0078896 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1301-54_0_3_load_103 | 110 | 0.00709 | 0.0017769 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1301-54_0_3_load_109 | 113 | 0.0029793 | 0.00074668 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1301-54_0_3_load_107 | 114 | 0.010523 | 0.0026372 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1301-54_0_3_load_129 | 115 | 0.0058965 | 0.0014778 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1301-54_0_3_load_127 | 116 | 0.0044642 | 0.0011188 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1301-54_0_3_load_105 | 117 | 0.0027925 | 0.00069986 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1301-54_0_3_load_133 | 119 | 0.0023816 | 0.00059688 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1301-54_0_3_load_132 | 120 | 0.005197 | 0.0013025 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1301-54_0_3_load_106 | 121 | 0.0041699 | 0.0010451 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1301-54_0_3_load_111 | 122 | 0.0052943 | 0.0013269 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1301-54_0_3_load_112 | 123 | 0.0034775 | 0.00087154 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1301-54_0_3_load_134 | 124 | 0.002856 | 0.00071577 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1301-54_0_3_load_131 | 125 | 0.0021888 | 0.00054856 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1301-54_0_3_load_113 | 126 | 0.0029558 | 0.00074079 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1301-54_0_3_load_121 | 127 | 0.00075584 | 0.00018943 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1301-54_0_3_load_122 | 128 | 0.0016263 | 0.00040759 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1301-54_0_3_load_137 | 129 | 0.0019729 | 0.00049444 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1301-54_0_3_load_139 | 130 | 0.0027343 | 0.00068529 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1301-54_0_3_load_138 | 131 | 0.0021867 | 0.00054804 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1301-54_0_3_load_136 | 132 | 0.0014785 | 0.00037055 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1301-54_0_3_load_125 | 135 | 0.0031768 | 0.00079619 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1301-54_0_3_load_135 | 136 | 0.0016747 | 0.00041973 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1301-54_0_3_load_126 | 137 | 0.0041549 | 0.0010413 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1301-54_0_3_load_128 | 138 | 0.0033727 | 0.00084528 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1301-54_0_3_load_130 | 139 | 0.0042391 | 0.0010624 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 109 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1301-54_0_3_line_0 |  | 0 | 1 | 0.021223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1301-54_0_3_line_1 |  | 0 | 2 | 0.010863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1301-54_0_3_line_2 |  | 1 | 3 | 0.031007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1301-54_0_3_line_3 |  | 2 | 4 | 0.027922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1301-54_0_3_line_4 |  | 3 | 5 | 0.016205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1301-54_0_3_line_5 |  | 4 | 6 | 0.004006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1301-54_0_3_line_6 |  | 5 | 7 | 0.02375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1301-54_0_3_line_7 |  | 6 | 8 | 0.017355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1301-54_0_3_line_8 |  | 6 | 9 | 0.015012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1301-54_0_3_line_9 |  | 7 | 10 | 0.058479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1301-54_0_3_line_10 |  | 8 | 11 | 0.014406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1301-54_0_3_line_11 |  | 9 | 12 | 0.060676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1301-54_0_3_line_12 |  | 10 | 34 | 0.02321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1301-54_0_3_line_13 |  | 11 | 58 | 0.0028033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1301-54_0_3_line_14 |  | 12 | 33 | 0.079501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1301-54_0_3_line_15 |  | 13 | 14 | 0.0091586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1301-54_0_3_line_16 |  | 13 | 15 | 0.019506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1301-54_0_3_line_17 |  | 14 | 16 | 0.012357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1301-54_0_3_line_18 |  | 15 | 17 | 0.094618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1301-54_0_3_line_19 |  | 17 | 18 | 0.091622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1301-54_0_3_line_20 |  | 18 | 23 | 0.018881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1301-54_0_3_line_21 |  | 19 | 20 | 0.014699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1301-54_0_3_line_22 |  | 20 | 21 | 0.014747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1301-54_0_3_line_23 |  | 21 | 22 | 0.077922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1301-54_0_3_line_24 |  | 22 | 33 | 0.015892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1301-54_0_3_line_25 |  | 23 | 24 | 0.006632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1301-54_0_3_line_26 |  | 24 | 25 | 0.057303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1301-54_0_3_line_27 |  | 25 | 26 | 0.022379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1301-54_0_3_line_28 |  | 26 | 27 | 0.026866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1301-54_0_3_line_29 |  | 27 | 67 | 0.025439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1301-54_0_3_line_30 |  | 28 | 29 | 0.022058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1301-54_0_3_line_31 |  | 28 | 30 | 0.017121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1301-54_0_3_line_32 |  | 30 | 31 | 0.007826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1301-54_0_3_line_33 |  | 31 | 32 | 0.052534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1301-54_0_3_line_34 |  | 32 | 91 | 0.03678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1301-54_0_3_line_35 |  | 33 | 44 | 0.023567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1301-54_0_3_line_36 |  | 34 | 39 | 0.076778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1301-54_0_3_line_37 |  | 35 | 36 | 0.007745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1301-54_0_3_line_38 |  | 36 | 37 | 0.0087219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1301-54_0_3_line_39 |  | 37 | 38 | 0.033442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1301-54_0_3_line_40 |  | 38 | 112 | 0.018968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1301-54_0_3_line_41 |  | 39 | 40 | 0.052075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1301-54_0_3_line_42 |  | 40 | 50 | 0.10167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1301-54_0_3_line_43 |  | 40 | 55 | 0.033291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1301-54_0_3_line_44 |  | 41 | 42 | 0.0055962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1301-54_0_3_line_45 |  | 41 | 43 | 0.023902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1301-54_0_3_line_46 |  | 42 | 44 | 0.011382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1301-54_0_3_line_47 |  | 43 | 45 | 0.0030339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1301-54_0_3_line_48 |  | 46 | 47 | 0.0094309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1301-54_0_3_line_49 |  | 47 | 48 | 0.013388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1301-54_0_3_line_50 |  | 48 | 49 | 0.05387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1301-54_0_3_line_51 |  | 48 | 50 | 0.053332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1301-54_0_3_line_52 |  | 50 | 51 | 0.091123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1301-54_0_3_line_53 |  | 51 | 52 | 0.0063467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1301-54_0_3_line_54 |  | 52 | 53 | 0.021971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1301-54_0_3_line_55 |  | 54 | 55 | 0.046209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1301-54_0_3_line_56 |  | 54 | 56 | 0.010562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1301-54_0_3_line_57 |  | 56 | 57 | 0.181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1301-54_0_3_line_58 |  | 58 | 59 | 0.011538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1301-54_0_3_line_59 |  | 59 | 60 | 0.020684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1301-54_0_3_line_60 |  | 59 | 61 | 0.017528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1301-54_0_3_line_61 |  | 60 | 62 | 0.027502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1301-54_0_3_line_62 |  | 60 | 63 | 0.024062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1301-54_0_3_line_63 |  | 61 | 64 | 0.0209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1301-54_0_3_line_64 |  | 61 | 65 | 0.015134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1301-54_0_3_line_65 |  | 63 | 66 | 0.014663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1301-54_0_3_line_66 |  | 65 | 67 | 0.016125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1301-54_0_3_line_67 |  | 65 | 68 | 0.0095134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1301-54_0_3_line_68 |  | 68 | 69 | 0.020917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1301-54_0_3_line_69 |  | 69 | 92 | 0.020327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1301-54_0_3_line_70 |  | 70 | 71 | 0.035566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1301-54_0_3_line_71 |  | 70 | 72 | 0.00054434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1301-54_0_3_line_72 |  | 71 | 73 | 0.02082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1301-54_0_3_line_73 |  | 72 | 74 | 0.058713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1301-54_0_3_line_74 |  | 73 | 75 | 0.03361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_1301-54_0_3_line_75 |  | 73 | 76 | 0.04605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_1301-54_0_3_line_76 |  | 74 | 77 | 0.020621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1301-54_0_3_line_77 |  | 75 | 78 | 0.011638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_1301-54_0_3_line_78 |  | 76 | 79 | 0.021052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_1301-54_0_3_line_79 |  | 77 | 80 | 0.031337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1301-54_0_3_line_80 |  | 78 | 81 | 0.0068131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_1301-54_0_3_line_81 |  | 79 | 82 | 0.010275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_1301-54_0_3_line_82 |  | 79 | 83 | 0.029968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1301-54_0_3_line_83 |  | 80 | 84 | 0.0079077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1301-54_0_3_line_84 |  | 81 | 85 | 0.025139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_1301-54_0_3_line_85 |  | 82 | 86 | 0.016043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_1301-54_0_3_line_86 |  | 83 | 87 | 0.0087982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1301-54_0_3_line_87 |  | 85 | 106 | 0.027977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_1301-54_0_3_line_88 |  | 86 | 110 | 0.027712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_1301-54_0_3_line_89 |  | 88 | 89 | 0.035048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1301-54_0_3_line_90 |  | 88 | 90 | 0.052461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1301-54_0_3_line_91 |  | 89 | 99 | 0.013318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1301-54_0_3_line_92 |  | 90 | 91 | 0.010192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1301-54_0_3_line_93 |  | 92 | 93 | 0.0085381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1301-54_0_3_line_94 |  | 93 | 94 | 0.004068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1301-54_0_3_line_95 |  | 93 | 95 | 0.027683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1301-54_0_3_line_96 |  | 94 | 96 | 0.006461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1301-54_0_3_line_97 |  | 94 | 97 | 0.017872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
98 | LV_1301-54_0_3_line_98 |  | 95 | 98 | 0.01344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1301-54_0_3_line_99 |  | 95 | 99 | 0.030057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1301-54_0_3_line_100 |  | 97 | 104 | 0.010472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_1301-54_0_3_line_101 |  | 98 | 102 | 0.0012768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1301-54_0_3_line_102 |  | 99 | 100 | 0.010175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1301-54_0_3_line_103 |  | 100 | 101 | 0.0043047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1301-54_0_3_line_104 |  | 102 | 103 | 0.015772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1301-54_0_3_line_105 |  | 104 | 105 | 0.004332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1301-54_0_3_line_106 |  | 104 | 106 | 0.01737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_1301-54_0_3_line_107 |  | 106 | 107 | 0.032197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_1301-54_0_3_line_108 |  | 107 | 108 | 0.019378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_1301-54_0_3_line_109 |  | 108 | 109 | 0.012126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_1301-54_0_3_line_110 |  | 110 | 111 | 0.0072309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_1301-54_0_3_line_111 |  | 111 | 117 | 0.018274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
112 | LV_1301-54_0_3_line_112 |  | 112 | 113 | 0.015901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1301-54_0_3_line_113 |  | 112 | 114 | 0.01938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1301-54_0_3_line_114 |  | 113 | 122 | 0.029341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1301-54_0_3_line_115 |  | 113 | 115 | 0.034566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1301-54_0_3_line_116 |  | 114 | 121 | 0.025087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1301-54_0_3_line_117 |  | 115 | 116 | 0.019907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1301-54_0_3_line_118 |  | 116 | 137 | 0.0033968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1301-54_0_3_line_119 |  | 117 | 118 | 0.021362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
120 | LV_1301-54_0_3_line_120 |  | 118 | 119 | 0.0060721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_1301-54_0_3_line_121 |  | 118 | 120 | 0.019862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
122 | LV_1301-54_0_3_line_122 |  | 119 | 124 | 0.011606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_1301-54_0_3_line_123 |  | 120 | 125 | 0.021306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
124 | LV_1301-54_0_3_line_124 |  | 122 | 123 | 0.011509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1301-54_0_3_line_125 |  | 123 | 126 | 0.0078403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1301-54_0_3_line_126 |  | 124 | 134 | 0.014836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
127 | LV_1301-54_0_3_line_127 |  | 125 | 139 | 0.011724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
128 | LV_1301-54_0_3_line_128 |  | 127 | 128 | 0.024491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1301-54_0_3_line_129 |  | 128 | 129 | 0.046443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1301-54_0_3_line_130 |  | 129 | 131 | 0.00048865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1301-54_0_3_line_131 |  | 129 | 132 | 0.017942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1301-54_0_3_line_132 |  | 130 | 131 | 0.01507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1301-54_0_3_line_133 |  | 132 | 136 | 0.018235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1301-54_0_3_line_134 |  | 133 | 134 | 0.054862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
135 | LV_1301-54_0_3_line_135 |  | 133 | 135 | 0.010542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1301-54_0_3_line_136 |  | 135 | 136 | 0.02456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1301-54_0_3_line_137 |  | 137 | 138 | 0.019125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
138 | LV_1301-54_0_3_line_138 |  | 138 | 139 | 0.010616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1301-54_0_3_trafo_93 | 0.63 MVA 20/0.4 kV | 140 | 109 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2701381.3921 | 1219157.4073 | 2701360.1874 | 1219158.2836
1 | 2701381.3921 | 1219157.4073 | 2701392.2454 | 1219156.9588
2 | 2701360.1874 | 1219158.2836 | 2701346.4037 | 1219158.8532 | 2701329.6625 | 1219162.848
3 | 2701392.2454 | 1219156.9588 | 2701420.1433 | 1219155.8059
4 | 2701315.2915 | 1219170.1345 | 2701326.9618 | 1219163.4925 | 2701329.6625 | 1219162.848
5 | 2701424.1458 | 1219155.6405 | 2701420.1433 | 1219155.8059
6 | 2701315.2915 | 1219170.1345 | 2701294.6503 | 1219181.8824
7 | 2701424.1458 | 1219155.6405 | 2701441.5008 | 1219155.6641
8 | 2701424.1458 | 1219155.6405 | 2701414.6944 | 1219143.9778
9 | 2701241.5064 | 1219205.1918 | 2701251.8893 | 1219203.4448 | 2701273.9614 | 1219193.6574 | 2701294.6503 | 1219181.8824
10 | 2701441.5008 | 1219155.6641 | 2701455.9072 | 1219155.6837
11 | 2701414.6944 | 1219143.9778 | 2701401.4494 | 1219127.6341 | 2701376.3027 | 1219096.9929
12 | 2701218.2481 | 1219204.3961 | 2701229.9562 | 1219205.0621 | 2701241.5064 | 1219205.1918
13 | 2701458.7105 | 1219155.6875 | 2701455.9072 | 1219155.6837
14 | 2701376.3027 | 1219096.9929 | 2701325.8679 | 1219035.5381
15 | 2701404.1366 | 1218867.5835 | 2701400.2774 | 1218859.2777
16 | 2701404.1366 | 1218867.5835 | 2701405.48 | 1218870.4746 | 2701416.0682 | 1218882.8911
17 | 2701400.2774 | 1218859.2777 | 2701398.9704 | 1218856.4649 | 2701389.7729 | 1218855.4299
18 | 2701469.6125 | 1218960.9014 | 2701416.0682 | 1218882.8911
19 | 2701549.6864 | 1219005.4291 | 2701469.6125 | 1218960.9014
20 | 2701565.0374 | 1219016.4188 | 2701557.9411 | 1219011.4721 | 2701549.6864 | 1219005.4291
21 | 2701271.6107 | 1218925.6985 | 2701276.6599 | 1218939.5033
22 | 2701281.7256 | 1218953.3531 | 2701276.6599 | 1218939.5033
23 | 2701315.2964 | 1219023.6721 | 2701281.7256 | 1218953.3531
24 | 2701325.8679 | 1219035.5381 | 2701315.2964 | 1219023.6721
25 | 2701565.0374 | 1219016.4188 | 2701561.5482 | 1219022.0633
26 | 2701561.5482 | 1219022.0633 | 2701548.6308 | 1219042.8803 | 2701539.9524 | 1219059.9334 | 2701533.9903 | 1219072.2342
27 | 2701524.2295 | 1219092.3726 | 2701533.9903 | 1219072.2342
28 | 2701514.5282 | 1219117.4102 | 2701515.7413 | 1219113.6481 | 2701523.1794 | 1219094.539 | 2701524.2295 | 1219092.3726
29 | 2701506.82 | 1219141.6509 | 2701507.3185 | 1219139.7678 | 2701514.5282 | 1219117.4102
30 | 2701672.8193 | 1219139.3338 | 2701664.5029 | 1219132.5092 | 2701654.9249 | 1219126.5137
31 | 2701640.496 | 1219117.2999 | 2701645.0366 | 1219120.324 | 2701654.9249 | 1219126.5137
32 | 2701640.496 | 1219117.2999 | 2701632.6509 | 1219117.544
33 | 2701632.6509 | 1219117.544 | 2701642.124 | 1219131.3155 | 2701645.701 | 1219138.3148 | 2701646.7347 | 1219145.3486 | 2701645.7133 | 1219150.0456 | 2701642.3669 | 1219155.3257 | 2701635.3863 | 1219162.1918
34 | 2701635.3863 | 1219162.1918 | 2701609.1651 | 1219187.9834
35 | 2701325.8679 | 1219035.5381 | 2701304.8213 | 1219046.143
36 | 2701218.2481 | 1219204.3961 | 2701141.6595 | 1219209.7885
37 | 2701335.9252 | 1219233.5506 | 2701335.9252 | 1219233.5506 | 2701328.8154 | 1219236.6224
38 | 2701328.8154 | 1219236.6224 | 2701320.8088 | 1219240.0817
39 | 2701320.8088 | 1219240.0817 | 2701290.1096 | 1219253.3454
40 | 2701278.4737 | 1219266.6195 | 2701282.7899 | 1219256.5079 | 2701290.1096 | 1219253.3454
41 | 2701093.8003 | 1219220.3279 | 2701097.5882 | 1219214.9439 | 2701100.5744 | 1219212.0703 | 2701116.4792 | 1219209.2048 | 2701141.6595 | 1219209.7885
42 | 2701098.6607 | 1219118.7751 | 2701093.8003 | 1219220.3279
43 | 2701093.8003 | 1219220.3279 | 2701079.3839 | 1219241.0425 | 2701076.9084 | 1219248.706 | 2701076.9084 | 1219248.706
44 | 2701289.4643 | 1219053.3654 | 2701294.6051 | 1219051.1543
45 | 2701289.4643 | 1219053.3654 | 2701267.5073 | 1219062.809
46 | 2701304.8213 | 1219046.143 | 2701296.453 | 1219050.3596 | 2701294.6051 | 1219051.1543
47 | 2701264.7203 | 1219064.0077 | 2701267.5073 | 1219062.809
48 | 2701160.8896 | 1219085.0367 | 2701151.9936 | 1219081.9057
49 | 2701145.758 | 1219093.7527 | 2701151.9936 | 1219081.9057
50 | 2701145.758 | 1219093.7527 | 2701177.4089 | 1219137.3436
51 | 2701145.758 | 1219093.7527 | 2701098.6607 | 1219118.7751
52 | 2701098.6607 | 1219118.7751 | 2701024.543 | 1219065.7651
53 | 2701024.543 | 1219065.7651 | 2701018.6808 | 1219066.7998 | 2701018.3668 | 1219067.0375
54 | 2701018.3668 | 1219067.0375 | 2701008.6541 | 1219074.3908 | 2701003.3655 | 1219082.6274
55 | 2701034.5964 | 1219258.0716 | 2701040.815 | 1219253.2859 | 2701065.742 | 1219254.5874 | 2701072.1394 | 1219253.762 | 2701076.9084 | 1219248.706
56 | 2701026.2258 | 1219264.5132 | 2701034.5964 | 1219258.0716
57 | 2701026.2258 | 1219264.5132 | 2700846.1874 | 1219245.8507
58 | 2701470.2487 | 1219155.7033 | 2701458.7105 | 1219155.6875
59 | 2701470.2487 | 1219155.7033 | 2701476.1126 | 1219135.8667
60 | 2701487.8276 | 1219155.7249 | 2701470.2487 | 1219155.7033
61 | 2701483.9096 | 1219109.4918 | 2701476.1126 | 1219135.8667
62 | 2701476.1126 | 1219135.8667 | 2701458.7064 | 1219129.2656 | 2701454.7343 | 1219125.5389
63 | 2701487.8276 | 1219155.7249 | 2701486.0078 | 1219176.5421
64 | 2701487.8276 | 1219155.7249 | 2701496.849 | 1219156.3791 | 2701502.9133 | 1219157.2941
65 | 2701444.0409 | 1219115.506 | 2701454.7343 | 1219125.5389
66 | 2701502.9133 | 1219157.2941 | 2701505.2497 | 1219147.5825 | 2701506.82 | 1219141.6509
67 | 2701502.9133 | 1219157.2941 | 2701501.5398 | 1219166.7079
68 | 2701499.1588 | 1219187.486 | 2701500.842 | 1219171.4912 | 2701501.5398 | 1219166.7079
69 | 2701499.1588 | 1219187.486 | 2701498.2514 | 1219196.1091 | 2701496.7444 | 1219207.6681
70 | 2701428.2451 | 1219414.8252 | 2701431.9276 | 1219402.3604 | 2701439.8921 | 1219383.5047 | 2701440.8018 | 1219381.6125
71 | 2701428.0909 | 1219415.3472 | 2701428.2451 | 1219414.8252
72 | 2701449.8228 | 1219362.848 | 2701440.8018 | 1219381.6125
73 | 2701421.0181 | 1219473.394 | 2701420.9347 | 1219472.012 | 2701421.3409 | 1219453.072 | 2701422.2665 | 1219443.7366 | 2701423.8054 | 1219434.0448 | 2701427.1916 | 1219418.3912 | 2701428.0909 | 1219415.3472
74 | 2701449.8228 | 1219362.848 | 2701463.8182 | 1219332.2904
75 | 2701449.8228 | 1219362.848 | 2701424.2305 | 1219349.3915 | 2701407.1366 | 1219348.1896
76 | 2701421.9341 | 1219493.9891 | 2701421.9149 | 1219491.109 | 2701421.8818 | 1219487.706 | 2701421.0181 | 1219473.394
77 | 2701463.8182 | 1219332.2904 | 2701468.6644 | 1219321.7092
78 | 2701386.1354 | 1219346.7301 | 2701403.7768 | 1219347.9534 | 2701407.1366 | 1219348.1896
79 | 2701421.9341 | 1219493.9891 | 2701396.0679 | 1219488.6228 | 2701391.24 | 1219489.5683
80 | 2701471.5014 | 1219315.5149 | 2701468.6644 | 1219321.7092
81 | 2701386.1354 | 1219346.7301 | 2701382.8375 | 1219346.5071 | 2701376.1118 | 1219348.3346
82 | 2701386.1354 | 1219346.7301 | 2701404.5483 | 1219331.6215 | 2701409.0998 | 1219327.486
83 | 2701383.4798 | 1219491.0881 | 2701391.24 | 1219489.5683
84 | 2701480.8504 | 1219292.1839 | 2701472.8346 | 1219312.6039 | 2701471.5014 | 1219315.5149
85 | 2701362.0495 | 1219355.2554 | 2701367.5105 | 1219350.6716 | 2701376.1118 | 1219348.3346
86 | 2701415.6114 | 1219321.5693 | 2701409.0998 | 1219327.486
87 | 2701488.8798 | 1219265.4324 | 2701484.2289 | 1219283.5772 | 2701480.8504 | 1219292.1839
88 | 2701340.8238 | 1219373.0717 | 2701362.0495 | 1219355.2554
89 | 2701563.5015 | 1219230.8767 | 2701538.1573 | 1219255.0849
90 | 2701563.5015 | 1219230.8767 | 2701601.8988 | 1219195.1306
91 | 2701528.0736 | 1219263.7767 | 2701536.051 | 1219257.0968 | 2701538.1573 | 1219255.0849
92 | 2701601.8988 | 1219195.1306 | 2701609.1651 | 1219187.9834
93 | 2701495.6406 | 1219216.1345 | 2701496.7444 | 1219207.6681
94 | 2701495.0634 | 1219220.1609 | 2701495.6406 | 1219216.1345
95 | 2701512.934 | 1219237.7891 | 2701495.6406 | 1219216.1345
96 | 2701495.0634 | 1219220.1609 | 2701489.071 | 1219217.7015
97 | 2701495.0634 | 1219220.1609 | 2701493.0616 | 1219237.9207
98 | 2701512.934 | 1219237.7891 | 2701525.2533 | 1219232.4159
99 | 2701512.934 | 1219237.7891 | 2701528.0736 | 1219263.7767
100 | 2701491.8887 | 1219248.3269 | 2701493.0616 | 1219237.9207
101 | 2701525.2533 | 1219232.4159 | 2701526.4236 | 1219231.9054
102 | 2701528.0736 | 1219263.7767 | 2701518.3929 | 1219266.9089
103 | 2701514.2972 | 1219268.2341 | 2701518.3929 | 1219266.9089
104 | 2701539.5208 | 1219223.2095 | 2701528.9547 | 1219230.8015 | 2701526.4236 | 1219231.9054
105 | 2701496.1809 | 1219249.0005 | 2701491.8887 | 1219248.3269
106 | 2701488.8798 | 1219265.4324 | 2701491.8887 | 1219248.3269
107 | 2701488.8798 | 1219265.4324 | 2701479.3932 | 1219262.2463 | 2701467.8559 | 1219258.6917 | 2701458.986 | 1219253.826
108 | 2701458.986 | 1219253.826 | 2701457.0196 | 1219252.7473 | 2701446.78 | 1219245.6457 | 2701442.1537 | 1219244.9775
109 | 2701432.3262 | 1219251.993 | 2701437.1096 | 1219247.8938 | 2701442.1537 | 1219244.9775
110 | 2701335.2854 | 1219377.7205 | 2701340.8238 | 1219373.0717
111 | 2701335.2854 | 1219377.7205 | 2701331.8579 | 1219380.6532 | 2701326.7469 | 1219384.3911 | 2701321.1763 | 1219389.3097
112 | 2701278.4737 | 1219266.6195 | 2701271.6169 | 1219269.4605 | 2701263.7801 | 1219272.6978
113 | 2701278.4737 | 1219266.6195 | 2701289.4755 | 1219282.5735
114 | 2701263.7801 | 1219272.6978 | 2701262.9564 | 1219273.0381 | 2701236.6613 | 1219283.899 | 2701236.6613 | 1219283.899
115 | 2701262.2079 | 1219307.2276 | 2701263.7801 | 1219272.6978
116 | 2701303.7175 | 1219303.2261 | 2701289.4755 | 1219282.5735
117 | 2701262.2079 | 1219307.2276 | 2701268.7664 | 1219326.0234
118 | 2701269.8855 | 1219329.2305 | 2701268.7664 | 1219326.0234
119 | 2701305.1628 | 1219403.4488 | 2701321.1763 | 1219389.3097
120 | 2701305.1628 | 1219403.4488 | 2701300.4943 | 1219407.3314
121 | 2701305.1628 | 1219403.4488 | 2701294.8395 | 1219386.4798
122 | 2701300.4943 | 1219407.3314 | 2701291.5712 | 1219414.7522
123 | 2701283.766 | 1219368.2779 | 2701294.8395 | 1219386.4798
124 | 2701236.6613 | 1219283.899 | 2701228.5528 | 1219292.0671 | 2701228.5528 | 1219292.0671
125 | 2701220.7163 | 1219291.8227 | 2701228.5528 | 1219292.0671
126 | 2701280.1643 | 1219424.2387 | 2701291.5712 | 1219414.7522
127 | 2701283.766 | 1219368.2779 | 2701283.1672 | 1219367.2935 | 2701279.6841 | 1219357.3116
128 | 2701169.9761 | 1219374.6372 | 2701151.5307 | 1219371.8493 | 2701146.5249 | 1219374.8494
129 | 2701209.6489 | 1219350.4905 | 2701169.9761 | 1219374.6372
130 | 2701209.3991 | 1219350.0705 | 2701209.6489 | 1219350.4905
131 | 2701217.6485 | 1219366.5351 | 2701211.6982 | 1219353.936 | 2701209.6489 | 1219350.4905
132 | 2701209.3991 | 1219350.0705 | 2701201.8839 | 1219337.4353 | 2701201.5346 | 1219337.3175
133 | 2701217.6485 | 1219366.5351 | 2701225.4359 | 1219383.0239
134 | 2701226.4395 | 1219414.5743 | 2701255.6872 | 1219423.2997 | 2701280.1643 | 1219424.2387
135 | 2701226.4395 | 1219414.5743 | 2701232.2972 | 1219407.5354 | 2701232.2318 | 1219406.1519
136 | 2701232.2318 | 1219406.1519 | 2701231.7724 | 1219396.4408 | 2701225.4359 | 1219383.0239
137 | 2701269.8855 | 1219329.2305 | 2701276.1864 | 1219347.2878
138 | 2701276.1864 | 1219347.2878 | 2701279.6841 | 1219357.3116

## bus_geodata
| x | y | coords
0 | 2701381.3921 | 1219157.4073
1 | 2701360.1874 | 1219158.2836
2 | 2701392.2454 | 1219156.9588
3 | 2701329.6625 | 1219162.848
4 | 2701420.1433 | 1219155.8059
5 | 2701315.2915 | 1219170.1345
6 | 2701424.1458 | 1219155.6405
7 | 2701294.6503 | 1219181.8824
8 | 2701441.5008 | 1219155.6641
9 | 2701414.6944 | 1219143.9778
10 | 2701241.5064 | 1219205.1918
11 | 2701455.9072 | 1219155.6837
12 | 2701376.3027 | 1219096.9929
13 | 2701404.1366 | 1218867.5835
14 | 2701400.2774 | 1218859.2777
15 | 2701416.0682 | 1218882.8911
16 | 2701389.7729 | 1218855.4299
17 | 2701469.6125 | 1218960.9014
18 | 2701549.6864 | 1219005.4291
19 | 2701271.6107 | 1218925.6985
20 | 2701276.6599 | 1218939.5033
21 | 2701281.7256 | 1218953.3531
22 | 2701315.2964 | 1219023.6721
23 | 2701565.0374 | 1219016.4188
24 | 2701561.5482 | 1219022.0633
25 | 2701533.9903 | 1219072.2342
26 | 2701524.2295 | 1219092.3726
27 | 2701514.5282 | 1219117.4102
28 | 2701654.9249 | 1219126.5137
29 | 2701672.8193 | 1219139.3338
30 | 2701640.496 | 1219117.2999
31 | 2701632.6509 | 1219117.544
32 | 2701635.3863 | 1219162.1918
33 | 2701325.8679 | 1219035.5381
34 | 2701218.2481 | 1219204.3961
35 | 2701335.9252 | 1219233.5506
36 | 2701328.8154 | 1219236.6224
37 | 2701320.8088 | 1219240.0817
38 | 2701290.1096 | 1219253.3454
39 | 2701141.6595 | 1219209.7885
40 | 2701093.8003 | 1219220.3279
41 | 2701289.4643 | 1219053.3654
42 | 2701294.6051 | 1219051.1543
43 | 2701267.5073 | 1219062.809
44 | 2701304.8213 | 1219046.143
45 | 2701264.7203 | 1219064.0077
46 | 2701160.8896 | 1219085.0367
47 | 2701151.9936 | 1219081.9057
48 | 2701145.758 | 1219093.7527
49 | 2701177.4089 | 1219137.3436
50 | 2701098.6607 | 1219118.7751
51 | 2701024.543 | 1219065.7651
52 | 2701018.3668 | 1219067.0375
53 | 2701003.3655 | 1219082.6274
54 | 2701034.5964 | 1219258.0716
55 | 2701076.9084 | 1219248.706
56 | 2701026.2258 | 1219264.5132
57 | 2700846.1874 | 1219245.8507
58 | 2701458.7105 | 1219155.6875
59 | 2701470.2487 | 1219155.7033
60 | 2701476.1125 | 1219135.8667
61 | 2701487.8276 | 1219155.7249
62 | 2701483.9096 | 1219109.4918
63 | 2701454.7343 | 1219125.5389
64 | 2701486.0078 | 1219176.5421
65 | 2701502.9133 | 1219157.2941
66 | 2701444.0409 | 1219115.506
67 | 2701506.82 | 1219141.6509
68 | 2701501.5398 | 1219166.7079
69 | 2701499.1588 | 1219187.486
70 | 2701428.2451 | 1219414.8252
71 | 2701440.8018 | 1219381.6125
72 | 2701428.0909 | 1219415.3472
73 | 2701449.8228 | 1219362.848
74 | 2701421.0181 | 1219473.394
75 | 2701463.8182 | 1219332.2904
76 | 2701407.1366 | 1219348.1896
77 | 2701421.9341 | 1219493.9891
78 | 2701468.6644 | 1219321.7092
79 | 2701386.1354 | 1219346.7301
80 | 2701391.24 | 1219489.5683
81 | 2701471.5014 | 1219315.5149
82 | 2701376.1118 | 1219348.3346
83 | 2701409.0998 | 1219327.486
84 | 2701383.4798 | 1219491.0881
85 | 2701480.8504 | 1219292.1839
86 | 2701362.0495 | 1219355.2554
87 | 2701415.6114 | 1219321.5693
88 | 2701563.5015 | 1219230.8767
89 | 2701538.1573 | 1219255.0849
90 | 2701601.8988 | 1219195.1306
91 | 2701609.1651 | 1219187.9834
92 | 2701496.7444 | 1219207.6681
93 | 2701495.6406 | 1219216.1345
94 | 2701495.0634 | 1219220.1609
95 | 2701512.934 | 1219237.7891
96 | 2701489.071 | 1219217.7015
97 | 2701493.0616 | 1219237.9207
98 | 2701525.2533 | 1219232.4159
99 | 2701528.0736 | 1219263.7767
100 | 2701518.3929 | 1219266.9089
101 | 2701514.2972 | 1219268.2341
102 | 2701526.4236 | 1219231.9054
103 | 2701539.5208 | 1219223.2095
104 | 2701491.8887 | 1219248.3269
105 | 2701496.1809 | 1219249.0005
106 | 2701488.8798 | 1219265.4324
107 | 2701458.986 | 1219253.826
108 | 2701442.1537 | 1219244.9775
109 | 2701432.3262 | 1219251.993
110 | 2701340.8238 | 1219373.0717
111 | 2701335.2854 | 1219377.7205
112 | 2701278.4737 | 1219266.6195
113 | 2701263.7801 | 1219272.6978
114 | 2701289.4755 | 1219282.5735
115 | 2701262.2079 | 1219307.2276
116 | 2701268.7664 | 1219326.0234
117 | 2701321.1763 | 1219389.3097
118 | 2701305.1628 | 1219403.4488
119 | 2701300.4943 | 1219407.3314
120 | 2701294.8395 | 1219386.4798
121 | 2701303.7175 | 1219303.2261
122 | 2701236.6613 | 1219283.899
123 | 2701228.5528 | 1219292.0671
124 | 2701291.5712 | 1219414.7522
125 | 2701283.766 | 1219368.2779
126 | 2701220.7163 | 1219291.8227
127 | 2701146.5249 | 1219374.8494
128 | 2701169.9761 | 1219374.6372
129 | 2701209.6489 | 1219350.4905
130 | 2701201.5346 | 1219337.3175
131 | 2701209.3991 | 1219350.0705
132 | 2701217.6485 | 1219366.5351
133 | 2701226.4395 | 1219414.5743
134 | 2701280.1643 | 1219424.2387
135 | 2701232.2318 | 1219406.1519
136 | 2701225.4359 | 1219383.0239
137 | 2701269.8855 | 1219329.2305
138 | 2701276.1864 | 1219347.2878
139 | 2701279.6841 | 1219357.3116
140 | 2701488.8798 | 1219265.4324

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97566 | -0.46881 | 0.0269 | 0.0067418
1 | 0.97518 | -0.47828 | 0.0033952 | 0.00085092
2 | 0.97618 | -0.45862 | 0.0034398 | 0.0008621
3 | 0.97457 | -0.49019 | 0.0016687 | 0.00041821
4 | 0.9776 | -0.43073 | 0.001694 | 0.00042456
5 | 0.97428 | -0.49593 | 0.0023446 | 0.00058761
6 | 0.97781 | -0.42661 | 0 | 0
7 | 0.9739 | -0.50332 | 0.0017779 | 0.00044559
8 | 0.97891 | -0.40504 | 0.0023322 | 0.0005845
9 | 0.97764 | -0.42986 | 0.0021768 | 0.00054556
10 | 0.97308 | -0.51963 | 0 | 0
11 | 0.97985 | -0.38656 | 0.0011887 | 0.00029792
12 | 0.9771 | -0.44059 | 0.0025307 | 0.00063425
13 | 0.98022 | -0.37982 | 0.00083758 | 0.00020992
14 | 0.98018 | -0.38047 | 0.00051695 | 0.00012956
15 | 0.9803 | -0.37814 | 0.0011045 | 0.00027681
16 | 0.98015 | -0.38122 | 0.0033797 | 0.00084704
17 | 0.98081 | -0.36812 | 0.0017983 | 0.00045071
18 | 0.98146 | -0.35544 | 0.0018655 | 0.00046753
19 | 0.97644 | -0.45357 | 0.00034425 | 8.6278e-05
20 | 0.97644 | -0.45348 | 0.00057028 | 0.00014292
21 | 0.97645 | -0.45323 | 0.0003617 | 9.0652e-05
22 | 0.97655 | -0.45141 | 0.00018284 | 4.5825e-05
23 | 0.98163 | -0.3522 | 0 | 0
24 | 0.98168 | -0.35105 | 0 | 0
25 | 0.98219 | -0.3412 | 0.0017025 | 0.00042669
26 | 0.98242 | -0.33667 | 0.0015534 | 0.00038931
27 | 0.98274 | -0.33048 | 0.0019029 | 0.00047692
28 | 0.98538 | -0.27979 | 0.003506 | 0.00087867
29 | 0.98535 | -0.28047 | 0.0017187 | 0.00043075
30 | 0.98547 | -0.27819 | 0 | 0
31 | 0.9855 | -0.27745 | 0 | 0
32 | 0.98576 | -0.27252 | 0.0030783 | 0.0007715
33 | 0.97657 | -0.45099 | 0 | 0
34 | 0.97275 | -0.5261 | 0 | 0
35 | 0.97 | -0.57975 | 0.011009 | 0.0027591
36 | 0.97008 | -0.57817 | 0.010286 | 0.0025779
37 | 0.97025 | -0.57473 | 0.010002 | 0.0025068
38 | 0.97123 | -0.55537 | 0.0067105 | 0.0016818
39 | 0.97166 | -0.54756 | 0.0039127 | 0.00098063
40 | 0.97112 | -0.55838 | 0 | 0
41 | 0.97636 | -0.455 | 0.00036045 | 9.0337e-05
42 | 0.97639 | -0.45452 | 0.00051699 | 0.00012957
43 | 0.97627 | -0.45689 | 0.001999 | 0.00050101
44 | 0.97644 | -0.45344 | 0.00050091 | 0.00012554
45 | 0.97626 | -0.45701 | 0.0023155 | 0.00058032
46 | 0.97031 | -0.57442 | 0.00047957 | 0.00012019
47 | 0.97031 | -0.57433 | 0.00034076 | 8.5404e-05
48 | 0.97032 | -0.57413 | 0 | 0
49 | 0.97019 | -0.57679 | 0.0026671 | 0.00066845
50 | 0.9705 | -0.57069 | 0.00035217 | 8.8262e-05
51 | 0.97027 | -0.57524 | 0.00057943 | 0.00014522
52 | 0.97026 | -0.57549 | 0.00034524 | 8.6526e-05
53 | 0.97022 | -0.57621 | 0.0017718 | 0.00044405
54 | 0.97079 | -0.56483 | 0.0013233 | 0.00033165
55 | 0.97097 | -0.56127 | 0.00052414 | 0.00013136
56 | 0.97077 | -0.56539 | 0.0011119 | 0.00027866
57 | 0.97047 | -0.57118 | 0.001727 | 0.00043283
58 | 0.98004 | -0.38291 | 0.0027568 | 0.00069092
59 | 0.98084 | -0.36732 | 0 | 0
60 | 0.98072 | -0.36964 | 0 | 0
61 | 0.98215 | -0.34172 | 0 | 0
62 | 0.98068 | -0.37053 | 0.0017912 | 0.00044891
63 | 0.98062 | -0.37156 | 0.0021617 | 0.00054177
64 | 0.9821 | -0.34276 | 0.0027709 | 0.00069445
65 | 0.98333 | -0.31891 | 0 | 0
66 | 0.98059 | -0.37215 | 0.0022389 | 0.00056112
67 | 0.98308 | -0.32374 | 0.0019467 | 0.00048788
68 | 0.98421 | -0.30175 | 0.0036755 | 0.00092116
69 | 0.98623 | -0.26277 | 0.0014629 | 0.00036663
70 | 0.98477 | -0.29087 | 0.0050909 | 0.0012759
71 | 0.9854 | -0.27864 | 0.007656 | 0.0019188
72 | 0.98477 | -0.29101 | 0.010813 | 0.0027099
73 | 0.98591 | -0.26863 | 0 | 0
74 | 0.98459 | -0.29443 | 0.00069592 | 0.00017441
75 | 0.9878 | -0.23227 | 0.0022632 | 0.00056721
76 | 0.98371 | -0.31127 | 0.0019232 | 0.000482
77 | 0.98454 | -0.29537 | 0 | 0
78 | 0.98846 | -0.21955 | 0.016559 | 0.00415
79 | 0.98271 | -0.33057 | 0 | 0
80 | 0.98447 | -0.29681 | 0.0014088 | 0.00035308
81 | 0.98889 | -0.21145 | 0.0061076 | 0.0015307
82 | 0.98227 | -0.33922 | 0.0074274 | 0.0018615
83 | 0.98236 | -0.33753 | 0.0055883 | 0.0014006
84 | 0.98446 | -0.29697 | 0.0011331 | 0.00028397
85 | 0.99049 | -0.18069 | 0.0045332 | 0.0011361
86 | 0.98161 | -0.35201 | 0.0046551 | 0.0011667
87 | 0.9823 | -0.33869 | 0.007267 | 0.0018213
88 | 0.98675 | -0.25314 | 0.0034955 | 0.00087606
89 | 0.98727 | -0.24297 | 0.0040316 | 0.0010104
90 | 0.98614 | -0.26509 | 0.00203 | 0.00050877
91 | 0.98604 | -0.26705 | 0.0023853 | 0.00059781
92 | 0.98821 | -0.2245 | 0.00062479 | 0.00015659
93 | 0.98905 | -0.20838 | 0 | 0
94 | 0.98958 | -0.19825 | 0 | 0
95 | 0.98819 | -0.22515 | 0 | 0
96 | 0.98949 | -0.19996 | 0.014932 | 0.0037423
97 | 0.99086 | -0.17366 | 0.013274 | 0.0033268
98 | 0.98807 | -0.22749 | 0.0018209 | 0.00045637
99 | 0.98752 | -0.23814 | 0 | 0
100 | 0.98748 | -0.23886 | 0.0025908 | 0.00064932
101 | 0.98748 | -0.23897 | 0.0013567 | 0.00034003
102 | 0.98806 | -0.22768 | 0.00084637 | 0.00021212
103 | 0.98796 | -0.22968 | 0.0071024 | 0.00178
104 | 0.9914 | -0.16325 | 0 | 0
105 | 0.9914 | -0.16339 | 0.0018304 | 0.00045875
106 | 0.99231 | -0.14582 | 0 | 0
107 | 0.9961 | -0.073769 | 0.014815 | 0.0037129
108 | 0.99846 | -0.028993 | 0.015354 | 0.003848
109 | 1 | 0 | -0.41966 | -0.10753
110 | 0.98051 | -0.37337 | 0.00709 | 0.0017769
111 | 0.98024 | -0.37864 | 0 | 0
112 | 0.97191 | -0.54206 | 0 | 0
113 | 0.97269 | -0.52661 | 0.0029793 | 0.00074668
114 | 0.97164 | -0.54731 | 0.010523 | 0.0026372
115 | 0.97486 | -0.48378 | 0.0058965 | 0.0014778
116 | 0.97623 | -0.45705 | 0.0044642 | 0.0011188
117 | 0.97956 | -0.39197 | 0.0027925 | 0.00069986
118 | 0.97877 | -0.40722 | 0 | 0
119 | 0.97874 | -0.40799 | 0.0023816 | 0.00059688
120 | 0.97818 | -0.4189 | 0.005197 | 0.0013025
121 | 0.97154 | -0.54924 | 0.0041699 | 0.0010451
122 | 0.97237 | -0.53295 | 0.0052943 | 0.0013269
123 | 0.9723 | -0.53431 | 0.0034775 | 0.00087154
124 | 0.97867 | -0.40929 | 0.002856 | 0.00071577
125 | 0.97757 | -0.43078 | 0.0021888 | 0.00054856
126 | 0.97228 | -0.53474 | 0.0029558 | 0.00074079
127 | 0.97731 | -0.43603 | 0.00075584 | 0.00018943
128 | 0.97733 | -0.43569 | 0.0016263 | 0.00040759
129 | 0.97743 | -0.43367 | 0.0019729 | 0.00049444
130 | 0.97739 | -0.43447 | 0.0027343 | 0.00068529
131 | 0.97743 | -0.43371 | 0.0021867 | 0.00054804
132 | 0.97758 | -0.43063 | 0.0014785 | 0.00037055
133 | 0.9782 | -0.41849 | 0 | 0
134 | 0.9786 | -0.41069 | 0 | 0
135 | 0.97805 | -0.42149 | 0.0031768 | 0.00079619
136 | 0.97776 | -0.42706 | 0.0016747 | 0.00041973
137 | 0.97647 | -0.45222 | 0.0041549 | 0.0010413
138 | 0.97696 | -0.44267 | 0.0033727 | 0.00084528
139 | 0.97724 | -0.43716 | 0.0042391 | 0.0010624
140 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.024401 | 0.0061349 | -0.02439 | -0.0061281 | 1.1026e-05 | 6.7919e-06 | 0.037222 | 0.037222 | 0.037222 | 0.97566 | -0.46881 | 0.97518 | -0.47828 | 10.2258
1 | -0.051301 | -0.012877 | 0.051326 | 0.012893 | 2.4941e-05 | 1.5826e-05 | 0.078248 | 0.078248 | 0.078248 | 0.97566 | -0.46881 | 0.97618 | -0.45862 | 21.4968
2 | 0.020995 | 0.0052772 | -0.020983 | -0.0052699 | 1.1937e-05 | 7.2533e-06 | 0.032041 | 0.032041 | 0.032041 | 0.97518 | -0.47828 | 0.97457 | -0.49019 | 8.8026
3 | -0.054766 | -0.013755 | 0.054839 | 0.013801 | 7.2989e-05 | 4.6364e-05 | 0.083492 | 0.083492 | 0.083492 | 0.97618 | -0.45862 | 0.9776 | -0.43073 | 22.9373
4 | 0.019314 | 0.0048517 | -0.019309 | -0.0048485 | 5.2859e-06 | 3.1811e-06 | 0.029493 | 0.029494 | 0.029494 | 0.97457 | -0.49019 | 0.97428 | -0.49593 | 8.1026
5 | -0.056533 | -0.014226 | 0.056544 | 0.014233 | 1.1129e-05 | 7.0721e-06 | 0.08607 | 0.08607 | 0.08607 | 0.9776 | -0.43073 | 0.97781 | -0.42661 | 23.6456
6 | 0.016964 | 0.0042609 | -0.016958 | -0.0042574 | 5.9803e-06 | 3.5318e-06 | 0.025913 | 0.025913 | 0.025913 | 0.97428 | -0.49593 | 0.9739 | -0.50332 | 7.1189
7 | -0.068415 | -0.017208 | 0.068486 | 0.017253 | 7.0576e-05 | 4.4951e-05 | 0.10414 | 0.10414 | 0.10414 | 0.97781 | -0.42661 | 0.97891 | -0.40504 | 28.6088
8 | 0.011871 | 0.0029756 | -0.01187 | -0.0029746 | 1.8373e-06 | 9.876e-07 | 0.018066 | 0.018066 | 0.018066 | 0.97781 | -0.42661 | 0.97764 | -0.42986 | 4.9632
9 | 0.01518 | 0.0038118 | -0.015168 | -0.003805 | 1.18e-05 | 6.8248e-06 | 0.023196 | 0.023197 | 0.023197 | 0.9739 | -0.50332 | 0.97308 | -0.51963 | 6.3727
10 | -0.070818 | -0.017838 | 0.070881 | 0.017878 | 6.2642e-05 | 3.9909e-05 | 0.10768 | 0.10768 | 0.10768 | 0.97891 | -0.40504 | 0.97985 | -0.38656 | 29.5827
11 | 0.0096927 | 0.002429 | -0.0096878 | -0.0024266 | 4.9522e-06 | 2.409e-06 | 0.014753 | 0.014753 | 0.014753 | 0.97764 | -0.42986 | 0.9771 | -0.44059 | 4.053
12 | 0.015168 | 0.003805 | -0.015164 | -0.0038022 | 4.6833e-06 | 2.7091e-06 | 0.023197 | 0.023197 | 0.023197 | 0.97308 | -0.51963 | 0.97275 | -0.5261 | 6.3727
13 | -0.072069 | -0.018175 | 0.072082 | 0.018183 | 1.2601e-05 | 8.0295e-06 | 0.10949 | 0.10949 | 0.10949 | 0.97985 | -0.38656 | 0.98004 | -0.38291 | 30.0786
14 | 0.0071571 | 0.0017924 | -0.0071536 | -0.0017911 | 3.5415e-06 | 1.2714e-06 | 0.010899 | 0.010899 | 0.010899 | 0.9771 | -0.44059 | 0.97657 | -0.45099 | 2.9943
15 | 0.0038969 | 0.00097648 | -0.0038968 | -0.00097652 | 1.2019e-07 | -3.8522e-08 | 0.0059156 | 0.0059157 | 0.0059157 | 0.98022 | -0.37982 | 0.98018 | -0.38047 | 1.6252
16 | -0.0047345 | -0.0011864 | 0.0047349 | 0.0011864 | 3.7784e-07 | -4.0867e-09 | 0.0071871 | 0.007187 | 0.0071871 | 0.98022 | -0.37982 | 0.9803 | -0.37814 | 1.9745
17 | 0.0033798 | 0.00084696 | -0.0033797 | -0.00084704 | 1.2199e-07 | -7.7674e-08 | 0.0051309 | 0.0051309 | 0.0051309 | 0.98018 | -0.38047 | 0.98015 | -0.38122 | 1.4096
18 | -0.0058393 | -0.0014632 | 0.0058421 | 0.0014638 | 2.7874e-06 | 5.9041e-07 | 0.0088635 | 0.0088631 | 0.0088635 | 0.9803 | -0.37814 | 0.98081 | -0.36812 | 2.435
19 | -0.0076405 | -0.0019145 | 0.0076451 | 0.0019163 | 4.6162e-06 | 1.7973e-06 | 0.011591 | 0.011591 | 0.011591 | 0.98081 | -0.36812 | 0.98146 | -0.35544 | 3.1845
20 | -0.0095105 | -0.0023838 | 0.009512 | 0.0023845 | 1.4721e-06 | 7.0348e-07 | 0.014419 | 0.014419 | 0.014419 | 0.98146 | -0.35544 | 0.98163 | -0.3522 | 3.9613
21 | -0.00034425 | -8.6278e-05 | 0.00034425 | 8.6095e-05 | 1.5169e-09 | -1.8289e-07 | 0.00052461 | 0.00052455 | 0.00052461 | 0.97644 | -0.45357 | 0.97644 | -0.45348 | 0.14412
22 | -0.00091453 | -0.00022902 | 0.00091454 | 0.00022884 | 1.074e-08 | -1.7759e-07 | 0.0013936 | 0.0013935 | 0.0013936 | 0.97644 | -0.45348 | 0.97645 | -0.45323 | 0.38286
23 | -0.0012762 | -0.00031949 | 0.0012764 | 0.00031859 | 1.1049e-07 | -9.0408e-07 | 0.0019447 | 0.0019444 | 0.0019447 | 0.97645 | -0.45323 | 0.97655 | -0.45141 | 0.53427
24 | -0.0014592 | -0.00036441 | 0.0014592 | 0.00036423 | 2.9449e-08 | -1.7998e-07 | 0.002223 | 0.0022229 | 0.002223 | 0.97655 | -0.45141 | 0.97657 | -0.45099 | 0.61071
25 | -0.009512 | -0.0023845 | 0.0095125 | 0.0023848 | 5.1708e-07 | 2.4709e-07 | 0.014419 | 0.014419 | 0.014419 | 0.98163 | -0.3522 | 0.98168 | -0.35105 | 3.9613
26 | -0.0095125 | -0.0023848 | 0.009517 | 0.0023869 | 4.4677e-06 | 2.1344e-06 | 0.014419 | 0.014419 | 0.014419 | 0.98168 | -0.35105 | 0.98219 | -0.3412 | 3.9613
27 | -0.01122 | -0.0028136 | 0.011222 | 0.0028149 | 2.4248e-06 | 1.2686e-06 | 0.016998 | 0.016998 | 0.016998 | 0.98219 | -0.3412 | 0.98242 | -0.33667 | 4.6698
28 | -0.012775 | -0.0032042 | 0.012779 | 0.0032063 | 3.7725e-06 | 2.0741e-06 | 0.019351 | 0.019351 | 0.019351 | 0.98242 | -0.33667 | 0.98274 | -0.33048 | 5.3162
29 | -0.014682 | -0.0036832 | 0.014687 | 0.0036859 | 4.7152e-06 | 2.6953e-06 | 0.022232 | 0.022232 | 0.022232 | 0.98274 | -0.33048 | 0.98308 | -0.32374 | 6.1077
30 | 0.0017188 | 0.0004305 | -0.0017187 | -0.00043075 | 5.5721e-08 | -2.4532e-07 | 0.0025954 | 0.0025955 | 0.0025955 | 0.98538 | -0.27979 | 0.98535 | -0.28047 | 0.71305
31 | -0.0052247 | -0.0013092 | 0.0052251 | 0.0013092 | 3.9965e-07 | 3.7658e-08 | 0.0078897 | 0.0078896 | 0.0078897 | 0.98538 | -0.27979 | 0.98547 | -0.27819 | 2.1675
32 | -0.0052251 | -0.0013092 | 0.0052253 | 0.0013092 | 1.8268e-07 | 1.7199e-08 | 0.0078896 | 0.0078896 | 0.0078896 | 0.98547 | -0.27819 | 0.9855 | -0.27745 | 2.1675
33 | -0.0052253 | -0.0013092 | 0.0052265 | 0.0013093 | 1.2262e-06 | 1.1523e-07 | 0.0078896 | 0.0078893 | 0.0078896 | 0.9855 | -0.27745 | 0.98576 | -0.27252 | 2.1675
34 | -0.0083048 | -0.0020808 | 0.008307 | 0.0020818 | 2.1675e-06 | 9.1819e-07 | 0.012536 | 0.012536 | 0.012536 | 0.98576 | -0.27252 | 0.98604 | -0.26705 | 3.444
35 | 0.0056943 | 0.0014269 | -0.0056937 | -0.0014267 | 6.6533e-07 | 1.3098e-07 | 0.0086765 | 0.0086766 | 0.0086766 | 0.97657 | -0.45099 | 0.97644 | -0.45344 | 2.3837
36 | 0.015164 | 0.0038022 | -0.015148 | -0.0037933 | 1.5493e-05 | 8.9633e-06 | 0.023197 | 0.023197 | 0.023197 | 0.97275 | -0.5261 | 0.97166 | -0.54756 | 6.3728
37 | -0.011009 | -0.0027591 | 0.01101 | 0.0027595 | 8.2834e-07 | 4.3452e-07 | 0.016888 | 0.016888 | 0.016888 | 0.97 | -0.57975 | 0.97008 | -0.57817 | 4.6395
38 | -0.021295 | -0.0053374 | 0.021299 | 0.0053395 | 3.4899e-06 | 2.1259e-06 | 0.032665 | 0.032665 | 0.032665 | 0.97008 | -0.57817 | 0.97025 | -0.57473 | 8.974
39 | -0.031301 | -0.0078463 | 0.03133 | 0.0078644 | 2.89e-05 | 1.8083e-05 | 0.048005 | 0.048005 | 0.048005 | 0.97025 | -0.57473 | 0.97123 | -0.55537 | 13.1882
40 | -0.038041 | -0.0095462 | 0.038065 | 0.0095614 | 2.4165e-05 | 1.5231e-05 | 0.058286 | 0.058286 | 0.058286 | 0.97123 | -0.55537 | 0.97191 | -0.54206 | 16.0126
41 | 0.011236 | 0.0028127 | -0.01123 | -0.0028096 | 5.7807e-06 | 3.055e-06 | 0.017205 | 0.017205 | 0.017205 | 0.97166 | -0.54756 | 0.97112 | -0.55838 | 4.7267
42 | 0.0065415 | 0.0016372 | -0.0065377 | -0.001636 | 3.83e-06 | 1.1941e-06 | 0.010023 | 0.010023 | 0.010023 | 0.97112 | -0.55838 | 0.9705 | -0.57069 | 2.7536
43 | 0.0046882 | 0.0011724 | -0.0046876 | -0.0011724 | 6.4408e-07 | 3.864e-10 | 0.0071827 | 0.0071829 | 0.0071829 | 0.97112 | -0.55838 | 0.97097 | -0.56127 | 1.9733
44 | -0.0046754 | -0.0011716 | 0.0046755 | 0.0011716 | 1.0655e-07 | -1.8e-09 | 0.0071254 | 0.0071254 | 0.0071254 | 0.97636 | -0.455 | 0.97639 | -0.45452 | 1.9575
45 | 0.0043149 | 0.0010812 | -0.0043146 | -0.0010813 | 3.8761e-07 | -5.0822e-08 | 0.0065761 | 0.0065762 | 0.0065762 | 0.97636 | -0.455 | 0.97627 | -0.45689 | 1.8066
46 | -0.0051925 | -0.0013012 | 0.0051928 | 0.0013012 | 2.6728e-07 | 2.8694e-08 | 0.0079133 | 0.0079132 | 0.0079133 | 0.97639 | -0.45452 | 0.97644 | -0.45344 | 2.174
47 | 0.0023155 | 0.00058029 | -0.0023155 | -0.00058032 | 1.4171e-08 | -2.8866e-08 | 0.0035293 | 0.0035293 | 0.0035293 | 0.97627 | -0.45689 | 0.97626 | -0.45701 | 0.96958
48 | -0.00047957 | -0.00012019 | 0.00047957 | 0.00012008 | 1.9127e-09 | -1.1526e-07 | 0.00073544 | 0.00073539 | 0.00073544 | 0.97031 | -0.57442 | 0.97031 | -0.57433 | 0.20204
49 | -0.00082033 | -0.00020548 | 0.00082034 | 0.00020532 | 7.9445e-09 | -1.6028e-07 | 0.001258 | 0.0012579 | 0.001258 | 0.97031 | -0.57433 | 0.97032 | -0.57413 | 0.3456
50 | 0.0026675 | 0.000668 | -0.0026671 | -0.00066845 | 3.3802e-07 | -4.4898e-07 | 0.0040904 | 0.0040907 | 0.0040907 | 0.97032 | -0.57413 | 0.97019 | -0.57679 | 1.1238
51 | -0.0034878 | -0.00087332 | 0.0034884 | 0.00087302 | 5.7205e-07 | -2.9277e-07 | 0.0053483 | 0.0053481 | 0.0053483 | 0.97032 | -0.57413 | 0.9705 | -0.57069 | 1.4693
52 | 0.0026971 | 0.00067475 | -0.0026965 | -0.0006755 | 5.843e-07 | -7.5176e-07 | 0.0041349 | 0.0041353 | 0.0041353 | 0.9705 | -0.57069 | 0.97027 | -0.57524 | 1.1361
53 | 0.0021171 | 0.00053028 | -0.0021171 | -0.00053034 | 2.5088e-08 | -6.2329e-08 | 0.0032467 | 0.0032467 | 0.0032467 | 0.97027 | -0.57524 | 0.97026 | -0.57549 | 0.89196
54 | 0.0017718 | 0.00044382 | -0.0017718 | -0.00044405 | 6.0834e-08 | -2.324e-07 | 0.0027173 | 0.0027174 | 0.0027174 | 0.97026 | -0.57549 | 0.97022 | -0.57621 | 0.74653
55 | -0.0041628 | -0.0010411 | 0.0041635 | 0.001041 | 7.0527e-07 | -1.2006e-07 | 0.0063798 | 0.0063796 | 0.0063798 | 0.97079 | -0.56483 | 0.97097 | -0.56127 | 1.7527
56 | 0.0028394 | 0.00070948 | -0.0028394 | -0.00070956 | 7.5001e-08 | -8.2589e-08 | 0.0043515 | 0.0043515 | 0.0043515 | 0.97079 | -0.56483 | 0.97077 | -0.56539 | 1.1955
57 | 0.0017275 | 0.0004309 | -0.001727 | -0.00043283 | 4.7581e-07 | -1.9326e-06 | 0.0026472 | 0.002648 | 0.002648 | 0.97077 | -0.56539 | 0.97047 | -0.57118 | 0.72748
58 | -0.074839 | -0.018874 | 0.074895 | 0.01891 | 5.5908e-05 | 3.5636e-05 | 0.11367 | 0.11367 | 0.11367 | 0.98004 | -0.38291 | 0.98084 | -0.36732 | 31.2285
59 | 0.006193 | 0.0015515 | -0.0061923 | -0.0015513 | 6.8465e-07 | 1.7715e-07 | 0.0093951 | 0.0093951 | 0.0093951 | 0.98084 | -0.36732 | 0.98072 | -0.36964 | 2.5811
60 | -0.081088 | -0.020462 | 0.081187 | 0.020525 | 9.9551e-05 | 6.3491e-05 | 0.12307 | 0.12307 | 0.12307 | 0.98084 | -0.36732 | 0.98215 | -0.34172 | 33.8096
61 | 0.0017912 | 0.00044861 | -0.0017912 | -0.00044891 | 7.6175e-08 | -2.9826e-07 | 0.0027177 | 0.0027178 | 0.0027178 | 0.98072 | -0.36964 | 0.98068 | -0.37053 | 0.74665
62 | 0.0044011 | 0.0011027 | -0.0044007 | -0.0011027 | 4.0235e-07 | -4.6095e-08 | 0.0066775 | 0.0066776 | 0.0066776 | 0.98072 | -0.36964 | 0.98062 | -0.37156 | 1.8345
63 | 0.002771 | 0.00069427 | -0.0027709 | -0.00069445 | 1.3814e-07 | -1.7607e-07 | 0.0041982 | 0.0041982 | 0.0041982 | 0.98215 | -0.34172 | 0.9821 | -0.34276 | 1.1534
64 | -0.083958 | -0.021219 | 0.08405 | 0.021278 | 9.1918e-05 | 5.8636e-05 | 0.12726 | 0.12726 | 0.12726 | 0.98215 | -0.34172 | 0.98333 | -0.31891 | 34.9629
65 | 0.002239 | 0.00056098 | -0.0022389 | -0.00056112 | 6.3469e-08 | -1.4436e-07 | 0.0033974 | 0.0033975 | 0.0033975 | 0.98062 | -0.37156 | 0.98059 | -0.37215 | 0.93337
66 | 0.016637 | 0.004176 | -0.016633 | -0.0041738 | 3.8334e-06 | 2.2489e-06 | 0.025178 | 0.025179 | 0.025179 | 0.98333 | -0.31891 | 0.98308 | -0.32374 | 6.9172
67 | -0.10069 | -0.025454 | 0.10077 | 0.025507 | 8.2906e-05 | 5.2939e-05 | 0.15244 | 0.15244 | 0.15244 | 0.98333 | -0.31891 | 0.98421 | -0.30175 | 41.88
68 | -0.10445 | -0.026428 | 0.10464 | 0.026553 | 0.00019582 | 0.00012506 | 0.158 | 0.158 | 0.158 | 0.98421 | -0.30175 | 0.98623 | -0.26277 | 43.4066
69 | -0.1061 | -0.02692 | 0.1063 | 0.027045 | 0.00019565 | 0.00012496 | 0.16021 | 0.16021 | 0.16021 | 0.98623 | -0.26277 | 0.98821 | -0.2245 | 44.013
70 | -0.019142 | -0.0047964 | 0.019153 | 0.004803 | 1.1158e-05 | 6.6882e-06 | 0.028924 | 0.028924 | 0.028924 | 0.98477 | -0.29087 | 0.9854 | -0.27864 | 7.9462
71 | 0.014051 | 0.0035205 | -0.014051 | -0.0035204 | 9.2017e-08 | 5.1966e-08 | 0.021232 | 0.021232 | 0.021232 | 0.98477 | -0.29087 | 0.98477 | -0.29101 | 5.8329
72 | -0.026809 | -0.0067218 | 0.026822 | 0.0067297 | 1.2797e-05 | 7.9246e-06 | 0.040485 | 0.040485 | 0.040485 | 0.9854 | -0.27864 | 0.98591 | -0.26863 | 11.1222
73 | 0.0032386 | 0.00081048 | -0.0032381 | -0.00081089 | 5.272e-07 | -4.0944e-07 | 0.0048932 | 0.0048935 | 0.0048935 | 0.98477 | -0.29101 | 0.98459 | -0.29443 | 1.3444
74 | -0.18283 | -0.046396 | 0.18315 | 0.0466 | 0.00032038 | 0.00020375 | 0.27615 | 0.27615 | 0.27615 | 0.98591 | -0.26863 | 0.9878 | -0.23227 | 25.2882
75 | 0.15601 | 0.039666 | -0.15569 | -0.039463 | 0.00031969 | 0.00020284 | 0.23566 | 0.23566 | 0.23566 | 0.98591 | -0.26863 | 0.98371 | -0.31127 | 21.5808
76 | 0.0025422 | 0.00063648 | -0.002542 | -0.00063667 | 1.1413e-07 | -1.8921e-07 | 0.0038417 | 0.0038418 | 0.0038418 | 0.98459 | -0.29443 | 0.98454 | -0.29537 | 1.0554
77 | -0.18541 | -0.047167 | 0.18553 | 0.047239 | 0.00011369 | 7.2316e-05 | 0.27956 | 0.27956 | 0.27956 | 0.9878 | -0.23227 | 0.98846 | -0.21955 | 25.6003
78 | 0.15377 | 0.038981 | -0.15362 | -0.038891 | 0.00014256 | 9.0437e-05 | 0.23275 | 0.23275 | 0.23275 | 0.98371 | -0.31127 | 0.98271 | -0.33057 | 21.3145
79 | 0.002542 | 0.00063667 | -0.0025419 | -0.00063696 | 1.7345e-07 | -2.8747e-07 | 0.0038418 | 0.003842 | 0.003842 | 0.98454 | -0.29537 | 0.98447 | -0.29681 | 1.0555
80 | -0.20209 | -0.051389 | 0.20217 | 0.05144 | 7.8955e-05 | 5.0269e-05 | 0.30448 | 0.30448 | 0.30448 | 0.98846 | -0.21955 | 0.98889 | -0.21145 | 27.883
81 | 0.14076 | 0.035667 | -0.1407 | -0.03563 | 5.8425e-05 | 3.7002e-05 | 0.21328 | 0.21328 | 0.21328 | 0.98271 | -0.33057 | 0.98227 | -0.33922 | 19.5312
82 | 0.01286 | 0.0032244 | -0.012856 | -0.003222 | 4.2615e-06 | 2.3478e-06 | 0.019473 | 0.019473 | 0.019473 | 0.98271 | -0.33057 | 0.98236 | -0.33753 | 5.3498
83 | 0.0011331 | 0.00028388 | -0.0011331 | -0.00028397 | 8.6976e-09 | -9.4979e-08 | 0.0017126 | 0.0017126 | 0.0017126 | 0.98447 | -0.29681 | 0.98446 | -0.29697 | 0.4705
84 | -0.20827 | -0.05297 | 0.20858 | 0.053167 | 0.00030918 | 0.0001969 | 0.31367 | 0.31367 | 0.31367 | 0.98889 | -0.21145 | 0.99049 | -0.18069 | 28.7246
85 | 0.13328 | 0.033768 | -0.13319 | -0.033716 | 8.1851e-05 | 5.1776e-05 | 0.20203 | 0.20203 | 0.20203 | 0.98227 | -0.33922 | 0.98161 | -0.35201 | 18.5009
86 | 0.0072674 | 0.0018214 | -0.007267 | -0.0018213 | 3.9982e-07 | 1.445e-07 | 0.011008 | 0.011008 | 0.011008 | 0.98236 | -0.33753 | 0.9823 | -0.33869 | 3.0243
87 | -0.21312 | -0.054303 | 0.21347 | 0.054532 | 0.00035919 | 0.0002288 | 0.32048 | 0.32048 | 0.32048 | 0.99049 | -0.18069 | 0.99231 | -0.14582 | 29.3482
88 | 0.12854 | 0.03255 | -0.12841 | -0.032466 | 0.00013168 | 8.3227e-05 | 0.19497 | 0.19497 | 0.19497 | 0.98161 | -0.35201 | 0.98051 | -0.37337 | 17.8547
89 | -0.016226 | -0.0040689 | 0.016234 | 0.0040735 | 7.8695e-06 | 4.5885e-06 | 0.02447 | 0.024469 | 0.02447 | 0.98675 | -0.25314 | 0.98727 | -0.24297 | 6.7224
90 | 0.012731 | 0.0031928 | -0.012723 | -0.0031888 | 7.2511e-06 | 3.971e-06 | 0.019198 | 0.019199 | 0.019199 | 0.98675 | -0.25314 | 0.98614 | -0.26509 | 5.2744
91 | -0.020266 | -0.0050839 | 0.02027 | 0.0050867 | 4.6598e-06 | 2.8119e-06 | 0.030546 | 0.030546 | 0.030546 | 0.98727 | -0.24297 | 0.98752 | -0.23814 | 8.3917
92 | 0.010693 | 0.0026801 | -0.010692 | -0.0026796 | 9.951e-07 | 5.0684e-07 | 0.016136 | 0.016136 | 0.016136 | 0.98614 | -0.26509 | 0.98604 | -0.26705 | 4.4328
93 | -0.10692 | -0.027201 | 0.10701 | 0.027254 | 8.3146e-05 | 5.3104e-05 | 0.16115 | 0.16115 | 0.16115 | 0.98821 | -0.2245 | 0.98905 | -0.20838 | 44.2714
94 | -0.14104 | -0.035806 | 0.14111 | 0.03585 | 6.8792e-05 | 4.3975e-05 | 0.21236 | 0.21236 | 0.21236 | 0.98905 | -0.20838 | 0.98958 | -0.19825 | 58.3395
95 | 0.034032 | 0.0085515 | -0.034004 | -0.0085345 | 2.7222e-05 | 1.7067e-05 | 0.051208 | 0.051208 | 0.051208 | 0.98905 | -0.20838 | 0.98819 | -0.22515 | 14.0682
96 | 0.014933 | 0.003743 | -0.014932 | -0.0037423 | 1.2217e-06 | 6.9886e-07 | 0.022455 | 0.022455 | 0.022455 | 0.98958 | -0.19825 | 0.98949 | -0.19996 | 6.1689
97 | -0.15604 | -0.039593 | 0.15623 | 0.039711 | 0.00018476 | 0.00011779 | 0.23481 | 0.23481 | 0.23481 | 0.98958 | -0.19825 | 0.99086 | -0.17366 | 32.2542
98 | 0.0097715 | 0.0024493 | -0.0097704 | -0.0024488 | 1.0912e-06 | 5.262e-07 | 0.014714 | 0.014714 | 0.014714 | 0.98819 | -0.22515 | 0.98807 | -0.22749 | 4.0423
99 | 0.024233 | 0.0060852 | -0.024218 | -0.006076 | 1.5012e-05 | 9.2226e-06 | 0.036494 | 0.036494 | 0.036494 | 0.98819 | -0.22515 | 0.98752 | -0.23814 | 10.0259
100 | -0.1695 | -0.043037 | 0.16959 | 0.043091 | 8.4948e-05 | 5.3962e-05 | 0.25474 | 0.25474 | 0.25474 | 0.99086 | -0.17366 | 0.9914 | -0.16325 | 23.3283
101 | 0.0079495 | 0.0019924 | -0.0079494 | -0.0019924 | 6.8626e-08 | 2.7567e-08 | 0.011972 | 0.011972 | 0.011972 | 0.98807 | -0.22749 | 0.98806 | -0.22768 | 3.289
102 | 0.0039477 | 0.00098925 | -0.0039475 | -0.0009893 | 1.3501e-07 | -4.3765e-08 | 0.0059484 | 0.0059484 | 0.0059484 | 0.98752 | -0.23814 | 0.98748 | -0.23886 | 1.6342
103 | 0.0013567 | 0.00033998 | -0.0013567 | -0.00034003 | 6.7471e-09 | -5.0752e-08 | 0.0020444 | 0.0020444 | 0.0020444 | 0.98748 | -0.23886 | 0.98748 | -0.23897 | 0.56165
104 | 0.007103 | 0.0017803 | -0.0071024 | -0.00178 | 6.7681e-07 | 2.3117e-07 | 0.010697 | 0.010697 | 0.010697 | 0.98806 | -0.22768 | 0.98796 | -0.22968 | 2.9388
105 | 0.0018304 | 0.0004587 | -0.0018304 | -0.00045875 | 1.2262e-08 | -4.8012e-08 | 0.0027473 | 0.0027473 | 0.0027473 | 0.9914 | -0.16325 | 0.9914 | -0.16339 | 0.75476
106 | -0.17142 | -0.04355 | 0.17156 | 0.043642 | 0.00014396 | 9.1461e-05 | 0.25749 | 0.25749 | 0.25749 | 0.9914 | -0.16325 | 0.99231 | -0.14582 | 23.5798
107 | -0.38503 | -0.098174 | 0.38638 | 0.099033 | 0.0013444 | 0.00085918 | 0.57797 | 0.57797 | 0.57797 | 0.99231 | -0.14582 | 0.9961 | -0.073769 | 52.928
108 | -0.40119 | -0.10275 | 0.40207 | 0.1033 | 0.00087233 | 0.00055753 | 0.6001 | 0.6001 | 0.6001 | 0.9961 | -0.073769 | 0.99846 | -0.028993 | 54.9545
109 | -0.41742 | -0.10715 | 0.41801 | 0.10753 | 0.00058828 | 0.00037602 | 0.62298 | 0.62298 | 0.62298 | 0.99846 | -0.028993 | 1 | 0 | 57.0499
110 | 0.12132 | 0.03069 | -0.12129 | -0.03067 | 3.0672e-05 | 1.9357e-05 | 0.18421 | 0.18421 | 0.18421 | 0.98051 | -0.37337 | 0.98024 | -0.37864 | 16.8694
111 | 0.12129 | 0.03067 | -0.12121 | -0.030621 | 7.7517e-05 | 4.892e-05 | 0.18421 | 0.18421 | 0.18421 | 0.98024 | -0.37864 | 0.97956 | -0.39197 | 16.8694
112 | -0.052761 | -0.013246 | 0.0528 | 0.01327 | 3.8918e-05 | 2.471e-05 | 0.080787 | 0.080787 | 0.080787 | 0.97191 | -0.54206 | 0.97269 | -0.52661 | 22.1943
113 | 0.014697 | 0.0036844 | -0.014693 | -0.0036822 | 3.6796e-06 | 2.1148e-06 | 0.022501 | 0.022502 | 0.022502 | 0.97191 | -0.54206 | 0.97164 | -0.54731 | 6.1817
114 | 0.011732 | 0.0029412 | -0.011728 | -0.0029393 | 3.5441e-06 | 1.9042e-06 | 0.017947 | 0.017947 | 0.017947 | 0.97269 | -0.52661 | 0.97237 | -0.53295 | 4.9306
115 | -0.067511 | -0.016958 | 0.067649 | 0.017046 | 0.0001383 | 8.808e-05 | 0.10329 | 0.10329 | 0.10329 | 0.97269 | -0.52661 | 0.97486 | -0.48378 | 28.377
116 | 0.0041702 | 0.001045 | -0.0041699 | -0.0010451 | 3.8372e-07 | -6.5113e-08 | 0.0063865 | 0.0063866 | 0.0063866 | 0.97164 | -0.54731 | 0.97154 | -0.54924 | 1.7546
117 | -0.073546 | -0.018524 | 0.07364 | 0.018584 | 9.4133e-05 | 5.9997e-05 | 0.11229 | 0.11229 | 0.11229 | 0.97486 | -0.48378 | 0.97623 | -0.45705 | 30.8496
118 | -0.078104 | -0.019703 | 0.078122 | 0.019715 | 1.8067e-05 | 1.1521e-05 | 0.1191 | 0.1191 | 0.1191 | 0.97623 | -0.45705 | 0.97647 | -0.45222 | 32.7189
119 | 0.11842 | 0.029921 | -0.11833 | -0.029867 | 8.649e-05 | 5.4548e-05 | 0.17997 | 0.17997 | 0.17997 | 0.97956 | -0.39197 | 0.97877 | -0.40722 | 16.481
120 | 0.020861 | 0.0052307 | -0.020861 | -0.0052305 | 7.635e-07 | 2.5971e-07 | 0.031716 | 0.031716 | 0.031716 | 0.97877 | -0.40722 | 0.97874 | -0.40799 | 2.9044
121 | 0.097469 | 0.024636 | -0.097415 | -0.024602 | 5.4572e-05 | 3.4178e-05 | 0.14826 | 0.14826 | 0.14826 | 0.97877 | -0.40722 | 0.97818 | -0.4189 | 13.5766
122 | 0.018479 | 0.0046336 | -0.018478 | -0.0046333 | 1.1451e-06 | 2.9536e-07 | 0.028096 | 0.028096 | 0.028096 | 0.97874 | -0.40799 | 0.97867 | -0.40929 | 2.5729
123 | 0.092218 | 0.023299 | -0.092165 | -0.023267 | 5.2461e-05 | 3.2773e-05 | 0.14035 | 0.14035 | 0.14035 | 0.97818 | -0.4189 | 0.97757 | -0.43078 | 12.8527
124 | 0.0064338 | 0.0016124 | -0.0064334 | -0.0016123 | 4.1838e-07 | 1.2501e-07 | 0.0098456 | 0.0098457 | 0.0098457 | 0.97237 | -0.53295 | 0.9723 | -0.53431 | 2.7049
125 | 0.0029559 | 0.00074073 | -0.0029558 | -0.00074079 | 6.0165e-08 | -5.8732e-08 | 0.0045236 | 0.0045237 | 0.0045237 | 0.9723 | -0.53431 | 0.97228 | -0.53474 | 1.2428
126 | 0.015622 | 0.0039175 | -0.015621 | -0.0039174 | 1.0464e-06 | 1.1044e-07 | 0.023753 | 0.023754 | 0.023754 | 0.97867 | -0.40929 | 0.9786 | -0.41069 | 2.1752
127 | 0.089977 | 0.022718 | -0.089949 | -0.022701 | 2.7515e-05 | 1.7169e-05 | 0.13702 | 0.13702 | 0.13702 | 0.97757 | -0.43078 | 0.97724 | -0.43716 | 12.5476
128 | -0.00075584 | -0.00018943 | 0.00075586 | 0.00018913 | 1.2162e-08 | -2.9911e-07 | 0.0011508 | 0.0011507 | 0.0011508 | 0.97731 | -0.43603 | 0.97733 | -0.43569 | 0.31616
129 | -0.0023822 | -0.00059673 | 0.0023824 | 0.00059629 | 2.2908e-07 | -4.3544e-07 | 0.0036268 | 0.0036266 | 0.0036268 | 0.97733 | -0.43569 | 0.97743 | -0.43367 | 0.99638
130 | 0.0049212 | 0.0012332 | -0.0049211 | -0.0012332 | 1.0285e-08 | 4.5786e-10 | 0.0074918 | 0.0074918 | 0.0074918 | 0.97743 | -0.43367 | 0.97743 | -0.43371 | 2.0582
131 | -0.0092764 | -0.0023239 | 0.0092777 | 0.0023246 | 1.3418e-06 | 6.3384e-07 | 0.014122 | 0.014122 | 0.014122 | 0.97743 | -0.43367 | 0.97758 | -0.43063 | 3.8796
132 | -0.0027343 | -0.00068529 | 0.0027344 | 0.00068516 | 9.7929e-08 | -1.262e-07 | 0.0041628 | 0.0041628 | 0.0041628 | 0.97739 | -0.43447 | 0.97743 | -0.43371 | 1.1436
133 | -0.010756 | -0.0026951 | 0.010758 | 0.0026961 | 1.833e-06 | 9.4444e-07 | 0.016372 | 0.016372 | 0.016372 | 0.97758 | -0.43063 | 0.97776 | -0.42706 | 4.4979
134 | -0.015615 | -0.0039151 | 0.015621 | 0.0039174 | 5.8041e-06 | 2.3367e-06 | 0.023754 | 0.023754 | 0.023754 | 0.9782 | -0.41849 | 0.9786 | -0.41069 | 3.2629
135 | 0.015615 | 0.0039151 | -0.015613 | -0.0039138 | 2.2307e-06 | 1.2953e-06 | 0.023754 | 0.023754 | 0.023754 | 0.9782 | -0.41849 | 0.97805 | -0.42149 | 6.5258
136 | 0.012436 | 0.0031176 | -0.012433 | -0.0031158 | 3.2971e-06 | 1.802e-06 | 0.018921 | 0.018921 | 0.018921 | 0.97805 | -0.42149 | 0.97776 | -0.42706 | 5.198
137 | -0.082277 | -0.020756 | 0.082315 | 0.020779 | 3.761e-05 | 2.3352e-05 | 0.12543 | 0.12543 | 0.12543 | 0.97647 | -0.45222 | 0.97696 | -0.44267 | 11.4861
138 | -0.085688 | -0.021624 | 0.08571 | 0.021639 | 2.2623e-05 | 1.408e-05 | 0.13057 | 0.13056 | 0.13057 | 0.97696 | -0.44267 | 0.97724 | -0.43716 | 11.9565

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45114 | 0.11542

## res_load
| p_mw | q_mvar
0 | 0.0269 | 0.0067418
1 | 0.0033952 | 0.00085092
2 | 0.0034398 | 0.0008621
3 | 0.0016687 | 0.00041821
4 | 0.001694 | 0.00042456
5 | 0.0023446 | 0.00058761
6 | 0.0017779 | 0.00044559
7 | 0.0023322 | 0.0005845
8 | 0.0021768 | 0.00054556
9 | 0.0011887 | 0.00029792
10 | 0.0025307 | 0.00063425
11 | 0.00083758 | 0.00020992
12 | 0.00051695 | 0.00012956
13 | 0.0011045 | 0.00027681
14 | 0.0033797 | 0.00084704
15 | 0.0017983 | 0.00045071
16 | 0.0018655 | 0.00046753
17 | 0.00034425 | 8.6278e-05
18 | 0.00057028 | 0.00014292
19 | 0.0003617 | 9.0652e-05
20 | 0.00018284 | 4.5825e-05
21 | 0.0017025 | 0.00042669
22 | 0.0015534 | 0.00038931
23 | 0.0019029 | 0.00047692
24 | 0.003506 | 0.00087867
25 | 0.0017187 | 0.00043075
26 | 0.0030783 | 0.0007715
27 | 0.011009 | 0.0027591
28 | 0.010286 | 0.0025779
29 | 0.010002 | 0.0025068
30 | 0.0067105 | 0.0016818
31 | 0.0039127 | 0.00098063
32 | 0.00036045 | 9.0337e-05
33 | 0.00051699 | 0.00012957
34 | 0.001999 | 0.00050101
35 | 0.00050091 | 0.00012554
36 | 0.0023155 | 0.00058032
37 | 0.00047957 | 0.00012019
38 | 0.00034076 | 8.5404e-05
39 | 0.0026671 | 0.00066845
40 | 0.00035217 | 8.8262e-05
41 | 0.00057943 | 0.00014522
42 | 0.00034524 | 8.6526e-05
43 | 0.0017718 | 0.00044405
44 | 0.0013233 | 0.00033165
45 | 0.00052414 | 0.00013136
46 | 0.0011119 | 0.00027866
47 | 0.001727 | 0.00043283
48 | 0.0027568 | 0.00069092
49 | 0.0017912 | 0.00044891
50 | 0.0021617 | 0.00054177
51 | 0.0027709 | 0.00069445
52 | 0.0022389 | 0.00056112
53 | 0.0019467 | 0.00048788
54 | 0.0036755 | 0.00092116
55 | 0.0014629 | 0.00036663
56 | 0.0050909 | 0.0012759
57 | 0.007656 | 0.0019188
58 | 0.010813 | 0.0027099
59 | 0.00069592 | 0.00017441
60 | 0.0022632 | 0.00056721
61 | 0.0019232 | 0.000482
62 | 0.016559 | 0.00415
63 | 0.0014088 | 0.00035308
64 | 0.0061076 | 0.0015307
65 | 0.0074274 | 0.0018615
66 | 0.0055883 | 0.0014006
67 | 0.0011331 | 0.00028397
68 | 0.0045332 | 0.0011361
69 | 0.0046551 | 0.0011667
70 | 0.007267 | 0.0018213
71 | 0.0034955 | 0.00087606
72 | 0.0040316 | 0.0010104
73 | 0.00203 | 0.00050877
74 | 0.0023853 | 0.00059781
75 | 0.00062479 | 0.00015659
76 | 0.014932 | 0.0037423
77 | 0.013274 | 0.0033268
78 | 0.0018209 | 0.00045637
79 | 0.0025908 | 0.00064932
80 | 0.0013567 | 0.00034003
81 | 0.00084637 | 0.00021212
82 | 0.0071024 | 0.00178
83 | 0.0018304 | 0.00045875
84 | 0.014815 | 0.0037129
85 | 0.015354 | 0.003848
86 | 0.03148 | 0.0078896
87 | 0.00709 | 0.0017769
88 | 0.0029793 | 0.00074668
89 | 0.010523 | 0.0026372
90 | 0.0058965 | 0.0014778
91 | 0.0044642 | 0.0011188
92 | 0.0027925 | 0.00069986
93 | 0.0023816 | 0.00059688
94 | 0.005197 | 0.0013025
95 | 0.0041699 | 0.0010451
96 | 0.0052943 | 0.0013269
97 | 0.0034775 | 0.00087154
98 | 0.002856 | 0.00071577
99 | 0.0021888 | 0.00054856
100 | 0.0029558 | 0.00074079
101 | 0.00075584 | 0.00018943
102 | 0.0016263 | 0.00040759
103 | 0.0019729 | 0.00049444
104 | 0.0027343 | 0.00068529
105 | 0.0021867 | 0.00054804
106 | 0.0014785 | 0.00037055
107 | 0.0031768 | 0.00079619
108 | 0.0016747 | 0.00041973
109 | 0.0041549 | 0.0010413
110 | 0.0033727 | 0.00084528
111 | 0.0042391 | 0.0010624

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1