## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1322-11_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1322-11_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1322-11_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1322-11_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1322-11_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1322-11_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1322-11_0_4_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_1322-11_0_4_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_1322-11_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_1322-11_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1322-11_0_4_node_38 | 0.4 | n |  | TRUE
11 | bus_LV_1322-11_0_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_1322-11_0_4_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_1322-11_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1322-11_0_4_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_1322-11_0_4_node_37 | 0.4 | n |  | TRUE
16 | bus_LV_1322-11_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1322-11_0_4_node_27 | 0.4 | n |  | TRUE
18 | bus_LV_1322-11_0_4_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_1322-11_0_4_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_1322-11_0_4_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_1322-11_0_4_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_1322-11_0_4_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_1322-11_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1322-11_0_4_node_42 | 0.4 | n |  | TRUE
25 | bus_LV_1322-11_0_4_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1322-11_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1322-11_0_4_node_41 | 0.4 | n |  | TRUE
28 | bus_LV_1322-11_0_4_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_1322-11_0_4_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_1322-11_0_4_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_1322-11_0_4_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_1322-11_0_4_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_1322-11_0_4_node_39 | 0.4 | n |  | TRUE
34 | bus_LV_1322-11_0_4_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_1322-11_0_4_node_23 | 0.4 | n |  | TRUE
36 | bus_MV_16_0_node_16 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1322-11_0_4_load_0 | 0 | 0.020766 | 0.0052045 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1322-11_0_4_load_5 | 4 | 0.019028 | 0.0047689 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1322-11_0_4_load_13 | 7 | 0.012806 | 0.0032094 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1322-11_0_4_load_7 | 9 | 0.037562 | 0.009414 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1322-11_0_4_load_38 | 10 | 0.011037 | 0.0027662 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1322-11_0_4_load_12 | 11 | 0.0030668 | 0.00076861 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1322-11_0_4_load_26 | 12 | 0.061642 | 0.015449 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1322-11_0_4_load_37 | 15 | 0.019674 | 0.0049308 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1322-11_0_4_load_27 | 17 | 0.06227 | 0.015606 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1322-11_0_4_load_28 | 18 | 0.050428 | 0.012638 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1322-11_0_4_load_40 | 21 | 0.042939 | 0.010762 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1322-11_0_4_load_42 | 24 | 0.0052977 | 0.0013277 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1322-11_0_4_load_41 | 27 | 0.0057832 | 0.0014494 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1322-11_0_4_load_20 | 28 | 0.0253 | 0.0063407 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1322-11_0_4_load_36 | 30 | 0.09262 | 0.023213 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1322-11_0_4_load_39 | 33 | 0.029868 | 0.0074855 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1322-11_0_4_load_21 | 34 | 0.023644 | 0.0059257 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1322-11_0_4_load_23 | 35 | 0.034308 | 0.0085984 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1322-11_0_4_line_0 |  | 0 | 1 | 1.239e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1322-11_0_4_line_1 |  | 0 | 2 | 0.018502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1322-11_0_4_line_2 |  | 1 | 3 | 0.032214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1322-11_0_4_line_3 |  | 2 | 4 | 0.0011272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1322-11_0_4_line_4 |  | 2 | 5 | 0.027406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1322-11_0_4_line_5 |  | 3 | 8 | 0.011366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1322-11_0_4_line_6 |  | 3 | 9 | 0.023662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1322-11_0_4_line_7 |  | 3 | 6 | 0.026368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1322-11_0_4_line_8 |  | 5 | 10 | 0.13725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1322-11_0_4_line_9 |  | 6 | 7 | 0.015318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1322-11_0_4_line_10 |  | 7 | 11 | 0.013694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1322-11_0_4_line_11 |  | 8 | 12 | 0.016509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1322-11_0_4_line_12 |  | 11 | 14 | 0.0054759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1322-11_0_4_line_13 |  | 12 | 17 | 0.028964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1322-11_0_4_line_14 |  | 13 | 14 | 0.021995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1322-11_0_4_line_15 |  | 13 | 15 | 0.016295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1322-11_0_4_line_16 |  | 14 | 23 | 0.035118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1322-11_0_4_line_17 |  | 15 | 20 | 0.021773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1322-11_0_4_line_18 |  | 16 | 17 | 0.021285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1322-11_0_4_line_19 |  | 16 | 18 | 0.044327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1322-11_0_4_line_20 |  | 18 | 31 | 0.020478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1322-11_0_4_line_21 |  | 19 | 20 | 0.0069602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1322-11_0_4_line_22 |  | 19 | 21 | 0.028569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1322-11_0_4_line_23 |  | 20 | 22 | 0.026387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1322-11_0_4_line_24 |  | 22 | 35 | 0.020112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1322-11_0_4_line_25 |  | 22 | 34 | 0.051274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1322-11_0_4_line_26 |  | 23 | 24 | 0.01032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1322-11_0_4_line_27 |  | 24 | 27 | 0.010062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1322-11_0_4_line_28 |  | 25 | 26 | 0.033239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1322-11_0_4_line_29 |  | 25 | 27 | 1.3515e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1322-11_0_4_line_30 |  | 26 | 28 | 0.0069479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1322-11_0_4_line_31 |  | 29 | 30 | 0.035037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1322-11_0_4_line_32 |  | 29 | 31 | 0.028598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1322-11_0_4_line_33 |  | 31 | 32 | 0.0067798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1322-11_0_4_line_34 |  | 32 | 33 | 0.0085035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1322-11_0_4_trafo_26 | 0.63 MVA 20/0.4 kV | 36 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2701501.9324 | 1228886.2356 | 2701501.932 | 1228886.2232
1 | 2701502.5936 | 1228904.7259 | 2701501.9324 | 1228886.2356
2 | 2701501.932 | 1228886.2232 | 2701501.4767 | 1228871.171 | 2701501.0607 | 1228861.8015 | 2701501.5717 | 1228861.1653 | 2701502.254 | 1228860.2652 | 2701505.7813 | 1228855.6219
3 | 2701502.5936 | 1228904.7259 | 2701501.4677 | 1228904.7812
4 | 2701502.5936 | 1228904.7259 | 2701503.1138 | 1228919.0787 | 2701493.4233 | 1228919.4247 | 2701493.4495 | 1228922.7721
5 | 2701510.161 | 1228845.8784 | 2701510.2603 | 1228850.2722 | 2701505.7813 | 1228855.6219
6 | 2701505.7813 | 1228855.6219 | 2701482.1573 | 1228856.9596
7 | 2701505.7813 | 1228855.6219 | 2701502.254 | 1228860.2652 | 2701501.5717 | 1228861.1653 | 2701506.5759 | 1228861.0061 | 2701506.6422 | 1228862.4528 | 2701519.586 | 1228861.9733
8 | 2701493.4495 | 1228922.7721 | 2701394.893 | 1228926.216 | 2701356.3538 | 1228928.8686
9 | 2701519.586 | 1228861.9733 | 2701534.8876 | 1228861.2749
10 | 2701548.5675 | 1228860.6504 | 2701534.8876 | 1228861.2749
11 | 2701510.161 | 1228845.8784 | 2701493.6728 | 1228846.7023
12 | 2701553.2036 | 1228858.7781 | 2701551.848 | 1228860.5007 | 2701548.5675 | 1228860.6504
13 | 2701464.7447 | 1228848.1478 | 2701493.6728 | 1228846.7023
14 | 2701532.9602 | 1228851.8274 | 2701538.9672 | 1228851.5186 | 2701553.2036 | 1228858.7781
15 | 2701532.9602 | 1228851.8274 | 2701530.0486 | 1228835.7948
16 | 2701553.2036 | 1228858.7781 | 2701555.6359 | 1228855.684 | 2701555.9302 | 1228855.311 | 2701557.5153 | 1228855.238 | 2701564.7807 | 1228854.9063 | 2701567.5336 | 1228854.7865 | 2701575.0948 | 1228854.4376 | 2701577.5899 | 1228854.3246 | 2701569.5202 | 1228850.2838
17 | 2701526.1583 | 1228814.3727 | 2701530.0486 | 1228835.7948
18 | 2701443.4858 | 1228849.2101 | 2701464.7447 | 1228848.1478
19 | 2701443.4858 | 1228849.2101 | 2701440.8562 | 1228804.9607
20 | 2701439.6414 | 1228784.5191 | 2701440.8562 | 1228804.9607
21 | 2701521.392 | 1228812.5789 | 2701521.8787 | 1228815.1446 | 2701526.1583 | 1228814.3727
22 | 2701521.392 | 1228812.5789 | 2701516.3177 | 1228784.4637
23 | 2701521.0837 | 1228788.4781 | 2701525.6946 | 1228811.7962 | 2701526.1583 | 1228814.3727
24 | 2701521.0837 | 1228788.4781 | 2701517.628 | 1228768.6653
25 | 2701521.0837 | 1228788.4781 | 2701565.1447 | 1228780.3798 | 2701571.5814 | 1228779.6772
26 | 2701569.5202 | 1228850.2838 | 2701579.8632 | 1228849.8934
27 | 2701579.8632 | 1228849.8934 | 2701589.9139 | 1228849.4212
28 | 2701589.9274 | 1228849.4205 | 2701599.6568 | 1228849.0197 | 2701604.8529 | 1228848.7194 | 2701611.8202 | 1228847.2039 | 2701616.968 | 1228847.0695 | 2701618.9498 | 1228847.2813 | 2701620.7277 | 1228847.9011 | 2701622.6752 | 1228848.7905
29 | 2701589.9274 | 1228849.4205 | 2701589.9139 | 1228849.4212
30 | 2701622.6752 | 1228848.7905 | 2701624.1708 | 1228845.9696 | 2701623.9848 | 1228842.2192
31 | 2701412.238 | 1228785.4637 | 2701414.1128 | 1228820.4507
32 | 2701412.238 | 1228785.4637 | 2701413.8436 | 1228784.6349 | 2701416.3849 | 1228784.4781 | 2701419.487 | 1228784.3198 | 2701419.5453 | 1228785.3437 | 2701439.6414 | 1228784.5191
33 | 2701442.2001 | 1228778.9031 | 2701439.52 | 1228781.4148 | 2701439.6414 | 1228784.5191
34 | 2701442.2001 | 1228778.9031 | 2701445.4133 | 1228775.7889 | 2701445.2164 | 1228771.7649

## bus_geodata
| x | y | coords
0 | 2701501.9324 | 1228886.2356
1 | 2701501.932 | 1228886.2232
2 | 2701502.5936 | 1228904.7259
3 | 2701505.7813 | 1228855.6219
4 | 2701501.4677 | 1228904.7813
5 | 2701493.4495 | 1228922.7721
6 | 2701519.586 | 1228861.9733
7 | 2701534.8876 | 1228861.2749
8 | 2701510.161 | 1228845.8784
9 | 2701482.1573 | 1228856.9596
10 | 2701356.3538 | 1228928.8686
11 | 2701548.5675 | 1228860.6504
12 | 2701493.6728 | 1228846.7023
13 | 2701532.9602 | 1228851.8274
14 | 2701553.2036 | 1228858.7781
15 | 2701530.0486 | 1228835.7948
16 | 2701443.4858 | 1228849.2101
17 | 2701464.7447 | 1228848.1478
18 | 2701440.8562 | 1228804.9607
19 | 2701521.392 | 1228812.5789
20 | 2701526.1583 | 1228814.3727
21 | 2701516.3177 | 1228784.4637
22 | 2701521.0837 | 1228788.4781
23 | 2701569.5202 | 1228850.2838
24 | 2701579.8632 | 1228849.8934
25 | 2701589.9274 | 1228849.4205
26 | 2701622.6752 | 1228848.7905
27 | 2701589.9139 | 1228849.4212
28 | 2701623.9848 | 1228842.2192
29 | 2701412.238 | 1228785.4637
30 | 2701414.1128 | 1228820.4507
31 | 2701439.6414 | 1228784.5191
32 | 2701442.2001 | 1228778.9031
33 | 2701445.2164 | 1228771.7649
34 | 2701571.5814 | 1228779.6772
35 | 2701517.628 | 1228768.6653
36 | 2701510.161 | 1228845.8784

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99517 | -0.092462 | 0.020766 | 0.0052045
1 | 0.99517 | -0.092451 | 0 | 0
2 | 0.99466 | -0.10226 | 0 | 0
3 | 0.99666 | -0.063672 | 0 | 0
4 | 0.99464 | -0.10264 | 0.019028 | 0.0047689
5 | 0.99438 | -0.10759 | 0 | 0
6 | 0.99456 | -0.10374 | 0 | 0
7 | 0.99335 | -0.12709 | 0.012806 | 0.0032094
8 | 0.99802 | -0.037658 | 0 | 0
9 | 0.99585 | -0.07928 | 0.037562 | 0.009414
10 | 0.993 | -0.13434 | 0.011037 | 0.0027662
11 | 0.99234 | -0.14646 | 0.0030668 | 0.00076861
12 | 1 | 0 | -0.50291 | -0.12751
13 | 0.9895 | -0.20117 | 0 | 0
14 | 0.99194 | -0.15407 | 0 | 0
15 | 0.98769 | -0.2362 | 0.019674 | 0.0049308
16 | 0.99518 | -0.091885 | 0 | 0
17 | 0.99688 | -0.059552 | 0.06227 | 0.015606
18 | 0.99166 | -0.15957 | 0.050428 | 0.012638
19 | 0.98539 | -0.2809 | 0 | 0
20 | 0.98566 | -0.27553 | 0 | 0
21 | 0.98426 | -0.30294 | 0.042939 | 0.010762
22 | 0.98425 | -0.30301 | 0 | 0
23 | 0.99077 | -0.17673 | 0 | 0
24 | 0.99043 | -0.1834 | 0.0052977 | 0.0013277
25 | 0.99014 | -0.18897 | 0 | 0
26 | 0.98937 | -0.20393 | 0 | 0
27 | 0.99014 | -0.18896 | 0.0057832 | 0.0014494
28 | 0.98921 | -0.20706 | 0.0253 | 0.0063407
29 | 0.98691 | -0.25141 | 0 | 0
30 | 0.98392 | -0.30966 | 0.09262 | 0.023213
31 | 0.98935 | -0.20413 | 0 | 0
32 | 0.98917 | -0.20774 | 0 | 0
33 | 0.98893 | -0.21226 | 0.029868 | 0.0074855
34 | 0.98314 | -0.32484 | 0.023644 | 0.0059257
35 | 0.98362 | -0.31543 | 0.034308 | 0.0085984
36 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.050863 | -0.012757 | 0.050863 | 0.012757 | 2.6875e-08 | 1.7041e-08 | 0.076056 | 0.076056 | 0.076056 | 0.99517 | -0.092462 | 0.99517 | -0.092451 | 20.8944
1 | 0.030097 | 0.0075527 | -0.030083 | -0.007544 | 1.4053e-05 | 8.7539e-06 | 0.045005 | 0.045005 | 0.045005 | 0.99517 | -0.092462 | 0.99466 | -0.10226 | 12.3641
2 | -0.050863 | -0.012757 | 0.050933 | 0.012802 | 6.9879e-05 | 4.4303e-05 | 0.076056 | 0.076056 | 0.076056 | 0.99517 | -0.092451 | 0.99666 | -0.063672 | 20.8944
3 | 0.019029 | 0.0047691 | -0.019028 | -0.0047689 | 3.4255e-07 | 2.046e-07 | 0.028467 | 0.028467 | 0.028467 | 0.99466 | -0.10226 | 0.99464 | -0.10264 | 7.8206
4 | 0.011054 | 0.0027748 | -0.011051 | -0.0027734 | 2.8111e-06 | 1.4435e-06 | 0.016538 | 0.016539 | 0.016539 | 0.99466 | -0.10226 | 0.99438 | -0.10759 | 4.5436
5 | -0.26301 | -0.066605 | 0.26333 | 0.066815 | 0.000329 | 0.00021026 | 0.39291 | 0.39291 | 0.39291 | 0.99666 | -0.063672 | 0.99802 | -0.037658 | 53.9713
6 | 0.03759 | 0.0094316 | -0.037562 | -0.009414 | 2.7952e-05 | 1.7581e-05 | 0.056126 | 0.056126 | 0.056126 | 0.99666 | -0.063672 | 0.99585 | -0.07928 | 15.4193
7 | 0.17448 | 0.044372 | -0.17415 | -0.044158 | 0.0003361 | 0.00021442 | 0.26073 | 0.26073 | 0.26073 | 0.99666 | -0.063672 | 0.99456 | -0.10374 | 35.8146
8 | 0.011051 | 0.0027734 | -0.011037 | -0.0027662 | 1.4078e-05 | 7.2321e-06 | 0.016539 | 0.016539 | 0.016539 | 0.99438 | -0.10759 | 0.993 | -0.13434 | 4.5437
9 | 0.17415 | 0.044158 | -0.17395 | -0.044033 | 0.00019524 | 0.00012456 | 0.26073 | 0.26073 | 0.26073 | 0.99456 | -0.10374 | 0.99335 | -0.12709 | 35.8146
10 | 0.16115 | 0.040824 | -0.161 | -0.040728 | 0.00014981 | 9.5524e-05 | 0.24155 | 0.24155 | 0.24155 | 0.99335 | -0.12709 | 0.99234 | -0.14646 | 33.1797
11 | -0.26333 | -0.066815 | 0.26381 | 0.067121 | 0.00047786 | 0.0003054 | 0.39291 | 0.39291 | 0.39291 | 0.99802 | -0.037658 | 1 | 0 | 53.9713
12 | 0.15793 | 0.03996 | -0.15787 | -0.039923 | 5.7646e-05 | 3.6752e-05 | 0.23695 | 0.23695 | 0.23695 | 0.99234 | -0.14646 | 0.99194 | -0.15407 | 32.548
13 | 0.23744 | 0.060384 | -0.23676 | -0.05995 | 0.00067914 | 0.00043389 | 0.35363 | 0.35363 | 0.35363 | 1 | 0 | 0.99688 | -0.059552 | 48.5755
14 | -0.12114 | -0.030579 | 0.12141 | 0.030754 | 0.00027394 | 0.00017504 | 0.18224 | 0.18224 | 0.18224 | 0.9895 | -0.20117 | 0.99194 | -0.15407 | 50.0666
15 | 0.12114 | 0.030579 | -0.12093 | -0.03045 | 0.00020295 | 0.00012968 | 0.18224 | 0.18224 | 0.18224 | 0.9895 | -0.20117 | 0.98769 | -0.2362 | 50.0667
16 | 0.036462 | 0.0091685 | -0.036422 | -0.0091437 | 3.9414e-05 | 2.4772e-05 | 0.054707 | 0.054707 | 0.054707 | 0.99194 | -0.15407 | 0.99077 | -0.17673 | 15.0295
17 | 0.10126 | 0.025519 | -0.10107 | -0.025397 | 0.00019013 | 0.00012141 | 0.1526 | 0.1526 | 0.1526 | 0.98769 | -0.2362 | 0.98566 | -0.27553 | 41.9237
18 | -0.17422 | -0.044171 | 0.17449 | 0.044344 | 0.00027121 | 0.00017302 | 0.26068 | 0.26068 | 0.26068 | 0.99518 | -0.091885 | 0.99688 | -0.059552 | 35.8077
19 | 0.17422 | 0.044171 | -0.17366 | -0.043811 | 0.0005648 | 0.00036032 | 0.26068 | 0.26068 | 0.26068 | 0.99518 | -0.091885 | 0.99166 | -0.15957 | 35.8078
20 | 0.12323 | 0.031172 | -0.12297 | -0.031004 | 0.00026285 | 0.00016796 | 0.18501 | 0.18501 | 0.18501 | 0.99166 | -0.15957 | 0.98935 | -0.20413 | 50.8275
21 | -0.042984 | -0.01079 | 0.042995 | 0.010797 | 1.0999e-05 | 6.9506e-06 | 0.064916 | 0.064916 | 0.064916 | 0.98539 | -0.2809 | 0.98566 | -0.27553 | 17.834
22 | 0.042984 | 0.01079 | -0.042939 | -0.010762 | 4.5147e-05 | 2.8531e-05 | 0.064916 | 0.064916 | 0.064916 | 0.98539 | -0.2809 | 0.98426 | -0.30294 | 17.834
23 | 0.058073 | 0.0146 | -0.057997 | -0.014552 | 7.6085e-05 | 4.8358e-05 | 0.087687 | 0.087687 | 0.087687 | 0.98566 | -0.27553 | 0.98425 | -0.30301 | 24.0898
24 | 0.034328 | 0.0086112 | -0.034308 | -0.0085984 | 2.0316e-05 | 1.2747e-05 | 0.051901 | 0.051901 | 0.051901 | 0.98425 | -0.30301 | 0.98362 | -0.31543 | 14.2586
25 | 0.023668 | 0.0059408 | -0.023644 | -0.0059257 | 2.4623e-05 | 1.5108e-05 | 0.035786 | 0.035786 | 0.035786 | 0.98425 | -0.30301 | 0.98314 | -0.32484 | 9.8313
26 | 0.036422 | 0.0091437 | -0.036411 | -0.0091364 | 1.1582e-05 | 7.2799e-06 | 0.054707 | 0.054707 | 0.054707 | 0.99077 | -0.17673 | 0.99043 | -0.1834 | 15.0295
27 | 0.031113 | 0.0078087 | -0.031105 | -0.0078036 | 8.2457e-06 | 5.1478e-06 | 0.046748 | 0.046748 | 0.046748 | 0.99043 | -0.1834 | 0.99014 | -0.18896 | 12.8428
28 | 0.025321 | 0.0063541 | -0.025303 | -0.006343 | 1.8053e-05 | 1.1127e-05 | 0.038057 | 0.038057 | 0.038057 | 0.99014 | -0.18897 | 0.98937 | -0.20393 | 10.4552
29 | -0.025321 | -0.0063541 | 0.025321 | 0.0063541 | 7.3541e-09 | 4.5248e-09 | 0.038057 | 0.038057 | 0.038057 | 0.99014 | -0.18897 | 0.99014 | -0.18896 | 10.4552
30 | 0.025303 | 0.006343 | -0.0253 | -0.0063407 | 3.7736e-06 | 2.3259e-06 | 0.038057 | 0.038057 | 0.038057 | 0.98937 | -0.20393 | 0.98921 | -0.20706 | 10.4552
31 | 0.092877 | 0.023377 | -0.09262 | -0.023213 | 0.00025779 | 0.00016454 | 0.14007 | 0.14007 | 0.14007 | 0.98691 | -0.25141 | 0.98392 | -0.30966 | 38.4813
32 | -0.092877 | -0.023377 | 0.093088 | 0.023512 | 0.00021041 | 0.0001343 | 0.14007 | 0.14007 | 0.14007 | 0.98691 | -0.25141 | 0.98935 | -0.20413 | 38.4812
33 | 0.029879 | 0.0074927 | -0.029874 | -0.0074895 | 5.1348e-06 | 3.1992e-06 | 0.044941 | 0.044941 | 0.044941 | 0.98935 | -0.20413 | 0.98917 | -0.20774 | 12.3463
34 | 0.029874 | 0.0074895 | -0.029868 | -0.0074855 | 6.4404e-06 | 4.0127e-06 | 0.044941 | 0.044941 | 0.044941 | 0.98917 | -0.20774 | 0.98893 | -0.21226 | 12.3464

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.56455 | 0.14295

## res_load
| p_mw | q_mvar
0 | 0.020766 | 0.0052045
1 | 0.019028 | 0.0047689
2 | 0.012806 | 0.0032094
3 | 0.037562 | 0.009414
4 | 0.011037 | 0.0027662
5 | 0.0030668 | 0.00076861
6 | 0.061642 | 0.015449
7 | 0.019674 | 0.0049308
8 | 0.06227 | 0.015606
9 | 0.050428 | 0.012638
10 | 0.042939 | 0.010762
11 | 0.0052977 | 0.0013277
12 | 0.0057832 | 0.0014494
13 | 0.0253 | 0.0063407
14 | 0.09262 | 0.023213
15 | 0.029868 | 0.0074855
16 | 0.023644 | 0.0059257
17 | 0.034308 | 0.0085984

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1