## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1322-14_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1322-14_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1322-14_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1322-14_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1322-14_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1322-14_0_4_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_1322-14_0_4_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_1322-14_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_1322-14_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1322-14_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1322-14_0_4_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_1322-14_0_4_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_1322-14_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1322-14_0_4_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_1322-14_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1322-14_0_4_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1322-14_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_1322-14_0_4_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_1322-14_0_4_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_1322-14_0_4_node_33 | 0.4 | n |  | TRUE
20 | bus_LV_1322-14_0_4_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_1322-14_0_4_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_1322-14_0_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_1322-14_0_4_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_1322-14_0_4_node_30 | 0.4 | n |  | TRUE
25 | bus_LV_1322-14_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1322-14_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1322-14_0_4_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_1322-14_0_4_node_29 | 0.4 | n |  | TRUE
29 | bus_MV_15_0_node_156 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1322-14_0_4_load_0 | 0 | 0.0049145 | 0.0012317 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1322-14_0_4_load_1 | 1 | 0.0055405 | 0.0013886 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1322-14_0_4_load_2 | 2 | 0.0054209 | 0.0013586 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1322-14_0_4_load_4 | 3 | 0.014794 | 0.0037078 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1322-14_0_4_load_5 | 4 | 0.038987 | 0.009771 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1322-14_0_4_load_10 | 5 | 0.0028889 | 0.00072402 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1322-14_0_4_load_9 | 7 | 0.0055583 | 0.001393 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1322-14_0_4_load_7 | 8 | 0.0037706 | 0.00094501 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1322-14_0_4_load_8 | 9 | 0.0093751 | 0.0023496 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1322-14_0_4_load_17 | 10 | 0.0056678 | 0.0014205 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1322-14_0_4_load_6 | 12 | 0.0054843 | 0.0013745 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1322-14_0_4_load_26 | 13 | 0.0090597 | 0.0022706 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1322-14_0_4_load_11 | 14 | 0.058659 | 0.014701 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1322-14_0_4_load_12 | 15 | 0.029191 | 0.007316 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1322-14_0_4_load_14 | 16 | 0.0061797 | 0.0015488 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1322-14_0_4_load_33 | 19 | 0.06869 | 0.017215 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1322-14_0_4_load_31 | 20 | 0.0051336 | 0.0012866 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1322-14_0_4_load_24 | 21 | 0.050387 | 0.012628 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1322-14_0_4_load_20 | 22 | 0.049756 | 0.01247 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1322-14_0_4_load_32 | 23 | 0.059516 | 0.014916 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1322-14_0_4_load_18 | 25 | 0.048905 | 0.012257 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1322-14_0_4_load_19 | 26 | 0.025041 | 0.0062758 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1322-14_0_4_load_28 | 27 | 0.0026444 | 0.00066274 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1322-14_0_4_load_29 | 28 | 0.0050179 | 0.0012576 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1322-14_0_4_line_0 |  | 0 | 1 | 0.011335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1322-14_0_4_line_1 |  | 0 | 2 | 0.014342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1322-14_0_4_line_2 |  | 2 | 3 | 0.040207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1322-14_0_4_line_3 |  | 2 | 4 | 0.013034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1322-14_0_4_line_4 |  | 3 | 5 | 0.00052133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1322-14_0_4_line_5 |  | 4 | 6 | 0.022615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1322-14_0_4_line_6 |  | 5 | 9 | 0.017791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1322-14_0_4_line_7 |  | 6 | 10 | 0.027914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1322-14_0_4_line_8 |  | 6 | 11 | 0.062895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1322-14_0_4_line_9 |  | 7 | 8 | 0.019626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1322-14_0_4_line_10 |  | 8 | 13 | 0.050632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1322-14_0_4_line_11 |  | 8 | 12 | 0.0071838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1322-14_0_4_line_12 |  | 9 | 12 | 0.016663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1322-14_0_4_line_13 |  | 10 | 20 | 0.035603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1322-14_0_4_line_14 |  | 11 | 17 | 0.098357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_1322-14_0_4_line_15 |  | 11 | 14 | 0.042573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1322-14_0_4_line_16 |  | 14 | 15 | 0.001931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1322-14_0_4_line_17 |  | 15 | 16 | 0.019716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1322-14_0_4_line_18 |  | 17 | 18 | 0.039346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1322-14_0_4_line_19 |  | 17 | 19 | 0.020578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_1322-14_0_4_line_20 |  | 18 | 21 | 0.0157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1322-14_0_4_line_21 |  | 18 | 22 | 0.044544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1322-14_0_4_line_22 |  | 19 | 23 | 0.002609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1322-14_0_4_line_23 |  | 20 | 24 | 0.021645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1322-14_0_4_line_24 |  | 22 | 25 | 0.025546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1322-14_0_4_line_25 |  | 24 | 27 | 0.0048547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1322-14_0_4_line_26 |  | 25 | 26 | 0.021371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1322-14_0_4_line_27 |  | 27 | 28 | 0.024318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1322-14_0_4_trafo_32 | 0.63 MVA 20/0.4 kV | 29 | 23 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2697512.7925 | 1227908.1371 | 2697522.181 | 1227901.7865
1 | 2697500.9127 | 1227916.1728 | 2697512.7925 | 1227908.1371
2 | 2697500.9127 | 1227916.1728 | 2697491.5751 | 1227901.8539 | 2697489.8678 | 1227878.8045
3 | 2697500.9127 | 1227916.1728 | 2697490.3387 | 1227923.7936
4 | 2697489.8293 | 1227878.2846 | 2697489.8678 | 1227878.8045
5 | 2697471.8571 | 1227936.8228 | 2697478.1798 | 1227932.5566 | 2697490.3387 | 1227923.7936
6 | 2697488.5151 | 1227860.5426 | 2697489.8293 | 1227878.2846
7 | 2697471.8571 | 1227936.8228 | 2697476.2845 | 1227943.2222 | 2697480.6665 | 1227947.2969 | 2697492.3637 | 1227955.2564
8 | 2697428.7226 | 1227928.6437 | 2697432.1376 | 1227933.0028 | 2697438.0619 | 1227946.5651 | 2697438.6137 | 1227952.2005 | 2697440.9975 | 1227951.4946 | 2697449.9696 | 1227948.8062 | 2697455.1316 | 1227946.9116 | 2697459.3363 | 1227944.7011 | 2697461.809 | 1227943.1961 | 2697471.8571 | 1227936.8228
9 | 2697486.7536 | 1227836.7612 | 2697506.2415 | 1227839.0859
10 | 2697486.7536 | 1227836.7612 | 2697495.8324 | 1227786.9496
11 | 2697486.7536 | 1227836.7612 | 2697486.7536 | 1227836.7612 | 2697487.2842 | 1227843.9254
12 | 2697488.5151 | 1227860.5426 | 2697487.2842 | 1227843.9254
13 | 2697524.1664 | 1227970.8574 | 2697512.7695 | 1227966.8038 | 2697500.7091 | 1227960.9352 | 2697492.3637 | 1227955.2564
14 | 2697428.7226 | 1227928.6437 | 2697432.1376 | 1227933.0028 | 2697438.0619 | 1227946.5651 | 2697438.6137 | 1227952.2005 | 2697432.2441 | 1227953.7862 | 2697433.1398 | 1227958.3264 | 2697437.6839 | 1227958.9902 | 2697447.1958 | 1227959.4352 | 2697447.2545 | 1227962.3271 | 2697431.1569 | 1227962.319 | 2697431.1867 | 1227965.5885 | 2697447.2619 | 1227965.574 | 2697447.1645 | 1227974.2898
15 | 2697428.7226 | 1227928.6437 | 2697448.0473 | 1227923.6677 | 2697450.7006 | 1227920.8536 | 2697448.917 | 1227902.1881
16 | 2697448.7333 | 1227900.2658 | 2697448.917 | 1227902.1881
17 | 2697446.8578 | 1227880.6393 | 2697448.7333 | 1227900.2658
18 | 2697435.1679 | 1228011.2312 | 2697446.5593 | 1227985.3212 | 2697446.8362 | 1227981.8343 | 2697447.1645 | 1227974.2898
19 | 2697447.1645 | 1227974.2898 | 2697467.7185 | 1227976.1501
20 | 2697435.1679 | 1228011.2312 | 2697428.5435 | 1228025.465
21 | 2697435.1679 | 1228011.2312 | 2697459.9512 | 1228015.8404 | 2697459.8918 | 1228019.4643 | 2697475.5667 | 1228021.6671
22 | 2697468.0716 | 1227973.5651 | 2697467.7185 | 1227976.1501
23 | 2697544.5596 | 1227978.1109 | 2697524.1664 | 1227970.8574
24 | 2697475.5667 | 1228021.6671 | 2697500.8661 | 1228025.2108
25 | 2697544.5596 | 1227978.1109 | 2697549.3637 | 1227978.8107
26 | 2697500.8661 | 1228025.2108 | 2697514.9471 | 1228027.1831 | 2697520.2694 | 1228031.9617
27 | 2697549.3637 | 1227978.8107 | 2697573.4279 | 1227982.3163

## bus_geodata
| x | y | coords
0 | 2697512.7925 | 1227908.1371
1 | 2697522.181 | 1227901.7865
2 | 2697500.9127 | 1227916.1728
3 | 2697489.8678 | 1227878.8045
4 | 2697490.3387 | 1227923.7936
5 | 2697489.8293 | 1227878.2846
6 | 2697471.8571 | 1227936.8228
7 | 2697506.2415 | 1227839.0859
8 | 2697486.7536 | 1227836.7612
9 | 2697488.5151 | 1227860.5426
10 | 2697492.3637 | 1227955.2564
11 | 2697428.7226 | 1227928.6437
12 | 2697487.2842 | 1227843.9254
13 | 2697495.8324 | 1227786.9496
14 | 2697448.917 | 1227902.1881
15 | 2697448.7333 | 1227900.2658
16 | 2697446.8578 | 1227880.6393
17 | 2697447.1645 | 1227974.2898
18 | 2697435.1679 | 1228011.2312
19 | 2697467.7185 | 1227976.1501
20 | 2697524.1664 | 1227970.8574
21 | 2697428.5435 | 1228025.465
22 | 2697475.5667 | 1228021.6671
23 | 2697468.0716 | 1227973.5651
24 | 2697544.5596 | 1227978.1109
25 | 2697500.8661 | 1228025.2108
26 | 2697520.2694 | 1228031.9617
27 | 2697549.3637 | 1227978.8107
28 | 2697573.4279 | 1227982.3163
29 | 2697467.7185 | 1227976.1501

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97749 | -0.433 | 0.0049145 | 0.0012317
1 | 0.97743 | -0.43415 | 0.0055405 | 0.0013886
2 | 0.97763 | -0.43027 | 0.0054209 | 0.0013586
3 | 0.97573 | -0.46769 | 0.014794 | 0.0037078
4 | 0.97844 | -0.4144 | 0.038987 | 0.009771
5 | 0.97571 | -0.46803 | 0.0028889 | 0.00072402
6 | 0.98066 | -0.37094 | 0 | 0
7 | 0.97456 | -0.49059 | 0.0055583 | 0.001393
8 | 0.97467 | -0.48859 | 0.0037706 | 0.00094501
9 | 0.97516 | -0.47887 | 0.0093751 | 0.0023496
10 | 0.98019 | -0.38029 | 0.0056678 | 0.0014205
11 | 0.98792 | -0.23033 | 0 | 0
12 | 0.97479 | -0.48617 | 0.0054843 | 0.0013745
13 | 0.97424 | -0.49701 | 0.0090597 | 0.0022706
14 | 0.98423 | -0.30209 | 0.058659 | 0.014701
15 | 0.98417 | -0.30332 | 0.029191 | 0.007316
16 | 0.98406 | -0.30551 | 0.0061797 | 0.0015488
17 | 0.99786 | -0.040514 | 0 | 0
18 | 0.99472 | -0.10065 | 0 | 0
19 | 0.99972 | -0.0052433 | 0.06869 | 0.017215
20 | 0.97976 | -0.38856 | 0.0051336 | 0.0012866
21 | 0.994 | -0.1146 | 0.050387 | 0.012628
22 | 0.98967 | -0.19821 | 0.049756 | 0.01247
23 | 1 | 0 | -0.46837 | -0.11916
24 | 0.97961 | -0.39157 | 0 | 0
25 | 0.98793 | -0.23189 | 0.048905 | 0.012257
26 | 0.98744 | -0.24145 | 0.025041 | 0.0062758
27 | 0.97958 | -0.39224 | 0.0026444 | 0.00066274
28 | 0.97946 | -0.39446 | 0.0050179 | 0.0012576
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0055408 | 0.0013886 | -0.0055405 | -0.0013886 | 3.0239e-07 | 5.1456e-08 | 0.0084346 | 0.0084347 | 0.0084347 | 0.97749 | -0.433 | 0.97743 | -0.43415 | 2.3172
1 | -0.010455 | -0.0026203 | 0.010457 | 0.002621 | 1.3624e-06 | 6.9213e-07 | 0.015916 | 0.015916 | 0.015916 | 0.97749 | -0.433 | 0.97763 | -0.43027 | 4.3725
2 | 0.051055 | 0.012842 | -0.050964 | -0.012784 | 9.1087e-05 | 5.7792e-05 | 0.077725 | 0.077725 | 0.077725 | 0.97763 | -0.43027 | 0.97573 | -0.46769 | 21.3531
3 | -0.066932 | -0.016821 | 0.066983 | 0.016854 | 5.0744e-05 | 3.2313e-05 | 0.10189 | 0.10189 | 0.10189 | 0.97763 | -0.43027 | 0.97844 | -0.4144 | 27.9922
4 | 0.036169 | 0.0090761 | -0.036169 | -0.0090757 | 5.949e-07 | 3.7422e-07 | 0.055163 | 0.055163 | 0.055163 | 0.97573 | -0.46769 | 0.97571 | -0.46803 | 15.1547
5 | -0.10597 | -0.026625 | 0.10619 | 0.026765 | 0.00022032 | 0.00014072 | 0.16118 | 0.16118 | 0.16118 | 0.97844 | -0.4144 | 0.98066 | -0.37094 | 44.2809
6 | 0.03328 | 0.0083517 | -0.033263 | -0.0083409 | 1.7188e-05 | 1.0778e-05 | 0.050758 | 0.050758 | 0.050758 | 0.97571 | -0.46803 | 0.97516 | -0.47887 | 13.9444
7 | 0.018479 | 0.0046357 | -0.018471 | -0.0046308 | 8.2306e-06 | 4.9155e-06 | 0.028041 | 0.028041 | 0.028041 | 0.98066 | -0.37094 | 0.98019 | -0.38029 | 7.7035
8 | -0.12467 | -0.031401 | 0.12551 | 0.031941 | 0.00084449 | 0.00053967 | 0.18922 | 0.18922 | 0.18922 | 0.98066 | -0.37094 | 0.98792 | -0.23033 | 51.9844
9 | -0.0055583 | -0.001393 | 0.0055588 | 0.0013931 | 5.3007e-07 | 9.4672e-08 | 0.0084867 | 0.0084866 | 0.0084867 | 0.97456 | -0.49059 | 0.97467 | -0.48859 | 2.3315
10 | 0.0090633 | 0.0022723 | -0.0090597 | -0.0022706 | 3.6355e-06 | 1.6959e-06 | 0.013837 | 0.013837 | 0.013837 | 0.97467 | -0.48859 | 0.97424 | -0.49701 | 3.8015
11 | -0.018393 | -0.0046104 | 0.018395 | 0.0046117 | 2.1242e-06 | 1.2699e-06 | 0.02808 | 0.02808 | 0.02808 | 0.97467 | -0.48859 | 0.97479 | -0.48617 | 7.7144
12 | 0.023887 | 0.0059913 | -0.023879 | -0.0059862 | 8.3028e-06 | 5.106e-06 | 0.036452 | 0.036452 | 0.036452 | 0.97516 | -0.47887 | 0.97479 | -0.48617 | 10.0143
13 | 0.012803 | 0.0032103 | -0.012798 | -0.0032075 | 5.0438e-06 | 2.7795e-06 | 0.019436 | 0.019437 | 0.019437 | 0.98019 | -0.38029 | 0.97976 | -0.38856 | 5.3397
14 | -0.21987 | -0.055714 | 0.22189 | 0.057008 | 0.0020252 | 0.0012936 | 0.33139 | 0.33139 | 0.33139 | 0.98792 | -0.23033 | 0.99786 | -0.040514 | 45.5202
15 | 0.094355 | 0.023774 | -0.094033 | -0.023568 | 0.00032266 | 0.00020596 | 0.14216 | 0.14216 | 0.14216 | 0.98792 | -0.23033 | 0.98423 | -0.30209 | 39.0561
16 | 0.035373 | 0.0088662 | -0.035371 | -0.0088649 | 2.0711e-06 | 1.301e-06 | 0.05348 | 0.05348 | 0.05348 | 0.98423 | -0.30209 | 0.98417 | -0.30332 | 14.6923
17 | 0.0061803 | 0.0015489 | -0.0061797 | -0.0015488 | 6.4558e-07 | 1.6267e-07 | 0.0093444 | 0.0093445 | 0.0093445 | 0.98417 | -0.30332 | 0.98406 | -0.30551 | 2.5672
18 | 0.17534 | 0.044427 | -0.17483 | -0.044105 | 0.00050499 | 0.00032217 | 0.26163 | 0.26163 | 0.26163 | 0.99786 | -0.040514 | 0.99472 | -0.10065 | 35.9386
19 | -0.39723 | -0.10143 | 0.39791 | 0.10187 | 0.00067844 | 0.00043312 | 0.59302 | 0.59302 | 0.59302 | 0.99786 | -0.040514 | 0.99972 | -0.0052433 | 40.7292
20 | 0.050421 | 0.012649 | -0.050387 | -0.012628 | 3.3497e-05 | 2.1234e-05 | 0.075429 | 0.075429 | 0.075429 | 0.99472 | -0.10065 | 0.994 | -0.1146 | 20.7223
21 | 0.12441 | 0.031455 | -0.12383 | -0.031085 | 0.00057916 | 0.00037009 | 0.1862 | 0.1862 | 0.1862 | 0.99472 | -0.10065 | 0.98967 | -0.19821 | 51.1551
22 | -0.4666 | -0.11908 | 0.46672 | 0.11916 | 0.00011823 | 7.5532e-05 | 0.69526 | 0.69526 | 0.69526 | 0.99972 | -0.0052433 | 1 | 0 | 47.7512
23 | 0.0076642 | 0.0019209 | -0.0076631 | -0.0019205 | 1.0997e-06 | 4.3129e-07 | 0.01164 | 0.01164 | 0.01164 | 0.97976 | -0.38856 | 0.97961 | -0.39157 | 3.1978
24 | 0.074075 | 0.018615 | -0.073957 | -0.018539 | 0.00011887 | 7.5751e-05 | 0.11139 | 0.11139 | 0.11139 | 0.98967 | -0.19821 | 0.98793 | -0.23189 | 30.6027
25 | 0.0076631 | 0.0019205 | -0.0076628 | -0.0019204 | 2.4667e-07 | 9.6749e-08 | 0.01164 | 0.01164 | 0.01164 | 0.97961 | -0.39157 | 0.97958 | -0.39224 | 3.1978
26 | 0.025052 | 0.0062828 | -0.025041 | -0.0062758 | 1.1411e-05 | 7.0298e-06 | 0.037735 | 0.037735 | 0.037735 | 0.98793 | -0.23189 | 0.98744 | -0.24145 | 10.3667
27 | 0.0050184 | 0.0012576 | -0.0050179 | -0.0012576 | 5.2996e-07 | 3.3071e-08 | 0.0076232 | 0.0076233 | 0.0076233 | 0.97958 | -0.39224 | 0.97946 | -0.39446 | 2.0943

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52788 | 0.13407

## res_load
| p_mw | q_mvar
0 | 0.0049145 | 0.0012317
1 | 0.0055405 | 0.0013886
2 | 0.0054209 | 0.0013586
3 | 0.014794 | 0.0037078
4 | 0.038987 | 0.009771
5 | 0.0028889 | 0.00072402
6 | 0.0055583 | 0.001393
7 | 0.0037706 | 0.00094501
8 | 0.0093751 | 0.0023496
9 | 0.0056678 | 0.0014205
10 | 0.0054843 | 0.0013745
11 | 0.0090597 | 0.0022706
12 | 0.058659 | 0.014701
13 | 0.029191 | 0.007316
14 | 0.0061797 | 0.0015488
15 | 0.06869 | 0.017215
16 | 0.0051336 | 0.0012866
17 | 0.050387 | 0.012628
18 | 0.049756 | 0.01247
19 | 0.059516 | 0.014916
20 | 0.048905 | 0.012257
21 | 0.025041 | 0.0062758
22 | 0.0026444 | 0.00066274
23 | 0.0050179 | 0.0012576

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1