## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1322-19_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1322-19_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1322-19_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1322-19_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1322-19_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1322-19_0_5_node_32 | 0.4 | n |  | TRUE
6 | bus_LV_1322-19_0_5_node_34 | 0.4 | n |  | TRUE
7 | bus_LV_1322-19_0_5_node_31 | 0.4 | n |  | TRUE
8 | bus_LV_1322-19_0_5_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1322-19_0_5_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_1322-19_0_5_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1322-19_0_5_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1322-19_0_5_node_40 | 0.4 | n |  | TRUE
13 | bus_LV_1322-19_0_5_node_33 | 0.4 | n |  | TRUE
14 | bus_LV_1322-19_0_5_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1322-19_0_5_node_41 | 0.4 | n |  | TRUE
16 | bus_LV_1322-19_0_5_node_37 | 0.4 | n |  | TRUE
17 | bus_LV_1322-19_0_5_node_36 | 0.4 | n |  | TRUE
18 | bus_LV_1322-19_0_5_node_39 | 0.4 | n |  | TRUE
19 | bus_LV_1322-19_0_5_node_38 | 0.4 | n |  | TRUE
20 | bus_LV_1322-19_0_5_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_1322-19_0_5_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_1322-19_0_5_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1322-19_0_5_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1322-19_0_5_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_1322-19_0_5_node_64 | 0.4 | n |  | TRUE
26 | bus_LV_1322-19_0_5_node_76 | 0.4 | n |  | TRUE
27 | bus_LV_1322-19_0_5_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1322-19_0_5_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_1322-19_0_5_node_75 | 0.4 | n |  | TRUE
30 | bus_LV_1322-19_0_5_node_73 | 0.4 | n |  | TRUE
31 | bus_LV_1322-19_0_5_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_1322-19_0_5_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_1322-19_0_5_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_1322-19_0_5_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_1322-19_0_5_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_1322-19_0_5_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_1322-19_0_5_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_1322-19_0_5_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_1322-19_0_5_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_1322-19_0_5_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_1322-19_0_5_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_1322-19_0_5_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_1322-19_0_5_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_1322-19_0_5_node_45 | 0.4 | n |  | TRUE
45 | bus_LV_1322-19_0_5_node_69 | 0.4 | n |  | TRUE
46 | bus_LV_1322-19_0_5_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_1322-19_0_5_node_67 | 0.4 | n |  | TRUE
48 | bus_LV_1322-19_0_5_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_1322-19_0_5_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_1322-19_0_5_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_1322-19_0_5_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_1322-19_0_5_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_1322-19_0_5_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_1322-19_0_5_node_49 | 0.4 | n |  | TRUE
55 | bus_LV_1322-19_0_5_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_1322-19_0_5_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_1322-19_0_5_node_52 | 0.4 | n |  | TRUE
58 | bus_LV_1322-19_0_5_node_53 | 0.4 | n |  | TRUE
59 | bus_LV_1322-19_0_5_node_56 | 0.4 | n |  | TRUE
60 | bus_LV_1322-19_0_5_node_54 | 0.4 | n |  | TRUE
61 | bus_LV_1322-19_0_5_node_55 | 0.4 | n |  | TRUE
62 | bus_LV_1322-19_0_5_node_57 | 0.4 | n |  | TRUE
63 | bus_LV_1322-19_0_5_node_82 | 0.4 | n |  | TRUE
64 | bus_LV_1322-19_0_5_node_83 | 0.4 | n |  | TRUE
65 | bus_LV_1322-19_0_5_node_59 | 0.4 | n |  | TRUE
66 | bus_LV_1322-19_0_5_node_61 | 0.4 | n |  | TRUE
67 | bus_LV_1322-19_0_5_node_58 | 0.4 | n |  | TRUE
68 | bus_LV_1322-19_0_5_node_60 | 0.4 | n |  | TRUE
69 | bus_LV_1322-19_0_5_node_62 | 0.4 | n |  | TRUE
70 | bus_LV_1322-19_0_5_node_63 | 0.4 | n |  | TRUE
71 | bus_LV_1322-19_0_5_node_65 | 0.4 | n |  | TRUE
72 | bus_LV_1322-19_0_5_node_72 | 0.4 | n |  | TRUE
73 | bus_LV_1322-19_0_5_node_68 | 0.4 | n |  | TRUE
74 | bus_LV_1322-19_0_5_node_79 | 0.4 | n |  | TRUE
75 | bus_LV_1322-19_0_5_node_74 | 0.4 | n |  | TRUE
76 | bus_LV_1322-19_0_5_node_70 | 0.4 | n |  | TRUE
77 | bus_LV_1322-19_0_5_node_66 | 0.4 | n |  | TRUE
78 | bus_LV_1322-19_0_5_node_80 | 0.4 | n |  | TRUE
79 | bus_LV_1322-19_0_5_node_71 | 0.4 | n |  | TRUE
80 | bus_LV_1322-19_0_5_node_81 | 0.4 | n |  | TRUE
81 | bus_MV_16_0_node_37 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1322-19_0_5_load_0 | 0 | 0.0045798 | 0.0011478 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1322-19_0_5_load_1 | 1 | 0.0016723 | 0.00041913 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1322-19_0_5_load_3 | 3 | 0.0046352 | 0.0011617 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1322-19_0_5_load_4 | 4 | 0.0031799 | 0.00079697 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1322-19_0_5_load_32 | 5 | 0.0044879 | 0.0011248 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1322-19_0_5_load_34 | 6 | 0.0087104 | 0.002183 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1322-19_0_5_load_31 | 7 | 0.0015522 | 0.00038902 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1322-19_0_5_load_28 | 9 | 0.0015985 | 0.00040062 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1322-19_0_5_load_7 | 10 | 0.0030027 | 0.00075254 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1322-19_0_5_load_40 | 12 | 0.00098391 | 0.00024659 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1322-19_0_5_load_41 | 15 | 0.0063886 | 0.0016011 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1322-19_0_5_load_36 | 17 | 0.00040703 | 0.00010201 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1322-19_0_5_load_39 | 18 | 0.00049218 | 0.00012335 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1322-19_0_5_load_38 | 19 | 0.00069119 | 0.00017323 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1322-19_0_5_load_9 | 20 | 0.0034522 | 0.00086521 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1322-19_0_5_load_13 | 22 | 0.0089236 | 0.0022365 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1322-19_0_5_load_14 | 23 | 0.0054921 | 0.0013765 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1322-19_0_5_load_76 | 26 | 0.0076349 | 0.0019135 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1322-19_0_5_load_15 | 27 | 0.008847 | 0.0022173 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1322-19_0_5_load_73 | 30 | 0.01666 | 0.0041753 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1322-19_0_5_load_16 | 31 | 0.031101 | 0.0077946 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1322-19_0_5_load_21 | 32 | 0.0044672 | 0.0011196 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1322-19_0_5_load_17 | 33 | 0.014758 | 0.0036986 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1322-19_0_5_load_18 | 34 | 0.014121 | 0.003539 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1322-19_0_5_load_20 | 35 | 0.031289 | 0.0078419 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1322-19_0_5_load_22 | 36 | 0.0070225 | 0.00176 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1322-19_0_5_load_23 | 37 | 0.0036149 | 0.00090597 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1322-19_0_5_load_24 | 38 | 0.0032075 | 0.00080389 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1322-19_0_5_load_25 | 40 | 0.0087714 | 0.0021983 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1322-19_0_5_load_29 | 42 | 0.0038984 | 0.00097702 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1322-19_0_5_load_30 | 43 | 0.031217 | 0.0078236 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1322-19_0_5_load_45 | 44 | 0.0031905 | 0.00079962 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1322-19_0_5_load_69 | 45 | 0.017633 | 0.0044191 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1322-19_0_5_load_67 | 47 | 0.015469 | 0.0038769 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1322-19_0_5_load_42 | 48 | 0.0079742 | 0.0019985 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1322-19_0_5_load_43 | 49 | 0.00066927 | 0.00016773 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1322-19_0_5_load_44 | 50 | 0.00060829 | 0.00015245 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1322-19_0_5_load_46 | 51 | 0.00080163 | 0.00020091 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1322-19_0_5_load_48 | 53 | 0.0019887 | 0.00049843 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1322-19_0_5_load_49 | 54 | 0.0060051 | 0.001505 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1322-19_0_5_load_50 | 55 | 0.0064029 | 0.0016047 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1322-19_0_5_load_51 | 56 | 0.0053991 | 0.0013531 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1322-19_0_5_load_52 | 57 | 0.005082 | 0.0012737 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1322-19_0_5_load_56 | 59 | 0.033577 | 0.0084152 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1322-19_0_5_load_54 | 60 | 0.0073142 | 0.0018331 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1322-19_0_5_load_55 | 61 | 0.0073773 | 0.0018489 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1322-19_0_5_load_82 | 63 | 0.0036767 | 0.00092147 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1322-19_0_5_load_83 | 64 | 0.0036801 | 0.00092232 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1322-19_0_5_load_59 | 65 | 0.013673 | 0.0034267 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1322-19_0_5_load_58 | 67 | 0.011657 | 0.0029216 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1322-19_0_5_load_60 | 68 | 0.0036746 | 0.00092094 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1322-19_0_5_load_62 | 69 | 0.0036772 | 0.0009216 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1322-19_0_5_load_63 | 70 | 0.0088539 | 0.002219 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1322-19_0_5_load_72 | 72 | 0.0085764 | 0.0021494 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1322-19_0_5_load_79 | 74 | 0.009099 | 0.0022804 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1322-19_0_5_load_74 | 75 | 0.026055 | 0.00653 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1322-19_0_5_load_70 | 76 | 0.018042 | 0.0045217 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1322-19_0_5_load_66 | 77 | 0.026768 | 0.0067087 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1322-19_0_5_load_80 | 78 | 0.0036766 | 0.00092143 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1322-19_0_5_load_71 | 79 | 0.017826 | 0.0044675 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1322-19_0_5_load_81 | 80 | 0.0036766 | 0.00092145 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 76 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1322-19_0_5_line_0 |  | 0 | 1 | 0.024372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1322-19_0_5_line_1 |  | 0 | 2 | 0.029907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1322-19_0_5_line_2 |  | 1 | 3 | 0.049223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1322-19_0_5_line_3 |  | 2 | 4 | 0.020288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1322-19_0_5_line_4 |  | 3 | 8 | 0.02082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1322-19_0_5_line_5 |  | 4 | 10 | 0.024143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1322-19_0_5_line_6 |  | 5 | 6 | 0.042211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1322-19_0_5_line_7 |  | 5 | 7 | 0.051136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1322-19_0_5_line_8 |  | 6 | 9 | 0.020149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1322-19_0_5_line_9 |  | 7 | 10 | 0.13795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1322-19_0_5_line_10 |  | 7 | 13 | 0.013666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1322-19_0_5_line_11 |  | 8 | 14 | 0.078973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1322-19_0_5_line_12 |  | 9 | 39 | 0.019757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1322-19_0_5_line_13 |  | 11 | 12 | 0.096514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1322-19_0_5_line_14 |  | 11 | 13 | 0.071899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1322-19_0_5_line_15 |  | 12 | 15 | 0.033766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1322-19_0_5_line_16 |  | 14 | 16 | 0.014941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1322-19_0_5_line_17 |  | 14 | 17 | 0.080972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1322-19_0_5_line_18 |  | 16 | 18 | 0.035498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1322-19_0_5_line_19 |  | 16 | 19 | 0.026735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1322-19_0_5_line_20 |  | 20 | 21 | 0.02694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1322-19_0_5_line_21 |  | 21 | 22 | 0.018317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_1322-19_0_5_line_22 |  | 21 | 23 | 0.010499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1322-19_0_5_line_23 |  | 22 | 27 | 0.028095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_1322-19_0_5_line_24 |  | 23 | 28 | 0.019982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1322-19_0_5_line_25 |  | 24 | 25 | 0.078828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1322-19_0_5_line_26 |  | 24 | 26 | 0.062388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1322-19_0_5_line_27 |  | 25 | 29 | 0.11469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_1322-19_0_5_line_28 |  | 25 | 30 | 0.012173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1322-19_0_5_line_29 |  | 27 | 31 | 0.029684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_1322-19_0_5_line_30 |  | 28 | 32 | 0.017113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_1322-19_0_5_line_31 |  | 28 | 33 | 0.044002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1322-19_0_5_line_32 |  | 29 | 31 | 0.015424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_1322-19_0_5_line_33 |  | 30 | 75 | 0.052302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1322-19_0_5_line_34 |  | 32 | 36 | 0.023382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_1322-19_0_5_line_35 |  | 33 | 34 | 0.024291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1322-19_0_5_line_36 |  | 34 | 35 | 0.030639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1322-19_0_5_line_37 |  | 36 | 37 | 0.0042946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_1322-19_0_5_line_38 |  | 37 | 38 | 0.013213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_1322-19_0_5_line_39 |  | 38 | 39 | 0.013631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_1322-19_0_5_line_40 |  | 39 | 40 | 0.013689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_1322-19_0_5_line_41 |  | 40 | 41 | 0.052007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_1322-19_0_5_line_42 |  | 41 | 42 | 0.020942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1322-19_0_5_line_43 |  | 41 | 43 | 0.025929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_1322-19_0_5_line_44 |  | 42 | 44 | 0.042847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1322-19_0_5_line_45 |  | 43 | 45 | 0.047076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_1322-19_0_5_line_46 |  | 44 | 46 | 0.034705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1322-19_0_5_line_47 |  | 45 | 47 | 0.017128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_1322-19_0_5_line_48 |  | 46 | 48 | 0.016328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1322-19_0_5_line_49 |  | 47 | 77 | 0.022813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_1322-19_0_5_line_50 |  | 48 | 49 | 0.0083112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1322-19_0_5_line_51 |  | 49 | 50 | 0.032495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1322-19_0_5_line_52 |  | 50 | 51 | 0.0088264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1322-19_0_5_line_53 |  | 51 | 52 | 0.017235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1322-19_0_5_line_54 |  | 52 | 53 | 0.065151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1322-19_0_5_line_55 |  | 54 | 55 | 0.0031446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1322-19_0_5_line_56 |  | 55 | 56 | 0.01608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1322-19_0_5_line_57 |  | 56 | 57 | 0.0013367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1322-19_0_5_line_58 |  | 57 | 58 | 0.056668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1322-19_0_5_line_59 |  | 58 | 59 | 0.076391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1322-19_0_5_line_60 |  | 59 | 60 | 0.026462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1322-19_0_5_line_61 |  | 60 | 61 | 0.018947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1322-19_0_5_line_62 |  | 61 | 62 | 0.0059064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1322-19_0_5_line_63 |  | 62 | 65 | 0.070479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1322-19_0_5_line_64 |  | 63 | 64 | 0.0060163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1322-19_0_5_line_65 |  | 64 | 80 | 0.0060187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1322-19_0_5_line_66 |  | 65 | 66 | 0.037112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1322-19_0_5_line_67 |  | 65 | 67 | 0.00767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1322-19_0_5_line_68 |  | 66 | 70 | 0.071566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1322-19_0_5_line_69 |  | 67 | 68 | 0.022822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1322-19_0_5_line_70 |  | 68 | 69 | 0.00012118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1322-19_0_5_line_71 |  | 69 | 71 | 0.014052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1322-19_0_5_line_72 |  | 70 | 72 | 0.023677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1322-19_0_5_line_73 |  | 71 | 73 | 0.018535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_1322-19_0_5_line_74 |  | 71 | 74 | 0.017714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1322-19_0_5_line_75 |  | 73 | 76 | 0.048946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_1322-19_0_5_line_76 |  | 73 | 77 | 0.01192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_1322-19_0_5_line_77 |  | 74 | 78 | 5.2186e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1322-19_0_5_line_78 |  | 76 | 79 | 0.021079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1322-19_0_5_line_79 |  | 78 | 80 | 0.0060169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1322-19_0_5_trafo_70 | 0.63 MVA 20/0.4 kV | 81 | 76 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2701822.3547 | 1228001.3596 | 2701845.3597 | 1227993.3128
1 | 2701797.3104 | 1228016.8086 | 2701805.2734 | 1228008.9946 | 2701810.3464 | 1228006.1905 | 2701817.1738 | 1228003.1718 | 2701822.3547 | 1228001.3596
2 | 2701845.3597 | 1227993.3128 | 2701851.6912 | 1227991.0982 | 2701863.9427 | 1227983.3689 | 2701869.2754 | 1227979.1238 | 2701880.5878 | 1227968.6987 | 2701884.4983 | 1227964.3754
3 | 2701797.3104 | 1228016.8086 | 2701777.809 | 1228011.2127
4 | 2701898.4647 | 1227948.9348 | 2701884.4983 | 1227964.3754
5 | 2701755.7311 | 1228001.7751 | 2701768.1755 | 1228008.4484 | 2701777.809 | 1228011.2127
6 | 2701710.9801 | 1228134.581 | 2701723.7296 | 1228143.2207 | 2701745.2805 | 1228159.1691
7 | 2701667.4979 | 1228107.8182 | 2701685.0629 | 1228117.0182 | 2701710.9801 | 1228134.581
8 | 2701745.2805 | 1228159.1691 | 2701756.6298 | 1228167.5679 | 2701760.9853 | 1228171.7375
9 | 2701667.4979 | 1228107.8182 | 2701755.7311 | 1228001.7751
10 | 2701655.3918 | 1228101.4775 | 2701667.4979 | 1228107.8182
11 | 2701935.3618 | 1227881.6507 | 2701935.8815 | 1227888.031 | 2701934.5778 | 1227895.5475 | 2701930.5513 | 1227905.3858 | 2701924.812 | 1227915.2169 | 2701913.2086 | 1227933.3203 | 2701898.4647 | 1227948.9348
12 | 2701775.2566 | 1228185.3996 | 2701760.9853 | 1228171.7375
13 | 2701675.9421 | 1228032.578 | 2701680.5698 | 1228014.5883 | 2701681.427 | 1227996.3785 | 2701677.2623 | 1227979.317 | 2701674.7312 | 1227939.8559 | 2701673.1994 | 1227937.7499
14 | 2701655.3918 | 1228101.4775 | 2701675.9421 | 1228032.578
15 | 2701647.4267 | 1227950.7417 | 2701663.9316 | 1227934.9344 | 2701670.8657 | 1227934.5415 | 2701673.1994 | 1227937.7499
16 | 2701935.3618 | 1227881.6507 | 2701949.0335 | 1227875.536
17 | 2701935.3618 | 1227881.6507 | 2701933.3241 | 1227876.7233 | 2701930.2706 | 1227873.5687 | 2701924.7479 | 1227870.3272 | 2701915.9667 | 1227867.4858 | 2701881.0086 | 1227857.4575 | 2701863.1747 | 1227850.2149
18 | 2701949.0335 | 1227875.536 | 2701956.7214 | 1227866.5501 | 2701966.8977 | 1227850.8018 | 2701969.6443 | 1227846.7169
19 | 2701949.0335 | 1227875.536 | 2701959.5638 | 1227889.082 | 2701968.2963 | 1227893.0161
20 | 2701850.368 | 1228254.5693 | 2701865.7599 | 1228267.4312 | 2701871.2795 | 1228271.5412
21 | 2701850.368 | 1228254.5693 | 2701846.723 | 1228258.0873 | 2701844.1122 | 1228271.0785
22 | 2701850.368 | 1228254.5693 | 2701842.5442 | 1228247.5681
23 | 2701845.3653 | 1228294.241 | 2701849.2581 | 1228274.6762 | 2701843.6409 | 1228273.4236 | 2701844.1122 | 1228271.0785
24 | 2701827.6539 | 1228234.2433 | 2701842.5442 | 1228247.5681
25 | 2701806.0064 | 1228360.0654 | 2701828.8948 | 1228385.2312 | 2701859.0429 | 1228418.3829
26 | 2701859.0429 | 1228418.3829 | 2701846.3095 | 1228428.6391 | 2701810.3419 | 1228457.3765
27 | 2701854.0842 | 1228326.5192 | 2701856.5739 | 1228327.1734 | 2701865.8807 | 1228341.321 | 2701861.3703 | 1228362.1702 | 2701828.8948 | 1228385.2312 | 2701806.0064 | 1228360.0654
28 | 2701806.0064 | 1228360.0654 | 2701800.3159 | 1228353.8079 | 2701798.2254 | 1228350.7367
29 | 2701845.3653 | 1228294.241 | 2701844.8131 | 1228297.0166 | 2701852.1671 | 1228298.6325 | 2701848.0316 | 1228317.509
30 | 2701827.6539 | 1228234.2433 | 2701815.1724 | 1228222.5351
31 | 2701827.6539 | 1228234.2433 | 2701823.9998 | 1228239.6181 | 2701819.8546 | 1228247.1193 | 2701817.4509 | 1228246.7445 | 2701814.4593 | 1228261.671 | 2701808.9958 | 1228260.7435 | 2701807.7964 | 1228266.3515
32 | 2701854.0842 | 1228326.5192 | 2701855.7189 | 1228319.1307 | 2701848.0316 | 1228317.509
33 | 2701759.8187 | 1228319.0895 | 2701769.6261 | 1228321.7147 | 2701782.3738 | 1228327.4481 | 2701798.2254 | 1228350.7367
34 | 2701815.1724 | 1228222.5351 | 2701798.1189 | 1228206.5381
35 | 2701807.6545 | 1228289.213 | 2701811.006 | 1228274.3546 | 2701807.3728 | 1228268.3324 | 2701807.7964 | 1228266.3515
36 | 2701811.9289 | 1228312.5095 | 2701814.9768 | 1228299.163 | 2701811.5689 | 1228298.1261 | 2701812.7528 | 1228293.165 | 2701807.1185 | 1228291.5896 | 2701807.6545 | 1228289.213
37 | 2701794.9867 | 1228203.6 | 2701798.1189 | 1228206.5381
38 | 2701785.3503 | 1228194.5606 | 2701794.9867 | 1228203.6
39 | 2701775.2566 | 1228185.3996 | 2701784.5856 | 1228193.8432 | 2701785.3503 | 1228194.5606
40 | 2701775.2566 | 1228185.3996 | 2701768.0141 | 1228191.4246 | 2701763.8195 | 1228192.2111
41 | 2701712.0353 | 1228192.3902 | 2701753.2866 | 1228194.1859 | 2701763.8195 | 1228192.2111
42 | 2701712.0353 | 1228192.3902 | 2701691.0935 | 1228192.2892
43 | 2701712.0353 | 1228192.3902 | 2701713.3209 | 1228218.2877
44 | 2701649.0151 | 1228188.7789 | 2701655.8957 | 1228192.1194 | 2701691.0935 | 1228192.2892
45 | 2701713.3209 | 1228218.2877 | 2701714.6279 | 1228244.6174 | 2701694.4562 | 1228249.3241
46 | 2701617.7947 | 1228173.6215 | 2701649.0151 | 1228188.7789
47 | 2701677.7768 | 1228253.216 | 2701677.7768 | 1228253.216 | 2701694.4562 | 1228249.3241
48 | 2701617.7947 | 1228173.6215 | 2701601.4689 | 1228173.8627
49 | 2701680.2212 | 1228275.8977 | 2701677.7768 | 1228253.216
50 | 2701601.4689 | 1228173.8627 | 2701593.1586 | 1228173.9854
51 | 2701560.6762 | 1228174.8325 | 2701577.3133 | 1228174.2195 | 2701593.1586 | 1228173.9854
52 | 2701551.8557 | 1228175.1575 | 2701560.6762 | 1228174.8325
53 | 2701534.6325 | 1228175.7921 | 2701551.8557 | 1228175.1575
54 | 2701534.6325 | 1228175.7921 | 2701525.1646 | 1228179.0106 | 2701511.7025 | 1228185.7859 | 2701506.0554 | 1228196.9311 | 2701500.8766 | 1228217.9359 | 2701498.1058 | 1228223.2042
55 | 2701477.6645 | 1228303.1592 | 2701480.7492 | 1228303.77
56 | 2701496.5233 | 1228306.8937 | 2701496.5233 | 1228306.8937 | 2701480.7492 | 1228303.77
57 | 2701496.5233 | 1228306.8937 | 2701496.5914 | 1228308.2286
58 | 2701497.2704 | 1228364.7823 | 2701496.0955 | 1228349.7067 | 2701497.5341 | 1228326.7032 | 2701496.5914 | 1228308.2286
59 | 2701497.2704 | 1228364.7823 | 2701572.7326 | 1228376.6568
60 | 2701572.7326 | 1228376.6568 | 2701599.1168 | 1228378.6788
61 | 2701599.1168 | 1228378.6788 | 2701618.008 | 1228380.1266
62 | 2701623.8971 | 1228380.5779 | 2701618.008 | 1228380.1266
63 | 2701687.6925 | 1228350.6208 | 2701623.8971 | 1228380.5779
64 | 2701646.8843 | 1228308.9659 | 2701652.8833 | 1228308.5093
65 | 2701652.8833 | 1228308.5093 | 2701658.8846 | 1228308.0526
66 | 2701695.2871 | 1228386.3688 | 2701691.5497 | 1228380.6785 | 2701690.6198 | 1228373.4573 | 2701687.6925 | 1228350.6208
67 | 2701686.7735 | 1228343.0066 | 2701687.0158 | 1228345.3417 | 2701687.6925 | 1228350.6208
68 | 2701695.2871 | 1228386.3688 | 2701689.8114 | 1228328.1212 | 2701698.272 | 1228320.4269 | 2701699.8888 | 1228320.2645
69 | 2701686.7735 | 1228343.0066 | 2701685.2851 | 1228328.6665 | 2701684.2853 | 1228320.3212
70 | 2701684.2709 | 1228320.2008 | 2701684.2853 | 1228320.3212
71 | 2701682.5992 | 1228306.2485 | 2701684.2709 | 1228320.2008
72 | 2701723.4477 | 1228317.8984 | 2701699.8888 | 1228320.2645
73 | 2701681.4984 | 1228287.7494 | 2701682.5992 | 1228306.2485
74 | 2701682.5992 | 1228306.2485 | 2701677.3403 | 1228306.6478 | 2701664.9362 | 1228307.592
75 | 2701681.4984 | 1228287.7494 | 2701730.255 | 1228283.4463
76 | 2701681.4984 | 1228287.7494 | 2701680.2212 | 1228275.8977
77 | 2701664.8842 | 1228307.5959 | 2701664.9362 | 1228307.592
78 | 2701751.2524 | 1228281.5931 | 2701730.255 | 1228283.4463
79 | 2701658.8846 | 1228308.0526 | 2701664.8842 | 1228307.5959

## bus_geodata
| x | y | coords
0 | 2701822.3547 | 1228001.3596
1 | 2701845.3597 | 1227993.3128
2 | 2701797.3104 | 1228016.8086
3 | 2701884.4983 | 1227964.3754
4 | 2701777.809 | 1228011.2127
5 | 2701710.9801 | 1228134.581
6 | 2701745.2805 | 1228159.1691
7 | 2701667.4979 | 1228107.8182
8 | 2701898.4647 | 1227948.9348
9 | 2701760.9853 | 1228171.7375
10 | 2701755.7311 | 1228001.7751
11 | 2701675.9421 | 1228032.578
12 | 2701673.1994 | 1227937.7499
13 | 2701655.3918 | 1228101.4775
14 | 2701935.3618 | 1227881.6507
15 | 2701647.4267 | 1227950.7417
16 | 2701949.0335 | 1227875.536
17 | 2701863.1747 | 1227850.2149
18 | 2701969.6443 | 1227846.7169
19 | 2701968.2963 | 1227893.0161
20 | 2701871.2795 | 1228271.5412
21 | 2701850.368 | 1228254.5693
22 | 2701844.1122 | 1228271.0785
23 | 2701842.5442 | 1228247.5681
24 | 2701859.0429 | 1228418.3829
25 | 2701806.0064 | 1228360.0654
26 | 2701810.3419 | 1228457.3765
27 | 2701845.3653 | 1228294.241
28 | 2701827.6539 | 1228234.2433
29 | 2701854.0842 | 1228326.5192
30 | 2701798.2254 | 1228350.7367
31 | 2701848.0316 | 1228317.509
32 | 2701815.1724 | 1228222.5351
33 | 2701807.7964 | 1228266.3515
34 | 2701807.6545 | 1228289.213
35 | 2701811.9289 | 1228312.5095
36 | 2701798.1189 | 1228206.5381
37 | 2701794.9867 | 1228203.6
38 | 2701785.3503 | 1228194.5606
39 | 2701775.2566 | 1228185.3996
40 | 2701763.8195 | 1228192.2111
41 | 2701712.0353 | 1228192.3902
42 | 2701691.0935 | 1228192.2892
43 | 2701713.3209 | 1228218.2877
44 | 2701649.0151 | 1228188.7789
45 | 2701694.4563 | 1228249.3241
46 | 2701617.7947 | 1228173.6215
47 | 2701677.7768 | 1228253.216
48 | 2701601.4689 | 1228173.8627
49 | 2701593.1586 | 1228173.9854
50 | 2701560.6762 | 1228174.8325
51 | 2701551.8557 | 1228175.1575
52 | 2701534.6325 | 1228175.7921
53 | 2701498.1058 | 1228223.2042
54 | 2701477.6645 | 1228303.1592
55 | 2701480.7492 | 1228303.77
56 | 2701496.5233 | 1228306.8937
57 | 2701496.5914 | 1228308.2286
58 | 2701497.2704 | 1228364.7823
59 | 2701572.7326 | 1228376.6568
60 | 2701599.1168 | 1228378.6788
61 | 2701618.008 | 1228380.1266
62 | 2701623.8971 | 1228380.5779
63 | 2701646.8843 | 1228308.9659
64 | 2701652.8833 | 1228308.5093
65 | 2701687.6925 | 1228350.6208
66 | 2701695.2871 | 1228386.3688
67 | 2701686.7735 | 1228343.0066
68 | 2701684.2853 | 1228320.3212
69 | 2701684.2709 | 1228320.2008
70 | 2701699.8888 | 1228320.2645
71 | 2701682.5992 | 1228306.2485
72 | 2701723.4477 | 1228317.8984
73 | 2701681.4984 | 1228287.7494
74 | 2701664.9362 | 1228307.592
75 | 2701759.8187 | 1228319.0895
76 | 2701730.255 | 1228283.4463
77 | 2701680.2212 | 1228275.8977
78 | 2701664.8842 | 1228307.5959
79 | 2701751.2524 | 1228281.5931
80 | 2701658.8846 | 1228308.0526
81 | 2701751.2524 | 1228281.5931

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97482 | -0.48558 | 0.0045798 | 0.0011478
1 | 0.97464 | -0.48912 | 0.0016723 | 0.00041913
2 | 0.97516 | -0.47873 | 0 | 0
3 | 0.97435 | -0.49475 | 0.0046352 | 0.0011617
4 | 0.9754 | -0.47409 | 0.0031799 | 0.00079697
5 | 0.97946 | -0.39443 | 0.0044879 | 0.0011248
6 | 0.98071 | -0.36984 | 0.0087104 | 0.002183
7 | 0.97814 | -0.42011 | 0.0015522 | 0.00038902
8 | 0.97432 | -0.49536 | 0 | 0
9 | 0.98148 | -0.35495 | 0.0015985 | 0.00040062
10 | 0.97575 | -0.46716 | 0.0030027 | 0.00075254
11 | 0.97756 | -0.43162 | 0 | 0
12 | 0.9769 | -0.44461 | 0.00098391 | 0.00024659
13 | 0.97805 | -0.42195 | 0 | 0
14 | 0.9742 | -0.49768 | 0 | 0
15 | 0.9767 | -0.44855 | 0.0063886 | 0.0016011
16 | 0.97419 | -0.498 | 0 | 0
17 | 0.97417 | -0.49828 | 0.00040703 | 0.00010201
18 | 0.97417 | -0.49832 | 0.00049218 | 0.00012335
19 | 0.97417 | -0.49834 | 0.00069119 | 0.00017323
20 | 0.97847 | -0.4136 | 0.0034522 | 0.00086521
21 | 0.97856 | -0.4119 | 0 | 0
22 | 0.97813 | -0.42018 | 0.0089236 | 0.0022365
23 | 0.97881 | -0.407 | 0.0054921 | 0.0013765
24 | 0.97355 | -0.51029 | 0 | 0
25 | 0.97411 | -0.49922 | 0 | 0
26 | 0.97311 | -0.51905 | 0.0076349 | 0.0019135
27 | 0.97754 | -0.43174 | 0.008847 | 0.0022173
28 | 0.97931 | -0.39717 | 0 | 0
29 | 0.9768 | -0.44632 | 0 | 0
30 | 0.97363 | -0.50878 | 0.01666 | 0.0041753
31 | 0.97698 | -0.44278 | 0.031101 | 0.0077946
32 | 0.97998 | -0.38409 | 0.0044672 | 0.0011196
33 | 0.97685 | -0.44541 | 0.014758 | 0.0036986
34 | 0.97582 | -0.46558 | 0.014121 | 0.003539
35 | 0.97493 | -0.48314 | 0.031289 | 0.0078419
36 | 0.98092 | -0.36577 | 0.0070225 | 0.00176
37 | 0.9811 | -0.36227 | 0.0036149 | 0.00090597
38 | 0.98166 | -0.3513 | 0.0032075 | 0.00080389
39 | 0.98225 | -0.3398 | 0 | 0
40 | 0.98298 | -0.32565 | 0.0087714 | 0.0021983
41 | 0.98585 | -0.27003 | 0 | 0
42 | 0.98549 | -0.27722 | 0.0038984 | 0.00097702
43 | 0.9874 | -0.24019 | 0.031217 | 0.0078236
44 | 0.98488 | -0.28894 | 0.0031905 | 0.00079962
45 | 0.99055 | -0.17974 | 0.017633 | 0.0044191
46 | 0.9845 | -0.29646 | 0 | 0
47 | 0.99176 | -0.15651 | 0.015469 | 0.0038769
48 | 0.98432 | -0.3 | 0.0079742 | 0.0019985
49 | 0.98429 | -0.3006 | 0.00066927 | 0.00016773
50 | 0.98419 | -0.30259 | 0.00060829 | 0.00015245
51 | 0.98416 | -0.30304 | 0.00080163 | 0.00020091
52 | 0.98413 | -0.30365 | 0 | 0
53 | 0.98401 | -0.30599 | 0.0019887 | 0.00049843
54 | 0.9779 | -0.42615 | 0.0060051 | 0.001505
55 | 0.97791 | -0.42581 | 0.0064029 | 0.0016047
56 | 0.9781 | -0.42217 | 0.0053991 | 0.0013531
57 | 0.97812 | -0.42174 | 0.005082 | 0.0012737
58 | 0.97932 | -0.39814 | 0 | 0
59 | 0.98094 | -0.36641 | 0.033577 | 0.0084152
60 | 0.98233 | -0.33938 | 0.0073142 | 0.0018331
61 | 0.98344 | -0.31758 | 0.0073773 | 0.0018489
62 | 0.98383 | -0.31 | 0 | 0
63 | 0.99267 | -0.13933 | 0.0036767 | 0.00092147
64 | 0.99269 | -0.13894 | 0.0036801 | 0.00092232
65 | 0.98847 | -0.22011 | 0.013673 | 0.0034267
66 | 0.98788 | -0.23166 | 0 | 0
67 | 0.9892 | -0.20613 | 0.011657 | 0.0029216
68 | 0.9916 | -0.15993 | 0.0036746 | 0.00092094
69 | 0.99161 | -0.15967 | 0.0036772 | 0.0009216
70 | 0.98673 | -0.25397 | 0.0088539 | 0.002219
71 | 0.99318 | -0.12951 | 0 | 0
72 | 0.98655 | -0.2576 | 0.0085764 | 0.0021494
73 | 0.99442 | -0.10578 | 0 | 0
74 | 0.9928 | -0.13697 | 0.009099 | 0.0022804
75 | 0.97235 | -0.53387 | 0.026055 | 0.00653
76 | 1 | 0 | -0.52089 | -0.13332
77 | 0.99346 | -0.12408 | 0.026768 | 0.0067087
78 | 0.9928 | -0.13698 | 0.0036766 | 0.00092143
79 | 0.99966 | -0.0065514 | 0.017826 | 0.0044675
80 | 0.99274 | -0.13815 | 0.0036766 | 0.00092145
81 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0079012 | 0.0019774 | -0.0078999 | -0.0019768 | 1.3292e-06 | 5.4693e-07 | 0.01206 | 0.01206 | 0.01206 | 0.97482 | -0.48558 | 0.97464 | -0.48912 | 3.3132
1 | -0.012481 | -0.0031252 | 0.012485 | 0.0031274 | 4.0702e-06 | 2.232e-06 | 0.019051 | 0.019051 | 0.019051 | 0.97482 | -0.48558 | 0.97516 | -0.47873 | 5.2337
2 | 0.0062275 | 0.0015577 | -0.0062258 | -0.0015572 | 1.6683e-06 | 4.5444e-07 | 0.0095067 | 0.0095069 | 0.0095069 | 0.97464 | -0.48912 | 0.97435 | -0.49475 | 2.6118
3 | -0.012485 | -0.0031274 | 0.012488 | 0.0031289 | 2.7612e-06 | 1.514e-06 | 0.019051 | 0.01905 | 0.019051 | 0.97516 | -0.47873 | 0.9754 | -0.47409 | 5.2337
4 | 0.0015907 | 0.00039555 | -0.0015906 | -0.00039578 | 4.6033e-08 | -2.2984e-07 | 0.0024281 | 0.0024282 | 0.0024282 | 0.97435 | -0.49475 | 0.97432 | -0.49536 | 0.66709
5 | -0.015668 | -0.0039259 | 0.015673 | 0.0039289 | 5.1722e-06 | 3.0087e-06 | 0.023902 | 0.023902 | 0.023902 | 0.9754 | -0.47409 | 0.97575 | -0.46716 | 6.5664
6 | -0.032174 | -0.0080928 | 0.032212 | 0.0081164 | 3.7836e-05 | 2.3683e-05 | 0.04889 | 0.04889 | 0.04889 | 0.97946 | -0.39443 | 0.98071 | -0.36984 | 13.4314
7 | 0.027686 | 0.006968 | -0.027652 | -0.0069469 | 3.3942e-05 | 2.108e-05 | 0.042072 | 0.042072 | 0.042072 | 0.97946 | -0.39443 | 0.97814 | -0.42011 | 11.5583
8 | -0.040922 | -0.010299 | 0.040951 | 0.010318 | 2.9144e-05 | 1.8397e-05 | 0.062106 | 0.062106 | 0.062106 | 0.98071 | -0.36984 | 0.98148 | -0.35495 | 17.0621
9 | 0.018718 | 0.0047066 | -0.018676 | -0.0046814 | 4.196e-05 | 2.5127e-05 | 0.02848 | 0.028481 | 0.028481 | 0.97814 | -0.42011 | 0.97575 | -0.46716 | 7.8243
10 | 0.0073824 | 0.0018513 | -0.0073817 | -0.0018511 | 6.4642e-07 | 2.4218e-07 | 0.011231 | 0.011231 | 0.011231 | 0.97814 | -0.42011 | 0.97805 | -0.42195 | 3.0854
11 | 0.0015906 | 0.00039578 | -0.0015904 | -0.00039665 | 1.7464e-07 | -8.7165e-07 | 0.0024282 | 0.0024286 | 0.0024286 | 0.97432 | -0.49536 | 0.9742 | -0.49768 | 0.66719
12 | -0.04255 | -0.010718 | 0.042581 | 0.010738 | 3.085e-05 | 1.9494e-05 | 0.064529 | 0.064529 | 0.064529 | 0.98148 | -0.35495 | 0.98225 | -0.3398 | 17.7278
13 | 0.0073783 | 0.0018498 | -0.0073738 | -0.0018481 | 4.5656e-06 | 1.7128e-06 | 0.011231 | 0.011232 | 0.011232 | 0.97756 | -0.43162 | 0.9769 | -0.44461 | 3.0856
14 | -0.0073783 | -0.0018498 | 0.0073817 | 0.0018511 | 3.401e-06 | 1.2748e-06 | 0.011231 | 0.011231 | 0.011231 | 0.97756 | -0.43162 | 0.97805 | -0.42195 | 3.0855
15 | 0.0063898 | 0.0016015 | -0.0063886 | -0.0016011 | 1.1996e-06 | 3.4504e-07 | 0.0097331 | 0.0097332 | 0.0097332 | 0.9769 | -0.44461 | 0.9767 | -0.44855 | 2.674
16 | 0.0011834 | 0.00029564 | -0.0011834 | -0.00029582 | 1.83e-08 | -1.7432e-07 | 0.0018072 | 0.0018073 | 0.0018073 | 0.9742 | -0.49768 | 0.97419 | -0.498 | 0.4965
17 | 0.00040704 | 0.00010101 | -0.00040703 | -0.00010201 | 1.173e-08 | -1.0007e-06 | 0.00062136 | 0.00062172 | 0.00062172 | 0.9742 | -0.49768 | 0.97417 | -0.49828 | 0.1708
18 | 0.00049218 | 0.00012291 | -0.00049218 | -0.00012335 | 7.522e-09 | -4.3716e-07 | 0.00075162 | 0.00075178 | 0.00075178 | 0.97419 | -0.498 | 0.97417 | -0.49832 | 0.20653
19 | 0.0006912 | 0.0001729 | -0.00069119 | -0.00017323 | 1.1174e-08 | -3.2572e-07 | 0.0010557 | 0.0010558 | 0.0010558 | 0.97419 | -0.498 | 0.97417 | -0.49834 | 0.29005
20 | -0.0034522 | -0.00086521 | 0.0034525 | 0.00086505 | 2.7844e-07 | -1.6021e-07 | 0.00525 | 0.0052498 | 0.00525 | 0.97847 | -0.4136 | 0.97856 | -0.4119 | 1.4423
21 | 0.099548 | 0.025066 | -0.099508 | -0.025042 | 3.937e-05 | 2.4277e-05 | 0.15142 | 0.15142 | 0.15142 | 0.97856 | -0.4119 | 0.97813 | -0.42018 | 10.3995
22 | -0.103 | -0.025931 | 0.10302 | 0.025946 | 2.4159e-05 | 1.4934e-05 | 0.15667 | 0.15667 | 0.15667 | 0.97856 | -0.4119 | 0.97881 | -0.407 | 10.7601
23 | 0.090585 | 0.022805 | -0.090535 | -0.022775 | 5.0046e-05 | 3.062e-05 | 0.13784 | 0.13784 | 0.13784 | 0.97813 | -0.42018 | 0.97754 | -0.43174 | 9.4672
24 | -0.10852 | -0.027323 | 0.10857 | 0.027354 | 5.101e-05 | 3.1641e-05 | 0.16502 | 0.16502 | 0.16502 | 0.97881 | -0.407 | 0.97931 | -0.39717 | 11.3335
25 | -0.0076381 | -0.0019148 | 0.0076422 | 0.0019164 | 4.0289e-06 | 1.5977e-06 | 0.011675 | 0.011674 | 0.011675 | 0.97355 | -0.51029 | 0.97411 | -0.49922 | 3.2073
26 | 0.0076381 | 0.0019148 | -0.0076349 | -0.0019135 | 3.1888e-06 | 1.2654e-06 | 0.011675 | 0.011675 | 0.011675 | 0.97355 | -0.51029 | 0.97311 | -0.51905 | 3.2074
27 | -0.050408 | -0.012653 | 0.050535 | 0.012732 | 0.00012752 | 7.8751e-05 | 0.077008 | 0.077007 | 0.077008 | 0.97411 | -0.49922 | 0.9768 | -0.44632 | 10.5781
28 | 0.042766 | 0.010737 | -0.042746 | -0.010725 | 1.9486e-05 | 1.2319e-05 | 0.065334 | 0.065334 | 0.065334 | 0.97411 | -0.49922 | 0.97363 | -0.50878 | 17.9489
29 | 0.081688 | 0.020557 | -0.081645 | -0.020531 | 4.3048e-05 | 2.6063e-05 | 0.12438 | 0.12438 | 0.12438 | 0.97754 | -0.43174 | 0.97698 | -0.44278 | 8.5423
30 | -0.16894 | -0.042566 | 0.16905 | 0.042633 | 0.00010579 | 6.6844e-05 | 0.25678 | 0.25678 | 0.25678 | 0.97931 | -0.39717 | 0.97998 | -0.38409 | 17.6362
31 | 0.060377 | 0.015212 | -0.060238 | -0.015124 | 0.00013896 | 8.8383e-05 | 0.091768 | 0.091769 | 0.091769 | 0.97931 | -0.39717 | 0.97685 | -0.44541 | 25.2112
32 | -0.050535 | -0.012732 | 0.050544 | 0.012737 | 8.5748e-06 | 4.7154e-06 | 0.077007 | 0.077007 | 0.077007 | 0.9768 | -0.44632 | 0.97698 | -0.44278 | 5.289
33 | 0.026086 | 0.0065493 | -0.026055 | -0.00653 | 3.1182e-05 | 1.9307e-05 | 0.039873 | 0.039873 | 0.039873 | 0.97363 | -0.50878 | 0.97235 | -0.53387 | 10.9541
34 | -0.17352 | -0.043753 | 0.17367 | 0.043849 | 0.00015228 | 9.6278e-05 | 0.26357 | 0.26357 | 0.26357 | 0.97998 | -0.38409 | 0.98092 | -0.36577 | 18.1021
35 | 0.04548 | 0.011425 | -0.045436 | -0.011397 | 4.3732e-05 | 2.7685e-05 | 0.069289 | 0.069289 | 0.069289 | 0.97685 | -0.44541 | 0.97582 | -0.46558 | 19.0354
36 | 0.031316 | 0.0078583 | -0.031289 | -0.0078419 | 2.6204e-05 | 1.6388e-05 | 0.047756 | 0.047756 | 0.047756 | 0.97582 | -0.46558 | 0.97493 | -0.48314 | 13.1199
37 | -0.18069 | -0.045609 | 0.18072 | 0.045628 | 3.0275e-05 | 1.9159e-05 | 0.27422 | 0.27422 | 0.27422 | 0.98092 | -0.36577 | 0.9811 | -0.36227 | 18.8337
38 | -0.18434 | -0.046534 | 0.18443 | 0.046595 | 9.6905e-05 | 6.1352e-05 | 0.2797 | 0.2797 | 0.2797 | 0.9811 | -0.36227 | 0.98166 | -0.3513 | 19.2103
39 | -0.18764 | -0.047399 | 0.18775 | 0.047465 | 0.00010348 | 6.5539e-05 | 0.28456 | 0.28456 | 0.28456 | 0.98166 | -0.3513 | 0.98225 | -0.3398 | 19.5442
40 | -0.23033 | -0.058203 | 0.23048 | 0.058302 | 0.00015639 | 9.9397e-05 | 0.34909 | 0.34909 | 0.34909 | 0.98225 | -0.3398 | 0.98298 | -0.32565 | 23.9761
41 | -0.23925 | -0.0605 | 0.23989 | 0.060908 | 0.00064023 | 0.0004071 | 0.36237 | 0.36237 | 0.36237 | 0.98298 | -0.32565 | 0.98585 | -0.27003 | 24.888
42 | 0.019153 | 0.0048058 | -0.019147 | -0.0048018 | 6.5642e-06 | 3.9342e-06 | 0.028911 | 0.028911 | 0.028911 | 0.98585 | -0.27003 | 0.98549 | -0.27722 | 7.9427
43 | -0.25905 | -0.065713 | 0.25942 | 0.06595 | 0.00037217 | 0.00023686 | 0.39128 | 0.39128 | 0.39128 | 0.98585 | -0.27003 | 0.9874 | -0.24019 | 26.8736
44 | 0.015248 | 0.0038248 | -0.01524 | -0.0038199 | 8.5184e-06 | 4.9062e-06 | 0.023025 | 0.023025 | 0.023025 | 0.98549 | -0.27722 | 0.98488 | -0.28894 | 6.3256
45 | -0.29064 | -0.073774 | 0.29148 | 0.074314 | 0.00084792 | 0.00054025 | 0.43832 | 0.43832 | 0.43832 | 0.9874 | -0.24019 | 0.99055 | -0.17974 | 30.1046
46 | 0.012049 | 0.0030203 | -0.012045 | -0.003018 | 4.3133e-06 | 2.319e-06 | 0.018205 | 0.018205 | 0.018205 | 0.98488 | -0.28894 | 0.9845 | -0.29646 | 5.0014
47 | -0.30912 | -0.078733 | 0.30946 | 0.078954 | 0.00034691 | 0.00022114 | 0.46481 | 0.46481 | 0.46481 | 0.99055 | -0.17974 | 0.99176 | -0.15651 | 31.9238
48 | 0.012045 | 0.003018 | -0.012043 | -0.0030169 | 2.0293e-06 | 1.0911e-06 | 0.018205 | 0.018205 | 0.018205 | 0.9845 | -0.29646 | 0.98432 | -0.3 | 5.0014
49 | -0.32493 | -0.082831 | 0.32544 | 0.083156 | 0.00050936 | 0.00032481 | 0.48802 | 0.48802 | 0.48802 | 0.99176 | -0.15651 | 0.99346 | -0.12408 | 33.5178
50 | 0.0040687 | 0.0010183 | -0.0040686 | -0.0010184 | 1.1789e-07 | -3.0189e-08 | 0.0061503 | 0.0061503 | 0.0061503 | 0.98432 | -0.3 | 0.98429 | -0.3006 | 1.6897
51 | 0.0033993 | 0.00085064 | -0.003399 | -0.00085085 | 3.2177e-07 | -2.0705e-07 | 0.0051385 | 0.0051387 | 0.0051387 | 0.98429 | -0.3006 | 0.98419 | -0.30259 | 1.4117
52 | 0.0027907 | 0.00069839 | -0.0027907 | -0.00069847 | 5.8917e-08 | -7.4453e-08 | 0.004219 | 0.004219 | 0.004219 | 0.98419 | -0.30259 | 0.98416 | -0.30304 | 1.1591
53 | 0.001989 | 0.00049756 | -0.001989 | -0.00049774 | 5.8441e-08 | -1.816e-07 | 0.003007 | 0.0030071 | 0.0030071 | 0.98416 | -0.30304 | 0.98413 | -0.30365 | 0.82612
54 | 0.001989 | 0.00049774 | -0.0019887 | -0.00049843 | 2.2095e-07 | -6.8632e-07 | 0.0030071 | 0.0030074 | 0.0030074 | 0.98413 | -0.30365 | 0.98401 | -0.30599 | 0.8262
55 | -0.0060051 | -0.001505 | 0.0060052 | 0.001505 | 9.8462e-08 | 2.3563e-08 | 0.0091376 | 0.0091376 | 0.0091376 | 0.9779 | -0.42615 | 0.97791 | -0.42581 | 2.5103
56 | -0.012408 | -0.0031098 | 0.01241 | 0.0031109 | 2.1496e-06 | 1.1739e-06 | 0.01888 | 0.01888 | 0.01888 | 0.97791 | -0.42581 | 0.9781 | -0.42217 | 5.1869
57 | -0.017809 | -0.0044641 | 0.01781 | 0.0044643 | 3.6796e-07 | 2.1872e-07 | 0.027094 | 0.027094 | 0.027094 | 0.9781 | -0.42217 | 0.97812 | -0.42174 | 7.4435
58 | -0.022892 | -0.005738 | 0.022918 | 0.0057538 | 2.5773e-05 | 1.5783e-05 | 0.034826 | 0.034825 | 0.034826 | 0.97812 | -0.42174 | 0.97932 | -0.39814 | 9.5675
59 | -0.022918 | -0.0057538 | 0.022952 | 0.005775 | 3.4742e-05 | 2.1272e-05 | 0.034825 | 0.034825 | 0.034825 | 0.97932 | -0.39814 | 0.98094 | -0.36641 | 9.5674
60 | -0.056529 | -0.01419 | 0.056602 | 0.014237 | 7.298e-05 | 4.6373e-05 | 0.085759 | 0.085759 | 0.085759 | 0.98094 | -0.36641 | 0.98233 | -0.33938 | 23.5601
61 | -0.063916 | -0.01607 | 0.063983 | 0.016112 | 6.6627e-05 | 4.2401e-05 | 0.096838 | 0.096838 | 0.096838 | 0.98233 | -0.33938 | 0.98344 | -0.31758 | 26.6039
62 | -0.07136 | -0.017961 | 0.071386 | 0.017977 | 2.5835e-05 | 1.6459e-05 | 0.108 | 0.108 | 0.108 | 0.98344 | -0.31758 | 0.98383 | -0.31 | 29.6704
63 | -0.071386 | -0.017977 | 0.071694 | 0.018174 | 0.00030828 | 0.0001964 | 0.108 | 0.108 | 0.108 | 0.98383 | -0.31 | 0.98847 | -0.22011 | 29.6704
64 | -0.0036767 | -0.00092147 | 0.0036768 | 0.00092143 | 6.853e-08 | -3.392e-08 | 0.0055114 | 0.0055113 | 0.0055114 | 0.99267 | -0.13933 | 0.99269 | -0.13894 | 1.5141
65 | -0.0073569 | -0.0018438 | 0.0073571 | 0.0018438 | 2.7447e-07 | 9.7848e-08 | 0.011028 | 0.011028 | 0.011028 | 0.99269 | -0.13894 | 0.99274 | -0.13815 | 3.0296
66 | 0.01746 | 0.0043857 | -0.01745 | -0.00438 | 9.6169e-06 | 5.6794e-06 | 0.026287 | 0.026287 | 0.026287 | 0.98847 | -0.22011 | 0.98788 | -0.23166 | 7.2218
67 | -0.10283 | -0.025986 | 0.1029 | 0.02603 | 6.8985e-05 | 4.4052e-05 | 0.15487 | 0.15487 | 0.15487 | 0.98847 | -0.22011 | 0.9892 | -0.20613 | 42.5465
68 | 0.01745 | 0.00438 | -0.017432 | -0.0043691 | 1.8545e-05 | 1.0954e-05 | 0.026287 | 0.026288 | 0.026288 | 0.98788 | -0.23166 | 0.98673 | -0.25397 | 7.2219
69 | -0.11455 | -0.028952 | 0.11481 | 0.029114 | 0.00025438 | 0.00016251 | 0.1724 | 0.1724 | 0.1724 | 0.9892 | -0.20613 | 0.9916 | -0.15993 | 47.3639
70 | -0.11848 | -0.030035 | 0.11848 | 0.030036 | 1.4384e-06 | 9.1904e-07 | 0.17792 | 0.17792 | 0.17792 | 0.9916 | -0.15993 | 0.99161 | -0.15967 | 48.8788
71 | -0.12216 | -0.030958 | 0.12234 | 0.031071 | 0.00017731 | 0.0001133 | 0.18344 | 0.18344 | 0.18344 | 0.99161 | -0.15967 | 0.99318 | -0.12951 | 50.3947
72 | 0.0085779 | 0.0021501 | -0.0085764 | -0.0021494 | 1.4858e-06 | 6.485e-07 | 0.012936 | 0.012936 | 0.012936 | 0.98673 | -0.25397 | 0.98655 | -0.2576 | 3.5538
73 | -0.14616 | -0.037044 | 0.14632 | 0.03715 | 0.00016687 | 0.00010631 | 0.21912 | 0.21912 | 0.21912 | 0.99318 | -0.12951 | 0.99442 | -0.10578 | 30.0993
74 | 0.023818 | 0.0059727 | -0.02381 | -0.0059675 | 8.4598e-06 | 5.1851e-06 | 0.035687 | 0.035687 | 0.035687 | 0.99318 | -0.12951 | 0.9928 | -0.13697 | 9.804
75 | -0.49884 | -0.12721 | 0.50141 | 0.12885 | 0.0025621 | 0.0016372 | 0.74723 | 0.74723 | 0.74723 | 0.99442 | -0.10578 | 1 | 0 | 51.321
76 | 0.35252 | 0.090064 | -0.35221 | -0.089865 | 0.00031168 | 0.00019886 | 0.52811 | 0.52811 | 0.52811 | 0.99442 | -0.10578 | 0.99346 | -0.12408 | 36.2714
77 | 0.014711 | 0.0036871 | -0.014711 | -0.003687 | 9.516e-09 | 5.4154e-09 | 0.022049 | 0.022049 | 0.022049 | 0.9928 | -0.13697 | 0.9928 | -0.13698 | 6.0574
78 | 0.017831 | 0.0044708 | -0.017826 | -0.0044675 | 5.5652e-06 | 3.2853e-06 | 0.026534 | 0.026534 | 0.026534 | 1 | 0 | 0.99966 | -0.0065514 | 7.2895
79 | 0.011034 | 0.0027656 | -0.011034 | -0.0027653 | 6.1716e-07 | 3.1718e-07 | 0.016539 | 0.016539 | 0.016539 | 0.9928 | -0.13698 | 0.99274 | -0.13815 | 4.5436

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53893 | 0.13784

## res_load
| p_mw | q_mvar
0 | 0.0045798 | 0.0011478
1 | 0.0016723 | 0.00041913
2 | 0.0046352 | 0.0011617
3 | 0.0031799 | 0.00079697
4 | 0.0044879 | 0.0011248
5 | 0.0087104 | 0.002183
6 | 0.0015522 | 0.00038902
7 | 0.0015985 | 0.00040062
8 | 0.0030027 | 0.00075254
9 | 0.00098391 | 0.00024659
10 | 0.0063886 | 0.0016011
11 | 0.00040703 | 0.00010201
12 | 0.00049218 | 0.00012335
13 | 0.00069119 | 0.00017323
14 | 0.0034522 | 0.00086521
15 | 0.0089236 | 0.0022365
16 | 0.0054921 | 0.0013765
17 | 0.0076349 | 0.0019135
18 | 0.008847 | 0.0022173
19 | 0.01666 | 0.0041753
20 | 0.031101 | 0.0077946
21 | 0.0044672 | 0.0011196
22 | 0.014758 | 0.0036986
23 | 0.014121 | 0.003539
24 | 0.031289 | 0.0078419
25 | 0.0070225 | 0.00176
26 | 0.0036149 | 0.00090597
27 | 0.0032075 | 0.00080389
28 | 0.0087714 | 0.0021983
29 | 0.0038984 | 0.00097702
30 | 0.031217 | 0.0078236
31 | 0.0031905 | 0.00079962
32 | 0.017633 | 0.0044191
33 | 0.015469 | 0.0038769
34 | 0.0079742 | 0.0019985
35 | 0.00066927 | 0.00016773
36 | 0.00060829 | 0.00015245
37 | 0.00080163 | 0.00020091
38 | 0.0019887 | 0.00049843
39 | 0.0060051 | 0.001505
40 | 0.0064029 | 0.0016047
41 | 0.0053991 | 0.0013531
42 | 0.005082 | 0.0012737
43 | 0.033577 | 0.0084152
44 | 0.0073142 | 0.0018331
45 | 0.0073773 | 0.0018489
46 | 0.0036767 | 0.00092147
47 | 0.0036801 | 0.00092232
48 | 0.013673 | 0.0034267
49 | 0.011657 | 0.0029216
50 | 0.0036746 | 0.00092094
51 | 0.0036772 | 0.0009216
52 | 0.0088539 | 0.002219
53 | 0.0085764 | 0.0021494
54 | 0.009099 | 0.0022804
55 | 0.026055 | 0.00653
56 | 0.018042 | 0.0045217
57 | 0.026768 | 0.0067087
58 | 0.0036766 | 0.00092143
59 | 0.017826 | 0.0044675
60 | 0.0036766 | 0.00092145

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1