## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1322-22_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1322-22_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1322-22_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1322-22_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1322-22_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1322-22_0_4_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_1322-22_0_4_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_1322-22_0_4_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_1322-22_0_4_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_1322-22_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1322-22_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1322-22_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1322-22_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1322-22_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1322-22_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1322-22_0_4_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_1322-22_0_4_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_1322-22_0_4_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_1322-22_0_4_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_1322-22_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1322-22_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1322-22_0_4_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_1322-22_0_4_node_27 | 0.4 | n |  | TRUE
23 | bus_LV_1322-22_0_4_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_1322-22_0_4_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_1322-22_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1322-22_0_4_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1322-22_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1322-22_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1322-22_0_4_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_1322-22_0_4_node_29 | 0.4 | n |  | TRUE
31 | bus_MV_16_0_node_51 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1322-22_0_4_load_0 | 0 | 0.026356 | 0.0066055 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1322-22_0_4_load_1 | 1 | 0.0051211 | 0.0012835 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1322-22_0_4_load_2 | 2 | 0.077666 | 0.019465 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1322-22_0_4_load_3 | 3 | 0.033384 | 0.0083668 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1322-22_0_4_load_4 | 4 | 0.034657 | 0.0086858 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1322-22_0_4_load_10 | 6 | 0.088761 | 0.022246 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1322-22_0_4_load_12 | 8 | 0.046166 | 0.01157 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1322-22_0_4_load_5 | 10 | 0.011091 | 0.0027796 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1322-22_0_4_load_7 | 12 | 0.027107 | 0.0067937 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1322-22_0_4_load_9 | 13 | 0.0029297 | 0.00073426 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1322-22_0_4_load_11 | 14 | 0.0034598 | 0.00086711 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1322-22_0_4_load_20 | 15 | 0.0071277 | 0.0017864 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1322-22_0_4_load_21 | 17 | 0.013743 | 0.0034444 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1322-22_0_4_load_13 | 19 | 0.025332 | 0.0063488 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1322-22_0_4_load_27 | 22 | 0.045242 | 0.011339 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1322-22_0_4_load_30 | 23 | 0.022811 | 0.0057169 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1322-22_0_4_load_26 | 24 | 0.0059337 | 0.0014871 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1322-22_0_4_load_22 | 25 | 0.020844 | 0.005224 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1322-22_0_4_load_24 | 27 | 0.002049 | 0.00051354 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1322-22_0_4_load_29 | 30 | 0.015456 | 0.0038735 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1322-22_0_4_line_0 |  | 0 | 1 | 0.048727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_1322-22_0_4_line_1 |  | 0 | 2 | 0.078231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_1322-22_0_4_line_2 |  | 1 | 3 | 0.025913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_1322-22_0_4_line_3 |  | 2 | 4 | 0.025941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1322-22_0_4_line_4 |  | 3 | 5 | 0.045158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1322-22_0_4_line_5 |  | 4 | 6 | 0.027665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1322-22_0_4_line_6 |  | 5 | 7 | 0.025683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1322-22_0_4_line_7 |  | 5 | 8 | 0.122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1322-22_0_4_line_8 |  | 6 | 9 | 0.027634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1322-22_0_4_line_9 |  | 7 | 22 | 0.041202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1322-22_0_4_line_10 |  | 8 | 19 | 0.018343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1322-22_0_4_line_11 |  | 9 | 14 | 0.073841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1322-22_0_4_line_12 |  | 10 | 11 | 0.039019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1322-22_0_4_line_13 |  | 10 | 12 | 0.0079842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1322-22_0_4_line_14 |  | 11 | 13 | 0.030893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1322-22_0_4_line_15 |  | 13 | 15 | 0.066699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1322-22_0_4_line_16 |  | 14 | 16 | 0.077423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_1322-22_0_4_line_17 |  | 15 | 17 | 0.0010013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1322-22_0_4_line_18 |  | 16 | 18 | 0.09014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1322-22_0_4_line_19 |  | 17 | 18 | 0.056848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1322-22_0_4_line_20 |  | 19 | 20 | 0.10696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_1322-22_0_4_line_21 |  | 20 | 21 | 0.1742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_1322-22_0_4_line_22 |  | 21 | 23 | 0.015467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_1322-22_0_4_line_23 |  | 22 | 24 | 0.055958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1322-22_0_4_line_24 |  | 23 | 28 | 0.22347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_1322-22_0_4_line_25 |  | 24 | 29 | 0.04194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1322-22_0_4_line_26 |  | 25 | 26 | 0.083348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_1322-22_0_4_line_27 |  | 25 | 27 | 0.018663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1322-22_0_4_line_28 |  | 26 | 28 | 0.08249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_1322-22_0_4_line_29 |  | 29 | 30 | 0.021348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1322-22_0_4_trafo_0 | 0.63 MVA 20/0.4 kV | 31 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2699841.7704 | 1228582.1094 | 2699796.0074 | 1228565.3732
1 | 2699841.7704 | 1228582.1094 | 2699915.2427 | 1228608.9792
2 | 2699796.0074 | 1228565.3732 | 2699771.6711 | 1228556.4731
3 | 2699915.2427 | 1228608.9792 | 2699939.6054 | 1228617.889
4 | 2699732.3595 | 1228535.5683 | 2699746.4412 | 1228547.2462 | 2699771.6711 | 1228556.4731
5 | 2699965.5873 | 1228627.3909 | 2699939.6054 | 1228617.889
6 | 2699732.3595 | 1228535.5683 | 2699730.5537 | 1228509.9526
7 | 2699732.3595 | 1228535.5683 | 2699703.1095 | 1228530.9079 | 2699702.8505 | 1228534.6062 | 2699719.1035 | 1228548.3109 | 2699725.696 | 1228563.2545 | 2699726.827 | 1228579.4075 | 2699722.8204 | 1228596.8865 | 2699712.6351 | 1228610.4479
8 | 2699991.5398 | 1228636.8821 | 2699965.5873 | 1228627.3909
9 | 2699730.5537 | 1228509.9526 | 2699771.7501 | 1228510.6264
10 | 2699697.187 | 1228620.3392 | 2699712.6351 | 1228610.4479 | 2699712.6351 | 1228610.4479
11 | 2699991.5398 | 1228636.8821 | 2699997.8214 | 1228639.1782 | 2700060.1958 | 1228664.0566
12 | 2699950.5359 | 1228721.4993 | 2699915.2276 | 1228704.8908
13 | 2699908.0028 | 1228701.4924 | 2699915.2276 | 1228704.8908
14 | 2699950.5359 | 1228721.4993 | 2699978.4895 | 1228734.6523
15 | 2699978.4895 | 1228734.6523 | 2700038.8409 | 1228763.0496
16 | 2700126.073 | 1228704.5389 | 2700066.0748 | 1228666.4014 | 2700060.1958 | 1228664.0566
17 | 2700038.8409 | 1228763.0496 | 2700039.7469 | 1228763.4759
18 | 2700126.073 | 1228704.5389 | 2700091.1853 | 1228787.6793
19 | 2700091.1853 | 1228787.6793 | 2700039.7469 | 1228763.4759
20 | 2699591.7392 | 1228631.2712 | 2699669.1936 | 1228629.1558 | 2699694.3418 | 1228622.1609 | 2699697.187 | 1228620.3392
21 | 2699591.7392 | 1228631.2712 | 2699548.4555 | 1228632.4476 | 2699548.7013 | 1228638.1336 | 2699561.3566 | 1228645.8399 | 2699555.0224 | 1228655.2741 | 2699559.4287 | 1228658.2389 | 2699589.0289 | 1228678.1489 | 2699607.0662 | 1228690.282 | 2699636.81 | 1228711.1065
22 | 2699636.81 | 1228711.1065 | 2699649.481 | 1228719.9757
23 | 2699827.7009 | 1228511.5415 | 2699771.7501 | 1228510.6264
24 | 2699835.4613 | 1228843.8342 | 2699761.0956 | 1228793.9167 | 2699678.6052 | 1228740.3614 | 2699649.481 | 1228719.9757
25 | 2699869.5256 | 1228513.5756 | 2699859.1385 | 1228512.0557 | 2699827.7009 | 1228511.5415
26 | 2699907.4232 | 1228882.9599 | 2699910.4173 | 1228872.9918 | 2699943.2276 | 1228807.8475
27 | 2699951.6225 | 1228791.1797 | 2699943.2276 | 1228807.8475
28 | 2699835.4613 | 1228843.8342 | 2699843.3393 | 1228849.8819 | 2699857.726 | 1228860.4867 | 2699870.2389 | 1228868.5027 | 2699880.5503 | 1228873.5906 | 2699891.5419 | 1228878.3342 | 2699907.4232 | 1228882.9599
29 | 2699869.5256 | 1228513.5756 | 2699890.6183 | 1228516.8662

## bus_geodata
| x | y | coords
0 | 2699841.7704 | 1228582.1094
1 | 2699796.0074 | 1228565.3732
2 | 2699915.2427 | 1228608.9792
3 | 2699771.6711 | 1228556.4731
4 | 2699939.6054 | 1228617.889
5 | 2699732.3595 | 1228535.5683
6 | 2699965.5873 | 1228627.3909
7 | 2699730.5537 | 1228509.9526
8 | 2699712.6351 | 1228610.4479
9 | 2699991.5398 | 1228636.8821
10 | 2699915.2276 | 1228704.8908
11 | 2699950.5359 | 1228721.4993
12 | 2699908.0028 | 1228701.4924
13 | 2699978.4895 | 1228734.6523
14 | 2700060.1958 | 1228664.0566
15 | 2700038.8409 | 1228763.0496
16 | 2700126.073 | 1228704.5389
17 | 2700039.7469 | 1228763.4759
18 | 2700091.1853 | 1228787.6793
19 | 2699697.187 | 1228620.3392
20 | 2699591.7392 | 1228631.2712
21 | 2699636.81 | 1228711.1065
22 | 2699771.7501 | 1228510.6264
23 | 2699649.481 | 1228719.9757
24 | 2699827.7009 | 1228511.5415
25 | 2699943.2276 | 1228807.8475
26 | 2699907.4232 | 1228882.9599
27 | 2699951.6225 | 1228791.1797
28 | 2699835.4614 | 1228843.8342
29 | 2699869.5256 | 1228513.5756
30 | 2699890.6183 | 1228516.8662
31 | 2699732.3595 | 1228535.5683

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.498 | -0.12726
1 | 0.99499 | -0.094917 | 0.0051211 | 0.0012835
2 | 0.99039 | -0.1835 | 0.077666 | 0.019465
3 | 0.99239 | -0.14461 | 0.033384 | 0.0083668
4 | 0.98813 | -0.22714 | 0.034657 | 0.0086858
5 | 0.98855 | -0.21838 | 0 | 0
6 | 0.98615 | -0.26531 | 0.088761 | 0.022246
7 | 0.98697 | -0.24895 | 0 | 0
8 | 0.98192 | -0.34681 | 0.046166 | 0.01157
9 | 0.98531 | -0.28153 | 0 | 0
10 | 0.97147 | -0.55171 | 0.011091 | 0.0027796
11 | 0.97286 | -0.52422 | 0 | 0
12 | 0.97127 | -0.55571 | 0.027107 | 0.0067937
13 | 0.97397 | -0.50252 | 0.0029297 | 0.00073426
14 | 0.98306 | -0.32504 | 0.0034598 | 0.00086711
15 | 0.97653 | -0.45224 | 0.0071277 | 0.0017864
16 | 0.98082 | -0.36843 | 0 | 0
17 | 0.97657 | -0.45136 | 0.013743 | 0.0034444
18 | 0.97821 | -0.4192 | 0 | 0
19 | 0.98131 | -0.3586 | 0.025332 | 0.0063488
20 | 0.97903 | -0.40298 | 0 | 0
21 | 0.97532 | -0.4757 | 0 | 0
22 | 0.98444 | -0.2982 | 0.045242 | 0.011339
23 | 0.97499 | -0.48218 | 0.022811 | 0.0057169
24 | 0.98334 | -0.31975 | 0.0059337 | 0.0014871
25 | 0.97083 | -0.56428 | 0.020844 | 0.005224
26 | 0.97172 | -0.54665 | 0 | 0
27 | 0.9708 | -0.56499 | 0.002049 | 0.00051354
28 | 0.97261 | -0.52923 | 0 | 0
29 | 0.98274 | -0.33145 | 0 | 0
30 | 0.98243 | -0.3374 | 0.015456 | 0.0038735
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.22598 | 0.058026 | -0.22494 | -0.057364 | 0.0010361 | 0.00066182 | 0.33675 | 0.33675 | 0.33675 | 1 | 0 | 0.99499 | -0.094917 | 46.2571
1 | 0.27037 | 0.069238 | -0.26799 | -0.067717 | 0.0023804 | 0.0015214 | 0.40284 | 0.40284 | 0.40284 | 1 | 0 | 0.99039 | -0.1835 | 55.3351
2 | 0.21982 | 0.056081 | -0.21929 | -0.055745 | 0.0005262 | 0.0003361 | 0.32909 | 0.32909 | 0.32909 | 0.99499 | -0.094917 | 0.99239 | -0.14461 | 45.2052
3 | 0.19032 | 0.048252 | -0.18993 | -0.047997 | 0.00039826 | 0.00025422 | 0.28615 | 0.28615 | 0.28615 | 0.99039 | -0.1835 | 0.98813 | -0.22714 | 39.3063
4 | 0.18591 | 0.047378 | -0.18525 | -0.046957 | 0.00065927 | 0.00042077 | 0.27904 | 0.27904 | 0.27904 | 0.99239 | -0.14461 | 0.98855 | -0.21838 | 38.3294
5 | 0.15527 | 0.039312 | -0.15498 | -0.03913 | 0.00028393 | 0.00018101 | 0.23396 | 0.23396 | 0.23396 | 0.98813 | -0.22714 | 0.98615 | -0.26531 | 32.1374
6 | 0.066921 | 0.016882 | -0.066823 | -0.01682 | 9.7804e-05 | 6.2266e-05 | 0.10077 | 0.10077 | 0.10077 | 0.98855 | -0.21838 | 0.98697 | -0.24895 | 27.6846
7 | 0.11833 | 0.030075 | -0.1176 | -0.029613 | 0.00072697 | 0.00046215 | 0.17827 | 0.17827 | 0.17827 | 0.98855 | -0.21838 | 0.98192 | -0.34681 | 24.4873
8 | 0.066223 | 0.016885 | -0.066171 | -0.016852 | 5.1842e-05 | 3.2474e-05 | 0.10003 | 0.10003 | 0.10003 | 0.98615 | -0.26531 | 0.98531 | -0.28153 | 13.7402
9 | 0.066823 | 0.01682 | -0.066666 | -0.01672 | 0.0001569 | 9.9892e-05 | 0.10077 | 0.10077 | 0.10077 | 0.98697 | -0.24895 | 0.98444 | -0.2982 | 27.6846
10 | 0.071438 | 0.018043 | -0.071397 | -0.018017 | 4.0346e-05 | 2.5358e-05 | 0.10831 | 0.10831 | 0.10831 | 0.98192 | -0.34681 | 0.98131 | -0.3586 | 14.8774
11 | 0.066171 | 0.016852 | -0.066033 | -0.016766 | 0.00013853 | 8.6783e-05 | 0.10003 | 0.10003 | 0.10003 | 0.98531 | -0.28153 | 0.98306 | -0.32504 | 13.7403
12 | -0.038203 | -0.0095765 | 0.038253 | 0.0096081 | 5.0104e-05 | 3.1583e-05 | 0.058517 | 0.058517 | 0.058517 | 0.97147 | -0.55171 | 0.97286 | -0.52422 | 16.0761
13 | 0.027112 | 0.0067969 | -0.027107 | -0.0067937 | 5.1638e-06 | 3.206e-06 | 0.041529 | 0.041529 | 0.041529 | 0.97147 | -0.55171 | 0.97127 | -0.55571 | 11.4091
14 | -0.038253 | -0.0096081 | 0.038293 | 0.0096331 | 3.9669e-05 | 2.5004e-05 | 0.058517 | 0.058517 | 0.058517 | 0.97286 | -0.52422 | 0.97397 | -0.50252 | 16.076
15 | -0.041223 | -0.010367 | 0.041322 | 0.01043 | 9.9249e-05 | 6.2687e-05 | 0.062993 | 0.062992 | 0.062993 | 0.97397 | -0.50252 | 0.97653 | -0.45224 | 17.3057
16 | 0.062573 | 0.015898 | -0.062443 | -0.015817 | 0.00013044 | 8.1524e-05 | 0.094792 | 0.094793 | 0.094793 | 0.98306 | -0.32504 | 0.98082 | -0.36843 | 13.021
17 | -0.04845 | -0.012216 | 0.048452 | 0.012218 | 2.048e-06 | 1.2982e-06 | 0.073853 | 0.073853 | 0.073853 | 0.97653 | -0.45224 | 0.97657 | -0.45136 | 20.2894
18 | 0.062443 | 0.015817 | -0.062291 | -0.015722 | 0.00015187 | 9.4928e-05 | 0.094793 | 0.094794 | 0.094794 | 0.98082 | -0.36843 | 0.97821 | -0.4192 | 13.0211
19 | -0.062195 | -0.015662 | 0.062291 | 0.015722 | 9.5781e-05 | 5.9875e-05 | 0.094794 | 0.094794 | 0.094794 | 0.97657 | -0.45136 | 0.97821 | -0.4192 | 13.0212
20 | 0.046065 | 0.011668 | -0.045967 | -0.011608 | 9.7982e-05 | 6.0012e-05 | 0.069895 | 0.069896 | 0.069896 | 0.98131 | -0.3586 | 0.97903 | -0.40298 | 9.6011
21 | 0.045967 | 0.011608 | -0.045808 | -0.011511 | 0.00015958 | 9.7766e-05 | 0.069896 | 0.069898 | 0.069898 | 0.97903 | -0.40298 | 0.97532 | -0.4757 | 9.6014
22 | 0.045808 | 0.011511 | -0.045793 | -0.011502 | 1.4169e-05 | 8.682e-06 | 0.069898 | 0.069898 | 0.069898 | 0.97532 | -0.4757 | 0.97499 | -0.48218 | 9.6014
23 | 0.021424 | 0.0053815 | -0.021402 | -0.0053682 | 2.2012e-05 | 1.3377e-05 | 0.032388 | 0.032388 | 0.032388 | 0.98444 | -0.2982 | 0.98334 | -0.31975 | 8.8978
24 | 0.022983 | 0.0057852 | -0.022931 | -0.0057577 | 5.158e-05 | 2.7451e-05 | 0.035085 | 0.035087 | 0.035087 | 0.97499 | -0.48218 | 0.97261 | -0.52923 | 4.8197
25 | 0.015469 | 0.003881 | -0.01546 | -0.0038761 | 8.6183e-06 | 4.984e-06 | 0.023409 | 0.023409 | 0.023409 | 0.98334 | -0.31975 | 0.98274 | -0.33145 | 6.4311
26 | -0.022893 | -0.0057373 | 0.022912 | 0.0057476 | 1.9241e-05 | 1.0251e-05 | 0.035089 | 0.035088 | 0.035089 | 0.97083 | -0.56428 | 0.97172 | -0.54665 | 4.8199
27 | 0.0020491 | 0.00051335 | -0.002049 | -0.00051354 | 6.9032e-08 | -1.8658e-07 | 0.0031406 | 0.0031407 | 0.0031407 | 0.97083 | -0.56428 | 0.9708 | -0.56499 | 0.86283
28 | -0.022912 | -0.0057476 | 0.022931 | 0.0057577 | 1.9042e-05 | 1.0141e-05 | 0.035088 | 0.035087 | 0.035088 | 0.97172 | -0.54665 | 0.97261 | -0.52923 | 4.8198
29 | 0.01546 | 0.0038761 | -0.015456 | -0.0038735 | 4.3869e-06 | 2.5372e-06 | 0.023409 | 0.023409 | 0.023409 | 0.98274 | -0.33145 | 0.98243 | -0.3374 | 6.4311

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52435 | 0.13387

## res_load
| p_mw | q_mvar
0 | 0.026356 | 0.0066055
1 | 0.0051211 | 0.0012835
2 | 0.077666 | 0.019465
3 | 0.033384 | 0.0083668
4 | 0.034657 | 0.0086858
5 | 0.088761 | 0.022246
6 | 0.046166 | 0.01157
7 | 0.011091 | 0.0027796
8 | 0.027107 | 0.0067937
9 | 0.0029297 | 0.00073426
10 | 0.0034598 | 0.00086711
11 | 0.0071277 | 0.0017864
12 | 0.013743 | 0.0034444
13 | 0.025332 | 0.0063488
14 | 0.045242 | 0.011339
15 | 0.022811 | 0.0057169
16 | 0.0059337 | 0.0014871
17 | 0.020844 | 0.005224
18 | 0.002049 | 0.00051354
19 | 0.015456 | 0.0038735

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1