## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1322-26_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1322-26_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1322-26_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1322-26_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1322-26_0_4_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_1322-26_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1322-26_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1322-26_0_4_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_1322-26_0_4_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_1322-26_0_4_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_1322-26_0_4_node_21 | 0.4 | n |  | TRUE
11 | bus_LV_1322-26_0_4_node_41 | 0.4 | n |  | TRUE
12 | bus_LV_1322-26_0_4_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_1322-26_0_4_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1322-26_0_4_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_1322-26_0_4_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1322-26_0_4_node_42 | 0.4 | n |  | TRUE
17 | bus_LV_1322-26_0_4_node_38 | 0.4 | n |  | TRUE
18 | bus_LV_1322-26_0_4_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_1322-26_0_4_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_1322-26_0_4_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_1322-26_0_4_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_1322-26_0_4_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_1322-26_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_1322-26_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1322-26_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_1322-26_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1322-26_0_4_node_40 | 0.4 | n |  | TRUE
28 | bus_LV_1322-26_0_4_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_1322-26_0_4_node_34 | 0.4 | n |  | TRUE
30 | bus_LV_1322-26_0_4_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_1322-26_0_4_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_1322-26_0_4_node_36 | 0.4 | n |  | TRUE
33 | bus_LV_1322-26_0_4_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_1322-26_0_4_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_1322-26_0_4_node_46 | 0.4 | n |  | TRUE
36 | bus_LV_1322-26_0_4_node_45 | 0.4 | n |  | TRUE
37 | bus_LV_1322-26_0_4_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_1322-26_0_4_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_1322-26_0_4_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_1322-26_0_4_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_1322-26_0_4_node_43 | 0.4 | n |  | TRUE
42 | bus_MV_16_0_node_68 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1322-26_0_4_load_0 | 0 | 0.042535 | 0.01066 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1322-26_0_4_load_5 | 5 | 0.031687 | 0.0079415 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1322-26_0_4_load_19 | 7 | 0.0040373 | 0.0010118 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1322-26_0_4_load_17 | 8 | 0.014888 | 0.0037313 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1322-26_0_4_load_20 | 9 | 0.0048915 | 0.0012259 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1322-26_0_4_load_21 | 10 | 0.0082173 | 0.0020594 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1322-26_0_4_load_41 | 11 | 0.028562 | 0.0071583 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1322-26_0_4_load_39 | 12 | 0.06136 | 0.015378 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1322-26_0_4_load_22 | 14 | 0.0069674 | 0.0017462 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1322-26_0_4_load_24 | 15 | 0.0076365 | 0.0019139 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1322-26_0_4_load_42 | 16 | 0.026477 | 0.0066358 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1322-26_0_4_load_38 | 17 | 0.032182 | 0.0080656 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1322-26_0_4_load_7 | 18 | 0.02542 | 0.0063708 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1322-26_0_4_load_8 | 19 | 0.042233 | 0.010585 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1322-26_0_4_load_9 | 20 | 0.013201 | 0.0033084 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1322-26_0_4_load_13 | 23 | 0.013807 | 0.0034603 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1322-26_0_4_load_18 | 26 | 0.002958 | 0.00074134 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1322-26_0_4_load_40 | 27 | 0.05164 | 0.012942 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1322-26_0_4_load_34 | 29 | 0.0056978 | 0.001428 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1322-26_0_4_load_32 | 30 | 0.0037664 | 0.00094394 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1322-26_0_4_load_23 | 31 | 0.0075426 | 0.0018903 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1322-26_0_4_load_36 | 32 | 0.0074002 | 0.0018547 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1322-26_0_4_load_35 | 33 | 0.0030908 | 0.00077462 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1322-26_0_4_load_25 | 34 | 0.0018751 | 0.00046994 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1322-26_0_4_load_46 | 35 | 0.0082587 | 0.0020698 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1322-26_0_4_load_28 | 37 | 0.0078369 | 0.0019641 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1322-26_0_4_load_29 | 38 | 0.0098379 | 0.0024656 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1322-26_0_4_load_30 | 39 | 0.0059065 | 0.0014803 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1322-26_0_4_load_31 | 40 | 0.0068038 | 0.0017052 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1322-26_0_4_load_43 | 41 | 0.029861 | 0.0074839 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1322-26_0_4_line_0 |  | 0 | 1 | 0.01871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_1322-26_0_4_line_1 |  | 1 | 2 | 0.033246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_1322-26_0_4_line_2 |  | 1 | 3 | 0.032084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1322-26_0_4_line_3 |  | 2 | 7 | 0.017443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1322-26_0_4_line_4 |  | 2 | 8 | 0.0059269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_1322-26_0_4_line_5 |  | 3 | 9 | 0.022081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1322-26_0_4_line_6 |  | 3 | 10 | 0.038673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1322-26_0_4_line_7 |  | 4 | 5 | 0.029659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1322-26_0_4_line_8 |  | 4 | 6 | 0.004535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1322-26_0_4_line_9 |  | 5 | 11 | 0.022839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1322-26_0_4_line_10 |  | 6 | 12 | 0.0046029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1322-26_0_4_line_11 |  | 8 | 13 | 0.010805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_1322-26_0_4_line_12 |  | 9 | 14 | 0.004155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1322-26_0_4_line_13 |  | 10 | 15 | 0.039557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1322-26_0_4_line_14 |  | 11 | 16 | 0.020805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1322-26_0_4_line_15 |  | 12 | 17 | 0.048301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_1322-26_0_4_line_16 |  | 13 | 25 | 0.028121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1322-26_0_4_line_17 |  | 13 | 23 | 0.015114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1322-26_0_4_line_18 |  | 14 | 31 | 0.018568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1322-26_0_4_line_19 |  | 15 | 22 | 0.0023904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1322-26_0_4_line_20 |  | 16 | 41 | 0.021277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1322-26_0_4_line_21 |  | 17 | 27 | 0.0063478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_1322-26_0_4_line_22 |  | 18 | 19 | 0.010448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1322-26_0_4_line_23 |  | 18 | 20 | 0.010689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1322-26_0_4_line_24 |  | 19 | 21 | 0.031918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1322-26_0_4_line_25 |  | 21 | 22 | 0.032824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1322-26_0_4_line_26 |  | 23 | 24 | 0.014427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1322-26_0_4_line_27 |  | 24 | 26 | 0.036639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1322-26_0_4_line_28 |  | 25 | 27 | 0.017746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_1322-26_0_4_line_29 |  | 26 | 28 | 0.01717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1322-26_0_4_line_30 |  | 28 | 29 | 0.013623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1322-26_0_4_line_31 |  | 28 | 30 | 0.02847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1322-26_0_4_line_32 |  | 29 | 36 | 0.0056493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1322-26_0_4_line_33 |  | 30 | 40 | 0.0051041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1322-26_0_4_line_34 |  | 31 | 32 | 0.017905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1322-26_0_4_line_35 |  | 32 | 33 | 0.020608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1322-26_0_4_line_36 |  | 34 | 35 | 0.057755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1322-26_0_4_line_37 |  | 35 | 36 | 0.014129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1322-26_0_4_line_38 |  | 37 | 38 | 0.0013893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1322-26_0_4_line_39 |  | 37 | 39 | 0.021695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1322-26_0_4_line_40 |  | 39 | 40 | 0.0010669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1322-26_0_4_trafo_0 | 0.63 MVA 20/0.4 kV | 42 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2701715.2237 | 1228517.6285 | 2701710.7826 | 1228532.2522 | 2701710.3573 | 1228535.6525
1 | 2701715.2237 | 1228517.6285 | 2701702.4899 | 1228513.3187 | 2701691.5282 | 1228512.6197 | 2701682.7147 | 1228513.9366
2 | 2701735.7452 | 1228493.7729 | 2701731.4091 | 1228496.5008 | 2701727.4135 | 1228499.7015 | 2701723.8045 | 1228503.3424 | 2701720.3645 | 1228507.7313 | 2701717.4861 | 1228512.5189 | 2701715.2237 | 1228517.6285
3 | 2701682.7147 | 1228513.9366 | 2701698.3591 | 1228506.2216
4 | 2701682.7147 | 1228513.9366 | 2701677.2939 | 1228516.3332
5 | 2701735.7452 | 1228493.7729 | 2701728.3261 | 1228472.9757
6 | 2701735.7452 | 1228493.7729 | 2701771.2998 | 1228478.5588
7 | 2701704.7613 | 1228590.5143 | 2701709.642 | 1228590.9425 | 2701734.4015 | 1228591.0615
8 | 2701700.2177 | 1228590.3143 | 2701704.7613 | 1228590.5143
9 | 2701734.4015 | 1228591.0615 | 2701757.24 | 1228591.1713
10 | 2701700.2177 | 1228590.3143 | 2701700.5671 | 1228585.7247
11 | 2701667.4118 | 1228520.7023 | 2701677.2939 | 1228516.3332
12 | 2701726.9301 | 1228469.0623 | 2701728.3261 | 1228472.9757
13 | 2701771.2998 | 1228478.5588 | 2701783.1931 | 1228473.4696 | 2701791.5881 | 1228469.1545 | 2701800.267 | 1228464.6442 | 2701806.3258 | 1228460.3943
14 | 2701757.24 | 1228591.1713 | 2701778.0448 | 1228591.2712
15 | 2701689.8727 | 1228550.1361 | 2701703.2187 | 1228550.8921 | 2701700.5671 | 1228585.7247
16 | 2701667.4118 | 1228520.7023 | 2701665.8176 | 1228548.7735
17 | 2701667.4118 | 1228520.7023 | 2701653.4511 | 1228526.4939
18 | 2701726.9301 | 1228469.0623 | 2701724.5145 | 1228462.291 | 2701718.8447 | 1228452.4249
19 | 2701808.2828 | 1228459.0216 | 2701806.3258 | 1228460.3943
20 | 2701778.0448 | 1228591.2712 | 2701799.3219 | 1228591.3735
21 | 2701689.8727 | 1228550.1361 | 2701683.5351 | 1228549.7771
22 | 2701813.0541 | 1228519.8258 | 2701813.0541 | 1228519.8258 | 2701808.6909 | 1228514.8475 | 2701809.8226 | 1228511.1901
23 | 2701813.0541 | 1228519.8258 | 2701823.0923 | 1228523.4991
24 | 2701827.5462 | 1228485.6376 | 2701813.1915 | 1228500.3027 | 2701809.8226 | 1228511.1901
25 | 2701808.2828 | 1228459.0216 | 2701827.5462 | 1228485.6376
26 | 2701640.1253 | 1228532.0221 | 2701653.4511 | 1228526.4939
27 | 2701640.1253 | 1228532.0221 | 2701626.1005 | 1228498.1737
28 | 2701665.8176 | 1228548.7735 | 2701683.5351 | 1228549.7771
29 | 2701619.5282 | 1228482.3114 | 2701626.1005 | 1228498.1737
30 | 2701619.5282 | 1228482.3114 | 2701613.6689 | 1228470.0127
31 | 2701619.5282 | 1228482.3114 | 2701646.1191 | 1228472.1403
32 | 2701611.2391 | 1228464.9126 | 2701613.6689 | 1228470.0127
33 | 2701646.1191 | 1228472.1403 | 2701650.8864 | 1228470.3169
34 | 2701718.8447 | 1228452.4249 | 2701709.9232 | 1228436.9005
35 | 2701699.6552 | 1228419.0329 | 2701709.9232 | 1228436.9005
36 | 2701605.5699 | 1228451.9709 | 2701609.9665 | 1228394.3834
37 | 2701611.2391 | 1228464.9126 | 2701605.5699 | 1228451.9709
38 | 2701672.1463 | 1228462.1849 | 2701673.4439 | 1228461.6886
39 | 2701672.1463 | 1228462.1849 | 2701651.8829 | 1228469.9357
40 | 2701651.8829 | 1228469.9357 | 2701650.8864 | 1228470.3169

## bus_geodata
| x | y | coords
0 | 2701710.3573 | 1228535.6525
1 | 2701715.2237 | 1228517.6285
2 | 2701682.7147 | 1228513.9366
3 | 2701735.7452 | 1228493.7729
4 | 2701704.7613 | 1228590.5143
5 | 2701734.4015 | 1228591.0615
6 | 2701700.2177 | 1228590.3143
7 | 2701698.3591 | 1228506.2216
8 | 2701677.2939 | 1228516.3332
9 | 2701728.3261 | 1228472.9757
10 | 2701771.2998 | 1228478.5588
11 | 2701757.24 | 1228591.1713
12 | 2701700.5671 | 1228585.7247
13 | 2701667.4118 | 1228520.7023
14 | 2701726.9301 | 1228469.0623
15 | 2701806.3258 | 1228460.3943
16 | 2701778.0448 | 1228591.2712
17 | 2701689.8727 | 1228550.1361
18 | 2701813.0541 | 1228519.8258
19 | 2701809.8226 | 1228511.1901
20 | 2701823.0923 | 1228523.4991
21 | 2701827.5462 | 1228485.6376
22 | 2701808.2828 | 1228459.0216
23 | 2701653.4511 | 1228526.4939
24 | 2701640.1253 | 1228532.0221
25 | 2701665.8176 | 1228548.7735
26 | 2701626.1005 | 1228498.1737
27 | 2701683.5351 | 1228549.7771
28 | 2701619.5282 | 1228482.3114
29 | 2701613.6689 | 1228470.0127
30 | 2701646.1191 | 1228472.1403
31 | 2701718.8447 | 1228452.4249
32 | 2701709.9232 | 1228436.9005
33 | 2701699.6552 | 1228419.0329
34 | 2701609.9665 | 1228394.3834
35 | 2701605.5699 | 1228451.9709
36 | 2701611.2391 | 1228464.9126
37 | 2701672.1463 | 1228462.1849
38 | 2701673.4439 | 1228461.6886
39 | 2701651.8829 | 1228469.9357
40 | 2701650.8864 | 1228470.3169
41 | 2701799.3219 | 1228591.3735
42 | 2701715.2237 | 1228517.6285

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.4816 | -0.12257
1 | 0.99796 | -0.038729 | 0 | 0
2 | 0.9953 | -0.089406 | 0 | 0
3 | 0.99422 | -0.11009 | 0 | 0
4 | 0.986 | -0.26869 | 0 | 0
5 | 0.9828 | -0.33088 | 0.031687 | 0.0079415
6 | 0.98649 | -0.25921 | 0 | 0
7 | 0.99524 | -0.090645 | 0.0040373 | 0.0010118
8 | 0.99484 | -0.098363 | 0.014888 | 0.0037313
9 | 0.99362 | -0.12173 | 0.0048915 | 0.0012259
10 | 0.99077 | -0.17627 | 0.0082173 | 0.0020594
11 | 0.98101 | -0.36594 | 0.028562 | 0.0071583
12 | 0.98698 | -0.24961 | 0.06136 | 0.015378
13 | 0.99402 | -0.114 | 0 | 0
14 | 0.99352 | -0.12357 | 0.0069674 | 0.0017462
15 | 0.98754 | -0.23862 | 0.0076365 | 0.0019139
16 | 0.97992 | -0.38719 | 0.026477 | 0.0066358
17 | 0.99095 | -0.17302 | 0.032182 | 0.0080656
18 | 0.98215 | -0.34342 | 0.02542 | 0.0063708
19 | 0.98253 | -0.33613 | 0.042233 | 0.010585
20 | 0.98202 | -0.34597 | 0.013201 | 0.0033084
21 | 0.98491 | -0.28965 | 0 | 0
22 | 0.98736 | -0.24208 | 0 | 0
23 | 0.9931 | -0.13182 | 0.013807 | 0.0034603
24 | 0.9924 | -0.14533 | 0 | 0
25 | 0.99233 | -0.14652 | 0 | 0
26 | 0.99062 | -0.17972 | 0.002958 | 0.00074134
27 | 0.99126 | -0.1671 | 0.05164 | 0.012942
28 | 0.98983 | -0.19498 | 0 | 0
29 | 0.98963 | -0.19882 | 0.0056978 | 0.001428
30 | 0.98894 | -0.21229 | 0.0037664 | 0.00094394
31 | 0.99322 | -0.12948 | 0.0075426 | 0.0018903
32 | 0.99305 | -0.1328 | 0.0074002 | 0.0018547
33 | 0.99299 | -0.13393 | 0.0030908 | 0.00077462
34 | 0.98935 | -0.20431 | 0.0018751 | 0.00046994
35 | 0.98945 | -0.20239 | 0.0082587 | 0.0020698
36 | 0.98958 | -0.19984 | 0 | 0
37 | 0.98842 | -0.22234 | 0.0078369 | 0.0019641
38 | 0.98841 | -0.22259 | 0.0098379 | 0.0024656
39 | 0.98877 | -0.2155 | 0.0059065 | 0.0014803
40 | 0.9888 | -0.21506 | 0.0068038 | 0.0017052
41 | 0.97933 | -0.39873 | 0.029861 | 0.0074839
42 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.47995 | 0.12257 | -0.47905 | -0.122 | 0.00089666 | 0.00057288 | 0.71498 | 0.71498 | 0.71498 | 1 | 0 | 0.99796 | -0.038729 | 49.1055
1 | 0.35101 | 0.089352 | -0.35016 | -0.088807 | 0.00085539 | 0.00054571 | 0.52387 | 0.52387 | 0.52387 | 0.99796 | -0.038729 | 0.9953 | -0.089406 | 35.9803
2 | 0.12803 | 0.032643 | -0.1276 | -0.032363 | 0.0004394 | 0.0002808 | 0.1911 | 0.1911 | 0.1911 | 0.99796 | -0.038729 | 0.99422 | -0.11009 | 52.5011
3 | 0.0040375 | 0.0010118 | -0.0040373 | -0.0010118 | 2.3834e-07 | -7.4147e-08 | 0.0060362 | 0.0060363 | 0.0060363 | 0.9953 | -0.089406 | 0.99524 | -0.090645 | 1.6583
4 | 0.34612 | 0.087795 | -0.34597 | -0.0877 | 0.000149 | 9.5052e-05 | 0.51784 | 0.51784 | 0.51784 | 0.9953 | -0.089406 | 0.99484 | -0.098363 | 35.5657
5 | 0.029918 | 0.0075071 | -0.029902 | -0.0074968 | 1.6605e-05 | 1.0341e-05 | 0.044781 | 0.044781 | 0.044781 | 0.99422 | -0.11009 | 0.99362 | -0.12173 | 12.3024
6 | 0.097677 | 0.024856 | -0.097367 | -0.024657 | 0.00031051 | 0.00019822 | 0.14632 | 0.14632 | 0.14632 | 0.99422 | -0.11009 | 0.99077 | -0.17627 | 40.1988
7 | 0.11715 | 0.029579 | -0.1168 | -0.029357 | 0.00034796 | 0.00022232 | 0.17688 | 0.17688 | 0.17688 | 0.986 | -0.26869 | 0.9828 | -0.33088 | 48.5925
8 | -0.11715 | -0.029579 | 0.1172 | 0.029613 | 5.3205e-05 | 3.3993e-05 | 0.17688 | 0.17688 | 0.17688 | 0.986 | -0.26869 | 0.98649 | -0.25921 | 48.5925
9 | 0.085116 | 0.021415 | -0.084974 | -0.021325 | 0.0001423 | 9.0785e-05 | 0.1289 | 0.1289 | 0.1289 | 0.9828 | -0.33088 | 0.98101 | -0.36594 | 35.4123
10 | -0.1172 | -0.029613 | 0.11726 | 0.029648 | 5.4001e-05 | 3.4502e-05 | 0.17688 | 0.17688 | 0.17688 | 0.98649 | -0.25921 | 0.98698 | -0.24961 | 48.5925
11 | 0.33108 | 0.083968 | -0.33084 | -0.08381 | 0.00024877 | 0.00015865 | 0.49557 | 0.49557 | 0.49557 | 0.99484 | -0.098363 | 0.99402 | -0.114 | 34.0363
12 | 0.02501 | 0.0062709 | -0.025008 | -0.0062695 | 2.1859e-06 | 1.3452e-06 | 0.037455 | 0.037455 | 0.037455 | 0.99362 | -0.12173 | 0.99352 | -0.12357 | 10.29
13 | 0.089149 | 0.022598 | -0.088883 | -0.022428 | 0.00026629 | 0.00016992 | 0.13398 | 0.13398 | 0.13398 | 0.99077 | -0.17627 | 0.98754 | -0.23862 | 36.8084
14 | 0.056412 | 0.014166 | -0.056355 | -0.01413 | 5.7137e-05 | 3.6305e-05 | 0.085577 | 0.085577 | 0.085577 | 0.98101 | -0.36594 | 0.97992 | -0.38719 | 23.5102
15 | -0.17862 | -0.045026 | 0.17928 | 0.045445 | 0.00065721 | 0.00041937 | 0.26939 | 0.26939 | 0.26939 | 0.98698 | -0.24961 | 0.99095 | -0.17302 | 37.0036
16 | 0.26383 | 0.066919 | -0.26342 | -0.066657 | 0.00041181 | 0.0002621 | 0.39523 | 0.39523 | 0.39523 | 0.99402 | -0.114 | 0.99233 | -0.14652 | 27.1448
17 | 0.067006 | 0.016891 | -0.066949 | -0.016855 | 5.7066e-05 | 3.6326e-05 | 0.10034 | 0.10034 | 0.10034 | 0.99402 | -0.114 | 0.9931 | -0.13182 | 27.5662
18 | 0.01804 | 0.0045233 | -0.018035 | -0.0045203 | 5.0837e-06 | 3.0132e-06 | 0.02702 | 0.02702 | 0.02702 | 0.99352 | -0.12357 | 0.99322 | -0.12948 | 7.4231
19 | 0.081247 | 0.020514 | -0.081233 | -0.020506 | 1.3447e-05 | 8.5752e-06 | 0.12248 | 0.12248 | 0.12248 | 0.98754 | -0.23862 | 0.98736 | -0.24208 | 33.6473
20 | 0.029878 | 0.0074941 | -0.029861 | -0.0074839 | 1.6425e-05 | 1.0244e-05 | 0.045371 | 0.045371 | 0.045371 | 0.97992 | -0.38719 | 0.97933 | -0.39873 | 12.4647
21 | -0.21146 | -0.053511 | 0.21152 | 0.053549 | 6.007e-05 | 3.8117e-05 | 0.31771 | 0.31771 | 0.31771 | 0.99095 | -0.17302 | 0.99126 | -0.1671 | 21.8208
22 | -0.038622 | -0.0096801 | 0.038636 | 0.0096886 | 1.3416e-05 | 8.4537e-06 | 0.058515 | 0.058515 | 0.058515 | 0.98215 | -0.34342 | 0.98253 | -0.33613 | 16.0755
23 | 0.013202 | 0.0033093 | -0.013201 | -0.0033084 | 1.6038e-06 | 8.9117e-07 | 0.020003 | 0.020003 | 0.020003 | 0.98215 | -0.34342 | 0.98202 | -0.34597 | 5.4952
24 | -0.080869 | -0.020273 | 0.081048 | 0.020388 | 0.00017954 | 0.0001145 | 0.12248 | 0.12248 | 0.12248 | 0.98253 | -0.33613 | 0.98491 | -0.28965 | 33.6473
25 | -0.081048 | -0.020388 | 0.081233 | 0.020506 | 0.00018464 | 0.00011775 | 0.12248 | 0.12248 | 0.12248 | 0.98491 | -0.28965 | 0.98736 | -0.24208 | 33.6473
26 | 0.053142 | 0.013394 | -0.053108 | -0.013373 | 3.4325e-05 | 2.1782e-05 | 0.079653 | 0.079653 | 0.079653 | 0.9931 | -0.13182 | 0.9924 | -0.14533 | 21.8828
27 | 0.053108 | 0.013373 | -0.053021 | -0.013317 | 8.7173e-05 | 5.5318e-05 | 0.079653 | 0.079654 | 0.079654 | 0.9924 | -0.14533 | 0.99062 | -0.17972 | 21.8828
28 | 0.26342 | 0.066657 | -0.26316 | -0.066491 | 0.00025988 | 0.0001654 | 0.39523 | 0.39523 | 0.39523 | 0.99233 | -0.14652 | 0.99126 | -0.1671 | 27.1448
29 | 0.050063 | 0.012576 | -0.050027 | -0.012553 | 3.6421e-05 | 2.3089e-05 | 0.07521 | 0.07521 | 0.07521 | 0.99062 | -0.17972 | 0.98983 | -0.19498 | 20.6622
30 | 0.015836 | 0.0039697 | -0.015834 | -0.003968 | 2.8955e-06 | 1.6781e-06 | 0.023807 | 0.023807 | 0.023807 | 0.98983 | -0.19498 | 0.98963 | -0.19882 | 6.5405
31 | 0.03419 | 0.0085831 | -0.034162 | -0.0085654 | 2.821e-05 | 1.7689e-05 | 0.051403 | 0.051403 | 0.051403 | 0.98983 | -0.19498 | 0.98894 | -0.21229 | 14.1218
32 | 0.010136 | 0.00254 | -0.010135 | -0.0025397 | 4.9204e-07 | 2.4232e-07 | 0.01524 | 0.01524 | 0.01524 | 0.98963 | -0.19882 | 0.98958 | -0.19984 | 4.1868
33 | 0.030396 | 0.0076215 | -0.030392 | -0.007619 | 4.0038e-06 | 2.4969e-06 | 0.045736 | 0.045736 | 0.045736 | 0.98894 | -0.21229 | 0.9888 | -0.21506 | 12.5649
34 | 0.010493 | 0.00263 | -0.010491 | -0.0026291 | 1.6593e-06 | 8.3028e-07 | 0.01572 | 0.01572 | 0.01572 | 0.99322 | -0.12948 | 0.99305 | -0.1328 | 4.3187
35 | 0.0030909 | 0.00077446 | -0.0030908 | -0.00077462 | 1.6577e-07 | -1.605e-07 | 0.0046315 | 0.0046316 | 0.0046316 | 0.99305 | -0.1328 | 0.99299 | -0.13393 | 1.2724
36 | -0.0018751 | -0.00046994 | 0.0018753 | 0.00046931 | 1.7224e-07 | -6.3149e-07 | 0.0028202 | 0.0028199 | 0.0028202 | 0.98935 | -0.20431 | 0.98945 | -0.20239 | 0.77478
37 | -0.010134 | -0.0025391 | 0.010135 | 0.0025397 | 1.2306e-06 | 6.0608e-07 | 0.01524 | 0.01524 | 0.01524 | 0.98945 | -0.20239 | 0.98958 | -0.19984 | 4.1868
38 | 0.009838 | 0.0024657 | -0.0098379 | -0.0024656 | 1.1428e-07 | 5.5332e-08 | 0.014811 | 0.014811 | 0.014811 | 0.98842 | -0.22234 | 0.98841 | -0.22259 | 4.0689
39 | -0.017675 | -0.0044298 | 0.017681 | 0.0044332 | 5.7602e-06 | 3.4084e-06 | 0.026609 | 0.026609 | 0.026609 | 0.98842 | -0.22234 | 0.98877 | -0.2155 | 7.3101
40 | -0.023587 | -0.0059135 | 0.023588 | 0.0059138 | 5.0414e-07 | 3.0897e-07 | 0.035497 | 0.035497 | 0.035497 | 0.98877 | -0.2155 | 0.9888 | -0.21506 | 9.752

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52413 | 0.13323

## res_load
| p_mw | q_mvar
0 | 0.042535 | 0.01066
1 | 0.031687 | 0.0079415
2 | 0.0040373 | 0.0010118
3 | 0.014888 | 0.0037313
4 | 0.0048915 | 0.0012259
5 | 0.0082173 | 0.0020594
6 | 0.028562 | 0.0071583
7 | 0.06136 | 0.015378
8 | 0.0069674 | 0.0017462
9 | 0.0076365 | 0.0019139
10 | 0.026477 | 0.0066358
11 | 0.032182 | 0.0080656
12 | 0.02542 | 0.0063708
13 | 0.042233 | 0.010585
14 | 0.013201 | 0.0033084
15 | 0.013807 | 0.0034603
16 | 0.002958 | 0.00074134
17 | 0.05164 | 0.012942
18 | 0.0056978 | 0.001428
19 | 0.0037664 | 0.00094394
20 | 0.0075426 | 0.0018903
21 | 0.0074002 | 0.0018547
22 | 0.0030908 | 0.00077462
23 | 0.0018751 | 0.00046994
24 | 0.0082587 | 0.0020698
25 | 0.0078369 | 0.0019641
26 | 0.0098379 | 0.0024656
27 | 0.0059065 | 0.0014803
28 | 0.0068038 | 0.0017052
29 | 0.029861 | 0.0074839

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1