## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1322-28_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1322-28_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1322-28_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1322-28_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1322-28_0_6_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_1322-28_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1322-28_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1322-28_0_6_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_1322-28_0_6_node_40 | 0.4 | n |  | TRUE
9 | bus_LV_1322-28_0_6_node_60 | 0.4 | n |  | TRUE
10 | bus_LV_1322-28_0_6_node_57 | 0.4 | n |  | TRUE
11 | bus_LV_1322-28_0_6_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1322-28_0_6_node_61 | 0.4 | n |  | TRUE
13 | bus_LV_1322-28_0_6_node_39 | 0.4 | n |  | TRUE
14 | bus_LV_1322-28_0_6_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1322-28_0_6_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1322-28_0_6_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1322-28_0_6_node_28 | 0.4 | n |  | TRUE
18 | bus_LV_1322-28_0_6_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_1322-28_0_6_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_1322-28_0_6_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1322-28_0_6_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1322-28_0_6_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1322-28_0_6_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1322-28_0_6_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1322-28_0_6_node_58 | 0.4 | n |  | TRUE
26 | bus_LV_1322-28_0_6_node_35 | 0.4 | n |  | TRUE
27 | bus_LV_1322-28_0_6_node_38 | 0.4 | n |  | TRUE
28 | bus_LV_1322-28_0_6_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_1322-28_0_6_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_1322-28_0_6_node_59 | 0.4 | n |  | TRUE
31 | bus_LV_1322-28_0_6_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_1322-28_0_6_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_1322-28_0_6_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_1322-28_0_6_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_1322-28_0_6_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_1322-28_0_6_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_1322-28_0_6_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_1322-28_0_6_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_1322-28_0_6_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_1322-28_0_6_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_1322-28_0_6_node_45 | 0.4 | n |  | TRUE
42 | bus_LV_1322-28_0_6_node_49 | 0.4 | n |  | TRUE
43 | bus_LV_1322-28_0_6_node_46 | 0.4 | n |  | TRUE
44 | bus_LV_1322-28_0_6_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_1322-28_0_6_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_1322-28_0_6_node_42 | 0.4 | n |  | TRUE
47 | bus_LV_1322-28_0_6_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_1322-28_0_6_node_52 | 0.4 | n |  | TRUE
49 | bus_LV_1322-28_0_6_node_53 | 0.4 | n |  | TRUE
50 | bus_LV_1322-28_0_6_node_50 | 0.4 | n |  | TRUE
51 | bus_LV_1322-28_0_6_node_55 | 0.4 | n |  | TRUE
52 | bus_LV_1322-28_0_6_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_1322-28_0_6_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_1322-28_0_6_node_51 | 0.4 | n |  | TRUE
55 | bus_LV_1322-28_0_6_node_56 | 0.4 | n |  | TRUE
56 | bus_LV_1322-28_0_6_node_54 | 0.4 | n |  | TRUE
57 | bus_MV_16_0_node_191 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1322-28_0_6_load_0 | 0 | 0.030457 | 0.0076333 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1322-28_0_6_load_3 | 2 | 0.020953 | 0.0052512 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1322-28_0_6_load_4 | 3 | 0.026354 | 0.0066049 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1322-28_0_6_load_5 | 5 | 0.015074 | 0.0037779 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1322-28_0_6_load_11 | 7 | 0.028029 | 0.0070247 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1322-28_0_6_load_60 | 9 | 0.0072917 | 0.0018275 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1322-28_0_6_load_57 | 10 | 0.0040927 | 0.0010257 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1322-28_0_6_load_61 | 12 | 0.0054344 | 0.001362 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1322-28_0_6_load_39 | 13 | 0.0074142 | 0.0018582 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1322-28_0_6_load_7 | 14 | 0.021679 | 0.0054334 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1322-28_0_6_load_8 | 15 | 0.025511 | 0.0063936 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1322-28_0_6_load_12 | 16 | 0.03757 | 0.0094159 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1322-28_0_6_load_29 | 18 | 0.0079624 | 0.0019956 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1322-28_0_6_load_27 | 19 | 0.0084165 | 0.0021094 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1322-28_0_6_load_13 | 20 | 0.0045331 | 0.0011361 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1322-28_0_6_load_14 | 21 | 0.0048131 | 0.0012063 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1322-28_0_6_load_15 | 22 | 0.069024 | 0.017299 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1322-28_0_6_load_16 | 23 | 0.02515 | 0.0063032 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1322-28_0_6_load_58 | 25 | 0.007831 | 0.0019626 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1322-28_0_6_load_38 | 27 | 0.0071757 | 0.0017984 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1322-28_0_6_load_33 | 28 | 0.01168 | 0.0029272 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1322-28_0_6_load_59 | 30 | 0.0052151 | 0.001307 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1322-28_0_6_load_19 | 31 | 0.091734 | 0.022991 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1322-28_0_6_load_20 | 32 | 0.02328 | 0.0058345 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1322-28_0_6_load_22 | 34 | 0.0093185 | 0.0023354 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1322-28_0_6_load_23 | 35 | 0.0096528 | 0.0024192 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1322-28_0_6_load_25 | 37 | 0.028925 | 0.0072493 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1322-28_0_6_load_31 | 39 | 0.0048274 | 0.0012099 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1322-28_0_6_load_49 | 42 | 0.0013008 | 0.000326 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1322-28_0_6_load_46 | 43 | 0.0013 | 0.0003258 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1322-28_0_6_load_43 | 44 | 0.0027443 | 0.00068778 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1322-28_0_6_load_41 | 45 | 0.0012399 | 0.00031074 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1322-28_0_6_load_42 | 46 | 0.0013643 | 0.00034192 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1322-28_0_6_load_44 | 47 | 0.0013386 | 0.00033549 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1322-28_0_6_load_52 | 48 | 0.0012524 | 0.00031388 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1322-28_0_6_load_53 | 49 | 0.0015227 | 0.00038162 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1322-28_0_6_load_50 | 50 | 0.0017329 | 0.00043431 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1322-28_0_6_load_55 | 51 | 0.0017329 | 0.00043431 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1322-28_0_6_load_47 | 52 | 0.0013368 | 0.00033503 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1322-28_0_6_load_48 | 53 | 0.0013366 | 0.00033498 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1322-28_0_6_load_51 | 54 | 0.0027956 | 0.00070064 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1322-28_0_6_load_56 | 55 | 0.0020124 | 0.00050435 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1322-28_0_6_load_54 | 56 | 0.0059584 | 0.0014933 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1322-28_0_6_line_0 |  | 0 | 1 | 0.029153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1322-28_0_6_line_1 |  | 1 | 2 | 0.012455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1322-28_0_6_line_2 |  | 1 | 3 | 0.0087672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_1322-28_0_6_line_3 |  | 2 | 7 | 0.0018138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1322-28_0_6_line_4 |  | 3 | 8 | 0.014276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_1322-28_0_6_line_5 |  | 4 | 5 | 0.015476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_1322-28_0_6_line_6 |  | 4 | 6 | 0.014276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_1322-28_0_6_line_7 |  | 5 | 8 | 0.022449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_1322-28_0_6_line_8 |  | 6 | 9 | 0.0010405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1322-28_0_6_line_9 |  | 6 | 10 | 0.01507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_1322-28_0_6_line_10 |  | 7 | 11 | 0.017281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1322-28_0_6_line_11 |  | 9 | 12 | 0.009638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1322-28_0_6_line_12 |  | 10 | 13 | 0.002905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_1322-28_0_6_line_13 |  | 11 | 16 | 0.056937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1322-28_0_6_line_14 |  | 11 | 14 | 0.019881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1322-28_0_6_line_15 |  | 12 | 30 | 0.012118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1322-28_0_6_line_16 |  | 13 | 26 | 0.0094541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1322-28_0_6_line_17 |  | 14 | 15 | 0.0024027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1322-28_0_6_line_18 |  | 17 | 18 | 0.011936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1322-28_0_6_line_19 |  | 17 | 19 | 0.028048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1322-28_0_6_line_20 |  | 18 | 39 | 0.029237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1322-28_0_6_line_21 |  | 19 | 37 | 0.025868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1322-28_0_6_line_22 |  | 20 | 21 | 0.0003186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1322-28_0_6_line_23 |  | 20 | 22 | 0.037206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1322-28_0_6_line_24 |  | 21 | 23 | 0.033174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1322-28_0_6_line_25 |  | 22 | 24 | 0.030353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1322-28_0_6_line_26 |  | 24 | 25 | 0.031136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1322-28_0_6_line_27 |  | 25 | 29 | 0.010318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1322-28_0_6_line_28 |  | 26 | 27 | 0.017659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1322-28_0_6_line_29 |  | 26 | 28 | 0.035782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1322-28_0_6_line_30 |  | 27 | 38 | 0.021306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_1322-28_0_6_line_31 |  | 29 | 30 | 0.012133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1322-28_0_6_line_32 |  | 31 | 32 | 0.0038685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1322-28_0_6_line_33 |  | 31 | 33 | 0.011609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1322-28_0_6_line_34 |  | 33 | 34 | 0.014878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1322-28_0_6_line_35 |  | 33 | 35 | 0.019908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1322-28_0_6_line_36 |  | 34 | 36 | 0.015322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1322-28_0_6_line_37 |  | 36 | 37 | 0.004703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1322-28_0_6_line_38 |  | 36 | 38 | 0.019408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_1322-28_0_6_line_39 |  | 39 | 40 | 0.012635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1322-28_0_6_line_40 |  | 40 | 41 | 0.019264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1322-28_0_6_line_41 |  | 41 | 42 | 0.01039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1322-28_0_6_line_42 |  | 41 | 43 | 0.017656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1322-28_0_6_line_43 |  | 41 | 44 | 0.0099165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1322-28_0_6_line_44 |  | 43 | 52 | 0.017637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1322-28_0_6_line_45 |  | 44 | 45 | 0.0091224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1322-28_0_6_line_46 |  | 45 | 46 | 0.014233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1322-28_0_6_line_47 |  | 46 | 47 | 0.01174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1322-28_0_6_line_48 |  | 47 | 48 | 0.0036505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1322-28_0_6_line_49 |  | 48 | 49 | 0.014908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1322-28_0_6_line_50 |  | 49 | 56 | 0.0057379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1322-28_0_6_line_51 |  | 50 | 51 | 0.012625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1322-28_0_6_line_52 |  | 51 | 54 | 0.033271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1322-28_0_6_line_53 |  | 52 | 53 | 0.024464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1322-28_0_6_line_54 |  | 53 | 54 | 0.04095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1322-28_0_6_line_55 |  | 55 | 56 | 0.047953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1322-28_0_6_trafo_40 | 0.63 MVA 20/0.4 kV | 57 | 8 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2701621.8255 | 1228612.1351 | 2701614.376 | 1228617.0114 | 2701594.1552 | 1228615.9326
1 | 2701621.8255 | 1228612.1351 | 2701634.2026 | 1228613.5276
2 | 2701621.8255 | 1228612.1351 | 2701613.1446 | 1228610.9079
3 | 2701634.2026 | 1228613.5276 | 2701636.0049 | 1228613.7303
4 | 2701599.0093 | 1228608.9097 | 2701613.1446 | 1228610.9079
5 | 2701561.9852 | 1228617.1279 | 2701577.0935 | 1228613.7743
6 | 2701548.0107 | 1228620.2361 | 2701561.9852 | 1228617.1279
7 | 2701599.0093 | 1228608.9097 | 2701577.0935 | 1228613.7743
8 | 2701548.0107 | 1228620.2361 | 2701548.2816 | 1228621.2407
9 | 2701548.0107 | 1228620.2361 | 2701544.0914 | 1228605.6843
10 | 2701653.1774 | 1228615.6623 | 2701636.0049 | 1228613.7303
11 | 2701548.2816 | 1228621.2407 | 2701550.7908 | 1228630.5463
12 | 2701543.3359 | 1228602.8792 | 2701544.0914 | 1228605.6843
13 | 2701653.1774 | 1228615.6623 | 2701658.6859 | 1228558.9925
14 | 2701653.1774 | 1228615.6623 | 2701672.9056 | 1228618.119
15 | 2701553.9457 | 1228642.2461 | 2701550.7908 | 1228630.5463
16 | 2701540.8773 | 1228593.7504 | 2701543.3359 | 1228602.8792
17 | 2701672.9056 | 1228618.119 | 2701675.2898 | 1228618.4159
18 | 2701640.1253 | 1228532.0221 | 2701635.5563 | 1228520.9951
19 | 2701640.1253 | 1228532.0221 | 2701615.269 | 1228545.0157
20 | 2701624.3648 | 1228493.9845 | 2701635.5563 | 1228520.9951
21 | 2701593.6018 | 1228559.072 | 2701609.2707 | 1228548.1513 | 2701615.269 | 1228545.0157
22 | 2701635.3472 | 1228700.5056 | 2701635.0301 | 1228700.4752
23 | 2701635.0301 | 1228700.4752 | 2701597.9943 | 1228696.9184
24 | 2701635.3472 | 1228700.5056 | 2701668.3688 | 1228703.6769
25 | 2701567.7798 | 1228694.0168 | 2701597.9943 | 1228696.9184
26 | 2701567.7798 | 1228694.0168 | 2701559.7616 | 1228663.9306
27 | 2701557.1045 | 1228653.9606 | 2701559.7616 | 1228663.9306
28 | 2701540.8773 | 1228593.7504 | 2701555.7063 | 1228584.1622
29 | 2701540.8773 | 1228593.7504 | 2701534.351 | 1228574.3025 | 2701529.0476 | 1228559.9846
30 | 2701573.5983 | 1228572.5935 | 2701555.7063 | 1228584.1622
31 | 2701557.1045 | 1228653.9606 | 2701553.9457 | 1228642.2461
32 | 2701566.3931 | 1228527.5018 | 2701564.9253 | 1228523.9226
33 | 2701570.7977 | 1228538.2426 | 2701566.3931 | 1228527.5018
34 | 2701570.7977 | 1228538.2426 | 2701580.1312 | 1228549.8288
35 | 2701588.1316 | 1228528.3646 | 2701570.7977 | 1228538.2426
36 | 2701589.7435 | 1228561.7612 | 2701580.1312 | 1228549.8288
37 | 2701589.7435 | 1228561.7612 | 2701593.6018 | 1228559.072
38 | 2701573.5983 | 1228572.5935 | 2701582.02 | 1228567.1444 | 2701589.7435 | 1228561.7612
39 | 2701619.5282 | 1228482.3114 | 2701624.3648 | 1228493.9845
40 | 2701611.2391 | 1228464.9126 | 2701619.5282 | 1228482.3114
41 | 2701611.2391 | 1228464.9126 | 2701607.0699 | 1228455.3953
42 | 2701611.2391 | 1228464.9126 | 2701594.8492 | 1228471.4774
43 | 2701611.2391 | 1228464.9126 | 2701602.0336 | 1228468.5998
44 | 2701594.8492 | 1228471.4774 | 2701578.4763 | 1228478.0353
45 | 2701593.5652 | 1228471.9916 | 2701602.0336 | 1228468.5998
46 | 2701593.5652 | 1228471.9916 | 2701580.3528 | 1228477.2837
47 | 2701580.3528 | 1228477.2837 | 2701569.4548 | 1228481.6487
48 | 2701569.4548 | 1228481.6487 | 2701566.066 | 1228483.006
49 | 2701566.066 | 1228483.006 | 2701552.2267 | 1228488.5492
50 | 2701552.2267 | 1228488.5492 | 2701546.9001 | 1228490.6827
51 | 2701570.2323 | 1228459.5409 | 2701581.9277 | 1228454.7852
52 | 2701539.4121 | 1228472.0733 | 2701570.2323 | 1228459.5409
53 | 2701578.4763 | 1228478.0353 | 2701555.7666 | 1228487.1313
54 | 2701555.7666 | 1228487.1313 | 2701543.3715 | 1228492.096 | 2701538.9893 | 1228490.8758 | 2701533.4743 | 1228477.4385 | 2701535.433 | 1228473.6914 | 2701539.4121 | 1228472.0733
55 | 2701546.9001 | 1228490.6827 | 2701543.3715 | 1228492.096 | 2701538.9893 | 1228490.8758 | 2701533.4743 | 1228477.4385 | 2701535.433 | 1228473.6914 | 2701554.7467 | 1228465.8378

## bus_geodata
| x | y | coords
0 | 2701594.1552 | 1228615.9326
1 | 2701621.8255 | 1228612.1351
2 | 2701634.2026 | 1228613.5276
3 | 2701613.1446 | 1228610.9079
4 | 2701561.9852 | 1228617.1279
5 | 2701577.0935 | 1228613.7743
6 | 2701548.0107 | 1228620.2361
7 | 2701636.0049 | 1228613.7303
8 | 2701599.0093 | 1228608.9097
9 | 2701548.2816 | 1228621.2407
10 | 2701544.0914 | 1228605.6843
11 | 2701653.1774 | 1228615.6623
12 | 2701550.7908 | 1228630.5463
13 | 2701543.3359 | 1228602.8792
14 | 2701672.9056 | 1228618.119
15 | 2701675.2898 | 1228618.4159
16 | 2701658.6859 | 1228558.9925
17 | 2701640.1253 | 1228532.0221
18 | 2701635.5563 | 1228520.9951
19 | 2701615.269 | 1228545.0157
20 | 2701635.0301 | 1228700.4752
21 | 2701635.3472 | 1228700.5056
22 | 2701597.9943 | 1228696.9184
23 | 2701668.3688 | 1228703.6769
24 | 2701567.7798 | 1228694.0168
25 | 2701559.7616 | 1228663.9306
26 | 2701540.8773 | 1228593.7504
27 | 2701555.7063 | 1228584.1622
28 | 2701529.0476 | 1228559.9846
29 | 2701557.1045 | 1228653.9606
30 | 2701553.9457 | 1228642.2461
31 | 2701566.3931 | 1228527.5018
32 | 2701564.9253 | 1228523.9226
33 | 2701570.7977 | 1228538.2426
34 | 2701580.1312 | 1228549.8288
35 | 2701588.1316 | 1228528.3646
36 | 2701589.7435 | 1228561.7612
37 | 2701593.6018 | 1228559.072
38 | 2701573.5983 | 1228572.5935
39 | 2701624.3648 | 1228493.9845
40 | 2701619.5282 | 1228482.3114
41 | 2701611.2391 | 1228464.9126
42 | 2701607.0699 | 1228455.3953
43 | 2701594.8492 | 1228471.4774
44 | 2701602.0336 | 1228468.5997
45 | 2701593.5652 | 1228471.9917
46 | 2701580.3528 | 1228477.2837
47 | 2701569.4548 | 1228481.6487
48 | 2701566.066 | 1228483.006
49 | 2701552.2267 | 1228488.5492
50 | 2701581.9277 | 1228454.7852
51 | 2701570.2323 | 1228459.5409
52 | 2701578.4763 | 1228478.0353
53 | 2701555.7666 | 1228487.1313
54 | 2701539.4121 | 1228472.0733
55 | 2701554.7467 | 1228465.8378
56 | 2701546.9001 | 1228490.6827
57 | 2701621.8255 | 1228612.1351

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99771 | -0.043927 | 0.030457 | 0.0076333
1 | 0.99852 | -0.028393 | 0 | 0
2 | 0.997 | -0.057557 | 0.020953 | 0.0052512
3 | 0.99917 | -0.015818 | 0.026354 | 0.0066049
4 | 0.99555 | -0.084478 | 0 | 0
5 | 0.99732 | -0.050721 | 0.015074 | 0.0037779
6 | 0.99392 | -0.11572 | 0 | 0
7 | 0.99681 | -0.061145 | 0.028029 | 0.0070247
8 | 1 | 0 | -0.58612 | -0.14884
9 | 0.99379 | -0.1181 | 0.0072917 | 0.0018275
10 | 0.99279 | -0.13733 | 0.0040927 | 0.0010257
11 | 0.99548 | -0.086873 | 0 | 0
12 | 0.99271 | -0.13887 | 0.0054344 | 0.001362
13 | 0.99258 | -0.14143 | 0.0074142 | 0.0018582
14 | 0.99462 | -0.10339 | 0.021679 | 0.0054334
15 | 0.99457 | -0.10447 | 0.025511 | 0.0063936
16 | 0.99353 | -0.12457 | 0.03757 | 0.0094159
17 | 0.98478 | -0.29212 | 0 | 0
18 | 0.98432 | -0.30108 | 0.0079624 | 0.0019956
19 | 0.98586 | -0.27108 | 0.0084165 | 0.0021094
20 | 0.98204 | -0.34558 | 0.0045331 | 0.0011361
21 | 0.98203 | -0.34575 | 0.0048131 | 0.0012063
22 | 0.98322 | -0.32241 | 0.069024 | 0.017299
23 | 0.98126 | -0.36084 | 0.02515 | 0.0063032
24 | 0.98612 | -0.26593 | 0 | 0
25 | 0.9891 | -0.20833 | 0.007831 | 0.0019626
26 | 0.9919 | -0.15437 | 0 | 0
27 | 0.99071 | -0.17737 | 0.0071757 | 0.0017984
28 | 0.99152 | -0.16178 | 0.01168 | 0.0029272
29 | 0.99016 | -0.18788 | 0 | 0
30 | 0.9914 | -0.16389 | 0.0052151 | 0.001307
31 | 0.98256 | -0.33537 | 0.091734 | 0.022991
32 | 0.98248 | -0.33699 | 0.02328 | 0.0058345
33 | 0.9838 | -0.31129 | 0 | 0
34 | 0.98551 | -0.27795 | 0.0093185 | 0.0023354
35 | 0.98362 | -0.31475 | 0.0096528 | 0.0024192
36 | 0.9874 | -0.24118 | 0 | 0
37 | 0.98706 | -0.24783 | 0.028925 | 0.0072493
38 | 0.98931 | -0.20428 | 0 | 0
39 | 0.98341 | -0.31888 | 0.0048274 | 0.0012099
40 | 0.98307 | -0.32548 | 0 | 0
41 | 0.98256 | -0.33555 | 0 | 0
42 | 0.98254 | -0.3358 | 0.0013008 | 0.000326
43 | 0.98239 | -0.33882 | 0.0013 | 0.0003258
44 | 0.9824 | -0.33867 | 0.0027443 | 0.00068778
45 | 0.98227 | -0.34109 | 0.0012399 | 0.00031074
46 | 0.9821 | -0.34455 | 0.0013643 | 0.00034192
47 | 0.98197 | -0.34712 | 0.0013386 | 0.00033549
48 | 0.98193 | -0.34783 | 0.0012524 | 0.00031388
49 | 0.9818 | -0.35039 | 0.0015227 | 0.00038162
50 | 0.98171 | -0.35214 | 0.0017329 | 0.00043431
51 | 0.98173 | -0.35175 | 0.0017329 | 0.00043431
52 | 0.98224 | -0.34166 | 0.0013368 | 0.00033503
53 | 0.98207 | -0.34502 | 0.0013366 | 0.00033498
54 | 0.98184 | -0.34966 | 0.0027956 | 0.00070064
55 | 0.98167 | -0.35296 | 0.0020124 | 0.00050435
56 | 0.98176 | -0.35121 | 0.0059584 | 0.0014933
57 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.030457 | -0.0076333 | 0.03048 | 0.0076474 | 2.2558e-05 | 1.4056e-05 | 0.045425 | 0.045425 | 0.045425 | 0.99771 | -0.043927 | 0.99852 | -0.028393 | 12.4794
1 | 0.13416 | 0.033784 | -0.13397 | -0.033665 | 0.00018679 | 0.00011938 | 0.19998 | 0.19998 | 0.19998 | 0.99852 | -0.028393 | 0.997 | -0.057557 | 54.9401
2 | -0.16464 | -0.041431 | 0.16474 | 0.041494 | 9.9e-05 | 6.3131e-05 | 0.24541 | 0.24541 | 0.24541 | 0.99852 | -0.028393 | 0.99917 | -0.015818 | 33.7097
3 | 0.11302 | 0.028413 | -0.113 | -0.028401 | 1.9359e-05 | 1.2366e-05 | 0.16871 | 0.16871 | 0.16871 | 0.997 | -0.057557 | 0.99681 | -0.061145 | 46.349
4 | -0.19109 | -0.048099 | 0.19124 | 0.048191 | 0.00014459 | 9.1978e-05 | 0.28465 | 0.28465 | 0.28465 | 0.99917 | -0.015818 | 1 | 0 | 26.0672
5 | -0.37658 | -0.095862 | 0.37719 | 0.096255 | 0.00061402 | 0.00039237 | 0.56339 | 0.56339 | 0.56339 | 0.99555 | -0.084478 | 0.99732 | -0.050721 | 51.5922
6 | 0.37658 | 0.095862 | -0.37601 | -0.095501 | 0.00056641 | 0.00036195 | 0.56339 | 0.56339 | 0.56339 | 0.99555 | -0.084478 | 0.99392 | -0.11572 | 51.5922
7 | -0.39227 | -0.10003 | 0.39323 | 0.10065 | 0.00096322 | 0.00061558 | 0.58588 | 0.58588 | 0.58588 | 0.99732 | -0.050721 | 1 | 0 | 53.6517
8 | 0.13043 | 0.033132 | -0.13042 | -0.033123 | 1.4903e-05 | 9.5245e-06 | 0.19543 | 0.19543 | 0.19543 | 0.99392 | -0.11572 | 0.99379 | -0.1181 | 53.6904
9 | 0.24558 | 0.062368 | -0.24532 | -0.062206 | 0.00025505 | 0.00016264 | 0.36795 | 0.36795 | 0.36795 | 0.99392 | -0.11572 | 0.99279 | -0.13733 | 33.6954
10 | 0.08497 | 0.021376 | -0.084866 | -0.02131 | 0.00010431 | 6.6531e-05 | 0.12687 | 0.12687 | 0.12687 | 0.99681 | -0.061145 | 0.99548 | -0.086873 | 34.8542
11 | 0.12313 | 0.031295 | -0.123 | -0.031216 | 0.00012305 | 7.8627e-05 | 0.18452 | 0.18452 | 0.18452 | 0.99379 | -0.1181 | 0.99271 | -0.13887 | 50.691
12 | 0.24123 | 0.06118 | -0.24118 | -0.06115 | 4.7538e-05 | 3.0312e-05 | 0.36182 | 0.36182 | 0.36182 | 0.99279 | -0.13733 | 0.99258 | -0.14143 | 33.1337
13 | 0.037637 | 0.0094584 | -0.03757 | -0.0094159 | 6.7602e-05 | 4.2526e-05 | 0.056268 | 0.056269 | 0.056269 | 0.99548 | -0.086873 | 0.99353 | -0.12457 | 15.4584
14 | 0.047228 | 0.011851 | -0.047191 | -0.011828 | 3.7161e-05 | 2.3525e-05 | 0.070601 | 0.070601 | 0.070601 | 0.99548 | -0.086873 | 0.99462 | -0.10339 | 19.3959
15 | 0.11757 | 0.029854 | -0.11743 | -0.029764 | 0.00014135 | 9.0308e-05 | 0.17637 | 0.17637 | 0.17637 | 0.99271 | -0.13887 | 0.9914 | -0.16389 | 48.4531
16 | 0.23377 | 0.059292 | -0.23362 | -0.059199 | 0.00014535 | 9.2658e-05 | 0.3507 | 0.3507 | 0.3507 | 0.99258 | -0.14143 | 0.9919 | -0.15437 | 32.1158
17 | 0.025512 | 0.0063944 | -0.025511 | -0.0063936 | 1.3125e-06 | 8.0884e-07 | 0.038168 | 0.038168 | 0.038168 | 0.99462 | -0.10339 | 0.99457 | -0.10447 | 10.4856
18 | 0.041844 | 0.010516 | -0.041826 | -0.010505 | 1.7899e-05 | 1.1304e-05 | 0.063237 | 0.063237 | 0.063237 | 0.98478 | -0.29212 | 0.98432 | -0.30108 | 17.3727
19 | -0.041844 | -0.010516 | 0.041886 | 0.010542 | 4.2059e-05 | 2.6561e-05 | 0.063237 | 0.063236 | 0.063237 | 0.98478 | -0.29212 | 0.98586 | -0.27108 | 17.3727
20 | 0.033863 | 0.008509 | -0.033835 | -0.008491 | 2.8741e-05 | 1.8023e-05 | 0.0512 | 0.0512 | 0.0512 | 0.98432 | -0.30108 | 0.98341 | -0.31888 | 14.0659
21 | -0.050302 | -0.012652 | 0.050358 | 0.012687 | 5.5941e-05 | 3.5472e-05 | 0.07594 | 0.07594 | 0.07594 | 0.98586 | -0.27108 | 0.98706 | -0.24783 | 20.8626
22 | 0.029981 | 0.0075208 | -0.029981 | -0.0075206 | 2.466e-07 | 1.5379e-07 | 0.045431 | 0.045431 | 0.045431 | 0.98204 | -0.34558 | 0.98203 | -0.34575 | 12.4811
23 | -0.034515 | -0.0086569 | 0.034553 | 0.0086808 | 3.8164e-05 | 2.3953e-05 | 0.0523 | 0.0523 | 0.0523 | 0.98204 | -0.34558 | 0.98322 | -0.32241 | 14.3681
24 | 0.025168 | 0.0063144 | -0.02515 | -0.0063032 | 1.8095e-05 | 1.1161e-05 | 0.038138 | 0.038138 | 0.038138 | 0.98203 | -0.34575 | 0.98126 | -0.36084 | 10.4776
25 | -0.10358 | -0.02598 | 0.10386 | 0.026159 | 0.00027972 | 0.00017863 | 0.15676 | 0.15676 | 0.15676 | 0.98322 | -0.32241 | 0.98612 | -0.26593 | 43.0663
26 | -0.10386 | -0.026159 | 0.10414 | 0.026342 | 0.00028693 | 0.00018324 | 0.15676 | 0.15676 | 0.15676 | 0.98612 | -0.26593 | 0.9891 | -0.20833 | 43.0663
27 | -0.11197 | -0.028304 | 0.11208 | 0.028375 | 0.00010991 | 7.0211e-05 | 0.16854 | 0.16854 | 0.16854 | 0.9891 | -0.20833 | 0.99016 | -0.18788 | 46.3028
28 | 0.22194 | 0.056269 | -0.2217 | -0.056113 | 0.00024503 | 0.00015614 | 0.33318 | 0.33318 | 0.33318 | 0.9919 | -0.15437 | 0.99071 | -0.17737 | 30.5107
29 | 0.011684 | 0.0029294 | -0.01168 | -0.0029272 | 4.1226e-06 | 2.1768e-06 | 0.017528 | 0.017528 | 0.017528 | 0.9919 | -0.15437 | 0.99152 | -0.16178 | 4.8154
30 | 0.21452 | 0.054315 | -0.21424 | -0.054139 | 0.00027683 | 0.00017635 | 0.3224 | 0.3224 | 0.3224 | 0.99071 | -0.17737 | 0.98931 | -0.20428 | 29.5238
31 | -0.11208 | -0.028375 | 0.11221 | 0.028457 | 0.00012924 | 8.256e-05 | 0.16854 | 0.16854 | 0.16854 | 0.99016 | -0.18788 | 0.9914 | -0.16389 | 46.3028
32 | 0.023282 | 0.0058356 | -0.02328 | -0.0058345 | 1.8034e-06 | 1.1052e-06 | 0.035259 | 0.035259 | 0.035259 | 0.98256 | -0.33537 | 0.98248 | -0.33699 | 9.6864
33 | -0.11502 | -0.028826 | 0.11515 | 0.028911 | 0.00013208 | 8.4382e-05 | 0.17418 | 0.17418 | 0.17418 | 0.98256 | -0.33537 | 0.9838 | -0.31129 | 47.8523
34 | -0.1248 | -0.031331 | 0.125 | 0.031458 | 0.00019884 | 0.00012707 | 0.18879 | 0.18879 | 0.18879 | 0.9838 | -0.31129 | 0.98551 | -0.27795 | 51.864
35 | 0.0096544 | 0.00242 | -0.0096528 | -0.0024192 | 1.5919e-06 | 7.661e-07 | 0.014603 | 0.014603 | 0.014603 | 0.9838 | -0.31129 | 0.98362 | -0.31475 | 4.0117
36 | -0.13432 | -0.033793 | 0.13456 | 0.033944 | 0.00023645 | 0.00015113 | 0.20286 | 0.20285 | 0.20286 | 0.98551 | -0.27795 | 0.9874 | -0.24118 | 55.7294
37 | 0.079309 | 0.019953 | -0.079283 | -0.019937 | 2.5204e-05 | 1.607e-05 | 0.11955 | 0.11955 | 0.11955 | 0.9874 | -0.24118 | 0.98706 | -0.24783 | 32.842
38 | -0.21386 | -0.053897 | 0.21424 | 0.054139 | 0.00037824 | 0.00024158 | 0.3224 | 0.3224 | 0.3224 | 0.9874 | -0.24118 | 0.98931 | -0.20428 | 44.2857
39 | 0.029007 | 0.0072811 | -0.028998 | -0.0072755 | 9.1298e-06 | 5.6828e-06 | 0.043895 | 0.043895 | 0.043895 | 0.98341 | -0.31888 | 0.98307 | -0.32548 | 12.0592
40 | 0.028998 | 0.0072755 | -0.028984 | -0.0072668 | 1.3919e-05 | 8.6642e-06 | 0.043895 | 0.043896 | 0.043896 | 0.98307 | -0.32548 | 0.98256 | -0.33555 | 12.0592
41 | 0.0013008 | 0.00032588 | -0.0013008 | -0.000326 | 1.512e-08 | -1.2192e-07 | 0.0019699 | 0.0019699 | 0.0019699 | 0.98256 | -0.33555 | 0.98254 | -0.3358 | 0.54119
42 | 0.010241 | 0.0025669 | -0.010239 | -0.0025661 | 1.5925e-06 | 7.9561e-07 | 0.015509 | 0.015509 | 0.015509 | 0.98256 | -0.33555 | 0.98239 | -0.33882 | 4.2607
43 | 0.017443 | 0.004374 | -0.01744 | -0.0043725 | 2.5951e-06 | 1.5353e-06 | 0.026417 | 0.026417 | 0.026417 | 0.98256 | -0.33555 | 0.9824 | -0.33867 | 7.2574
44 | 0.008939 | 0.0022403 | -0.0089378 | -0.0022398 | 1.2125e-06 | 5.5274e-07 | 0.01354 | 0.01354 | 0.01354 | 0.98239 | -0.33882 | 0.98224 | -0.34166 | 3.7198
45 | 0.014696 | 0.0036847 | -0.014694 | -0.0036837 | 1.6951e-06 | 9.6939e-07 | 0.02226 | 0.02226 | 0.02226 | 0.9824 | -0.33867 | 0.98227 | -0.34109 | 6.1155
46 | 0.013454 | 0.003373 | -0.013452 | -0.0033717 | 2.2173e-06 | 1.2389e-06 | 0.020382 | 0.020382 | 0.020382 | 0.98227 | -0.34109 | 0.9821 | -0.34455 | 5.5995
47 | 0.012088 | 0.0030298 | -0.012086 | -0.003029 | 1.4767e-06 | 7.9658e-07 | 0.018315 | 0.018315 | 0.018315 | 0.9821 | -0.34455 | 0.98197 | -0.34712 | 5.0316
48 | 0.010748 | 0.0026935 | -0.010747 | -0.0026933 | 3.6312e-07 | 1.8622e-07 | 0.016287 | 0.016287 | 0.016287 | 0.98197 | -0.34712 | 0.98193 | -0.34783 | 4.4743
49 | 0.0094951 | 0.0023795 | -0.0094939 | -0.0023789 | 1.1575e-06 | 5.5222e-07 | 0.014389 | 0.014389 | 0.014389 | 0.98193 | -0.34783 | 0.9818 | -0.35039 | 3.953
50 | 0.0079712 | 0.0019973 | -0.0079709 | -0.0019972 | 3.1405e-07 | 1.2843e-07 | 0.012081 | 0.012081 | 0.012081 | 0.9818 | -0.35039 | 0.98176 | -0.35121 | 3.319
51 | -0.0017329 | -0.00043431 | 0.001733 | 0.00043418 | 3.2665e-08 | -1.3873e-07 | 0.0026267 | 0.0026266 | 0.0026267 | 0.98171 | -0.35214 | 0.98173 | -0.35175 | 0.72162
52 | -0.0034659 | -0.00086849 | 0.0034662 | 0.00086829 | 3.443e-07 | -2.0038e-07 | 0.0052532 | 0.0052531 | 0.0052532 | 0.98173 | -0.35175 | 0.98184 | -0.34966 | 1.4432
53 | 0.007601 | 0.0019047 | -0.0075998 | -0.0019043 | 1.2164e-06 | 4.6889e-07 | 0.011515 | 0.011515 | 0.011515 | 0.98224 | -0.34166 | 0.98207 | -0.34502 | 3.1634
54 | 0.0062632 | 0.0015693 | -0.0062618 | -0.0015689 | 1.3829e-06 | 3.6706e-07 | 0.0094898 | 0.00949 | 0.00949 | 0.98207 | -0.34502 | 0.98184 | -0.34966 | 2.6071
55 | -0.0020124 | -0.00050435 | 0.0020125 | 0.00050385 | 1.6731e-07 | -4.9923e-07 | 0.0030504 | 0.0030501 | 0.0030504 | 0.98167 | -0.35296 | 0.98176 | -0.35121 | 0.83801

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58612 | 0.14884

## res_load
| p_mw | q_mvar
0 | 0.030457 | 0.0076333
1 | 0.020953 | 0.0052512
2 | 0.026354 | 0.0066049
3 | 0.015074 | 0.0037779
4 | 0.028029 | 0.0070247
5 | 0.0072917 | 0.0018275
6 | 0.0040927 | 0.0010257
7 | 0.0054344 | 0.001362
8 | 0.0074142 | 0.0018582
9 | 0.021679 | 0.0054334
10 | 0.025511 | 0.0063936
11 | 0.03757 | 0.0094159
12 | 0.0079624 | 0.0019956
13 | 0.0084165 | 0.0021094
14 | 0.0045331 | 0.0011361
15 | 0.0048131 | 0.0012063
16 | 0.069024 | 0.017299
17 | 0.02515 | 0.0063032
18 | 0.007831 | 0.0019626
19 | 0.0071757 | 0.0017984
20 | 0.01168 | 0.0029272
21 | 0.0052151 | 0.001307
22 | 0.091734 | 0.022991
23 | 0.02328 | 0.0058345
24 | 0.0093185 | 0.0023354
25 | 0.0096528 | 0.0024192
26 | 0.028925 | 0.0072493
27 | 0.0048274 | 0.0012099
28 | 0.0013008 | 0.000326
29 | 0.0013 | 0.0003258
30 | 0.0027443 | 0.00068778
31 | 0.0012399 | 0.00031074
32 | 0.0013643 | 0.00034192
33 | 0.0013386 | 0.00033549
34 | 0.0012524 | 0.00031388
35 | 0.0015227 | 0.00038162
36 | 0.0017329 | 0.00043431
37 | 0.0017329 | 0.00043431
38 | 0.0013368 | 0.00033503
39 | 0.0013366 | 0.00033498
40 | 0.0027956 | 0.00070064
41 | 0.0020124 | 0.00050435
42 | 0.0059584 | 0.0014933

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1