## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1322-30_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1322-30_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1322-30_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1322-30_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1322-30_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1322-30_0_5_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_1322-30_0_5_node_102 | 0.4 | n |  | TRUE
7 | bus_LV_1322-30_0_5_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_1322-30_0_5_node_103 | 0.4 | n |  | TRUE
9 | bus_LV_1322-30_0_5_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1322-30_0_5_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1322-30_0_5_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1322-30_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1322-30_0_5_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1322-30_0_5_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_1322-30_0_5_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_1322-30_0_5_node_69 | 0.4 | n |  | TRUE
17 | bus_LV_1322-30_0_5_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_1322-30_0_5_node_118 | 0.4 | n |  | TRUE
19 | bus_LV_1322-30_0_5_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1322-30_0_5_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1322-30_0_5_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1322-30_0_5_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1322-30_0_5_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1322-30_0_5_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1322-30_0_5_node_97 | 0.4 | n |  | TRUE
26 | bus_LV_1322-30_0_5_node_106 | 0.4 | n |  | TRUE
27 | bus_LV_1322-30_0_5_node_96 | 0.4 | n |  | TRUE
28 | bus_LV_1322-30_0_5_node_105 | 0.4 | n |  | TRUE
29 | bus_LV_1322-30_0_5_node_68 | 0.4 | n |  | TRUE
30 | bus_LV_1322-30_0_5_node_119 | 0.4 | n |  | TRUE
31 | bus_LV_1322-30_0_5_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_1322-30_0_5_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_1322-30_0_5_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_1322-30_0_5_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_1322-30_0_5_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_1322-30_0_5_node_59 | 0.4 | n |  | TRUE
37 | bus_LV_1322-30_0_5_node_60 | 0.4 | n |  | TRUE
38 | bus_LV_1322-30_0_5_node_38 | 0.4 | n |  | TRUE
39 | bus_LV_1322-30_0_5_node_94 | 0.4 | n |  | TRUE
40 | bus_LV_1322-30_0_5_node_98 | 0.4 | n |  | TRUE
41 | bus_LV_1322-30_0_5_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_1322-30_0_5_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_1322-30_0_5_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_1322-30_0_5_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_1322-30_0_5_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_1322-30_0_5_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_1322-30_0_5_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_1322-30_0_5_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_1322-30_0_5_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_1322-30_0_5_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_1322-30_0_5_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_1322-30_0_5_node_42 | 0.4 | n |  | TRUE
53 | bus_LV_1322-30_0_5_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_1322-30_0_5_node_35 | 0.4 | n |  | TRUE
55 | bus_LV_1322-30_0_5_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_1322-30_0_5_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_1322-30_0_5_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_1322-30_0_5_node_70 | 0.4 | n |  | TRUE
59 | bus_LV_1322-30_0_5_node_71 | 0.4 | n |  | TRUE
60 | bus_LV_1322-30_0_5_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_1322-30_0_5_node_46 | 0.4 | n |  | TRUE
62 | bus_LV_1322-30_0_5_node_47 | 0.4 | n |  | TRUE
63 | bus_LV_1322-30_0_5_node_48 | 0.4 | n |  | TRUE
64 | bus_LV_1322-30_0_5_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_1322-30_0_5_node_78 | 0.4 | n |  | TRUE
66 | bus_LV_1322-30_0_5_node_123 | 0.4 | n |  | TRUE
67 | bus_LV_1322-30_0_5_node_77 | 0.4 | n |  | TRUE
68 | bus_LV_1322-30_0_5_node_124 | 0.4 | n |  | TRUE
69 | bus_LV_1322-30_0_5_node_50 | 0.4 | n |  | TRUE
70 | bus_LV_1322-30_0_5_node_51 | 0.4 | n |  | TRUE
71 | bus_LV_1322-30_0_5_node_52 | 0.4 | n |  | TRUE
72 | bus_LV_1322-30_0_5_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_1322-30_0_5_node_54 | 0.4 | n |  | TRUE
74 | bus_LV_1322-30_0_5_node_99 | 0.4 | n |  | TRUE
75 | bus_LV_1322-30_0_5_node_101 | 0.4 | n |  | TRUE
76 | bus_LV_1322-30_0_5_node_100 | 0.4 | n |  | TRUE
77 | bus_LV_1322-30_0_5_node_55 | 0.4 | n |  | TRUE
78 | bus_LV_1322-30_0_5_node_56 | 0.4 | n |  | TRUE
79 | bus_LV_1322-30_0_5_node_57 | 0.4 | n |  | TRUE
80 | bus_LV_1322-30_0_5_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_1322-30_0_5_node_72 | 0.4 | n |  | TRUE
82 | bus_LV_1322-30_0_5_node_75 | 0.4 | n |  | TRUE
83 | bus_LV_1322-30_0_5_node_95 | 0.4 | n |  | TRUE
84 | bus_LV_1322-30_0_5_node_61 | 0.4 | n |  | TRUE
85 | bus_LV_1322-30_0_5_node_63 | 0.4 | n |  | TRUE
86 | bus_LV_1322-30_0_5_node_65 | 0.4 | n |  | TRUE
87 | bus_LV_1322-30_0_5_node_66 | 0.4 | n |  | TRUE
88 | bus_LV_1322-30_0_5_node_82 | 0.4 | n |  | TRUE
89 | bus_LV_1322-30_0_5_node_80 | 0.4 | n |  | TRUE
90 | bus_LV_1322-30_0_5_node_67 | 0.4 | n |  | TRUE
91 | bus_LV_1322-30_0_5_node_73 | 0.4 | n |  | TRUE
92 | bus_LV_1322-30_0_5_node_74 | 0.4 | n |  | TRUE
93 | bus_LV_1322-30_0_5_node_76 | 0.4 | n |  | TRUE
94 | bus_LV_1322-30_0_5_node_79 | 0.4 | n |  | TRUE
95 | bus_LV_1322-30_0_5_node_81 | 0.4 | n |  | TRUE
96 | bus_LV_1322-30_0_5_node_83 | 0.4 | n |  | TRUE
97 | bus_LV_1322-30_0_5_node_93 | 0.4 | n |  | TRUE
98 | bus_LV_1322-30_0_5_node_91 | 0.4 | n |  | TRUE
99 | bus_LV_1322-30_0_5_node_84 | 0.4 | n |  | TRUE
100 | bus_LV_1322-30_0_5_node_85 | 0.4 | n |  | TRUE
101 | bus_LV_1322-30_0_5_node_86 | 0.4 | n |  | TRUE
102 | bus_LV_1322-30_0_5_node_87 | 0.4 | n |  | TRUE
103 | bus_LV_1322-30_0_5_node_88 | 0.4 | n |  | TRUE
104 | bus_LV_1322-30_0_5_node_109 | 0.4 | n |  | TRUE
105 | bus_LV_1322-30_0_5_node_115 | 0.4 | n |  | TRUE
106 | bus_LV_1322-30_0_5_node_110 | 0.4 | n |  | TRUE
107 | bus_LV_1322-30_0_5_node_113 | 0.4 | n |  | TRUE
108 | bus_LV_1322-30_0_5_node_89 | 0.4 | n |  | TRUE
109 | bus_LV_1322-30_0_5_node_90 | 0.4 | n |  | TRUE
110 | bus_LV_1322-30_0_5_node_92 | 0.4 | n |  | TRUE
111 | bus_LV_1322-30_0_5_node_104 | 0.4 | n |  | TRUE
112 | bus_LV_1322-30_0_5_node_117 | 0.4 | n |  | TRUE
113 | bus_LV_1322-30_0_5_node_111 | 0.4 | n |  | TRUE
114 | bus_LV_1322-30_0_5_node_107 | 0.4 | n |  | TRUE
115 | bus_LV_1322-30_0_5_node_108 | 0.4 | n |  | TRUE
116 | bus_LV_1322-30_0_5_node_121 | 0.4 | n |  | TRUE
117 | bus_LV_1322-30_0_5_node_116 | 0.4 | n |  | TRUE
118 | bus_LV_1322-30_0_5_node_112 | 0.4 | n |  | TRUE
119 | bus_LV_1322-30_0_5_node_114 | 0.4 | n |  | TRUE
120 | bus_LV_1322-30_0_5_node_120 | 0.4 | n |  | TRUE
121 | bus_MV_16_0_node_80 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1322-30_0_5_load_0 | 0 | 0.014437 | 0.0036181 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1322-30_0_5_load_1 | 1 | 0.0035607 | 0.00089241 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1322-30_0_5_load_2 | 2 | 0.0028994 | 0.00072666 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1322-30_0_5_load_3 | 3 | 0.0035626 | 0.00089287 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1322-30_0_5_load_4 | 4 | 0.0029227 | 0.00073249 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1322-30_0_5_load_20 | 5 | 0.002886 | 0.00072329 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1322-30_0_5_load_102 | 6 | 0.0029112 | 0.00072961 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1322-30_0_5_load_19 | 7 | 0.0028916 | 0.0007247 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1322-30_0_5_load_103 | 8 | 0.0035893 | 0.00089957 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1322-30_0_5_load_5 | 9 | 0.029736 | 0.0074524 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1322-30_0_5_load_6 | 10 | 0.0094179 | 0.0023604 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1322-30_0_5_load_7 | 11 | 0.026888 | 0.0067389 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1322-30_0_5_load_17 | 13 | 0.0015739 | 0.00039446 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1322-30_0_5_load_14 | 15 | 0.0040109 | 0.0010052 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1322-30_0_5_load_69 | 16 | 0.014801 | 0.0037094 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1322-30_0_5_load_118 | 18 | 0.0032191 | 0.00080678 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1322-30_0_5_load_10 | 19 | 0.027383 | 0.0068629 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1322-30_0_5_load_11 | 20 | 0.0076206 | 0.0019099 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1322-30_0_5_load_13 | 22 | 0.031279 | 0.0078392 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1322-30_0_5_load_15 | 23 | 0.0024447 | 0.00061269 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1322-30_0_5_load_16 | 24 | 0.0018542 | 0.00046471 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1322-30_0_5_load_97 | 25 | 0.0024417 | 0.00061195 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1322-30_0_5_load_106 | 26 | 0.0018565 | 0.00046527 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1322-30_0_5_load_96 | 27 | 0.0083929 | 0.0021035 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1322-30_0_5_load_105 | 28 | 0.0018542 | 0.00046471 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1322-30_0_5_load_119 | 30 | 0.0032195 | 0.00080688 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1322-30_0_5_load_22 | 31 | 0.0041049 | 0.0010288 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1322-30_0_5_load_23 | 32 | 0.0033055 | 0.00082845 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1322-30_0_5_load_24 | 33 | 0.0028774 | 0.00072113 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1322-30_0_5_load_26 | 35 | 0.0028725 | 0.00071993 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1322-30_0_5_load_59 | 36 | 0.0096636 | 0.0024219 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1322-30_0_5_load_38 | 38 | 0.0028775 | 0.00072117 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1322-30_0_5_load_94 | 39 | 0.0029142 | 0.00073037 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1322-30_0_5_load_98 | 40 | 0.0032675 | 0.0008189 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1322-30_0_5_load_37 | 41 | 0.0018405 | 0.00046127 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1322-30_0_5_load_27 | 42 | 0.0020709 | 0.00051903 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1322-30_0_5_load_28 | 43 | 0.003409 | 0.00085438 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1322-30_0_5_load_30 | 45 | 0.0030477 | 0.00076384 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1322-30_0_5_load_32 | 47 | 0.0047473 | 0.0011898 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1322-30_0_5_load_41 | 49 | 0.0015194 | 0.0003808 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1322-30_0_5_load_33 | 50 | 0.0026159 | 0.0006556 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1322-30_0_5_load_39 | 51 | 0.0044797 | 0.0011227 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1322-30_0_5_load_42 | 52 | 0.0044097 | 0.0011052 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1322-30_0_5_load_34 | 53 | 0.0020543 | 0.00051486 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1322-30_0_5_load_35 | 54 | 0.0022158 | 0.00055533 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1322-30_0_5_load_36 | 55 | 0.0018425 | 0.00046177 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1322-30_0_5_load_43 | 56 | 0.0077927 | 0.001953 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1322-30_0_5_load_44 | 57 | 0.010736 | 0.0026908 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1322-30_0_5_load_70 | 58 | 0.008835 | 0.0022143 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1322-30_0_5_load_71 | 59 | 0.004447 | 0.0011145 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1322-30_0_5_load_45 | 60 | 0.001598 | 0.00040049 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1322-30_0_5_load_46 | 61 | 0.0014796 | 0.00037083 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1322-30_0_5_load_47 | 62 | 0.0044906 | 0.0011255 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1322-30_0_5_load_48 | 63 | 0.0028534 | 0.00071513 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1322-30_0_5_load_49 | 64 | 0.0024417 | 0.00061195 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1322-30_0_5_load_78 | 65 | 0.0022649 | 0.00056765 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1322-30_0_5_load_123 | 66 | 0.0032693 | 0.00081936 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1322-30_0_5_load_77 | 67 | 0.0022667 | 0.00056809 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1322-30_0_5_load_124 | 68 | 0.0032664 | 0.00081863 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1322-30_0_5_load_50 | 69 | 0.006322 | 0.0015844 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1322-30_0_5_load_51 | 70 | 0.0029138 | 0.00073027 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1322-30_0_5_load_53 | 72 | 0.0021751 | 0.00054514 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1322-30_0_5_load_54 | 73 | 0.0050796 | 0.0012731 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1322-30_0_5_load_99 | 74 | 0.0082034 | 0.002056 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1322-30_0_5_load_101 | 75 | 0.0032219 | 0.00080749 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1322-30_0_5_load_100 | 76 | 0.0028725 | 0.00071993 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1322-30_0_5_load_55 | 77 | 0.0054713 | 0.0013712 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1322-30_0_5_load_56 | 78 | 0.0065033 | 0.0016299 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1322-30_0_5_load_57 | 79 | 0.011887 | 0.0029792 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1322-30_0_5_load_58 | 80 | 0.0024973 | 0.00062589 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1322-30_0_5_load_72 | 81 | 0.0022649 | 0.00056765 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1322-30_0_5_load_95 | 83 | 0.0028775 | 0.00072117 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1322-30_0_5_load_61 | 84 | 0.010344 | 0.0025924 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1322-30_0_5_load_65 | 86 | 0.0065859 | 0.0016506 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1322-30_0_5_load_66 | 87 | 0.011128 | 0.002789 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1322-30_0_5_load_82 | 88 | 0.0051087 | 0.0012804 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1322-30_0_5_load_80 | 89 | 0.011922 | 0.0029879 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1322-30_0_5_load_67 | 90 | 0.0098391 | 0.0024659 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1322-30_0_5_load_73 | 91 | 0.0029244 | 0.00073292 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1322-30_0_5_load_74 | 92 | 0.0045905 | 0.0011505 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1322-30_0_5_load_76 | 93 | 0.0029421 | 0.00073736 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1322-30_0_5_load_79 | 94 | 0.0029421 | 0.00073736 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1322-30_0_5_load_81 | 95 | 0.0093186 | 0.0023355 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1322-30_0_5_load_83 | 96 | 0.0029472 | 0.00073863 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1322-30_0_5_load_93 | 97 | 0.0029421 | 0.00073736 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1322-30_0_5_load_91 | 98 | 0.0029421 | 0.00073736 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1322-30_0_5_load_84 | 99 | 0.011515 | 0.0028858 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1322-30_0_5_load_85 | 100 | 0.0019002 | 0.00047623 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1322-30_0_5_load_86 | 101 | 0.0019002 | 0.00047623 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1322-30_0_5_load_87 | 102 | 0.0033403 | 0.00083716 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1322-30_0_5_load_88 | 103 | 0.0019002 | 0.00047623 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1322-30_0_5_load_109 | 104 | 0.003168 | 0.00079397 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1322-30_0_5_load_115 | 105 | 0.001899 | 0.00047593 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1322-30_0_5_load_110 | 106 | 0.003164 | 0.00079298 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1322-30_0_5_load_113 | 107 | 0.0017075 | 0.00042794 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1322-30_0_5_load_89 | 108 | 0.014813 | 0.0037124 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1322-30_0_5_load_90 | 109 | 0.003168 | 0.00079397 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1322-30_0_5_load_92 | 110 | 0.003164 | 0.00079298 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1322-30_0_5_load_104 | 111 | 0.003166 | 0.00079347 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1322-30_0_5_load_117 | 112 | 0.003168 | 0.00079397 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1322-30_0_5_load_111 | 113 | 0.0025894 | 0.00064897 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1322-30_0_5_load_107 | 114 | 0.0017088 | 0.00042826 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1322-30_0_5_load_108 | 115 | 0.0017088 | 0.00042826 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1322-30_0_5_load_121 | 116 | 0.0017099 | 0.00042853 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1322-30_0_5_load_116 | 117 | 0.0017081 | 0.0004281 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1322-30_0_5_load_112 | 118 | 0.0017075 | 0.00042794 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1322-30_0_5_load_114 | 119 | 0.011342 | 0.0028426 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1322-30_0_5_load_120 | 120 | 0.0032191 | 0.00080678 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1322-30_0_5_line_0 |  | 0 | 1 | 0.020958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1322-30_0_5_line_1 |  | 0 | 2 | 0.0083296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1322-30_0_5_line_2 |  | 1 | 3 | 0.0019578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1322-30_0_5_line_3 |  | 2 | 4 | 0.00043347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1322-30_0_5_line_4 |  | 3 | 5 | 0.0019618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1322-30_0_5_line_5 |  | 4 | 6 | 0.00049072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1322-30_0_5_line_6 |  | 5 | 7 | 0.0019534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1322-30_0_5_line_7 |  | 6 | 8 | 0.00046646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1322-30_0_5_line_8 |  | 7 | 22 | 0.021311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1322-30_0_5_line_9 |  | 8 | 17 | 0.030074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1322-30_0_5_line_10 |  | 9 | 10 | 0.048682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1322-30_0_5_line_11 |  | 9 | 11 | 0.047278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1322-30_0_5_line_12 |  | 10 | 12 | 0.043188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1322-30_0_5_line_13 |  | 12 | 13 | 0.0069061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1322-30_0_5_line_14 |  | 12 | 14 | 0.027805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1322-30_0_5_line_15 |  | 13 | 15 | 0.014867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1322-30_0_5_line_16 |  | 14 | 16 | 0.025282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1322-30_0_5_line_17 |  | 15 | 21 | 0.035343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1322-30_0_5_line_18 |  | 16 | 29 | 0.0033455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1322-30_0_5_line_19 |  | 17 | 18 | 0.015127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1322-30_0_5_line_20 |  | 18 | 30 | 0.0023619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1322-30_0_5_line_21 |  | 19 | 20 | 0.042654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1322-30_0_5_line_22 |  | 19 | 21 | 0.01942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1322-30_0_5_line_23 |  | 20 | 22 | 0.0073939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1322-30_0_5_line_24 |  | 21 | 23 | 0.026927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1322-30_0_5_line_25 |  | 21 | 24 | 0.027572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_1322-30_0_5_line_26 |  | 23 | 25 | 0.0036188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_1322-30_0_5_line_27 |  | 24 | 26 | 0.0053436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_1322-30_0_5_line_28 |  | 25 | 27 | 0.0050472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_1322-30_0_5_line_29 |  | 26 | 28 | 0.0053436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1322-30_0_5_line_30 |  | 27 | 37 | 0.0089901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_1322-30_0_5_line_31 |  | 28 | 114 | 0.016077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1322-30_0_5_line_32 |  | 29 | 90 | 0.034079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1322-30_0_5_line_33 |  | 30 | 120 | 0.0023723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1322-30_0_5_line_34 |  | 31 | 32 | 0.028367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1322-30_0_5_line_35 |  | 31 | 33 | 0.027387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1322-30_0_5_line_36 |  | 32 | 34 | 0.011188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1322-30_0_5_line_37 |  | 33 | 35 | 0.0052904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1322-30_0_5_line_38 |  | 34 | 36 | 0.032713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1322-30_0_5_line_39 |  | 34 | 37 | 0.017655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1322-30_0_5_line_40 |  | 35 | 38 | 0.0045284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1322-30_0_5_line_41 |  | 36 | 39 | 0.01656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1322-30_0_5_line_42 |  | 37 | 40 | 0.028366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1322-30_0_5_line_43 |  | 38 | 41 | 0.01624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1322-30_0_5_line_44 |  | 39 | 83 | 0.0063286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1322-30_0_5_line_45 |  | 40 | 68 | 0.0014505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1322-30_0_5_line_46 |  | 41 | 55 | 0.0049797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1322-30_0_5_line_47 |  | 42 | 43 | 0.0051345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1322-30_0_5_line_48 |  | 42 | 44 | 0.0086364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1322-30_0_5_line_49 |  | 43 | 45 | 0.013864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1322-30_0_5_line_50 |  | 44 | 46 | 0.010008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1322-30_0_5_line_51 |  | 45 | 47 | 0.0068483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1322-30_0_5_line_52 |  | 46 | 48 | 0.008896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1322-30_0_5_line_53 |  | 46 | 49 | 0.037625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1322-30_0_5_line_54 |  | 47 | 50 | 0.001809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1322-30_0_5_line_55 |  | 48 | 51 | 0.0089907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1322-30_0_5_line_56 |  | 49 | 52 | 0.026567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1322-30_0_5_line_57 |  | 50 | 53 | 0.025676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1322-30_0_5_line_58 |  | 52 | 56 | 0.02513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1322-30_0_5_line_59 |  | 53 | 54 | 0.00049893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1322-30_0_5_line_60 |  | 54 | 55 | 0.0067661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1322-30_0_5_line_61 |  | 56 | 57 | 0.023259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1322-30_0_5_line_62 |  | 57 | 58 | 0.022495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1322-30_0_5_line_63 |  | 58 | 59 | 0.01953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1322-30_0_5_line_64 |  | 60 | 61 | 4.0284e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1322-30_0_5_line_65 |  | 60 | 62 | 0.001576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1322-30_0_5_line_66 |  | 61 | 63 | 0.039858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1322-30_0_5_line_67 |  | 62 | 64 | 0.021707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1322-30_0_5_line_68 |  | 63 | 65 | 0.012762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1322-30_0_5_line_69 |  | 64 | 66 | 0.0038884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1322-30_0_5_line_70 |  | 65 | 67 | 0.0096211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1322-30_0_5_line_71 |  | 66 | 68 | 0.0014518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1322-30_0_5_line_72 |  | 67 | 82 | 0.048394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1322-30_0_5_line_73 |  | 69 | 70 | 0.018958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1322-30_0_5_line_74 |  | 69 | 71 | 0.0075992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1322-30_0_5_line_75 |  | 70 | 72 | 0.0134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1322-30_0_5_line_76 |  | 71 | 73 | 0.023367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1322-30_0_5_line_77 |  | 72 | 74 | 0.0013492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1322-30_0_5_line_78 |  | 73 | 75 | 0.0051953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1322-30_0_5_line_79 |  | 74 | 76 | 0.0031057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1322-30_0_5_line_80 |  | 76 | 83 | 0.0019524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1322-30_0_5_line_81 |  | 77 | 78 | 0.00016434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1322-30_0_5_line_82 |  | 77 | 79 | 0.01433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1322-30_0_5_line_83 |  | 78 | 80 | 0.036155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1322-30_0_5_line_84 |  | 80 | 81 | 0.036958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1322-30_0_5_line_85 |  | 81 | 82 | 0.023089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1322-30_0_5_line_86 |  | 82 | 91 | 0.002169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1322-30_0_5_line_87 |  | 84 | 85 | 0.023957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1322-30_0_5_line_88 |  | 85 | 86 | 0.018841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1322-30_0_5_line_89 |  | 86 | 87 | 0.028678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1322-30_0_5_line_90 |  | 87 | 90 | 0.024261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1322-30_0_5_line_91 |  | 88 | 89 | 0.017297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1322-30_0_5_line_92 |  | 89 | 95 | 0.017191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1322-30_0_5_line_93 |  | 91 | 92 | 0.014474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1322-30_0_5_line_94 |  | 92 | 93 | 0.045929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1322-30_0_5_line_95 |  | 93 | 94 | 0.00025333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1322-30_0_5_line_96 |  | 95 | 96 | 0.0097811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1322-30_0_5_line_97 |  | 96 | 97 | 0.0010268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1322-30_0_5_line_98 |  | 97 | 98 | 0.001026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1322-30_0_5_line_99 |  | 98 | 108 | 0.014995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1322-30_0_5_line_100 |  | 99 | 100 | 0.0011926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1322-30_0_5_line_101 |  | 99 | 101 | 0.0048563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1322-30_0_5_line_102 |  | 100 | 102 | 0.0060471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1322-30_0_5_line_103 |  | 101 | 103 | 0.0060491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1322-30_0_5_line_104 |  | 102 | 104 | 0.013213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1322-30_0_5_line_105 |  | 103 | 105 | 0.0060471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1322-30_0_5_line_106 |  | 104 | 106 | 0.006049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1322-30_0_5_line_107 |  | 105 | 107 | 0.013571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1322-30_0_5_line_108 |  | 106 | 113 | 0.0052047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1322-30_0_5_line_109 |  | 107 | 118 | 0.0059051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1322-30_0_5_line_110 |  | 108 | 109 | 0.0083024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1322-30_0_5_line_111 |  | 109 | 110 | 0.006049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1322-30_0_5_line_112 |  | 110 | 111 | 0.0060471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1322-30_0_5_line_113 |  | 111 | 112 | 0.0060509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1322-30_0_5_line_114 |  | 112 | 113 | 0.00084433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1322-30_0_5_line_115 |  | 114 | 115 | 0.0015505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1322-30_0_5_line_116 |  | 115 | 116 | 0.005812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1322-30_0_5_line_117 |  | 116 | 117 | 0.0059067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1322-30_0_5_line_118 |  | 117 | 119 | 0.005448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1322-30_0_5_line_119 |  | 118 | 119 | 0.00045739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1322-30_0_5_trafo_106 | 0.63 MVA 20/0.4 kV | 121 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2700875.547 | 1228726.1854 | 2700896.0852 | 1228722.0115
1 | 2700875.547 | 1228726.1854 | 2700875.1003 | 1228726.2761 | 2700867.2313 | 1228726.0002
2 | 2700896.0852 | 1228722.0115 | 2700898.0038 | 1228721.6216
3 | 2700866.7981 | 1228725.985 | 2700867.2313 | 1228726.0002
4 | 2700899.9262 | 1228721.2309 | 2700898.0038 | 1228721.6216
5 | 2700866.3077 | 1228725.9678 | 2700866.7981 | 1228725.985
6 | 2700899.9262 | 1228721.2309 | 2700901.8405 | 1228720.8419
7 | 2700865.8415 | 1228725.9514 | 2700866.3077 | 1228725.9678
8 | 2700922.7242 | 1228716.5978 | 2700901.8405 | 1228720.8419
9 | 2700835.7855 | 1228724.8974 | 2700865.8415 | 1228725.9514
10 | 2700955.059 | 1228762.7686 | 2701003.033 | 1228754.495
11 | 2700955.059 | 1228762.7686 | 2700908.4682 | 1228770.8036
12 | 2701041.2187 | 1228737.1034 | 2701022.8391 | 1228751.0793 | 2701003.033 | 1228754.495
13 | 2701041.2187 | 1228737.1034 | 2701034.8867 | 1228734.3465
14 | 2701057.6369 | 1228758.7093 | 2701052.7963 | 1228747.4632 | 2701045.8759 | 1228740.4183 | 2701041.2187 | 1228737.1034
15 | 2701034.8867 | 1228734.3465 | 2701021.256 | 1228728.4118
16 | 2701057.6369 | 1228758.7093 | 2701075.1478 | 1228756.1605 | 2701082.6551 | 1228755.069
17 | 2700991.7633 | 1228709.4766 | 2701008.4508 | 1228722.8364 | 2701021.256 | 1228728.4118
18 | 2701085.9658 | 1228754.5876 | 2701082.6551 | 1228755.069
19 | 2700835.7855 | 1228724.8974 | 2700822.4428 | 1228717.7708
20 | 2700822.4428 | 1228717.7708 | 2700820.3595 | 1228716.6581
21 | 2700972.4128 | 1228711.1134 | 2700933.5248 | 1228714.4029 | 2700929.97 | 1228715.1253
22 | 2700991.7633 | 1228709.4766 | 2700972.4128 | 1228711.1134
23 | 2700922.7242 | 1228716.5978 | 2700929.97 | 1228715.1253
24 | 2700991.7633 | 1228709.4766 | 2700976.542 | 1228687.2641
25 | 2700991.7633 | 1228709.4766 | 2701015.6664 | 1228695.7333
26 | 2700974.4965 | 1228684.279 | 2700976.542 | 1228687.2641
27 | 2701015.6664 | 1228695.7333 | 2701020.2989 | 1228693.0699
28 | 2700971.6434 | 1228680.1156 | 2700974.4965 | 1228684.279
29 | 2701024.9313 | 1228690.4064 | 2701020.2989 | 1228693.0699
30 | 2700966.5616 | 1228672.6996 | 2700971.6434 | 1228680.1156
31 | 2701024.9313 | 1228690.4064 | 2701026.8521 | 1228689.3021 | 2701040.315 | 1228686.0006
32 | 2701085.9658 | 1228754.5876 | 2701119.7719 | 1228750.2802
33 | 2700818.267 | 1228715.5404 | 2700820.3595 | 1228716.6581
34 | 2700950.8765 | 1228651.1272 | 2700949.2899 | 1228648.2107 | 2700946.7104 | 1228643.4746 | 2700945.123 | 1228640.5566 | 2700942.1027 | 1228635.0013 | 2700940.5521 | 1228632.1506 | 2700937.0487 | 1228628.2661 | 2700936.0228 | 1228627.1276
35 | 2700919.2955 | 1228605.4765 | 2700928.4774 | 1228618.0132 | 2700931.403 | 1228622.0102 | 2700934.5048 | 1228625.4431 | 2700936.0228 | 1228627.1276
36 | 2700952.5974 | 1228661.8435 | 2700952.729 | 1228654.5404 | 2700951.3108 | 1228651.9255 | 2700950.8765 | 1228651.1272
37 | 2700919.2955 | 1228605.4765 | 2700916.1696 | 1228601.2084
38 | 2700952.5974 | 1228661.8435 | 2700933.4847 | 1228653.3907 | 2700922.1414 | 1228650.0867
39 | 2700952.5974 | 1228661.8435 | 2700966.5616 | 1228672.6996
40 | 2700913.4939 | 1228597.555 | 2700916.1696 | 1228601.2084
41 | 2700922.1414 | 1228650.0867 | 2700906.2421 | 1228645.4555
42 | 2700966.5616 | 1228672.6996 | 2700986.7832 | 1228655.1299 | 2700988.3428 | 1228654.8932
43 | 2700913.4939 | 1228597.555 | 2700913.4939 | 1228597.555 | 2700918.091 | 1228584.3344 | 2700918.8278 | 1228582.2164
44 | 2700906.2421 | 1228645.4555 | 2700900.166 | 1228643.6856
45 | 2700988.3428 | 1228654.8932 | 2700989.7769 | 1228654.6756
46 | 2700920.4638 | 1228577.5132 | 2700918.8278 | 1228582.2164
47 | 2700935.5898 | 1228519.6478 | 2700935.9585 | 1228524.769
48 | 2700934.9697 | 1228511.0337 | 2700935.5898 | 1228519.6478
49 | 2700934.1305 | 1228538.2237 | 2700936.4475 | 1228531.5627 | 2700935.9585 | 1228524.769
50 | 2700935.2381 | 1228501.0309 | 2700934.9697 | 1228511.0337
51 | 2700934.1305 | 1228538.2237 | 2700931.8806 | 1228544.6919
52 | 2700935.2381 | 1228501.0309 | 2700935.48 | 1228492.1396
53 | 2700935.2381 | 1228501.0309 | 2700952.0531 | 1228502.9065 | 2700971.9987 | 1228508.466
54 | 2700931.2862 | 1228546.4006 | 2700931.8806 | 1228544.6919
55 | 2700935.48 | 1228492.1396 | 2700927.2318 | 1228488.5621
56 | 2700971.9987 | 1228508.466 | 2700997.59 | 1228515.5992
57 | 2700931.2862 | 1228546.4006 | 2700922.8506 | 1228570.6514
58 | 2700997.59 | 1228515.5992 | 2701021.7973 | 1228522.3466
59 | 2700922.8506 | 1228570.6514 | 2700922.6867 | 1228571.1226
60 | 2700920.4638 | 1228577.5132 | 2700922.6867 | 1228571.1226
61 | 2701021.7973 | 1228522.3466 | 2701044.2023 | 1228528.5916
62 | 2701044.2023 | 1228528.5916 | 2701065.8712 | 1228534.6315
63 | 2701065.8712 | 1228534.6315 | 2701083.6201 | 1228539.5787 | 2701084.7111 | 1228539.7535
64 | 2701018.116 | 1228650.3747 | 2701018.0762 | 1228650.3808
65 | 2701016.518 | 1228650.6172 | 2701018.0762 | 1228650.3808
66 | 2701056.8715 | 1228641.23 | 2701026.9757 | 1228649.0301 | 2701018.116 | 1228650.3747
67 | 2701016.518 | 1228650.6172 | 2700995.0567 | 1228653.8743
68 | 2701069.2265 | 1228638.0438 | 2701068.9865 | 1228638.069 | 2701056.8715 | 1228641.23
69 | 2700995.0567 | 1228653.8743 | 2700991.2123 | 1228654.4578
70 | 2701069.2265 | 1228638.0438 | 2701078.7949 | 1228637.0384
71 | 2700991.2123 | 1228654.4578 | 2700989.7769 | 1228654.6756
72 | 2701109.8039 | 1228612.6218 | 2701111.0334 | 1228624.0955 | 2701100.6824 | 1228634.7385 | 2701078.7949 | 1228637.0384
73 | 2700863.2093 | 1228632.1019 | 2700869.8842 | 1228634.865 | 2700881.1494 | 1228638.1464
74 | 2700856.1879 | 1228629.1953 | 2700863.2093 | 1228632.1019
75 | 2700894.0144 | 1228641.8937 | 2700881.1494 | 1228638.1464
76 | 2700856.1879 | 1228629.1953 | 2700844.2998 | 1228634.4309 | 2700834.4621 | 1228637.7317
77 | 2700895.3098 | 1228642.2711 | 2700894.0144 | 1228641.8937
78 | 2700834.4621 | 1228637.7317 | 2700829.5367 | 1228639.3843
79 | 2700895.3098 | 1228642.2711 | 2700898.2916 | 1228643.1396
80 | 2700900.166 | 1228643.6856 | 2700898.2916 | 1228643.1396
81 | 2701015.7583 | 1228594.6571 | 2701015.92 | 1228594.6862
82 | 2701001.6537 | 1228592.125 | 2701015.7583 | 1228594.6571
83 | 2701051.5059 | 1228601.0746 | 2701015.92 | 1228594.6862
84 | 2701088.1217 | 1228605.9222 | 2701064.7326 | 1228603.4491 | 2701051.5059 | 1228601.0746
85 | 2701109.8039 | 1228612.6218 | 2701099.0688 | 1228607.0797 | 2701088.1217 | 1228605.9222
86 | 2701109.8039 | 1228612.6218 | 2701111.7799 | 1228613.516
87 | 2701190.9762 | 1228741.2076 | 2701214.6913 | 1228737.8086
88 | 2701190.9762 | 1228741.2076 | 2701172.2866 | 1228743.5889
89 | 2701172.2866 | 1228743.5889 | 2701143.8381 | 1228747.2137
90 | 2701119.7719 | 1228750.2802 | 2701143.8381 | 1228747.2137
91 | 2701198.4442 | 1228678.9997 | 2701215.5705 | 1228676.5782
92 | 2701198.4442 | 1228678.9997 | 2701181.4222 | 1228681.4064
93 | 2701111.7799 | 1228613.516 | 2701124.9667 | 1228619.484
94 | 2701124.9667 | 1228619.484 | 2701136.3283 | 1228624.6259 | 2701169.7298 | 1228626.5632
95 | 2701169.7298 | 1228626.5632 | 2701169.9827 | 1228626.5779
96 | 2701181.4222 | 1228681.4064 | 2701171.7375 | 1228682.7758
97 | 2701170.7208 | 1228682.9195 | 2701171.7375 | 1228682.7758
98 | 2701170.7208 | 1228682.9195 | 2701169.7049 | 1228683.0631
99 | 2701154.8576 | 1228685.1624 | 2701169.7049 | 1228683.0631
100 | 2701095.873 | 1228685.5102 | 2701097.0656 | 1228685.5075
101 | 2701095.873 | 1228685.5102 | 2701091.0167 | 1228685.5211
102 | 2701097.0656 | 1228685.5075 | 2701103.1127 | 1228685.494
103 | 2701084.9676 | 1228685.5347 | 2701091.0167 | 1228685.5211
104 | 2701116.3257 | 1228685.4644 | 2701103.1127 | 1228685.494
105 | 2701078.9205 | 1228685.5482 | 2701084.9676 | 1228685.5347
106 | 2701116.3257 | 1228685.4644 | 2701122.3747 | 1228685.4508
107 | 2701078.9205 | 1228685.5482 | 2701065.35 | 1228685.5786
108 | 2701127.5794 | 1228685.4391 | 2701122.3747 | 1228685.4508
109 | 2701059.4449 | 1228685.5919 | 2701065.35 | 1228685.5786
110 | 2701154.8576 | 1228685.1624 | 2701153.308 | 1228685.3815 | 2701146.5706 | 1228685.3966
111 | 2701146.5706 | 1228685.3966 | 2701140.5217 | 1228685.4101
112 | 2701134.4745 | 1228685.4237 | 2701140.5217 | 1228685.4101
113 | 2701134.4745 | 1228685.4237 | 2701128.4237 | 1228685.4373
114 | 2701127.5794 | 1228685.4391 | 2701128.4237 | 1228685.4373
115 | 2701041.8208 | 1228685.6314 | 2701041.8208 | 1228685.6314 | 2701040.315 | 1228686.0006
116 | 2701041.8208 | 1228685.6314 | 2701047.6328 | 1228685.6183
117 | 2701053.5395 | 1228685.6051 | 2701047.6328 | 1228685.6183
118 | 2701058.9875 | 1228685.5929 | 2701053.5395 | 1228685.6051
119 | 2701058.9875 | 1228685.5929 | 2701059.4449 | 1228685.5919

## bus_geodata
| x | y | coords
0 | 2700875.547 | 1228726.1854
1 | 2700896.0852 | 1228722.0115
2 | 2700867.2313 | 1228726.0002
3 | 2700898.0038 | 1228721.6216
4 | 2700866.7981 | 1228725.985
5 | 2700899.9262 | 1228721.2309
6 | 2700866.3077 | 1228725.9678
7 | 2700901.8405 | 1228720.8419
8 | 2700865.8415 | 1228725.9514
9 | 2700955.059 | 1228762.7686
10 | 2701003.033 | 1228754.495
11 | 2700908.4682 | 1228770.8036
12 | 2701041.2187 | 1228737.1034
13 | 2701034.8867 | 1228734.3465
14 | 2701057.6369 | 1228758.7093
15 | 2701021.256 | 1228728.4118
16 | 2701082.6551 | 1228755.069
17 | 2700835.7855 | 1228724.8974
18 | 2700822.4428 | 1228717.7708
19 | 2700972.4128 | 1228711.1134
20 | 2700929.97 | 1228715.1253
21 | 2700991.7633 | 1228709.4766
22 | 2700922.7242 | 1228716.5978
23 | 2700976.542 | 1228687.2641
24 | 2701015.6664 | 1228695.7333
25 | 2700974.4965 | 1228684.279
26 | 2701020.2989 | 1228693.0699
27 | 2700971.6434 | 1228680.1156
28 | 2701024.9313 | 1228690.4064
29 | 2701085.9658 | 1228754.5876
30 | 2700820.3595 | 1228716.6581
31 | 2700936.0228 | 1228627.1276
32 | 2700950.8765 | 1228651.1272
33 | 2700919.2955 | 1228605.4765
34 | 2700952.5974 | 1228661.8435
35 | 2700916.1696 | 1228601.2084
36 | 2700922.1414 | 1228650.0867
37 | 2700966.5616 | 1228672.6996
38 | 2700913.4939 | 1228597.555
39 | 2700906.2421 | 1228645.4555
40 | 2700988.3428 | 1228654.8932
41 | 2700918.8278 | 1228582.2164
42 | 2700935.5898 | 1228519.6478
43 | 2700935.9585 | 1228524.769
44 | 2700934.9697 | 1228511.0337
45 | 2700934.1305 | 1228538.2237
46 | 2700935.2381 | 1228501.0309
47 | 2700931.8806 | 1228544.6919
48 | 2700935.48 | 1228492.1396
49 | 2700971.9987 | 1228508.466
50 | 2700931.2862 | 1228546.4006
51 | 2700927.2318 | 1228488.5621
52 | 2700997.59 | 1228515.5992
53 | 2700922.8506 | 1228570.6514
54 | 2700922.6867 | 1228571.1226
55 | 2700920.4638 | 1228577.5132
56 | 2701021.7973 | 1228522.3466
57 | 2701044.2023 | 1228528.5916
58 | 2701065.8712 | 1228534.6315
59 | 2701084.7111 | 1228539.7535
60 | 2701018.0762 | 1228650.3808
61 | 2701018.116 | 1228650.3747
62 | 2701016.518 | 1228650.6172
63 | 2701056.8715 | 1228641.23
64 | 2700995.0567 | 1228653.8743
65 | 2701069.2265 | 1228638.0438
66 | 2700991.2123 | 1228654.4578
67 | 2701078.7949 | 1228637.0384
68 | 2700989.7769 | 1228654.6756
69 | 2700863.2093 | 1228632.1019
70 | 2700881.1494 | 1228638.1464
71 | 2700856.1879 | 1228629.1953
72 | 2700894.0144 | 1228641.8937
73 | 2700834.4621 | 1228637.7317
74 | 2700895.3098 | 1228642.2711
75 | 2700829.5367 | 1228639.3843
76 | 2700898.2916 | 1228643.1396
77 | 2701015.7583 | 1228594.6571
78 | 2701015.92 | 1228594.6862
79 | 2701001.6537 | 1228592.125
80 | 2701051.5059 | 1228601.0746
81 | 2701088.1217 | 1228605.9222
82 | 2701109.8039 | 1228612.6218
83 | 2700900.166 | 1228643.6856
84 | 2701214.6913 | 1228737.8086
85 | 2701190.9762 | 1228741.2076
86 | 2701172.2866 | 1228743.5889
87 | 2701143.8381 | 1228747.2137
88 | 2701215.5705 | 1228676.5782
89 | 2701198.4442 | 1228678.9997
90 | 2701119.7719 | 1228750.2802
91 | 2701111.7799 | 1228613.516
92 | 2701124.9667 | 1228619.484
93 | 2701169.7298 | 1228626.5632
94 | 2701169.9827 | 1228626.5779
95 | 2701181.4222 | 1228681.4064
96 | 2701171.7375 | 1228682.7758
97 | 2701170.7208 | 1228682.9195
98 | 2701169.7049 | 1228683.0631
99 | 2701095.873 | 1228685.5102
100 | 2701097.0656 | 1228685.5075
101 | 2701091.0167 | 1228685.5211
102 | 2701103.1127 | 1228685.494
103 | 2701084.9676 | 1228685.5347
104 | 2701116.3257 | 1228685.4644
105 | 2701078.9205 | 1228685.5482
106 | 2701122.3747 | 1228685.4508
107 | 2701065.35 | 1228685.5786
108 | 2701154.8576 | 1228685.1624
109 | 2701146.5706 | 1228685.3966
110 | 2701140.5217 | 1228685.4101
111 | 2701134.4745 | 1228685.4237
112 | 2701128.4237 | 1228685.4373
113 | 2701127.5794 | 1228685.4391
114 | 2701040.315 | 1228686.0006
115 | 2701041.8208 | 1228685.6314
116 | 2701047.6328 | 1228685.6183
117 | 2701053.5395 | 1228685.6051
118 | 2701059.4449 | 1228685.5919
119 | 2701058.9875 | 1228685.5929
120 | 2700818.267 | 1228715.5404
121 | 2700991.7633 | 1228709.4766

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98864 | -0.21835 | 0.014437 | 0.0036181
1 | 0.98934 | -0.20474 | 0.0035607 | 0.00089241
2 | 0.98847 | -0.22161 | 0.0028994 | 0.00072666
3 | 0.98941 | -0.20335 | 0.0035626 | 0.00089287
4 | 0.98846 | -0.22176 | 0.0029227 | 0.00073249
5 | 0.98949 | -0.20183 | 0.002886 | 0.00072329
6 | 0.98846 | -0.2219 | 0.0029112 | 0.00072961
7 | 0.98957 | -0.20022 | 0.0028916 | 0.0007247
8 | 0.98845 | -0.22201 | 0.0035893 | 0.00089957
9 | 0.98497 | -0.28887 | 0.029736 | 0.0074524
10 | 0.98751 | -0.23947 | 0.0094179 | 0.0023604
11 | 0.9838 | -0.31173 | 0.026888 | 0.0067389
12 | 0.99014 | -0.18863 | 0 | 0
13 | 0.9909 | -0.17406 | 0.0015739 | 0.00039446
14 | 0.98879 | -0.21471 | 0 | 0
15 | 0.99254 | -0.14236 | 0.0040109 | 0.0010052
16 | 0.98757 | -0.2385 | 0.014801 | 0.0037094
17 | 0.98818 | -0.22719 | 0 | 0
18 | 0.98805 | -0.2298 | 0.0032191 | 0.00080678
19 | 0.99453 | -0.1044 | 0.027383 | 0.0068629
20 | 0.99108 | -0.17095 | 0.0076206 | 0.0019099
21 | 0.99659 | -0.064925 | 0 | 0
22 | 0.99054 | -0.18153 | 0.031279 | 0.0078392
23 | 0.99528 | -0.08987 | 0.0024447 | 0.00061269
24 | 0.99944 | -0.010546 | 0.0018542 | 0.00046471
25 | 0.99511 | -0.093188 | 0.0024417 | 0.00061195
26 | 1 | 0 | -0.57806 | -0.14689
27 | 0.99487 | -0.097764 | 0.0083929 | 0.0021035
28 | 0.99943 | -0.010949 | 0.0018542 | 0.00046471
29 | 0.98745 | -0.24076 | 0 | 0
30 | 0.98804 | -0.23007 | 0.0032195 | 0.00080688
31 | 0.98905 | -0.20951 | 0.0041049 | 0.0010288
32 | 0.99111 | -0.16976 | 0.0033055 | 0.00082845
33 | 0.98716 | -0.24603 | 0.0028774 | 0.00072113
34 | 0.99196 | -0.15347 | 0 | 0
35 | 0.9868 | -0.25283 | 0.0028725 | 0.00071993
36 | 0.99058 | -0.18031 | 0.0096636 | 0.0024219
37 | 0.99405 | -0.11342 | 0 | 0
38 | 0.98652 | -0.25842 | 0.0028775 | 0.00072117
39 | 0.99002 | -0.19108 | 0.0029142 | 0.00073037
40 | 0.99225 | -0.14812 | 0.0032675 | 0.0008189
41 | 0.98552 | -0.27766 | 0.0018405 | 0.00046127
42 | 0.98219 | -0.3425 | 0.0020709 | 0.00051903
43 | 0.9824 | -0.33839 | 0.003409 | 0.00085438
44 | 0.98185 | -0.34909 | 0 | 0
45 | 0.98301 | -0.32645 | 0.0030477 | 0.00076384
46 | 0.98146 | -0.35673 | 0 | 0
47 | 0.98333 | -0.32018 | 0.0047473 | 0.0011898
48 | 0.98142 | -0.35745 | 0 | 0
49 | 0.98014 | -0.38246 | 0.0015194 | 0.0003808
50 | 0.98343 | -0.31837 | 0.0026159 | 0.0006556
51 | 0.98139 | -0.35818 | 0.0044797 | 0.0011227
52 | 0.97925 | -0.39994 | 0.0044097 | 0.0011052
53 | 0.98481 | -0.29152 | 0.0020543 | 0.00051486
54 | 0.98484 | -0.29098 | 0.0022158 | 0.00055533
55 | 0.98523 | -0.2834 | 0.0018425 | 0.00046177
56 | 0.97851 | -0.41448 | 0.0077927 | 0.001953
57 | 0.97799 | -0.42465 | 0.010736 | 0.0026908
58 | 0.97771 | -0.4301 | 0.008835 | 0.0022143
59 | 0.97763 | -0.43168 | 0.004447 | 0.0011145
60 | 0.99065 | -0.17893 | 0.001598 | 0.00040049
61 | 0.99065 | -0.17896 | 0.0014796 | 0.00037083
62 | 0.99072 | -0.17746 | 0.0044906 | 0.0011255
63 | 0.98883 | -0.21401 | 0.0028534 | 0.00071513
64 | 0.99186 | -0.15552 | 0.0024417 | 0.00061195
65 | 0.98828 | -0.22461 | 0.0022649 | 0.00056765
66 | 0.99207 | -0.15143 | 0.0032693 | 0.00081936
67 | 0.98789 | -0.23222 | 0.0022667 | 0.00056809
68 | 0.99216 | -0.14981 | 0.0032664 | 0.00081863
69 | 0.9892 | -0.20707 | 0.006322 | 0.0015844
70 | 0.98945 | -0.20214 | 0.0029138 | 0.00073027
71 | 0.98914 | -0.2082 | 0 | 0
72 | 0.98967 | -0.19795 | 0.0021751 | 0.00054514
73 | 0.98896 | -0.21165 | 0.0050796 | 0.0012731
74 | 0.98969 | -0.19748 | 0.0082034 | 0.002056
75 | 0.98895 | -0.21195 | 0.0032219 | 0.00080749
76 | 0.98977 | -0.19594 | 0.0028725 | 0.00071993
77 | 0.98371 | -0.31355 | 0.0054713 | 0.0013712
78 | 0.98372 | -0.3135 | 0.0065033 | 0.0016299
79 | 0.98356 | -0.31662 | 0.011887 | 0.0029792
80 | 0.98451 | -0.29797 | 0.0024973 | 0.00062589
81 | 0.98541 | -0.28047 | 0.0022649 | 0.00056765
82 | 0.98602 | -0.26861 | 0 | 0
83 | 0.98983 | -0.19487 | 0.0028775 | 0.00072117
84 | 0.98478 | -0.29275 | 0.010344 | 0.0025924
85 | 0.98501 | -0.2883 | 0 | 0
86 | 0.98519 | -0.2848 | 0.0065859 | 0.0016506
87 | 0.98564 | -0.27608 | 0.011128 | 0.002789
88 | 0.98814 | -0.2283 | 0.0051087 | 0.0012804
89 | 0.98822 | -0.22672 | 0.011922 | 0.0029879
90 | 0.98626 | -0.26388 | 0.0098391 | 0.0024659
91 | 0.98599 | -0.26913 | 0.0029244 | 0.00073292
92 | 0.98585 | -0.27185 | 0.0045905 | 0.0011505
93 | 0.9856 | -0.2767 | 0.0029421 | 0.00073736
94 | 0.9856 | -0.27671 | 0.0029421 | 0.00073736
95 | 0.98849 | -0.2215 | 0.0093186 | 0.0023355
96 | 0.98873 | -0.2169 | 0.0029472 | 0.00073863
97 | 0.98876 | -0.21636 | 0.0029421 | 0.00073736
98 | 0.98879 | -0.21577 | 0.0029421 | 0.00073736
99 | 0.99269 | -0.1401 | 0.011515 | 0.0028858
100 | 0.99261 | -0.14172 | 0.0019002 | 0.00047623
101 | 0.99309 | -0.13251 | 0.0019002 | 0.00047623
102 | 0.99219 | -0.14974 | 0.0033403 | 0.00083716
103 | 0.99359 | -0.12287 | 0.0019002 | 0.00047623
104 | 0.99133 | -0.1665 | 0.003168 | 0.00079397
105 | 0.9941 | -0.11304 | 0.001899 | 0.00047593
106 | 0.99095 | -0.17384 | 0.003164 | 0.00079298
107 | 0.99527 | -0.090559 | 0.0017075 | 0.00042794
108 | 0.98927 | -0.20637 | 0.014813 | 0.0037124
109 | 0.98965 | -0.19898 | 0.003168 | 0.00079397
110 | 0.98995 | -0.19326 | 0.003164 | 0.00079298
111 | 0.99026 | -0.18721 | 0.003166 | 0.00079347
112 | 0.99059 | -0.18081 | 0.003168 | 0.00079397
113 | 0.99064 | -0.17987 | 0.0025894 | 0.00064897
114 | 0.99772 | -0.043444 | 0.0017088 | 0.00042826
115 | 0.99756 | -0.046537 | 0.0017088 | 0.00042826
116 | 0.99697 | -0.057967 | 0.0017099 | 0.00042853
117 | 0.99637 | -0.06942 | 0.0017081 | 0.0004281
118 | 0.99578 | -0.080615 | 0.0017075 | 0.00042794
119 | 0.99582 | -0.079832 | 0.011342 | 0.0028426
120 | 0.98803 | -0.23021 | 0.0032191 | 0.00080678
121 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.036424 | -0.0091309 | 0.036448 | 0.0091458 | 2.3622e-05 | 1.4849e-05 | 0.054823 | 0.054823 | 0.054823 | 0.98864 | -0.21835 | 0.98934 | -0.20474 | 15.0614
1 | 0.021988 | 0.0055128 | -0.021984 | -0.0055107 | 3.4212e-06 | 2.0828e-06 | 0.033095 | 0.033095 | 0.033095 | 0.98864 | -0.21835 | 0.98847 | -0.22161 | 9.092
2 | -0.040009 | -0.010038 | 0.040011 | 0.01004 | 2.6588e-06 | 1.6765e-06 | 0.060179 | 0.060179 | 0.060179 | 0.98934 | -0.20474 | 0.98941 | -0.20335 | 16.5327
3 | 0.019085 | 0.004784 | -0.019085 | -0.0047839 | 1.3417e-07 | 8.0313e-08 | 0.02873 | 0.02873 | 0.02873 | 0.98847 | -0.22161 | 0.98846 | -0.22176 | 7.8929
4 | -0.043574 | -0.010933 | 0.043577 | 0.010935 | 3.1597e-06 | 1.997e-06 | 0.065537 | 0.065537 | 0.065537 | 0.98941 | -0.20335 | 0.98949 | -0.20183 | 18.0046
5 | 0.016162 | 0.0040514 | -0.016162 | -0.0040514 | 1.0893e-07 | 6.3427e-08 | 0.02433 | 0.02433 | 0.02433 | 0.98846 | -0.22176 | 0.98846 | -0.2219 | 6.6842
6 | -0.046463 | -0.011658 | 0.046467 | 0.01166 | 3.5768e-06 | 2.2641e-06 | 0.069877 | 0.069877 | 0.069877 | 0.98949 | -0.20183 | 0.98957 | -0.20022 | 19.1969
7 | 0.013251 | 0.0033218 | -0.013251 | -0.0033217 | 6.9605e-08 | 3.8568e-08 | 0.019948 | 0.019948 | 0.019948 | 0.98846 | -0.2219 | 0.98845 | -0.22201 | 5.4802
8 | -0.049358 | -0.012385 | 0.049402 | 0.012413 | 4.4028e-05 | 2.7904e-05 | 0.074225 | 0.074225 | 0.074225 | 0.98957 | -0.20022 | 0.99054 | -0.18153 | 20.3914
9 | 0.0096614 | 0.0024222 | -0.009659 | -0.002421 | 2.3858e-06 | 1.1415e-06 | 0.014544 | 0.014545 | 0.014545 | 0.98845 | -0.22201 | 0.98818 | -0.22719 | 3.9958
10 | -0.056653 | -0.014209 | 0.056787 | 0.014294 | 0.00013374 | 8.4971e-05 | 0.085591 | 0.085591 | 0.085591 | 0.98497 | -0.28887 | 0.98751 | -0.23947 | 23.514
11 | 0.026918 | 0.006757 | -0.026888 | -0.0067389 | 2.9324e-05 | 1.8166e-05 | 0.040669 | 0.040669 | 0.040669 | 0.98497 | -0.28887 | 0.9838 | -0.31173 | 11.1728
12 | -0.066205 | -0.016655 | 0.066366 | 0.016757 | 0.00016125 | 0.00010265 | 0.099782 | 0.099782 | 0.099782 | 0.98751 | -0.23947 | 0.99014 | -0.18863 | 27.4126
13 | -0.11926 | -0.03009 | 0.11935 | 0.030143 | 8.3261e-05 | 5.3198e-05 | 0.1793 | 0.1793 | 0.1793 | 0.99014 | -0.18863 | 0.9909 | -0.17406 | 49.2591
14 | 0.052897 | 0.013332 | -0.052831 | -0.01329 | 6.5936e-05 | 4.1842e-05 | 0.079521 | 0.079522 | 0.079522 | 0.99014 | -0.18863 | 0.98879 | -0.21471 | 21.8466
15 | -0.12092 | -0.030537 | 0.1211 | 0.030655 | 0.00018399 | 0.00011756 | 0.18167 | 0.18167 | 0.18167 | 0.9909 | -0.17406 | 0.99254 | -0.14236 | 49.9084
16 | 0.052831 | 0.01329 | -0.052771 | -0.013252 | 5.9952e-05 | 3.8046e-05 | 0.079522 | 0.079522 | 0.079522 | 0.98879 | -0.21471 | 0.98757 | -0.2385 | 21.8466
17 | -0.12511 | -0.03166 | 0.12558 | 0.031958 | 0.00046684 | 0.00029832 | 0.18768 | 0.18768 | 0.18768 | 0.99254 | -0.14236 | 0.99659 | -0.064925 | 51.5603
18 | 0.03797 | 0.009543 | -0.037966 | -0.0095404 | 4.1078e-06 | 2.5862e-06 | 0.057221 | 0.057221 | 0.057221 | 0.98757 | -0.2385 | 0.98745 | -0.24076 | 15.72
19 | 0.009659 | 0.002421 | -0.0096578 | -0.0024204 | 1.2e-06 | 5.7424e-07 | 0.014545 | 0.014545 | 0.014545 | 0.98818 | -0.22719 | 0.98805 | -0.2298 | 3.9958
20 | 0.0064387 | 0.0016137 | -0.0064386 | -0.0016136 | 8.3279e-08 | 2.3049e-08 | 0.0096967 | 0.0096967 | 0.0096967 | 0.98805 | -0.2298 | 0.98804 | -0.23007 | 2.6639
21 | 0.088624 | 0.022368 | -0.088342 | -0.022188 | 0.00028147 | 0.00017959 | 0.13265 | 0.13265 | 0.13265 | 0.99453 | -0.1044 | 0.99108 | -0.17095 | 36.4435
22 | -0.11601 | -0.02923 | 0.11623 | 0.029371 | 0.00021953 | 0.00014025 | 0.17362 | 0.17362 | 0.17362 | 0.99453 | -0.1044 | 0.99659 | -0.064925 | 47.6991
23 | 0.080722 | 0.020278 | -0.080681 | -0.020252 | 4.0738e-05 | 2.5977e-05 | 0.12121 | 0.12121 | 0.12121 | 0.99108 | -0.17095 | 0.99054 | -0.18153 | 33.3002
24 | 0.2129 | 0.054147 | -0.21265 | -0.053985 | 0.00025555 | 0.00016215 | 0.31817 | 0.31817 | 0.31817 | 0.99659 | -0.064925 | 0.99528 | -0.08987 | 21.8523
25 | -0.45471 | -0.11548 | 0.45591 | 0.11624 | 0.0011934 | 0.00076234 | 0.67947 | 0.67947 | 0.67947 | 0.99659 | -0.064925 | 0.99944 | -0.010546 | 46.6671
26 | 0.2102 | 0.053373 | -0.21017 | -0.053351 | 3.3559e-05 | 2.129e-05 | 0.31451 | 0.31451 | 0.31451 | 0.99528 | -0.08987 | 0.99511 | -0.093188 | 21.6013
27 | -0.45776 | -0.1167 | 0.45799 | 0.11685 | 0.00023317 | 0.00014895 | 0.68223 | 0.68223 | 0.68223 | 0.99944 | -0.010546 | 1 | 0 | 46.8567
28 | 0.20773 | 0.052739 | -0.20768 | -0.05271 | 4.5725e-05 | 2.9002e-05 | 0.31086 | 0.31086 | 0.31086 | 0.99511 | -0.093188 | 0.99487 | -0.097764 | 21.3505
29 | 0.11842 | 0.030042 | -0.11836 | -0.030002 | 6.2311e-05 | 3.9809e-05 | 0.17634 | 0.17634 | 0.17634 | 1 | 0 | 0.99943 | -0.010949 | 48.4453
30 | 0.19929 | 0.050607 | -0.19914 | -0.050511 | 0.00015 | 9.5769e-05 | 0.29831 | 0.29831 | 0.29831 | 0.99487 | -0.097764 | 0.99405 | -0.11342 | 40.9767
31 | 0.1165 | 0.029538 | -0.11632 | -0.029422 | 0.00018165 | 0.00011605 | 0.17358 | 0.17358 | 0.17358 | 0.99943 | -0.010949 | 0.99772 | -0.043444 | 47.6869
32 | 0.037966 | 0.0095404 | -0.037924 | -0.0095141 | 4.1844e-05 | 2.6345e-05 | 0.057221 | 0.057221 | 0.057221 | 0.98745 | -0.24076 | 0.98626 | -0.26388 | 15.7201
33 | 0.0032191 | 0.00080677 | -0.0032191 | -0.00080678 | 2.0909e-08 | -1.7e-08 | 0.0048481 | 0.0048481 | 0.0048481 | 0.98804 | -0.23007 | 0.98803 | -0.23021 | 1.3319
34 | -0.079348 | -0.020097 | 0.0795 | 0.020194 | 0.00015179 | 9.678e-05 | 0.11945 | 0.11945 | 0.11945 | 0.98905 | -0.20951 | 0.99111 | -0.16976 | 32.8169
35 | 0.075243 | 0.019069 | -0.075111 | -0.018985 | 0.00013179 | 8.3992e-05 | 0.11328 | 0.11328 | 0.11328 | 0.98905 | -0.20951 | 0.98716 | -0.24603 | 31.1203
36 | -0.082805 | -0.021023 | 0.08287 | 0.021064 | 6.4943e-05 | 4.1419e-05 | 0.12442 | 0.12442 | 0.12442 | 0.99111 | -0.16976 | 0.99196 | -0.15347 | 34.1803
37 | 0.072234 | 0.018263 | -0.07221 | -0.018248 | 2.3545e-05 | 1.5001e-05 | 0.10894 | 0.10894 | 0.10894 | 0.98716 | -0.24603 | 0.9868 | -0.25283 | 29.9287
38 | 0.046341 | 0.01165 | -0.046281 | -0.011613 | 5.9301e-05 | 3.7531e-05 | 0.069527 | 0.069527 | 0.069527 | 0.99196 | -0.15347 | 0.99058 | -0.18031 | 19.1009
39 | -0.12921 | -0.032714 | 0.12946 | 0.032873 | 0.00024903 | 0.00015915 | 0.19394 | 0.19394 | 0.19394 | 0.99196 | -0.15347 | 0.99405 | -0.11342 | 53.2811
40 | 0.069338 | 0.017528 | -0.069319 | -0.017517 | 1.8583e-05 | 1.1835e-05 | 0.10461 | 0.10461 | 0.10461 | 0.9868 | -0.25283 | 0.98652 | -0.25842 | 28.7387
41 | 0.036618 | 0.0091907 | -0.036599 | -0.0091789 | 1.8793e-05 | 1.1814e-05 | 0.055011 | 0.055011 | 0.055011 | 0.99058 | -0.18031 | 0.99002 | -0.19108 | 15.1129
42 | 0.06968 | 0.017638 | -0.069564 | -0.017564 | 0.00011587 | 7.3787e-05 | 0.10437 | 0.10437 | 0.10437 | 0.99405 | -0.11342 | 0.99225 | -0.14812 | 28.6724
43 | 0.066441 | 0.016795 | -0.06638 | -0.016756 | 6.1226e-05 | 3.8978e-05 | 0.10027 | 0.10027 | 0.10027 | 0.98652 | -0.25842 | 0.98552 | -0.27766 | 27.5464
44 | 0.033685 | 0.0084485 | -0.033679 | -0.0084447 | 6.0838e-06 | 3.8123e-06 | 0.050631 | 0.050631 | 0.050631 | 0.99002 | -0.19108 | 0.98983 | -0.19487 | 13.9096
45 | 0.066297 | 0.016745 | -0.066291 | -0.016742 | 5.3815e-06 | 3.4254e-06 | 0.099467 | 0.099467 | 0.099467 | 0.99225 | -0.14812 | 0.99216 | -0.14981 | 27.3262
46 | 0.06454 | 0.016295 | -0.064522 | -0.016284 | 1.7748e-05 | 1.1295e-05 | 0.09749 | 0.09749 | 0.09749 | 0.98552 | -0.27766 | 0.98523 | -0.2834 | 26.7829
47 | -0.044434 | -0.01119 | 0.044443 | 0.011195 | 8.7305e-06 | 5.5225e-06 | 0.067337 | 0.067337 | 0.067337 | 0.98219 | -0.3425 | 0.9824 | -0.33839 | 18.4991
48 | 0.042363 | 0.010671 | -0.04235 | -0.010662 | 1.3348e-05 | 8.4336e-06 | 0.064199 | 0.064199 | 0.064199 | 0.98219 | -0.3425 | 0.98185 | -0.34909 | 17.6372
49 | -0.047852 | -0.01205 | 0.047879 | 0.012067 | 2.7327e-05 | 1.7314e-05 | 0.0725 | 0.0725 | 0.0725 | 0.9824 | -0.33839 | 0.98301 | -0.32645 | 19.9177
50 | 0.04235 | 0.010662 | -0.042334 | -0.010652 | 1.5468e-05 | 9.7731e-06 | 0.064199 | 0.064199 | 0.064199 | 0.98185 | -0.34909 | 0.98146 | -0.35673 | 17.6372
51 | -0.050927 | -0.012831 | 0.050942 | 0.01284 | 1.5271e-05 | 9.6869e-06 | 0.077114 | 0.077114 | 0.077114 | 0.98301 | -0.32645 | 0.98333 | -0.32018 | 21.1851
52 | 0.00448 | 0.0011227 | -0.0044798 | -0.0011227 | 1.539e-07 | -1.392e-08 | 0.0067921 | 0.0067922 | 0.0067922 | 0.98146 | -0.35673 | 0.98142 | -0.35745 | 1.866
53 | 0.037854 | 0.0095297 | -0.037808 | -0.0095005 | 4.6499e-05 | 2.9285e-05 | 0.057407 | 0.057407 | 0.057407 | 0.98146 | -0.35673 | 0.98014 | -0.38246 | 15.7713
54 | -0.055689 | -0.01403 | 0.055694 | 0.014033 | 4.8207e-06 | 3.0623e-06 | 0.084297 | 0.084297 | 0.084297 | 0.98333 | -0.32018 | 0.98343 | -0.31837 | 23.1586
55 | 0.0044798 | 0.0011227 | -0.0044797 | -0.0011227 | 1.5554e-07 | -1.4059e-08 | 0.0067922 | 0.0067922 | 0.0067922 | 0.98142 | -0.35745 | 0.98139 | -0.35818 | 1.866
56 | 0.036288 | 0.0091197 | -0.036258 | -0.0091006 | 3.0247e-05 | 1.9024e-05 | 0.055101 | 0.055101 | 0.055101 | 0.98014 | -0.38246 | 0.97925 | -0.39994 | 15.1376
57 | -0.05831 | -0.014689 | 0.058385 | 0.014736 | 7.4997e-05 | 4.7672e-05 | 0.088255 | 0.088255 | 0.088255 | 0.98343 | -0.31837 | 0.98481 | -0.29152 | 24.246
58 | 0.031849 | 0.0079955 | -0.031826 | -0.0079816 | 2.2076e-05 | 1.3813e-05 | 0.0484 | 0.0484 | 0.0484 | 0.97925 | -0.39994 | 0.97851 | -0.41448 | 13.2968
59 | -0.060439 | -0.015251 | 0.060441 | 0.015252 | 1.5616e-06 | 9.9309e-07 | 0.091359 | 0.091359 | 0.091359 | 0.98481 | -0.29152 | 0.98484 | -0.29098 | 25.0987
60 | -0.062657 | -0.015808 | 0.06268 | 0.015822 | 2.2758e-05 | 1.4479e-05 | 0.094707 | 0.094707 | 0.094707 | 0.98484 | -0.29098 | 0.98523 | -0.2834 | 26.0185
61 | 0.024034 | 0.0060286 | -0.024022 | -0.0060214 | 1.1652e-05 | 7.1652e-06 | 0.03655 | 0.03655 | 0.03655 | 0.97851 | -0.41448 | 0.97799 | -0.42465 | 10.0412
62 | 0.013286 | 0.0033307 | -0.013282 | -0.0033288 | 3.4471e-06 | 1.924e-06 | 0.020215 | 0.020215 | 0.020215 | 0.97799 | -0.42465 | 0.97771 | -0.4301 | 5.5535
63 | 0.0044474 | 0.0011145 | -0.004447 | -0.0011145 | 3.3553e-07 | -3.017e-08 | 0.0067685 | 0.0067686 | 0.0067686 | 0.97771 | -0.4301 | 0.97763 | -0.43168 | 1.8595
64 | 0.051145 | 0.012915 | -0.051145 | -0.012915 | 8.9233e-08 | 5.6593e-08 | 0.076857 | 0.076857 | 0.076857 | 0.99065 | -0.17893 | 0.99065 | -0.17896 | 21.1146
65 | -0.052743 | -0.013315 | 0.052746 | 0.013317 | 3.7124e-06 | 2.3556e-06 | 0.079257 | 0.079257 | 0.079257 | 0.99065 | -0.17893 | 0.99072 | -0.17746 | 21.774
66 | 0.049665 | 0.012544 | -0.049582 | -0.012491 | 8.3258e-05 | 5.2773e-05 | 0.074635 | 0.074635 | 0.074635 | 0.99065 | -0.17896 | 0.98883 | -0.21401 | 20.5041
67 | -0.057237 | -0.014443 | 0.057297 | 0.014481 | 6.0207e-05 | 3.8253e-05 | 0.086002 | 0.086002 | 0.086002 | 0.99072 | -0.17746 | 0.99186 | -0.15552 | 23.6269
68 | 0.046728 | 0.011776 | -0.046705 | -0.011761 | 2.3679e-05 | 1.4991e-05 | 0.070341 | 0.070341 | 0.070341 | 0.98883 | -0.21401 | 0.98828 | -0.22461 | 19.3244
69 | -0.059739 | -0.015093 | 0.059751 | 0.015101 | 1.1723e-05 | 7.4528e-06 | 0.089665 | 0.089665 | 0.089665 | 0.99186 | -0.15552 | 0.99207 | -0.15143 | 24.6332
70 | 0.04444 | 0.011193 | -0.044424 | -0.011183 | 1.6162e-05 | 1.0221e-05 | 0.066931 | 0.066931 | 0.066931 | 0.98828 | -0.22461 | 0.98789 | -0.23222 | 18.3876
71 | -0.06302 | -0.01592 | 0.063025 | 0.015923 | 4.8689e-06 | 3.0974e-06 | 0.094569 | 0.094569 | 0.094569 | 0.99207 | -0.15143 | 0.99216 | -0.14981 | 25.9804
72 | 0.042157 | 0.010615 | -0.042084 | -0.010569 | 7.3215e-05 | 4.6239e-05 | 0.063517 | 0.063517 | 0.063517 | 0.98789 | -0.23222 | 0.98602 | -0.26861 | 17.4497
73 | -0.014625 | -0.0036657 | 0.014629 | 0.0036677 | 3.4409e-06 | 1.9588e-06 | 0.022 | 0.022 | 0.022 | 0.9892 | -0.20707 | 0.98945 | -0.20214 | 6.0441
74 | 0.0083034 | 0.0020813 | -0.0083029 | -0.0020811 | 4.4459e-07 | 1.8699e-07 | 0.012491 | 0.012491 | 0.012491 | 0.9892 | -0.20707 | 0.98914 | -0.2082 | 3.4315
75 | -0.017543 | -0.0043979 | 0.017546 | 0.0044 | 3.4975e-06 | 2.0662e-06 | 0.026382 | 0.026382 | 0.026382 | 0.98945 | -0.20214 | 0.98967 | -0.19795 | 7.2479
76 | 0.0083029 | 0.0020811 | -0.0083015 | -0.0020805 | 1.3671e-06 | 5.7506e-07 | 0.012491 | 0.012491 | 0.012491 | 0.98914 | -0.2082 | 0.98896 | -0.21165 | 3.4315
77 | -0.019721 | -0.0049451 | 0.019722 | 0.0049454 | 4.4489e-07 | 2.6739e-07 | 0.029653 | 0.029653 | 0.029653 | 0.98967 | -0.19795 | 0.98969 | -0.19748 | 8.1464
78 | 0.003222 | 0.00080746 | -0.0032219 | -0.00080749 | 4.5788e-08 | -3.7358e-08 | 0.0048479 | 0.0048479 | 0.0048479 | 0.98896 | -0.21165 | 0.98895 | -0.21195 | 1.3318
79 | -0.027925 | -0.0070014 | 0.027927 | 0.0070027 | 2.0531e-06 | 1.2741e-06 | 0.041987 | 0.041987 | 0.041987 | 0.98969 | -0.19748 | 0.98977 | -0.19594 | 11.5348
80 | -0.0308 | -0.0077226 | 0.030801 | 0.0077236 | 1.5698e-06 | 9.796e-07 | 0.046305 | 0.046305 | 0.046305 | 0.98977 | -0.19594 | 0.98983 | -0.19487 | 12.7212
81 | -0.01736 | -0.0043513 | 0.01736 | 0.0043514 | 4.2496e-08 | 2.511e-08 | 0.02626 | 0.02626 | 0.02626 | 0.98371 | -0.31355 | 0.98372 | -0.3135 | 7.2142
82 | 0.011889 | 0.0029801 | -0.011887 | -0.0029792 | 1.738e-06 | 9.304e-07 | 0.017984 | 0.017984 | 0.017984 | 0.98371 | -0.31355 | 0.98356 | -0.31662 | 4.9406
83 | -0.023863 | -0.0059812 | 0.023881 | 0.0059921 | 1.7666e-05 | 1.0847e-05 | 0.036097 | 0.036097 | 0.036097 | 0.98372 | -0.3135 | 0.98451 | -0.29797 | 9.9168
84 | -0.026378 | -0.006618 | 0.0264 | 0.0066316 | 2.2032e-05 | 1.363e-05 | 0.039871 | 0.039871 | 0.039871 | 0.98451 | -0.29797 | 0.98541 | -0.28047 | 10.9537
85 | -0.028665 | -0.0071993 | 0.028682 | 0.0072093 | 1.6227e-05 | 1.0091e-05 | 0.043291 | 0.043291 | 0.043291 | 0.98541 | -0.28047 | 0.98602 | -0.26861 | 11.8932
86 | 0.013402 | 0.0033593 | -0.013402 | -0.0033591 | 3.3272e-07 | 1.8528e-07 | 0.020225 | 0.020225 | 0.020225 | 0.98602 | -0.26861 | 0.98599 | -0.26913 | 5.5565
87 | -0.010344 | -0.0025924 | 0.010346 | 0.0025935 | 2.1946e-06 | 1.0997e-06 | 0.01563 | 0.015629 | 0.01563 | 0.98478 | -0.29275 | 0.98501 | -0.2883 | 4.2938
88 | -0.010346 | -0.0025935 | 0.010348 | 0.0025944 | 1.7259e-06 | 8.647e-07 | 0.015629 | 0.015629 | 0.015629 | 0.98501 | -0.2883 | 0.98519 | -0.2848 | 4.2938
89 | -0.016934 | -0.0042449 | 0.016941 | 0.0042491 | 7.0351e-06 | 4.1371e-06 | 0.025577 | 0.025576 | 0.025577 | 0.98519 | -0.2848 | 0.98564 | -0.27608 | 7.0265
90 | -0.028069 | -0.007038 | 0.028085 | 0.0070482 | 1.6338e-05 | 1.0147e-05 | 0.042377 | 0.042376 | 0.042377 | 0.98564 | -0.27608 | 0.98626 | -0.26388 | 11.6419
91 | -0.0051087 | -0.0012804 | 0.0051091 | 0.0012804 | 3.8387e-07 | 2.409e-08 | 0.0076931 | 0.007693 | 0.0076931 | 0.98814 | -0.2283 | 0.98822 | -0.22672 | 2.1135
92 | -0.017031 | -0.0042683 | 0.017035 | 0.0042708 | 4.2395e-06 | 2.493e-06 | 0.025644 | 0.025644 | 0.025644 | 0.98822 | -0.22672 | 0.98849 | -0.2215 | 7.0451
93 | 0.010477 | 0.0026262 | -0.010476 | -0.0026255 | 1.3571e-06 | 6.8397e-07 | 0.015812 | 0.015812 | 0.015812 | 0.98599 | -0.26913 | 0.98585 | -0.27185 | 4.344
94 | 0.0058856 | 0.001475 | -0.0058842 | -0.0014747 | 1.3592e-06 | 2.8443e-07 | 0.0088835 | 0.0088837 | 0.0088837 | 0.98585 | -0.27185 | 0.9856 | -0.2767 | 2.4406
95 | 0.0029421 | 0.00073736 | -0.0029421 | -0.00073736 | 1.8744e-09 | -2.0284e-09 | 0.0044418 | 0.0044418 | 0.0044418 | 0.9856 | -0.2767 | 0.9856 | -0.27671 | 1.2203
96 | -0.026354 | -0.0066062 | 0.026359 | 0.0066098 | 5.7727e-06 | 3.5691e-06 | 0.039672 | 0.039672 | 0.039672 | 0.98849 | -0.2215 | 0.98873 | -0.2169 | 10.8988
97 | -0.029307 | -0.0073484 | 0.029307 | 0.0073489 | 7.4911e-07 | 4.6626e-07 | 0.044107 | 0.044107 | 0.044107 | 0.98873 | -0.2169 | 0.98876 | -0.21636 | 12.1173
98 | -0.032249 | -0.0080862 | 0.03225 | 0.0080868 | 9.0629e-07 | 5.6687e-07 | 0.048535 | 0.048535 | 0.048535 | 0.98876 | -0.21636 | 0.98879 | -0.21577 | 13.3337
99 | -0.035192 | -0.0088242 | 0.035208 | 0.0088341 | 1.5773e-05 | 9.9022e-06 | 0.052962 | 0.052962 | 0.052962 | 0.98879 | -0.21577 | 0.98927 | -0.20637 | 14.5501
100 | 0.077053 | 0.0194 | -0.077047 | -0.019397 | 5.9695e-06 | 3.8051e-06 | 0.11553 | 0.11553 | 0.11553 | 0.99269 | -0.1401 | 0.99261 | -0.14172 | 31.7396
101 | -0.088568 | -0.022286 | 0.0886 | 0.022307 | 3.2113e-05 | 2.049e-05 | 0.13279 | 0.13279 | 0.13279 | 0.99269 | -0.1401 | 0.99309 | -0.13251 | 36.4814
102 | 0.075147 | 0.01892 | -0.075118 | -0.018902 | 2.8794e-05 | 1.835e-05 | 0.11268 | 0.11268 | 0.11268 | 0.99261 | -0.14172 | 0.99219 | -0.14974 | 30.957
103 | -0.0905 | -0.022783 | 0.090542 | 0.02281 | 4.1734e-05 | 2.6632e-05 | 0.13564 | 0.13564 | 0.13564 | 0.99309 | -0.13251 | 0.99359 | -0.12287 | 37.2636
104 | 0.071778 | 0.018065 | -0.071721 | -0.018028 | 5.7446e-05 | 3.6595e-05 | 0.10767 | 0.10767 | 0.10767 | 0.99219 | -0.14974 | 0.99133 | -0.1665 | 29.5808
105 | -0.092442 | -0.023286 | 0.092486 | 0.023313 | 4.3489e-05 | 2.7755e-05 | 0.13849 | 0.13849 | 0.13849 | 0.99359 | -0.12287 | 0.9941 | -0.11304 | 38.0454
106 | 0.068553 | 0.017234 | -0.068529 | -0.017219 | 2.4027e-05 | 1.53e-05 | 0.10292 | 0.10292 | 0.10292 | 0.99133 | -0.1665 | 0.99095 | -0.17384 | 28.2744
107 | -0.094385 | -0.023789 | 0.094486 | 0.023854 | 0.00010164 | 6.4876e-05 | 0.14133 | 0.14133 | 0.14133 | 0.9941 | -0.11304 | 0.99527 | -0.090559 | 38.8263
108 | 0.065365 | 0.016426 | -0.065346 | -0.016414 | 1.8809e-05 | 1.1971e-05 | 0.098168 | 0.098168 | 0.098168 | 0.99095 | -0.17384 | 0.99064 | -0.17987 | 26.9692
109 | -0.096194 | -0.024282 | 0.09624 | 0.024312 | 4.5842e-05 | 2.9262e-05 | 0.14388 | 0.14388 | 0.14388 | 0.99527 | -0.090559 | 0.99578 | -0.080615 | 39.5276
110 | -0.050021 | -0.012546 | 0.050039 | 0.012558 | 1.7626e-05 | 1.1174e-05 | 0.075243 | 0.075243 | 0.075243 | 0.98927 | -0.20637 | 0.98965 | -0.19898 | 20.6711
111 | -0.053207 | -0.013352 | 0.053221 | 0.013361 | 1.452e-05 | 9.215e-06 | 0.080006 | 0.080006 | 0.080006 | 0.98965 | -0.19898 | 0.98995 | -0.19326 | 21.9797
112 | -0.056385 | -0.014154 | 0.056401 | 0.014164 | 1.6292e-05 | 1.0349e-05 | 0.084762 | 0.084762 | 0.084762 | 0.98995 | -0.19326 | 0.99026 | -0.18721 | 23.2863
113 | -0.059567 | -0.014958 | 0.059586 | 0.014969 | 1.8184e-05 | 1.156e-05 | 0.089519 | 0.089519 | 0.089519 | 0.99026 | -0.18721 | 0.99059 | -0.18081 | 24.5933
114 | -0.062754 | -0.015763 | 0.062756 | 0.015765 | 2.8143e-06 | 1.7903e-06 | 0.094278 | 0.094278 | 0.094278 | 0.99059 | -0.18081 | 0.99064 | -0.17987 | 25.9006
115 | 0.11461 | 0.028993 | -0.1146 | -0.028983 | 1.7008e-05 | 1.0865e-05 | 0.17103 | 0.17103 | 0.17103 | 0.99772 | -0.043444 | 0.99756 | -0.046537 | 46.9867
116 | 0.11289 | 0.028554 | -0.11283 | -0.028515 | 6.1869e-05 | 3.952e-05 | 0.16848 | 0.16848 | 0.16848 | 0.99756 | -0.046537 | 0.99697 | -0.057967 | 46.2865
117 | 0.11112 | 0.028086 | -0.11106 | -0.028047 | 6.0986e-05 | 3.8954e-05 | 0.16593 | 0.16593 | 0.16593 | 0.99697 | -0.057967 | 0.99637 | -0.06942 | 45.5854
118 | 0.10935 | 0.027619 | -0.10929 | -0.027584 | 5.4534e-05 | 3.4831e-05 | 0.16338 | 0.16338 | 0.16338 | 0.99637 | -0.06942 | 0.99582 | -0.079832 | 44.8846
119 | -0.097947 | -0.024739 | 0.097951 | 0.024742 | 3.6778e-06 | 2.3478e-06 | 0.14643 | 0.14643 | 0.14643 | 0.99578 | -0.080615 | 0.99582 | -0.079832 | 40.2285

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57992 | 0.14736

## res_load
| p_mw | q_mvar
0 | 0.014437 | 0.0036181
1 | 0.0035607 | 0.00089241
2 | 0.0028994 | 0.00072666
3 | 0.0035626 | 0.00089287
4 | 0.0029227 | 0.00073249
5 | 0.002886 | 0.00072329
6 | 0.0029112 | 0.00072961
7 | 0.0028916 | 0.0007247
8 | 0.0035893 | 0.00089957
9 | 0.029736 | 0.0074524
10 | 0.0094179 | 0.0023604
11 | 0.026888 | 0.0067389
12 | 0.0015739 | 0.00039446
13 | 0.0040109 | 0.0010052
14 | 0.014801 | 0.0037094
15 | 0.0032191 | 0.00080678
16 | 0.027383 | 0.0068629
17 | 0.0076206 | 0.0019099
18 | 0.031279 | 0.0078392
19 | 0.0024447 | 0.00061269
20 | 0.0018542 | 0.00046471
21 | 0.0024417 | 0.00061195
22 | 0.0018565 | 0.00046527
23 | 0.0083929 | 0.0021035
24 | 0.0018542 | 0.00046471
25 | 0.0032195 | 0.00080688
26 | 0.0041049 | 0.0010288
27 | 0.0033055 | 0.00082845
28 | 0.0028774 | 0.00072113
29 | 0.0028725 | 0.00071993
30 | 0.0096636 | 0.0024219
31 | 0.0028775 | 0.00072117
32 | 0.0029142 | 0.00073037
33 | 0.0032675 | 0.0008189
34 | 0.0018405 | 0.00046127
35 | 0.0020709 | 0.00051903
36 | 0.003409 | 0.00085438
37 | 0.0030477 | 0.00076384
38 | 0.0047473 | 0.0011898
39 | 0.0015194 | 0.0003808
40 | 0.0026159 | 0.0006556
41 | 0.0044797 | 0.0011227
42 | 0.0044097 | 0.0011052
43 | 0.0020543 | 0.00051486
44 | 0.0022158 | 0.00055533
45 | 0.0018425 | 0.00046177
46 | 0.0077927 | 0.001953
47 | 0.010736 | 0.0026908
48 | 0.008835 | 0.0022143
49 | 0.004447 | 0.0011145
50 | 0.001598 | 0.00040049
51 | 0.0014796 | 0.00037083
52 | 0.0044906 | 0.0011255
53 | 0.0028534 | 0.00071513
54 | 0.0024417 | 0.00061195
55 | 0.0022649 | 0.00056765
56 | 0.0032693 | 0.00081936
57 | 0.0022667 | 0.00056809
58 | 0.0032664 | 0.00081863
59 | 0.006322 | 0.0015844
60 | 0.0029138 | 0.00073027
61 | 0.0021751 | 0.00054514
62 | 0.0050796 | 0.0012731
63 | 0.0082034 | 0.002056
64 | 0.0032219 | 0.00080749
65 | 0.0028725 | 0.00071993
66 | 0.0054713 | 0.0013712
67 | 0.0065033 | 0.0016299
68 | 0.011887 | 0.0029792
69 | 0.0024973 | 0.00062589
70 | 0.0022649 | 0.00056765
71 | 0.0028775 | 0.00072117
72 | 0.010344 | 0.0025924
73 | 0.0065859 | 0.0016506
74 | 0.011128 | 0.002789
75 | 0.0051087 | 0.0012804
76 | 0.011922 | 0.0029879
77 | 0.0098391 | 0.0024659
78 | 0.0029244 | 0.00073292
79 | 0.0045905 | 0.0011505
80 | 0.0029421 | 0.00073736
81 | 0.0029421 | 0.00073736
82 | 0.0093186 | 0.0023355
83 | 0.0029472 | 0.00073863
84 | 0.0029421 | 0.00073736
85 | 0.0029421 | 0.00073736
86 | 0.011515 | 0.0028858
87 | 0.0019002 | 0.00047623
88 | 0.0019002 | 0.00047623
89 | 0.0033403 | 0.00083716
90 | 0.0019002 | 0.00047623
91 | 0.003168 | 0.00079397
92 | 0.001899 | 0.00047593
93 | 0.003164 | 0.00079298
94 | 0.0017075 | 0.00042794
95 | 0.014813 | 0.0037124
96 | 0.003168 | 0.00079397
97 | 0.003164 | 0.00079298
98 | 0.003166 | 0.00079347
99 | 0.003168 | 0.00079397
100 | 0.0025894 | 0.00064897
101 | 0.0017088 | 0.00042826
102 | 0.0017088 | 0.00042826
103 | 0.0017099 | 0.00042853
104 | 0.0017081 | 0.0004281
105 | 0.0017075 | 0.00042794
106 | 0.011342 | 0.0028426
107 | 0.0032191 | 0.00080678

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1