## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1322-36_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1322-36_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1322-36_0_5_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_1322-36_0_5_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1322-36_0_5_node_33 | 0.4 | n |  | TRUE
5 | bus_LV_1322-36_0_5_node_77 | 0.4 | n |  | TRUE
6 | bus_LV_1322-36_0_5_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_1322-36_0_5_node_31 | 0.4 | n |  | TRUE
8 | bus_LV_1322-36_0_5_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1322-36_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1322-36_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1322-36_0_5_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1322-36_0_5_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_1322-36_0_5_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_1322-36_0_5_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_1322-36_0_5_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_1322-36_0_5_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_1322-36_0_5_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_1322-36_0_5_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_1322-36_0_5_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_1322-36_0_5_node_63 | 0.4 | n |  | TRUE
21 | bus_LV_1322-36_0_5_node_61 | 0.4 | n |  | TRUE
22 | bus_LV_1322-36_0_5_node_39 | 0.4 | n |  | TRUE
23 | bus_LV_1322-36_0_5_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_1322-36_0_5_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1322-36_0_5_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_1322-36_0_5_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_1322-36_0_5_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_1322-36_0_5_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_1322-36_0_5_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_1322-36_0_5_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_1322-36_0_5_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_1322-36_0_5_node_41 | 0.4 | n |  | TRUE
33 | bus_LV_1322-36_0_5_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_1322-36_0_5_node_42 | 0.4 | n |  | TRUE
35 | bus_LV_1322-36_0_5_node_62 | 0.4 | n |  | TRUE
36 | bus_LV_1322-36_0_5_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_1322-36_0_5_node_37 | 0.4 | n |  | TRUE
38 | bus_LV_1322-36_0_5_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_1322-36_0_5_node_40 | 0.4 | n |  | TRUE
40 | bus_LV_1322-36_0_5_node_60 | 0.4 | n |  | TRUE
41 | bus_LV_1322-36_0_5_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_1322-36_0_5_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_1322-36_0_5_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_1322-36_0_5_node_70 | 0.4 | n |  | TRUE
45 | bus_LV_1322-36_0_5_node_69 | 0.4 | n |  | TRUE
46 | bus_LV_1322-36_0_5_node_65 | 0.4 | n |  | TRUE
47 | bus_LV_1322-36_0_5_node_59 | 0.4 | n |  | TRUE
48 | bus_LV_1322-36_0_5_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_1322-36_0_5_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_1322-36_0_5_node_45 | 0.4 | n |  | TRUE
51 | bus_LV_1322-36_0_5_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_1322-36_0_5_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_1322-36_0_5_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_1322-36_0_5_node_49 | 0.4 | n |  | TRUE
55 | bus_LV_1322-36_0_5_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_1322-36_0_5_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_1322-36_0_5_node_52 | 0.4 | n |  | TRUE
58 | bus_LV_1322-36_0_5_node_76 | 0.4 | n |  | TRUE
59 | bus_LV_1322-36_0_5_node_66 | 0.4 | n |  | TRUE
60 | bus_LV_1322-36_0_5_node_71 | 0.4 | n |  | TRUE
61 | bus_LV_1322-36_0_5_node_75 | 0.4 | n |  | TRUE
62 | bus_LV_1322-36_0_5_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_1322-36_0_5_node_54 | 0.4 | n |  | TRUE
64 | bus_LV_1322-36_0_5_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_1322-36_0_5_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_1322-36_0_5_node_57 | 0.4 | n |  | TRUE
67 | bus_LV_1322-36_0_5_node_58 | 0.4 | n |  | TRUE
68 | bus_LV_1322-36_0_5_node_67 | 0.4 | n |  | TRUE
69 | bus_LV_1322-36_0_5_node_64 | 0.4 | n |  | TRUE
70 | bus_LV_1322-36_0_5_node_68 | 0.4 | n |  | TRUE
71 | bus_LV_1322-36_0_5_node_72 | 0.4 | n |  | TRUE
72 | bus_LV_1322-36_0_5_node_73 | 0.4 | n |  | TRUE
73 | bus_LV_1322-36_0_5_node_74 | 0.4 | n |  | TRUE
74 | bus_MV_15_0_node_44 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1322-36_0_5_load_0 | 0 | 0.00051472 | 0.000129 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1322-36_0_5_load_1 | 1 | 0.00047937 | 0.00012014 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1322-36_0_5_load_5 | 2 | 0.0034514 | 0.00086501 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1322-36_0_5_load_2 | 3 | 0.00075864 | 0.00019013 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1322-36_0_5_load_33 | 4 | 0.0034429 | 0.00086287 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1322-36_0_5_load_77 | 5 | 0.0035396 | 0.00088712 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1322-36_0_5_load_31 | 7 | 0.0021591 | 0.00054112 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1322-36_0_5_load_6 | 8 | 0.00043857 | 0.00010992 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1322-36_0_5_load_9 | 11 | 0.0021859 | 0.00054784 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1322-36_0_5_load_11 | 12 | 0.020865 | 0.0052291 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1322-36_0_5_load_12 | 13 | 0.019508 | 0.0048892 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1322-36_0_5_load_13 | 14 | 0.020791 | 0.0052107 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1322-36_0_5_load_14 | 15 | 0.020024 | 0.0050185 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1322-36_0_5_load_15 | 16 | 0.0062908 | 0.0015766 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1322-36_0_5_load_26 | 18 | 0.0049608 | 0.0012433 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1322-36_0_5_load_27 | 19 | 0.0048667 | 0.0012197 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1322-36_0_5_load_63 | 20 | 0.0036267 | 0.00090892 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1322-36_0_5_load_61 | 21 | 0.0035568 | 0.00089143 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1322-36_0_5_load_36 | 23 | 0.0044343 | 0.0011113 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1322-36_0_5_load_19 | 24 | 0.020791 | 0.0052107 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1322-36_0_5_load_20 | 25 | 0.024423 | 0.006121 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1322-36_0_5_load_22 | 27 | 0.03389 | 0.0084936 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1322-36_0_5_load_24 | 29 | 0.041896 | 0.0105 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1322-36_0_5_load_25 | 30 | 0.019221 | 0.0048173 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1322-36_0_5_load_28 | 31 | 0.021786 | 0.0054601 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1322-36_0_5_load_41 | 32 | 0.018303 | 0.0045871 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1322-36_0_5_load_29 | 33 | 0.016822 | 0.0042161 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1322-36_0_5_load_42 | 34 | 0.031905 | 0.0079962 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1322-36_0_5_load_62 | 35 | 0.0030409 | 0.00076213 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1322-36_0_5_load_35 | 36 | 0.0018016 | 0.00045154 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1322-36_0_5_load_37 | 37 | 0.005645 | 0.0014148 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1322-36_0_5_load_30 | 38 | 0.0094741 | 0.0023744 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1322-36_0_5_load_40 | 39 | 0.0076792 | 0.0019246 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1322-36_0_5_load_32 | 41 | 0.0041226 | 0.0010332 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1322-36_0_5_load_34 | 42 | 0.0018 | 0.00045112 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1322-36_0_5_load_38 | 43 | 0.0052856 | 0.0013247 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1322-36_0_5_load_70 | 44 | 0.0075988 | 0.0019044 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1322-36_0_5_load_69 | 45 | 0.0072869 | 0.0018263 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1322-36_0_5_load_43 | 48 | 0.016063 | 0.0040257 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1322-36_0_5_load_48 | 53 | 0.014896 | 0.0037334 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1322-36_0_5_load_49 | 54 | 0.017259 | 0.0043255 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1322-36_0_5_load_50 | 55 | 0.0035289 | 0.00088442 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1322-36_0_5_load_51 | 56 | 0.011515 | 0.0028859 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1322-36_0_5_load_52 | 57 | 0.016107 | 0.0040369 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1322-36_0_5_load_66 | 59 | 0.0063599 | 0.0015939 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1322-36_0_5_load_71 | 60 | 0.0043074 | 0.0010795 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1322-36_0_5_load_75 | 61 | 0.0036387 | 0.00091193 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1322-36_0_5_load_53 | 62 | 0.0063031 | 0.0015797 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1322-36_0_5_load_54 | 63 | 0.002038 | 0.00051078 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1322-36_0_5_load_56 | 65 | 0.0061572 | 0.0015431 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1322-36_0_5_load_57 | 66 | 0.0037674 | 0.00094421 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1322-36_0_5_load_58 | 67 | 0.016041 | 0.0040203 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1322-36_0_5_load_67 | 68 | 0.019632 | 0.0049203 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1322-36_0_5_load_64 | 69 | 0.0074166 | 0.0018588 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1322-36_0_5_load_68 | 70 | 0.019792 | 0.0049604 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1322-36_0_5_load_72 | 71 | 0.0035697 | 0.00089466 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1322-36_0_5_load_73 | 72 | 0.0042019 | 0.0010531 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1322-36_0_5_load_74 | 73 | 0.0033399 | 0.00083705 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1322-36_0_5_line_0 |  | 0 | 1 | 0.017501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1322-36_0_5_line_1 |  | 0 | 2 | 0.13917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1322-36_0_5_line_2 |  | 1 | 3 | 0.040791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1322-36_0_5_line_3 |  | 2 | 4 | 0.0063457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1322-36_0_5_line_4 |  | 3 | 5 | 0.099433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1322-36_0_5_line_5 |  | 4 | 7 | 0.013982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1322-36_0_5_line_6 |  | 5 | 6 | 0.0054906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1322-36_0_5_line_7 |  | 6 | 10 | 0.034362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1322-36_0_5_line_8 |  | 7 | 41 | 0.006062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1322-36_0_5_line_9 |  | 8 | 9 | 0.016727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1322-36_0_5_line_10 |  | 9 | 10 | 0.010734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1322-36_0_5_line_11 |  | 10 | 11 | 0.073545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1322-36_0_5_line_12 |  | 12 | 13 | 0.041663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1322-36_0_5_line_13 |  | 12 | 14 | 0.012136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1322-36_0_5_line_14 |  | 13 | 15 | 0.041029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1322-36_0_5_line_15 |  | 15 | 16 | 0.025004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1322-36_0_5_line_16 |  | 16 | 17 | 0.022515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1322-36_0_5_line_17 |  | 17 | 18 | 0.009394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1322-36_0_5_line_18 |  | 17 | 19 | 0.0074119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1322-36_0_5_line_19 |  | 18 | 22 | 0.013438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1322-36_0_5_line_20 |  | 19 | 23 | 0.016043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_1322-36_0_5_line_21 |  | 20 | 21 | 0.021797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1322-36_0_5_line_22 |  | 21 | 35 | 0.024412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1322-36_0_5_line_23 |  | 22 | 35 | 0.028719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1322-36_0_5_line_24 |  | 22 | 36 | 0.026722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1322-36_0_5_line_25 |  | 23 | 37 | 0.00086121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1322-36_0_5_line_26 |  | 24 | 25 | 0.024133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1322-36_0_5_line_27 |  | 24 | 26 | 0.035945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1322-36_0_5_line_28 |  | 25 | 27 | 0.032189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1322-36_0_5_line_29 |  | 26 | 28 | 0.009965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1322-36_0_5_line_30 |  | 27 | 29 | 0.019441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_1322-36_0_5_line_31 |  | 28 | 30 | 0.027186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1322-36_0_5_line_32 |  | 29 | 31 | 0.025453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1322-36_0_5_line_33 |  | 30 | 32 | 0.035088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1322-36_0_5_line_34 |  | 31 | 33 | 0.039677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_1322-36_0_5_line_35 |  | 32 | 34 | 0.034666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1322-36_0_5_line_36 |  | 33 | 38 | 0.016984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_1322-36_0_5_line_37 |  | 36 | 42 | 0.0076618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1322-36_0_5_line_38 |  | 37 | 43 | 0.010743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_1322-36_0_5_line_39 |  | 38 | 39 | 0.01823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_1322-36_0_5_line_40 |  | 39 | 40 | 0.014155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_1322-36_0_5_line_41 |  | 40 | 46 | 0.012072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_1322-36_0_5_line_42 |  | 40 | 47 | 0.025344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_1322-36_0_5_line_43 |  | 41 | 42 | 0.024202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1322-36_0_5_line_44 |  | 43 | 44 | 0.015758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_1322-36_0_5_line_45 |  | 44 | 45 | 0.021734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_1322-36_0_5_line_46 |  | 45 | 67 | 0.0093419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_1322-36_0_5_line_47 |  | 46 | 68 | 0.056659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1322-36_0_5_line_48 |  | 46 | 69 | 0.045318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1322-36_0_5_line_49 |  | 46 | 59 | 0.064134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1322-36_0_5_line_50 |  | 47 | 66 | 0.0089704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_1322-36_0_5_line_51 |  | 48 | 49 | 0.019805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1322-36_0_5_line_52 |  | 48 | 50 | 0.021752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1322-36_0_5_line_53 |  | 49 | 51 | 0.035852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1322-36_0_5_line_54 |  | 49 | 52 | 0.014989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1322-36_0_5_line_55 |  | 49 | 53 | 0.016804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1322-36_0_5_line_56 |  | 50 | 54 | 0.007401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1322-36_0_5_line_57 |  | 51 | 55 | 0.023511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1322-36_0_5_line_58 |  | 52 | 56 | 0.033603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1322-36_0_5_line_59 |  | 53 | 57 | 0.0060603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1322-36_0_5_line_60 |  | 55 | 58 | 0.0093454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1322-36_0_5_line_61 |  | 56 | 59 | 0.020982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1322-36_0_5_line_62 |  | 57 | 60 | 0.031524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1322-36_0_5_line_63 |  | 58 | 61 | 0.016915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1322-36_0_5_line_64 |  | 61 | 73 | 0.0016321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1322-36_0_5_line_65 |  | 62 | 63 | 0.014719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_1322-36_0_5_line_66 |  | 62 | 64 | 0.01019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_1322-36_0_5_line_67 |  | 63 | 65 | 0.0045006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_1322-36_0_5_line_68 |  | 64 | 66 | 0.03106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_1322-36_0_5_line_69 |  | 65 | 67 | 0.018658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_1322-36_0_5_line_70 |  | 68 | 70 | 0.019445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1322-36_0_5_line_71 |  | 71 | 72 | 0.022473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1322-36_0_5_line_72 |  | 71 | 73 | 0.0059073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1322-36_0_5_trafo_24 | 0.63 MVA 20/0.4 kV | 74 | 29 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2697888.9024 | 1227636.7014 | 2697906.0222 | 1227640.3322
1 | 2697800.8559 | 1227744.4742 | 2697888.9024 | 1227636.7014
2 | 2697906.0222 | 1227640.3322 | 2697908.7189 | 1227640.9041 | 2697933.3365 | 1227650.5829 | 2697943.2687 | 1227656.5414
3 | 2697800.8559 | 1227744.4742 | 2697805.2908 | 1227749.0129
4 | 2698035.8244 | 1227620.2042 | 2697943.2687 | 1227656.5414
5 | 2697815.0623 | 1227759.0131 | 2697805.2908 | 1227749.0129
6 | 2698041.2125 | 1227621.2606 | 2698035.8244 | 1227620.2042
7 | 2698041.2125 | 1227621.2606 | 2698040.497 | 1227626.0411 | 2698060.7655 | 1227647.5685
8 | 2697815.0623 | 1227759.0131 | 2697819.2989 | 1227763.3489
9 | 2698055.6754 | 1227657.0248 | 2698049.4616 | 1227672.5545
10 | 2698060.7655 | 1227647.5685 | 2698055.6754 | 1227657.0248
11 | 2698095.6907 | 1227624.1829 | 2698109.5758 | 1227626.0465 | 2698111.8182 | 1227629.7862 | 2698107.0226 | 1227635.1665 | 2698086.3517 | 1227641.2524 | 2698067.7722 | 1227644.1482 | 2698060.7655 | 1227647.5685
12 | 2697761.2764 | 1227820.0161 | 2697800.9735 | 1227832.6643
13 | 2697761.2764 | 1227820.0161 | 2697749.7134 | 1227816.332
14 | 2697800.9735 | 1227832.6643 | 2697840.0659 | 1227845.1197
15 | 2697859.266 | 1227838.5846 | 2697856.9649 | 1227845.0115 | 2697850.1949 | 1227848.347 | 2697840.0659 | 1227845.1197
16 | 2697866.8557 | 1227817.3875 | 2697859.266 | 1227838.5846
17 | 2697866.8557 | 1227817.3875 | 2697858.0373 | 1227814.1498
18 | 2697866.8557 | 1227817.3875 | 2697873.8135 | 1227819.9419
19 | 2697845.4224 | 1227809.5182 | 2697858.0373 | 1227814.1498
20 | 2697873.8135 | 1227819.9419 | 2697888.8741 | 1227825.4709
21 | 2697795.3602 | 1227791.7203 | 2697774.8227 | 1227784.4189
22 | 2697795.3602 | 1227791.7203 | 2697818.3623 | 1227799.8979
23 | 2697845.4224 | 1227809.5182 | 2697818.3623 | 1227799.8979
24 | 2697845.4224 | 1227809.5182 | 2697849.0169 | 1227799.2699 | 2697848.1147 | 1227792.8393 | 2697841.5676 | 1227786.139
25 | 2697889.6825 | 1227825.7677 | 2697888.8741 | 1227825.4709
26 | 2697762.1952 | 1227883.2812 | 2697773.1845 | 1227883.7621 | 2697785.723 | 1227887.6677
27 | 2697735.5208 | 1227905.6257 | 2697743.6327 | 1227893.0388 | 2697762.1952 | 1227883.2812
28 | 2697816.4557 | 1227897.2405 | 2697785.723 | 1227887.6677
29 | 2697735.5208 | 1227905.6257 | 2697739.2188 | 1227914.8821
30 | 2697835.0174 | 1227903.0222 | 2697816.4557 | 1227897.2405
31 | 2697739.2188 | 1227914.8821 | 2697764.7584 | 1227924.1993
32 | 2697835.0174 | 1227903.0222 | 2697851.4994 | 1227908.1562 | 2697858.6207 | 1227904.1926 | 2697858.6572 | 1227904.2083
33 | 2697764.7584 | 1227924.1993 | 2697797.7212 | 1227936.2247
34 | 2697858.6572 | 1227904.2083 | 2697895.1365 | 1227919.8143
35 | 2697797.7212 | 1227936.2247 | 2697830.2874 | 1227948.1054
36 | 2697895.1365 | 1227919.8143 | 2697910.7517 | 1227926.4946
37 | 2697836.213 | 1227780.659 | 2697841.5676 | 1227786.139
38 | 2697899.7676 | 1227829.4702 | 2697889.6825 | 1227825.7677
39 | 2697927.5122 | 1227933.6649 | 2697910.7517 | 1227926.4946
40 | 2697940.5264 | 1227939.2325 | 2697927.5122 | 1227933.6649
41 | 2697932.6898 | 1227948.4323 | 2697940.5264 | 1227939.2325
42 | 2697954.8621 | 1227918.3089 | 2697940.5264 | 1227939.2325
43 | 2697819.2989 | 1227763.3489 | 2697836.213 | 1227780.659
44 | 2697913.451 | 1227837.159 | 2697903.2581 | 1227830.7516 | 2697899.7676 | 1227829.4702
45 | 2697913.451 | 1227837.159 | 2697931.8516 | 1227848.7258
46 | 2697931.8516 | 1227848.7258 | 2697939.7606 | 1227853.6975
47 | 2697932.6898 | 1227948.4323 | 2697900.9963 | 1227960.7419 | 2697879.9746 | 1227952.2842
48 | 2697932.6898 | 1227948.4323 | 2697932.5373 | 1227954.4675 | 2697919.407 | 1227991.4893
49 | 2697932.6898 | 1227948.4323 | 2697921.8002 | 1227956.6257 | 2697900.6394 | 1227965.3838 | 2697874.6482 | 1227974.6821
50 | 2697954.8621 | 1227918.3089 | 2697959.3314 | 1227910.5311
51 | 2697836.4675 | 1228015.6201 | 2697817.8697 | 1228008.812
52 | 2697797.4437 | 1228001.3348 | 2697817.8697 | 1228008.812
53 | 2697836.4675 | 1228015.6201 | 2697827.4008 | 1228050.3072
54 | 2697836.4675 | 1228015.6201 | 2697838.7954 | 1228000.8143
55 | 2697836.4675 | 1228015.6201 | 2697852.2234 | 1228021.462
56 | 2697797.4437 | 1228001.3348 | 2697794.7459 | 1228008.2288
57 | 2697827.4008 | 1228050.3072 | 2697822.6994 | 1228073.3437
58 | 2697838.7954 | 1228000.8143 | 2697840.2282 | 1227984.6706 | 2697843.9446 | 1227981.2849 | 2697856.2048 | 1227982.9144
59 | 2697857.9057 | 1228023.5689 | 2697852.2234 | 1228021.462
60 | 2697820.8307 | 1228082.5003 | 2697822.6994 | 1228073.3437
61 | 2697874.6482 | 1227974.6821 | 2697873.1248 | 1227975.2271 | 2697860.2719 | 1227983.455 | 2697856.2048 | 1227982.9144
62 | 2697857.9057 | 1228023.5689 | 2697887.4633 | 1228034.5282
63 | 2697820.8307 | 1228082.5003 | 2697837.297 | 1228086.3683
64 | 2697837.297 | 1228086.3683 | 2697838.8859 | 1228086.7415
65 | 2697971.8289 | 1227873.8561 | 2697959.3672 | 1227866.0225
66 | 2697974.8061 | 1227883.601 | 2697971.8289 | 1227873.8561
67 | 2697955.5569 | 1227863.6273 | 2697959.3672 | 1227866.0225
68 | 2697974.8061 | 1227883.601 | 2697959.3314 | 1227910.5311
69 | 2697955.5569 | 1227863.6273 | 2697939.7606 | 1227853.6975
70 | 2697879.9746 | 1227952.2842 | 2697861.9346 | 1227945.0261
71 | 2697844.6366 | 1228088.0923 | 2697851.8295 | 1228089.782 | 2697850.4499 | 1228094.863 | 2697848.2073 | 1228103.1098 | 2697847.8763 | 1228104.3386 | 2697847.8763 | 1228104.3386
72 | 2697844.6366 | 1228088.0923 | 2697838.8859 | 1228086.7415

## bus_geodata
| x | y | coords
0 | 2697888.9024 | 1227636.7014
1 | 2697906.0222 | 1227640.3322
2 | 2697800.8559 | 1227744.4742
3 | 2697943.2687 | 1227656.5414
4 | 2697805.2908 | 1227749.0129
5 | 2698035.8244 | 1227620.2042
6 | 2698041.2125 | 1227621.2606
7 | 2697815.0623 | 1227759.0131
8 | 2698049.4616 | 1227672.5545
9 | 2698055.6754 | 1227657.0248
10 | 2698060.7655 | 1227647.5685
11 | 2698095.6907 | 1227624.1829
12 | 2697761.2764 | 1227820.0161
13 | 2697800.9735 | 1227832.6643
14 | 2697749.7134 | 1227816.332
15 | 2697840.0659 | 1227845.1197
16 | 2697859.266 | 1227838.5846
17 | 2697866.8557 | 1227817.3875
18 | 2697858.0373 | 1227814.1498
19 | 2697873.8135 | 1227819.9419
20 | 2697774.8227 | 1227784.4189
21 | 2697795.3602 | 1227791.7203
22 | 2697845.4224 | 1227809.5182
23 | 2697888.8741 | 1227825.4709
24 | 2697762.1952 | 1227883.2812
25 | 2697785.723 | 1227887.6677
26 | 2697735.5208 | 1227905.6257
27 | 2697816.4557 | 1227897.2405
28 | 2697739.2188 | 1227914.8821
29 | 2697835.0174 | 1227903.0222
30 | 2697764.7584 | 1227924.1993
31 | 2697858.6572 | 1227904.2083
32 | 2697797.7212 | 1227936.2247
33 | 2697895.1365 | 1227919.8143
34 | 2697830.2874 | 1227948.1054
35 | 2697818.3623 | 1227799.8979
36 | 2697841.5676 | 1227786.139
37 | 2697889.6825 | 1227825.7677
38 | 2697910.7517 | 1227926.4946
39 | 2697927.5122 | 1227933.6649
40 | 2697940.5264 | 1227939.2325
41 | 2697819.2989 | 1227763.3489
42 | 2697836.213 | 1227780.659
43 | 2697899.7676 | 1227829.4702
44 | 2697913.451 | 1227837.159
45 | 2697931.8516 | 1227848.7258
46 | 2697932.6898 | 1227948.4323
47 | 2697954.8621 | 1227918.3089
48 | 2697817.8697 | 1228008.812
49 | 2697836.4675 | 1228015.6201
50 | 2697797.4437 | 1228001.3348
51 | 2697827.4008 | 1228050.3072
52 | 2697838.7954 | 1228000.8143
53 | 2697852.2234 | 1228021.462
54 | 2697794.7459 | 1228008.2288
55 | 2697822.6994 | 1228073.3437
56 | 2697856.2048 | 1227982.9144
57 | 2697857.9057 | 1228023.5689
58 | 2697820.8307 | 1228082.5003
59 | 2697874.6482 | 1227974.6821
60 | 2697887.4634 | 1228034.5282
61 | 2697837.297 | 1228086.3683
62 | 2697971.8289 | 1227873.8561
63 | 2697959.3672 | 1227866.0225
64 | 2697974.8061 | 1227883.601
65 | 2697955.5569 | 1227863.6273
66 | 2697959.3314 | 1227910.5311
67 | 2697939.7606 | 1227853.6975
68 | 2697879.9746 | 1227952.2842
69 | 2697919.407 | 1227991.4893
70 | 2697861.9346 | 1227945.0261
71 | 2697844.6366 | 1228088.0923
72 | 2697847.8763 | 1228104.3386
73 | 2697838.8859 | 1228086.7415
74 | 2697735.5208 | 1227905.6257

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97282 | -0.52369 | 0.00051472 | 0.000129
1 | 0.97269 | -0.52608 | 0.00047937 | 0.00012014
2 | 0.97384 | -0.50339 | 0.0034514 | 0.00086501
3 | 0.97243 | -0.53129 | 0.00075864 | 0.00019013
4 | 0.97391 | -0.50206 | 0.0034429 | 0.00086287
5 | 0.97186 | -0.5426 | 0.0035396 | 0.00088712
6 | 0.97185 | -0.54287 | 0 | 0
7 | 0.9741 | -0.49825 | 0.0021591 | 0.00054112
8 | 0.97175 | -0.54476 | 0.00043857 | 0.00010992
9 | 0.97176 | -0.54462 | 0 | 0
10 | 0.97176 | -0.54453 | 0 | 0
11 | 0.97161 | -0.5475 | 0.0021859 | 0.00054784
12 | 0.97103 | -0.55877 | 0.020865 | 0.0052291
13 | 0.97265 | -0.52675 | 0.019508 | 0.0048892
14 | 0.9708 | -0.56344 | 0.020791 | 0.0052107
15 | 0.97499 | -0.48062 | 0.020024 | 0.0050185
16 | 0.97563 | -0.46822 | 0.0062908 | 0.0015766
17 | 0.97624 | -0.45621 | 0 | 0
18 | 0.97589 | -0.46307 | 0.0049608 | 0.0012433
19 | 0.97653 | -0.45045 | 0.0048667 | 0.0012197
20 | 0.97494 | -0.48171 | 0.0036267 | 0.00090892
21 | 0.97502 | -0.48026 | 0.0035568 | 0.00089143
22 | 0.97545 | -0.47166 | 0 | 0
23 | 0.97719 | -0.43754 | 0.0044343 | 0.0011113
24 | 0.9933 | -0.1283 | 0.020791 | 0.0052107
25 | 0.9953 | -0.089912 | 0.024423 | 0.006121
26 | 0.99101 | -0.17249 | 0 | 0
27 | 0.99868 | -0.0252 | 0.03389 | 0.0084936
28 | 0.99037 | -0.18478 | 0 | 0
29 | 1 | 0 | -0.56366 | -0.14445
30 | 0.98864 | -0.21838 | 0.019221 | 0.0048173
31 | 0.99682 | -0.059969 | 0.021786 | 0.0054601
32 | 0.98702 | -0.24985 | 0.018303 | 0.0045871
33 | 0.99212 | -0.14912 | 0.016822 | 0.0042161
34 | 0.986 | -0.26965 | 0.031905 | 0.0079962
35 | 0.97518 | -0.47704 | 0.0030409 | 0.00076213
36 | 0.97484 | -0.48376 | 0.0018016 | 0.00045154
37 | 0.97723 | -0.43682 | 0.005645 | 0.0014148
38 | 0.99019 | -0.18584 | 0.0094741 | 0.0023744
39 | 0.98818 | -0.22439 | 0.0076792 | 0.0019246
40 | 0.98665 | -0.25378 | 0 | 0
41 | 0.9742 | -0.49636 | 0.0041226 | 0.0010332
42 | 0.97467 | -0.48698 | 0.0018 | 0.00045112
43 | 0.9777 | -0.42752 | 0.0052856 | 0.0013247
44 | 0.97842 | -0.41339 | 0.0075988 | 0.0019044
45 | 0.97947 | -0.39294 | 0.0072869 | 0.0018263
46 | 0.9858 | -0.27019 | 0 | 0
47 | 0.9851 | -0.2836 | 0 | 0
48 | 0.97306 | -0.51857 | 0.016063 | 0.0040257
49 | 0.97368 | -0.50643 | 0 | 0
50 | 0.97271 | -0.52548 | 0 | 0
51 | 0.97306 | -0.51849 | 0 | 0
52 | 0.97489 | -0.48251 | 0 | 0
53 | 0.97312 | -0.51734 | 0.014896 | 0.0037334
54 | 0.97259 | -0.52783 | 0.017259 | 0.0043255
55 | 0.97266 | -0.5264 | 0.0035289 | 0.00088442
56 | 0.97761 | -0.42909 | 0.011515 | 0.0028859
57 | 0.97301 | -0.51962 | 0.016107 | 0.0040369
58 | 0.97253 | -0.52894 | 0 | 0
59 | 0.97954 | -0.3915 | 0.0063599 | 0.0015939
60 | 0.97288 | -0.52212 | 0.0043074 | 0.0010795
61 | 0.9723 | -0.53354 | 0.0036387 | 0.00091193
62 | 0.98209 | -0.34203 | 0.0063031 | 0.0015797
63 | 0.98123 | -0.3586 | 0.002038 | 0.00051078
64 | 0.9827 | -0.33019 | 0 | 0
65 | 0.98098 | -0.36362 | 0.0061572 | 0.0015431
66 | 0.98456 | -0.29418 | 0.0037674 | 0.00094421
67 | 0.97994 | -0.38375 | 0.016041 | 0.0040203
68 | 0.98374 | -0.31034 | 0.019632 | 0.0049203
69 | 0.98549 | -0.27622 | 0.0074166 | 0.0018588
70 | 0.98339 | -0.31727 | 0.019792 | 0.0049604
71 | 0.97224 | -0.53472 | 0.0035697 | 0.00089466
72 | 0.97215 | -0.53646 | 0.0042019 | 0.0010531
73 | 0.97229 | -0.53387 | 0.0033399 | 0.00083705
74 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0074086 | 0.0018556 | -0.0074077 | -0.0018552 | 8.4271e-07 | 3.2208e-07 | 0.011332 | 0.011332 | 0.011332 | 0.97282 | -0.52369 | 0.97269 | -0.52608 | 3.1131
1 | -0.0079233 | -0.0019846 | 0.007931 | 0.0019877 | 7.6644e-06 | 3.1755e-06 | 0.012119 | 0.012118 | 0.012119 | 0.97282 | -0.52369 | 0.97384 | -0.50339 | 3.3294
2 | 0.0069284 | 0.0017351 | -0.0069266 | -0.0017345 | 1.7183e-06 | 5.935e-07 | 0.010598 | 0.010599 | 0.010599 | 0.97269 | -0.52608 | 0.97243 | -0.53129 | 2.9117
3 | -0.011382 | -0.0028528 | 0.011383 | 0.0028531 | 7.198e-07 | 3.8172e-07 | 0.017392 | 0.017392 | 0.017392 | 0.97384 | -0.50339 | 0.97391 | -0.50206 | 4.7781
4 | 0.006168 | 0.0015444 | -0.0061647 | -0.0015435 | 3.3214e-06 | 8.9286e-07 | 0.0094378 | 0.0094382 | 0.0094382 | 0.97243 | -0.53129 | 0.97186 | -0.5426 | 2.5929
5 | -0.014826 | -0.003716 | 0.014829 | 0.0037176 | 2.6904e-06 | 1.5478e-06 | 0.022652 | 0.022652 | 0.022652 | 0.97391 | -0.50206 | 0.9741 | -0.49825 | 6.2232
6 | 0.002625 | 0.00065637 | -0.002625 | -0.00065641 | 3.3252e-08 | -4.6754e-08 | 0.0040186 | 0.0040187 | 0.0040187 | 0.97186 | -0.5426 | 0.97185 | -0.54287 | 1.104
7 | 0.002625 | 0.00065641 | -0.0026248 | -0.00065671 | 2.0811e-07 | -2.9255e-07 | 0.0040187 | 0.0040188 | 0.0040188 | 0.97185 | -0.54287 | 0.97176 | -0.54453 | 1.1041
8 | -0.016988 | -0.0042587 | 0.016989 | 0.0042596 | 1.5309e-06 | 9.0428e-07 | 0.025951 | 0.02595 | 0.025951 | 0.9741 | -0.49825 | 0.9742 | -0.49636 | 7.1293
9 | -0.00043857 | -0.00010992 | 0.00043857 | 0.00010971 | 2.8286e-09 | -2.0541e-07 | 0.00067156 | 0.00067149 | 0.00067156 | 0.97175 | -0.54476 | 0.97176 | -0.54462 | 0.1845
10 | -0.00043857 | -0.00010971 | 0.00043857 | 0.00010958 | 1.8149e-09 | -1.3182e-07 | 0.00067149 | 0.00067144 | 0.00067149 | 0.97176 | -0.54462 | 0.97176 | -0.54453 | 0.18448
11 | 0.0021862 | 0.00054713 | -0.0021859 | -0.00054784 | 3.0905e-07 | -7.132e-07 | 0.0033474 | 0.0033477 | 0.0033477 | 0.97176 | -0.54453 | 0.97161 | -0.5475 | 0.9197
12 | -0.04166 | -0.010443 | 0.041724 | 0.010483 | 6.3677e-05 | 4.0237e-05 | 0.063841 | 0.063841 | 0.063841 | 0.97103 | -0.55877 | 0.97265 | -0.52675 | 17.5387
13 | 0.020796 | 0.0052135 | -0.020791 | -0.0052107 | 4.6217e-06 | 2.8078e-06 | 0.031868 | 0.031868 | 0.031868 | 0.97103 | -0.55877 | 0.9708 | -0.56344 | 8.7549
14 | -0.061232 | -0.015372 | 0.061367 | 0.015458 | 0.00013504 | 8.5915e-05 | 0.093685 | 0.093685 | 0.093685 | 0.97265 | -0.52675 | 0.97499 | -0.48062 | 25.7377
15 | -0.081391 | -0.020477 | 0.081439 | 0.020506 | 4.8248e-05 | 2.9943e-05 | 0.12425 | 0.12425 | 0.12425 | 0.97499 | -0.48062 | 0.97563 | -0.46822 | 11.3778
16 | -0.08773 | -0.022083 | 0.087781 | 0.022115 | 5.0414e-05 | 3.1421e-05 | 0.13384 | 0.13384 | 0.13384 | 0.97563 | -0.46822 | 0.97624 | -0.45621 | 12.2564
17 | 0.039957 | 0.010037 | -0.039944 | -0.010029 | 1.3071e-05 | 8.2477e-06 | 0.060913 | 0.060913 | 0.060913 | 0.97624 | -0.45621 | 0.97589 | -0.46307 | 16.7342
18 | -0.12774 | -0.032151 | 0.12777 | 0.032174 | 3.514e-05 | 2.2211e-05 | 0.19475 | 0.19475 | 0.19475 | 0.97624 | -0.45621 | 0.97653 | -0.45045 | 17.8344
19 | 0.034984 | 0.0087853 | -0.034969 | -0.0087762 | 1.4342e-05 | 9.0112e-06 | 0.053348 | 0.053349 | 0.053349 | 0.97589 | -0.46307 | 0.97545 | -0.47166 | 14.6562
20 | -0.13264 | -0.033393 | 0.13272 | 0.033445 | 8.1966e-05 | 5.1855e-05 | 0.20217 | 0.20217 | 0.20217 | 0.97653 | -0.45045 | 0.97719 | -0.43754 | 18.5135
21 | -0.0036267 | -0.00090892 | 0.0036269 | 0.00090881 | 2.5043e-07 | -1.1155e-07 | 0.0055352 | 0.0055351 | 0.0055352 | 0.97494 | -0.48171 | 0.97502 | -0.48026 | 1.5207
22 | -0.0071837 | -0.0018002 | 0.0071848 | 0.0018006 | 1.1003e-06 | 3.997e-07 | 0.010963 | 0.010963 | 0.010963 | 0.97502 | -0.48026 | 0.97518 | -0.47704 | 3.0119
23 | 0.010228 | 0.0025641 | -0.010226 | -0.0025628 | 2.622e-06 | 1.3197e-06 | 0.015603 | 0.015603 | 0.015603 | 0.97545 | -0.47166 | 0.97518 | -0.47704 | 4.2866
24 | 0.024741 | 0.0062122 | -0.024726 | -0.0062033 | 1.4277e-05 | 8.8037e-06 | 0.037745 | 0.037745 | 0.037745 | 0.97545 | -0.47166 | 0.97484 | -0.48376 | 10.3696
25 | -0.13716 | -0.034556 | 0.13716 | 0.034559 | 4.6987e-06 | 2.9748e-06 | 0.20892 | 0.20892 | 0.20892 | 0.97719 | -0.43754 | 0.97723 | -0.43682 | 19.1319
26 | -0.090626 | -0.022869 | 0.090793 | 0.022976 | 0.00016694 | 0.00010653 | 0.13582 | 0.13582 | 0.13582 | 0.9933 | -0.1283 | 0.9953 | -0.089912 | 37.3128
27 | 0.069835 | 0.017659 | -0.069688 | -0.017565 | 0.00014769 | 9.4055e-05 | 0.10467 | 0.10467 | 0.10467 | 0.9933 | -0.1283 | 0.99101 | -0.17249 | 28.7562
28 | -0.11522 | -0.029097 | 0.11557 | 0.029326 | 0.00035848 | 0.00022901 | 0.17233 | 0.17233 | 0.17233 | 0.9953 | -0.089912 | 0.99868 | -0.0252 | 47.3438
29 | 0.069688 | 0.017565 | -0.069647 | -0.017538 | 4.0943e-05 | 2.6075e-05 | 0.10467 | 0.10467 | 0.10467 | 0.99101 | -0.17249 | 0.99037 | -0.18478 | 28.7562
30 | -0.14946 | -0.037819 | 0.14965 | 0.037935 | 0.00018099 | 0.00011533 | 0.22283 | 0.22283 | 0.22283 | 0.99868 | -0.0252 | 1 | 0 | 30.608
31 | 0.069647 | 0.017538 | -0.069535 | -0.017467 | 0.0001117 | 7.1137e-05 | 0.10467 | 0.10467 | 0.10467 | 0.99037 | -0.18478 | 0.98864 | -0.21838 | 28.7563
32 | 0.41237 | 0.10651 | -0.41117 | -0.10574 | 0.0012023 | 0.00076849 | 0.61474 | 0.61474 | 0.61474 | 1 | 0 | 0.99682 | -0.059969 | 56.2947
33 | 0.050314 | 0.01265 | -0.050238 | -0.012602 | 7.5486e-05 | 4.7862e-05 | 0.075743 | 0.075743 | 0.075743 | 0.98864 | -0.21838 | 0.98702 | -0.24985 | 20.8084
34 | 0.38938 | 0.10028 | -0.3877 | -0.099209 | 0.0016812 | 0.0010744 | 0.58222 | 0.58222 | 0.58222 | 0.99682 | -0.059969 | 0.99212 | -0.14912 | 53.3166
35 | 0.031935 | 0.0080151 | -0.031905 | -0.0079962 | 3.0138e-05 | 1.8846e-05 | 0.04815 | 0.04815 | 0.04815 | 0.98702 | -0.24985 | 0.986 | -0.26965 | 13.2279
36 | 0.37088 | 0.094993 | -0.37022 | -0.094572 | 0.00065863 | 0.00042087 | 0.55699 | 0.55699 | 0.55699 | 0.99212 | -0.14912 | 0.99019 | -0.18584 | 51.0062
37 | 0.022925 | 0.0057518 | -0.022921 | -0.0057497 | 3.5187e-06 | 2.1565e-06 | 0.034995 | 0.034995 | 0.034995 | 0.97484 | -0.48376 | 0.97467 | -0.48698 | 9.6141
38 | -0.14281 | -0.035974 | 0.14287 | 0.036014 | 6.3536e-05 | 4.0259e-05 | 0.21752 | 0.21752 | 0.21752 | 0.97723 | -0.43682 | 0.9777 | -0.42752 | 19.919
39 | 0.36074 | 0.092198 | -0.36007 | -0.091769 | 0.00067126 | 0.00042891 | 0.54275 | 0.54275 | 0.54275 | 0.99019 | -0.18584 | 0.98818 | -0.22439 | 49.7024
40 | 0.35239 | 0.089844 | -0.35189 | -0.089526 | 0.00049925 | 0.00031898 | 0.53119 | 0.53119 | 0.53119 | 0.98818 | -0.22439 | 0.98665 | -0.25378 | 48.6435
41 | 0.15302 | 0.038887 | -0.1529 | -0.03881 | 0.00012075 | 7.6973e-05 | 0.23097 | 0.23097 | 0.23097 | 0.98665 | -0.25378 | 0.9858 | -0.27019 | 31.7268
42 | 0.19887 | 0.050639 | -0.19859 | -0.050457 | 0.00028553 | 0.00018177 | 0.30022 | 0.30022 | 0.30022 | 0.98665 | -0.25378 | 0.9851 | -0.2836 | 27.4924
43 | -0.021112 | -0.0052928 | 0.021121 | 0.0052985 | 9.4377e-06 | 5.7387e-06 | 0.032247 | 0.032247 | 0.032247 | 0.9742 | -0.49636 | 0.97467 | -0.48698 | 8.8592
44 | -0.14815 | -0.037339 | 0.14826 | 0.037403 | 0.00010021 | 6.3544e-05 | 0.22556 | 0.22556 | 0.22556 | 0.9777 | -0.42752 | 0.97842 | -0.41339 | 20.6556
45 | -0.15585 | -0.039307 | 0.15601 | 0.039404 | 0.00015275 | 9.6939e-05 | 0.23712 | 0.23712 | 0.23712 | 0.97842 | -0.41339 | 0.97947 | -0.39294 | 21.7139
46 | -0.16329 | -0.04123 | 0.16337 | 0.041276 | 7.1928e-05 | 4.5681e-05 | 0.24819 | 0.24819 | 0.24819 | 0.97947 | -0.39294 | 0.97994 | -0.38375 | 22.7277
47 | 0.039507 | 0.0099323 | -0.039431 | -0.0098847 | 7.5586e-05 | 4.7654e-05 | 0.059644 | 0.059645 | 0.059645 | 0.9858 | -0.27019 | 0.98374 | -0.31034 | 16.3859
48 | 0.0074187 | 0.0018596 | -0.0074166 | -0.0018588 | 2.1312e-06 | 7.8635e-07 | 0.011198 | 0.011198 | 0.011198 | 0.9858 | -0.27019 | 0.98549 | -0.27622 | 3.0765
49 | 0.10597 | 0.027018 | -0.10536 | -0.026624 | 0.00061667 | 0.00039386 | 0.16013 | 0.16013 | 0.16013 | 0.9858 | -0.27019 | 0.97954 | -0.3915 | 43.9914
50 | 0.19859 | 0.050457 | -0.19849 | -0.050393 | 0.00010106 | 6.4338e-05 | 0.30022 | 0.30022 | 0.30022 | 0.9851 | -0.2836 | 0.98456 | -0.29418 | 27.4924
51 | -0.033329 | -0.0083557 | 0.033349 | 0.0083679 | 1.9293e-05 | 1.2102e-05 | 0.050969 | 0.050969 | 0.050969 | 0.97306 | -0.51857 | 0.97368 | -0.50643 | 14.0024
52 | 0.017267 | 0.00433 | -0.017261 | -0.0043267 | 5.6873e-06 | 3.3698e-06 | 0.026405 | 0.026405 | 0.026405 | 0.97306 | -0.51857 | 0.97271 | -0.52548 | 7.2542
53 | 0.018302 | 0.0045946 | -0.018292 | -0.0045883 | 1.052e-05 | 6.2874e-06 | 0.027973 | 0.027973 | 0.027973 | 0.97368 | -0.50643 | 0.97306 | -0.51849 | 7.685
54 | -0.086983 | -0.021825 | 0.087083 | 0.021889 | 9.934e-05 | 6.3391e-05 | 0.13294 | 0.13294 | 0.13294 | 0.97368 | -0.50643 | 0.97489 | -0.48251 | 36.5223
55 | 0.035332 | 0.0088626 | -0.035314 | -0.0088511 | 1.8375e-05 | 1.1551e-05 | 0.053999 | 0.053999 | 0.053999 | 0.97368 | -0.50643 | 0.97312 | -0.51734 | 14.835
56 | 0.017261 | 0.0043267 | -0.017259 | -0.0043255 | 1.9351e-06 | 1.1466e-06 | 0.026405 | 0.026405 | 0.026405 | 0.97271 | -0.52548 | 0.97259 | -0.52783 | 7.2542
57 | 0.018292 | 0.0045883 | -0.018285 | -0.0045842 | 6.8992e-06 | 4.1236e-06 | 0.027973 | 0.027974 | 0.027974 | 0.97306 | -0.51849 | 0.97266 | -0.5264 | 7.685
58 | -0.087083 | -0.021889 | 0.087305 | 0.022031 | 0.0002227 | 0.00014211 | 0.13294 | 0.13294 | 0.13294 | 0.97489 | -0.48251 | 0.97761 | -0.42909 | 36.5223
59 | 0.020418 | 0.0051177 | -0.020415 | -0.0051164 | 2.2152e-06 | 1.3425e-06 | 0.031221 | 0.031221 | 0.031221 | 0.97312 | -0.51734 | 0.97301 | -0.51962 | 8.5772
60 | 0.014756 | 0.0036998 | -0.014754 | -0.0036988 | 1.786e-06 | 1.0271e-06 | 0.022575 | 0.022575 | 0.022575 | 0.97266 | -0.5264 | 0.97253 | -0.52894 | 6.2019
61 | -0.09882 | -0.024917 | 0.098998 | 0.02503 | 0.00017814 | 0.00011374 | 0.15047 | 0.15047 | 0.15047 | 0.97761 | -0.42909 | 0.97954 | -0.3915 | 41.3372
62 | 0.0043079 | 0.0010795 | -0.0043074 | -0.0010795 | 5.1309e-07 | -6.312e-08 | 0.006588 | 0.0065882 | 0.0065882 | 0.97301 | -0.51962 | 0.97288 | -0.52212 | 1.8099
63 | 0.014754 | 0.0036988 | -0.014751 | -0.0036969 | 3.2326e-06 | 1.859e-06 | 0.022575 | 0.022575 | 0.022575 | 0.97253 | -0.52894 | 0.9723 | -0.53354 | 6.2019
64 | 0.011112 | 0.002785 | -0.011112 | -0.0027849 | 1.7701e-07 | 9.3045e-08 | 0.017006 | 0.017006 | 0.017006 | 0.9723 | -0.53354 | 0.97229 | -0.53387 | 4.6721
65 | 0.18797 | 0.047584 | -0.18782 | -0.047489 | 0.00014942 | 9.507e-05 | 0.28497 | 0.28497 | 0.28497 | 0.98209 | -0.34203 | 0.98123 | -0.3586 | 26.0965
66 | -0.19427 | -0.049164 | 0.19438 | 0.049234 | 0.00011049 | 7.0324e-05 | 0.29452 | 0.29452 | 0.29452 | 0.98209 | -0.34203 | 0.9827 | -0.33019 | 26.971
67 | 0.18578 | 0.046978 | -0.18574 | -0.04695 | 4.4701e-05 | 2.8438e-05 | 0.28188 | 0.28188 | 0.28188 | 0.98123 | -0.3586 | 0.98098 | -0.36362 | 25.8135
68 | -0.19438 | -0.049234 | 0.19472 | 0.049448 | 0.00033678 | 0.00021436 | 0.29452 | 0.29452 | 0.29452 | 0.9827 | -0.33019 | 0.98456 | -0.29418 | 26.971
69 | 0.17958 | 0.045406 | -0.17941 | -0.045296 | 0.00017324 | 0.00011017 | 0.27254 | 0.27254 | 0.27254 | 0.98098 | -0.36362 | 0.97994 | -0.38375 | 24.9582
70 | 0.019799 | 0.0049644 | -0.019792 | -0.0049604 | 6.5405e-06 | 3.9391e-06 | 0.029949 | 0.029949 | 0.029949 | 0.98374 | -0.31034 | 0.98339 | -0.31727 | 8.2277
71 | 0.0042023 | 0.001053 | -0.0042019 | -0.0010531 | 3.4859e-07 | -5.556e-08 | 0.0064315 | 0.0064316 | 0.0064316 | 0.97224 | -0.53472 | 0.97215 | -0.53646 | 1.7669
72 | -0.007772 | -0.0019477 | 0.0077723 | 0.0019478 | 3.1343e-07 | 1.2734e-07 | 0.011895 | 0.011895 | 0.011895 | 0.97224 | -0.53472 | 0.97229 | -0.53387 | 3.2679

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60556 | 0.15495

## res_load
| p_mw | q_mvar
0 | 0.00051472 | 0.000129
1 | 0.00047937 | 0.00012014
2 | 0.0034514 | 0.00086501
3 | 0.00075864 | 0.00019013
4 | 0.0034429 | 0.00086287
5 | 0.0035396 | 0.00088712
6 | 0.0021591 | 0.00054112
7 | 0.00043857 | 0.00010992
8 | 0.0021859 | 0.00054784
9 | 0.020865 | 0.0052291
10 | 0.019508 | 0.0048892
11 | 0.020791 | 0.0052107
12 | 0.020024 | 0.0050185
13 | 0.0062908 | 0.0015766
14 | 0.0049608 | 0.0012433
15 | 0.0048667 | 0.0012197
16 | 0.0036267 | 0.00090892
17 | 0.0035568 | 0.00089143
18 | 0.0044343 | 0.0011113
19 | 0.020791 | 0.0052107
20 | 0.024423 | 0.006121
21 | 0.03389 | 0.0084936
22 | 0.041896 | 0.0105
23 | 0.019221 | 0.0048173
24 | 0.021786 | 0.0054601
25 | 0.018303 | 0.0045871
26 | 0.016822 | 0.0042161
27 | 0.031905 | 0.0079962
28 | 0.0030409 | 0.00076213
29 | 0.0018016 | 0.00045154
30 | 0.005645 | 0.0014148
31 | 0.0094741 | 0.0023744
32 | 0.0076792 | 0.0019246
33 | 0.0041226 | 0.0010332
34 | 0.0018 | 0.00045112
35 | 0.0052856 | 0.0013247
36 | 0.0075988 | 0.0019044
37 | 0.0072869 | 0.0018263
38 | 0.016063 | 0.0040257
39 | 0.014896 | 0.0037334
40 | 0.017259 | 0.0043255
41 | 0.0035289 | 0.00088442
42 | 0.011515 | 0.0028859
43 | 0.016107 | 0.0040369
44 | 0.0063599 | 0.0015939
45 | 0.0043074 | 0.0010795
46 | 0.0036387 | 0.00091193
47 | 0.0063031 | 0.0015797
48 | 0.002038 | 0.00051078
49 | 0.0061572 | 0.0015431
50 | 0.0037674 | 0.00094421
51 | 0.016041 | 0.0040203
52 | 0.019632 | 0.0049203
53 | 0.0074166 | 0.0018588
54 | 0.019792 | 0.0049604
55 | 0.0035697 | 0.00089466
56 | 0.0042019 | 0.0010531
57 | 0.0033399 | 0.00083705

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1