## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1322-37_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1322-37_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1322-37_0_3_node_50 | 0.4 | n |  | TRUE
3 | bus_LV_1322-37_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1322-37_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1322-37_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1322-37_0_3_node_33 | 0.4 | n |  | TRUE
7 | bus_LV_1322-37_0_3_node_22 | 0.4 | n |  | TRUE
8 | bus_LV_1322-37_0_3_node_34 | 0.4 | n |  | TRUE
9 | bus_LV_1322-37_0_3_node_16 | 0.4 | n |  | TRUE
10 | bus_LV_1322-37_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1322-37_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1322-37_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1322-37_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1322-37_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1322-37_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1322-37_0_3_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_1322-37_0_3_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1322-37_0_3_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_1322-37_0_3_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_1322-37_0_3_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_1322-37_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1322-37_0_3_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1322-37_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1322-37_0_3_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1322-37_0_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1322-37_0_3_node_49 | 0.4 | n |  | TRUE
27 | bus_LV_1322-37_0_3_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_1322-37_0_3_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_1322-37_0_3_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_1322-37_0_3_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_1322-37_0_3_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_1322-37_0_3_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_1322-37_0_3_node_47 | 0.4 | n |  | TRUE
34 | bus_LV_1322-37_0_3_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_1322-37_0_3_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_1322-37_0_3_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_1322-37_0_3_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_1322-37_0_3_node_42 | 0.4 | n |  | TRUE
39 | bus_LV_1322-37_0_3_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_1322-37_0_3_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_1322-37_0_3_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_1322-37_0_3_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_1322-37_0_3_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_1322-37_0_3_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_1322-37_0_3_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_1322-37_0_3_node_46 | 0.4 | n |  | TRUE
47 | bus_LV_1322-37_0_3_node_48 | 0.4 | n |  | TRUE
48 | bus_MV_15_0_node_52 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1322-37_0_3_load_0 | 0 | 0.0066771 | 0.0016734 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1322-37_0_3_load_1 | 1 | 0.0098011 | 0.0024564 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1322-37_0_3_load_50 | 2 | 0.010123 | 0.002537 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1322-37_0_3_load_3 | 4 | 0.0064327 | 0.0016122 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1322-37_0_3_load_4 | 5 | 0.021905 | 0.00549 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1322-37_0_3_load_33 | 6 | 0.0098892 | 0.0024785 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1322-37_0_3_load_22 | 7 | 0.022183 | 0.0055596 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1322-37_0_3_load_5 | 10 | 0.011103 | 0.0027828 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1322-37_0_3_load_6 | 11 | 0.011068 | 0.0027739 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1322-37_0_3_load_7 | 12 | 0.0096451 | 0.0024173 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1322-37_0_3_load_11 | 14 | 0.0032974 | 0.0008264 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1322-37_0_3_load_20 | 16 | 0.0044928 | 0.001126 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1322-37_0_3_load_25 | 20 | 0.004597 | 0.0011521 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1322-37_0_3_load_13 | 21 | 0.002829 | 0.00070902 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1322-37_0_3_load_21 | 24 | 0.046347 | 0.011616 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1322-37_0_3_load_49 | 26 | 0.0081126 | 0.0020332 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1322-37_0_3_load_28 | 28 | 0.012919 | 0.0032379 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1322-37_0_3_load_29 | 29 | 0.017786 | 0.0044575 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1322-37_0_3_load_32 | 31 | 0.0060292 | 0.0015111 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1322-37_0_3_load_23 | 32 | 0.0050447 | 0.0012643 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1322-37_0_3_load_35 | 35 | 0.002971 | 0.0007446 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1322-37_0_3_load_24 | 36 | 0.0085712 | 0.0021481 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1322-37_0_3_load_41 | 37 | 0.001372 | 0.00034385 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1322-37_0_3_load_36 | 39 | 0.0030326 | 0.00076004 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1322-37_0_3_load_37 | 40 | 0.0026325 | 0.00065978 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1322-37_0_3_load_38 | 41 | 0.0026451 | 0.00066291 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1322-37_0_3_load_39 | 42 | 0.0027396 | 0.00068662 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1322-37_0_3_load_43 | 43 | 0.002297 | 0.00057569 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1322-37_0_3_load_45 | 45 | 0.0030995 | 0.0007768 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1322-37_0_3_load_46 | 46 | 0.0040761 | 0.0010216 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1322-37_0_3_load_48 | 47 | 0.0062654 | 0.0015703 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1322-37_0_3_line_0 |  | 0 | 1 | 0.1167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1322-37_0_3_line_1 |  | 0 | 2 | 0.052844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1322-37_0_3_line_2 |  | 1 | 3 | 0.036421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1322-37_0_3_line_3 |  | 3 | 4 | 0.027531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1322-37_0_3_line_4 |  | 3 | 5 | 0.025209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1322-37_0_3_line_5 |  | 4 | 6 | 0.042086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1322-37_0_3_line_6 |  | 5 | 7 | 0.023097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1322-37_0_3_line_7 |  | 6 | 8 | 0.036442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1322-37_0_3_line_8 |  | 7 | 9 | 0.037484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1322-37_0_3_line_9 |  | 8 | 34 | 0.014125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1322-37_0_3_line_10 |  | 9 | 25 | 0.054727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1322-37_0_3_line_11 |  | 9 | 22 | 0.057162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1322-37_0_3_line_12 |  | 10 | 11 | 0.019799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1322-37_0_3_line_13 |  | 10 | 12 | 0.00056727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1322-37_0_3_line_14 |  | 12 | 13 | 0.016246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1322-37_0_3_line_15 |  | 13 | 14 | 0.017939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1322-37_0_3_line_16 |  | 13 | 15 | 0.014159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1322-37_0_3_line_17 |  | 15 | 16 | 0.026254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1322-37_0_3_line_18 |  | 16 | 17 | 0.0076999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1322-37_0_3_line_19 |  | 17 | 24 | 0.0094798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1322-37_0_3_line_20 |  | 17 | 21 | 0.033553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1322-37_0_3_line_21 |  | 18 | 19 | 0.16484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1322-37_0_3_line_22 |  | 18 | 20 | 0.021321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1322-37_0_3_line_23 |  | 19 | 37 | 0.090071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1322-37_0_3_line_24 |  | 20 | 36 | 0.060735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1322-37_0_3_line_25 |  | 21 | 22 | 0.028817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1322-37_0_3_line_26 |  | 22 | 23 | 0.042678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1322-37_0_3_line_27 |  | 23 | 26 | 0.050018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1322-37_0_3_line_28 |  | 24 | 32 | 0.018696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1322-37_0_3_line_29 |  | 25 | 30 | 0.008395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1322-37_0_3_line_30 |  | 25 | 31 | 0.02504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1322-37_0_3_line_31 |  | 26 | 33 | 0.044491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1322-37_0_3_line_32 |  | 27 | 28 | 0.032418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1322-37_0_3_line_33 |  | 27 | 29 | 0.013832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1322-37_0_3_line_34 |  | 29 | 30 | 0.007689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1322-37_0_3_line_35 |  | 32 | 36 | 0.021475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1322-37_0_3_line_36 |  | 33 | 47 | 0.033041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1322-37_0_3_line_37 |  | 33 | 46 | 0.020308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1322-37_0_3_line_38 |  | 34 | 35 | 0.019074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1322-37_0_3_line_39 |  | 35 | 39 | 0.011896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1322-37_0_3_line_40 |  | 37 | 38 | 0.026267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1322-37_0_3_line_41 |  | 38 | 43 | 0.025247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1322-37_0_3_line_42 |  | 39 | 40 | 0.002345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1322-37_0_3_line_43 |  | 40 | 41 | 0.0067088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1322-37_0_3_line_44 |  | 41 | 42 | 0.0067286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1322-37_0_3_line_45 |  | 43 | 44 | 0.15771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1322-37_0_3_line_46 |  | 44 | 45 | 0.033599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1322-37_0_3_trafo_22 | 0.63 MVA 20/0.4 kV | 48 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2698266.1597 | 1227956.8547 | 2698272.0727 | 1227972.6016 | 2698310.8952 | 1228025.5926 | 2698313.0331 | 1228043.8856 | 2698305.6376 | 1228057.8209
1 | 2698266.1597 | 1227956.8547 | 2698223.6434 | 1227988.2367
2 | 2698288.564 | 1228089.9925 | 2698305.6376 | 1228057.8209
3 | 2698288.564 | 1228089.9925 | 2698276.9359 | 1228074.5337 | 2698269.0533 | 1228072.3224
4 | 2698288.564 | 1228089.9925 | 2698292.3521 | 1228099.2396 | 2698288.6539 | 1228113.9997
5 | 2698269.0533 | 1228072.3224 | 2698233.5962 | 1228062.3757 | 2698228.9576 | 1228059.8951
6 | 2698283.0403 | 1228136.4042 | 2698288.6539 | 1228113.9997
7 | 2698196.8225 | 1228042.7099 | 2698228.9576 | 1228059.8951
8 | 2698257.9305 | 1228162.4279 | 2698274.098 | 1228152.2209 | 2698282.0227 | 1228140.4655 | 2698283.0403 | 1228136.4042
9 | 2698196.8225 | 1228042.7099 | 2698194.1983 | 1228056.5878
10 | 2698227.9786 | 1228123.027 | 2698230.3324 | 1228129.1814 | 2698241.2107 | 1228145.9843 | 2698245.4114 | 1228143.1072 | 2698247.9495 | 1228147.2854 | 2698252.0763 | 1228153.9251 | 2698257.9305 | 1228162.4279
11 | 2698257.9305 | 1228162.4279 | 2698246.1133 | 1228169.8826 | 2698241.2596 | 1228174.6726 | 2698236.9732 | 1228179.9835 | 2698233.3237 | 1228185.7385 | 2698230.1843 | 1228192.2692 | 2698227.858 | 1228199.1246 | 2698226.155 | 1228207.2468
12 | 2698321.719 | 1228226.4533 | 2698315.5097 | 1228245.2534
13 | 2698321.8969 | 1228225.9147 | 2698321.719 | 1228226.4533
14 | 2698324.9186 | 1228210.1138 | 2698324.6273 | 1228217.6477 | 2698321.8969 | 1228225.9147
15 | 2698324.9186 | 1228210.1138 | 2698342.3864 | 1228214.1994
16 | 2698324.9186 | 1228210.1138 | 2698320.3887 | 1228196.6958
17 | 2698320.3887 | 1228196.6958 | 2698303.402 | 1228201.9078 | 2698295.2683 | 1228204.3266
18 | 2698287.8879 | 1228206.5215 | 2698295.2683 | 1228204.3266
19 | 2698287.8879 | 1228206.5215 | 2698288.9023 | 1228197.4205 | 2698289.0265 | 1228197.1229
20 | 2698287.8879 | 1228206.5215 | 2698277.9986 | 1228209.2156 | 2698266.4226 | 1228210.3363 | 2698258.9117 | 1228209.9008 | 2698254.8168 | 1228209.2298
21 | 2698374.2018 | 1228119.496 | 2698390.6805 | 1228085.0102 | 2698400.8734 | 1228077.262 | 2698409.0593 | 1228071.7267 | 2698409.6066 | 1228062.9294 | 2698404.2418 | 1228041.8031 | 2698398.1268 | 1228027.992 | 2698404.843 | 1228019.6748 | 2698428.5608 | 1228004.3671 | 2698440.0421 | 1227988.857
22 | 2698374.2018 | 1228119.496 | 2698361.356 | 1228136.5124
23 | 2698440.0421 | 1227988.857 | 2698421.5133 | 1227970.8929 | 2698395.9223 | 1227920.3218 | 2698391.0298 | 1227914.5245
24 | 2698361.356 | 1228136.5124 | 2698354.9929 | 1228144.9414 | 2698333.2391 | 1228161.605 | 2698311.8475 | 1228169.4104
25 | 2698226.155 | 1228207.2468 | 2698243.2133 | 1228207.3286 | 2698254.8168 | 1228209.2298
26 | 2698220.9611 | 1228249.6029 | 2698221.678 | 1228241.987 | 2698222.5649 | 1228235.5526 | 2698223.0114 | 1228231.4681 | 2698226.155 | 1228207.2468
27 | 2698220.9611 | 1228249.6029 | 2698231.8968 | 1228250.0727 | 2698247.5195 | 1228249.8861 | 2698269.434 | 1228258.2268
28 | 2698289.0265 | 1228197.1229 | 2698296.2241 | 1228179.8682
29 | 2698227.9786 | 1228123.027 | 2698219.9488 | 1228125.5518
30 | 2698227.9786 | 1228123.027 | 2698233.0976 | 1228098.5159
31 | 2698311.0154 | 1228274.0526 | 2698269.434 | 1228258.2268
32 | 2698202.2625 | 1228124.9371 | 2698208.5092 | 1228119.781 | 2698214.288 | 1228096.1592
33 | 2698202.2625 | 1228124.9371 | 2698215.623 | 1228128.6604
34 | 2698219.9488 | 1228125.5518 | 2698219.1248 | 1228129.5522 | 2698215.623 | 1228128.6604
35 | 2698311.8475 | 1228169.4104 | 2698307.9935 | 1228170.8166 | 2698299.7137 | 1228171.5025 | 2698296.2241 | 1228179.8682
36 | 2698311.0154 | 1228274.0526 | 2698302.3919 | 1228297.8274 | 2698303.1433 | 1228305.5454
37 | 2698311.0154 | 1228274.0526 | 2698329.9953 | 1228281.2759
38 | 2698194.1983 | 1228056.5878 | 2698181.4513 | 1228070.7766
39 | 2698181.4513 | 1228070.7766 | 2698181.4513 | 1228070.7766 | 2698171.7805 | 1228063.8495
40 | 2698370.4235 | 1227898.5066 | 2698387.1956 | 1227909.9811 | 2698391.0298 | 1227914.5245
41 | 2698370.4235 | 1227898.5066 | 2698368.709 | 1227885.3242 | 2698371.3404 | 1227873.6635
42 | 2698171.7805 | 1228063.8495 | 2698169.8741 | 1228062.484
43 | 2698169.8741 | 1228062.484 | 2698164.4201 | 1228058.5773
44 | 2698164.4201 | 1228058.5773 | 2698158.95 | 1228054.6591
45 | 2698492.198 | 1227800.0721 | 2698486.9993 | 1227810.5603 | 2698459.5036 | 1227833.7998 | 2698439.3973 | 1227841.5061 | 2698420.9981 | 1227862.3835 | 2698408.7216 | 1227868.2291 | 2698381.5653 | 1227860.9191 | 2698373.7062 | 1227863.1797 | 2698371.3404 | 1227873.6635
46 | 2698492.198 | 1227800.0721 | 2698483.4499 | 1227786.9066 | 2698471.6498 | 1227773.5905

## bus_geodata
| x | y | coords
0 | 2698266.1597 | 1227956.8547
1 | 2698305.6376 | 1228057.8209
2 | 2698223.6434 | 1227988.2367
3 | 2698288.564 | 1228089.9925
4 | 2698269.0533 | 1228072.3224
5 | 2698288.6539 | 1228113.9997
6 | 2698228.9576 | 1228059.8951
7 | 2698283.0403 | 1228136.4042
8 | 2698196.8225 | 1228042.7099
9 | 2698257.9305 | 1228162.4279
10 | 2698321.719 | 1228226.4533
11 | 2698315.5097 | 1228245.2535
12 | 2698321.8969 | 1228225.9147
13 | 2698324.9186 | 1228210.1138
14 | 2698342.3864 | 1228214.1994
15 | 2698320.3887 | 1228196.6958
16 | 2698295.2683 | 1228204.3266
17 | 2698287.8879 | 1228206.5215
18 | 2698374.2018 | 1228119.496
19 | 2698440.0421 | 1227988.857
20 | 2698361.356 | 1228136.5124
21 | 2698254.8168 | 1228209.2298
22 | 2698226.155 | 1228207.2468
23 | 2698220.9611 | 1228249.6029
24 | 2698289.0265 | 1228197.1229
25 | 2698227.9786 | 1228123.027
26 | 2698269.434 | 1228258.2268
27 | 2698202.2625 | 1228124.9371
28 | 2698214.288 | 1228096.1592
29 | 2698215.623 | 1228128.6604
30 | 2698219.9488 | 1228125.5518
31 | 2698233.0976 | 1228098.5159
32 | 2698296.2241 | 1228179.8682
33 | 2698311.0154 | 1228274.0526
34 | 2698194.1983 | 1228056.5878
35 | 2698181.4513 | 1228070.7766
36 | 2698311.8475 | 1228169.4104
37 | 2698391.0298 | 1227914.5245
38 | 2698370.4235 | 1227898.5066
39 | 2698171.7805 | 1228063.8495
40 | 2698169.8741 | 1228062.484
41 | 2698164.4201 | 1228058.5773
42 | 2698158.95 | 1228054.6591
43 | 2698371.3404 | 1227873.6635
44 | 2698492.198 | 1227800.0721
45 | 2698471.6498 | 1227773.5905
46 | 2698329.9953 | 1228281.2759
47 | 2698303.1433 | 1228305.5454
48 | 2698257.9305 | 1228162.4279

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99436 | -0.10845 | 0.0066771 | 0.0016734
1 | 0.99615 | -0.073948 | 0.0098011 | 0.0024564
2 | 0.99387 | -0.11789 | 0.010123 | 0.002537
3 | 0.99703 | -0.056942 | 0 | 0
4 | 0.99627 | -0.071602 | 0.0064327 | 0.0016122
5 | 0.99834 | -0.0318 | 0.021905 | 0.00549
6 | 0.99536 | -0.089292 | 0.0098892 | 0.0024785
7 | 1 | 0 | -0.252 | -0.063717
8 | 0.99489 | -0.098286 | 0 | 0
9 | 0.99708 | -0.055364 | 0 | 0
10 | 0.98156 | -0.35483 | 0.011103 | 0.0027828
11 | 0.98136 | -0.35879 | 0.011068 | 0.0027739
12 | 0.98157 | -0.3546 | 0.0096451 | 0.0024173
13 | 0.98205 | -0.34525 | 0 | 0
14 | 0.982 | -0.34632 | 0.0032974 | 0.0008264
15 | 0.98251 | -0.33627 | 0 | 0
16 | 0.98336 | -0.31964 | 0.0044928 | 0.001126
17 | 0.98364 | -0.31414 | 0 | 0
18 | 0.98142 | -0.35762 | 0 | 0
19 | 0.98039 | -0.37787 | 0 | 0
20 | 0.98155 | -0.35501 | 0.004597 | 0.0011521
21 | 0.98708 | -0.24731 | 0.002829 | 0.00070902
22 | 0.99011 | -0.18883 | 0 | 0
23 | 0.98938 | -0.20285 | 0 | 0
24 | 0.98302 | -0.32633 | 0.046347 | 0.011616
25 | 0.99525 | -0.090677 | 0 | 0
26 | 0.98854 | -0.2193 | 0.0081126 | 0.0020332
27 | 0.99464 | -0.10252 | 0 | 0
28 | 0.99426 | -0.1099 | 0.012919 | 0.0032379
29 | 0.9948 | -0.099372 | 0.017786 | 0.0044575
30 | 0.99502 | -0.095215 | 0 | 0
31 | 0.99511 | -0.093335 | 0.0060292 | 0.0015111
32 | 0.98259 | -0.33477 | 0.0050447 | 0.0012643
33 | 0.98811 | -0.22751 | 0 | 0
34 | 0.99471 | -0.10177 | 0 | 0
35 | 0.99446 | -0.10649 | 0.002971 | 0.0007446
36 | 0.98219 | -0.34251 | 0.0085712 | 0.0021481
37 | 0.97982 | -0.38895 | 0.001372 | 0.00034385
38 | 0.97969 | -0.39153 | 0 | 0
39 | 0.99434 | -0.1088 | 0.0030326 | 0.00076004
40 | 0.99433 | -0.10914 | 0.0026325 | 0.00065978
41 | 0.99429 | -0.10977 | 0.0026451 | 0.00066291
42 | 0.99428 | -0.1101 | 0.0027396 | 0.00068662
43 | 0.97957 | -0.39401 | 0.002297 | 0.00057569
44 | 0.97911 | -0.4029 | 0 | 0
45 | 0.97902 | -0.40479 | 0.0030995 | 0.0007768
46 | 0.98804 | -0.22899 | 0.0040761 | 0.0010216
47 | 0.98792 | -0.23121 | 0.0062654 | 0.0015703
48 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.016804 | -0.0042126 | 0.016832 | 0.0042288 | 2.7675e-05 | 1.6195e-05 | 0.025147 | 0.025147 | 0.025147 | 0.99436 | -0.10845 | 0.99615 | -0.073948 | 6.9085
1 | 0.010127 | 0.0025392 | -0.010123 | -0.002537 | 4.5515e-06 | 2.2278e-06 | 0.015155 | 0.015155 | 0.015155 | 0.99436 | -0.10845 | 0.99387 | -0.11789 | 4.1636
2 | -0.026633 | -0.0066852 | 0.026655 | 0.0066986 | 2.1621e-05 | 1.3363e-05 | 0.039787 | 0.039787 | 0.039787 | 0.99615 | -0.073948 | 0.99703 | -0.056942 | 10.9305
3 | 0.030397 | 0.0076373 | -0.030376 | -0.0076241 | 2.1254e-05 | 1.3244e-05 | 0.045373 | 0.045373 | 0.045373 | 0.99703 | -0.056942 | 0.99627 | -0.071602 | 12.4651
4 | -0.057052 | -0.014336 | 0.05712 | 0.014379 | 6.8558e-05 | 4.3548e-05 | 0.08516 | 0.08516 | 0.08516 | 0.99703 | -0.056942 | 0.99834 | -0.0318 | 23.3956
5 | 0.023943 | 0.0060119 | -0.023923 | -0.0059995 | 2.0188e-05 | 1.2373e-05 | 0.035765 | 0.035765 | 0.035765 | 0.99627 | -0.071602 | 0.99536 | -0.089292 | 9.8257
6 | -0.079026 | -0.019869 | 0.079146 | 0.019946 | 0.00012021 | 7.6633e-05 | 0.11781 | 0.11781 | 0.11781 | 0.99834 | -0.0318 | 1 | 0 | 32.3652
7 | 0.014034 | 0.003521 | -0.014028 | -0.0035177 | 6.0159e-06 | 3.3768e-06 | 0.020981 | 0.020982 | 0.020982 | 0.99536 | -0.089292 | 0.99489 | -0.098286 | 5.7642
8 | 0.17121 | 0.043771 | -0.17075 | -0.043479 | 0.00045724 | 0.00029166 | 0.25507 | 0.25507 | 0.25507 | 1 | 0 | 0.99708 | -0.055364 | 35.0365
9 | 0.014028 | 0.0035177 | -0.014026 | -0.0035164 | 2.3318e-06 | 1.309e-06 | 0.020982 | 0.020982 | 0.020982 | 0.99489 | -0.098286 | 0.99471 | -0.10177 | 5.7642
10 | 0.036816 | 0.009257 | -0.036754 | -0.009218 | 6.1977e-05 | 3.8952e-05 | 0.054953 | 0.054954 | 0.054954 | 0.99708 | -0.055364 | 0.99525 | -0.090677 | 15.0972
11 | 0.13393 | 0.034222 | -0.13308 | -0.033674 | 0.0008584 | 0.00054863 | 0.20011 | 0.20011 | 0.20011 | 0.99708 | -0.055364 | 0.99011 | -0.18883 | 54.976
12 | 0.01107 | 0.002775 | -0.011068 | -0.0027739 | 2.0911e-06 | 1.0881e-06 | 0.016782 | 0.016782 | 0.016782 | 0.98156 | -0.35483 | 0.98136 | -0.35879 | 4.6106
13 | -0.022174 | -0.0055578 | 0.022174 | 0.005558 | 2.4037e-07 | 1.4667e-07 | 0.033615 | 0.033615 | 0.033615 | 0.98156 | -0.35483 | 0.98157 | -0.3546 | 9.2348
14 | -0.031819 | -0.0079753 | 0.031833 | 0.0079841 | 1.4175e-05 | 8.8665e-06 | 0.048236 | 0.048236 | 0.048236 | 0.98157 | -0.3546 | 0.98205 | -0.34525 | 13.2517
15 | 0.0032975 | 0.00082628 | -0.0032974 | -0.0008264 | 1.6794e-07 | -1.1948e-07 | 0.0049964 | 0.0049965 | 0.0049965 | 0.98205 | -0.34525 | 0.982 | -0.34632 | 1.3727
16 | -0.035131 | -0.0088104 | 0.035146 | 0.0088198 | 1.5046e-05 | 9.4502e-06 | 0.053233 | 0.053233 | 0.053233 | 0.98205 | -0.34525 | 0.98251 | -0.33627 | 14.6244
17 | -0.035146 | -0.0088198 | 0.035174 | 0.0088374 | 2.7899e-05 | 1.7522e-05 | 0.053233 | 0.053233 | 0.053233 | 0.98251 | -0.33627 | 0.98336 | -0.31964 | 14.6243
18 | -0.039667 | -0.0099634 | 0.039677 | 0.0099699 | 1.0406e-05 | 6.5618e-06 | 0.060031 | 0.060031 | 0.060031 | 0.98336 | -0.31964 | 0.98364 | -0.31414 | 16.492
19 | 0.071408 | 0.017919 | -0.071366 | -0.017893 | 4.1488e-05 | 2.6432e-05 | 0.10803 | 0.10803 | 0.10803 | 0.98364 | -0.31414 | 0.98302 | -0.32633 | 29.6788
20 | -0.11108 | -0.027889 | 0.11144 | 0.028116 | 0.00035538 | 0.00022702 | 0.16806 | 0.16806 | 0.16806 | 0.98364 | -0.31414 | 0.98708 | -0.24731 | 46.1708
21 | 0.0067814 | 0.0016984 | -0.0067749 | -0.0016963 | 6.5348e-06 | 2.1015e-06 | 0.010281 | 0.010282 | 0.010282 | 0.98142 | -0.35762 | 0.98039 | -0.37787 | 2.8248
22 | -0.0067814 | -0.0016984 | 0.0067823 | 0.0016986 | 8.4516e-07 | 2.7145e-07 | 0.010281 | 0.010281 | 0.010281 | 0.98142 | -0.35762 | 0.98155 | -0.35501 | 2.8246
23 | 0.0067749 | 0.0016963 | -0.0067713 | -0.0016951 | 3.5711e-06 | 1.1504e-06 | 0.010282 | 0.010283 | 0.010283 | 0.98039 | -0.37787 | 0.97982 | -0.38895 | 2.8249
24 | -0.011379 | -0.0028508 | 0.011386 | 0.0028543 | 6.7773e-06 | 3.5693e-06 | 0.01725 | 0.01725 | 0.01725 | 0.98155 | -0.35501 | 0.98219 | -0.34251 | 4.7391
25 | -0.11427 | -0.028825 | 0.11459 | 0.02903 | 0.00032091 | 0.00020501 | 0.17233 | 0.17233 | 0.17233 | 0.98708 | -0.24731 | 0.99011 | -0.18883 | 47.3424
26 | 0.018486 | 0.0046432 | -0.018474 | -0.0046359 | 1.2357e-05 | 7.3599e-06 | 0.027786 | 0.027787 | 0.027787 | 0.99011 | -0.18883 | 0.98938 | -0.20285 | 7.6337
27 | 0.018474 | 0.0046359 | -0.01846 | -0.0046273 | 1.4482e-05 | 8.6267e-06 | 0.027787 | 0.027787 | 0.027787 | 0.98938 | -0.20285 | 0.98854 | -0.2193 | 7.6338
28 | 0.025019 | 0.0062774 | -0.025009 | -0.0062712 | 1.0057e-05 | 6.1996e-06 | 0.037875 | 0.037875 | 0.037875 | 0.98302 | -0.32633 | 0.98259 | -0.33477 | 10.4052
29 | 0.030724 | 0.0077068 | -0.030717 | -0.0077027 | 6.6436e-06 | 4.1428e-06 | 0.045938 | 0.045938 | 0.045938 | 0.99525 | -0.090677 | 0.99502 | -0.095215 | 12.6204
30 | 0.00603 | 0.0015112 | -0.0060292 | -0.0015111 | 7.6321e-07 | 1.6311e-07 | 0.0090155 | 0.0090156 | 0.0090156 | 0.99525 | -0.090677 | 0.99511 | -0.093335 | 2.4768
31 | 0.010347 | 0.0025941 | -0.010343 | -0.002592 | 4.0475e-06 | 2.0202e-06 | 0.015575 | 0.015575 | 0.015575 | 0.98854 | -0.2193 | 0.98811 | -0.22751 | 4.279
32 | 0.012924 | 0.0032403 | -0.012919 | -0.0032379 | 4.5447e-06 | 2.488e-06 | 0.019335 | 0.019335 | 0.019335 | 0.99464 | -0.10252 | 0.99426 | -0.1099 | 5.3118
33 | -0.012924 | -0.0032403 | 0.012926 | 0.0032414 | 1.9391e-06 | 1.0615e-06 | 0.019335 | 0.019335 | 0.019335 | 0.99464 | -0.10252 | 0.9948 | -0.099372 | 5.3118
34 | -0.030711 | -0.0076989 | 0.030717 | 0.0077027 | 6.0849e-06 | 3.7945e-06 | 0.045938 | 0.045938 | 0.045938 | 0.9948 | -0.099372 | 0.99502 | -0.095215 | 12.6204
35 | 0.019965 | 0.0050069 | -0.019957 | -0.0050025 | 7.3619e-06 | 4.4397e-06 | 0.030235 | 0.030235 | 0.030235 | 0.98259 | -0.33477 | 0.98219 | -0.34251 | 8.3064
36 | 0.0062665 | 0.0015705 | -0.0062654 | -0.0015703 | 1.1034e-06 | 2.8304e-07 | 0.0094368 | 0.009437 | 0.009437 | 0.98811 | -0.22751 | 0.98792 | -0.23121 | 2.5926
37 | 0.0040764 | 0.0010215 | -0.0040761 | -0.0010216 | 2.8698e-07 | -7.6445e-08 | 0.0061386 | 0.0061387 | 0.0061387 | 0.98811 | -0.22751 | 0.98804 | -0.22899 | 1.6865
38 | 0.014026 | 0.0035164 | -0.014022 | -0.0035146 | 3.1488e-06 | 1.7677e-06 | 0.020982 | 0.020982 | 0.020982 | 0.99471 | -0.10177 | 0.99446 | -0.10649 | 5.7642
39 | 0.011051 | 0.00277 | -0.01105 | -0.0027694 | 1.2198e-06 | 6.2636e-07 | 0.016536 | 0.016536 | 0.016536 | 0.99446 | -0.10649 | 0.99434 | -0.1088 | 4.5429
40 | 0.0053994 | 0.0013513 | -0.0053987 | -0.0013512 | 6.6218e-07 | 9.3003e-08 | 0.0081991 | 0.0081992 | 0.0081992 | 0.97982 | -0.38895 | 0.97969 | -0.39153 | 2.2525
41 | 0.0053987 | 0.0013512 | -0.0053981 | -0.0013511 | 6.365e-07 | 8.9489e-08 | 0.0081992 | 0.0081993 | 0.0081993 | 0.97969 | -0.39153 | 0.97957 | -0.39401 | 2.2526
42 | 0.0080176 | 0.0020093 | -0.0080174 | -0.0020093 | 1.2659e-07 | 5.06e-08 | 0.011998 | 0.011998 | 0.011998 | 0.99434 | -0.1088 | 0.99433 | -0.10914 | 3.2962
43 | 0.0053849 | 0.0013495 | -0.0053847 | -0.0013495 | 1.6338e-07 | 1.7544e-08 | 0.0080585 | 0.0080585 | 0.0080585 | 0.99433 | -0.10914 | 0.99429 | -0.10977 | 2.2139
44 | 0.0027397 | 0.00068656 | -0.0027396 | -0.00068662 | 4.2417e-08 | -6.0122e-08 | 0.0041 | 0.0041001 | 0.0041001 | 0.99429 | -0.10977 | 0.99428 | -0.1101 | 1.1264
45 | 0.003101 | 0.00077541 | -0.0030997 | -0.00077655 | 1.3122e-06 | -1.1446e-06 | 0.00471 | 0.0047107 | 0.0047107 | 0.97957 | -0.39401 | 0.97911 | -0.4029 | 1.2942
46 | 0.0030997 | 0.00077655 | -0.0030995 | -0.0007768 | 2.7961e-07 | -2.4358e-07 | 0.0047107 | 0.0047109 | 0.0047109 | 0.97911 | -0.4029 | 0.97902 | -0.40479 | 1.2942

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27419 | 0.069277

## res_load
| p_mw | q_mvar
0 | 0.0066771 | 0.0016734
1 | 0.0098011 | 0.0024564
2 | 0.010123 | 0.002537
3 | 0.0064327 | 0.0016122
4 | 0.021905 | 0.00549
5 | 0.0098892 | 0.0024785
6 | 0.022183 | 0.0055596
7 | 0.011103 | 0.0027828
8 | 0.011068 | 0.0027739
9 | 0.0096451 | 0.0024173
10 | 0.0032974 | 0.0008264
11 | 0.0044928 | 0.001126
12 | 0.004597 | 0.0011521
13 | 0.002829 | 0.00070902
14 | 0.046347 | 0.011616
15 | 0.0081126 | 0.0020332
16 | 0.012919 | 0.0032379
17 | 0.017786 | 0.0044575
18 | 0.0060292 | 0.0015111
19 | 0.0050447 | 0.0012643
20 | 0.002971 | 0.0007446
21 | 0.0085712 | 0.0021481
22 | 0.001372 | 0.00034385
23 | 0.0030326 | 0.00076004
24 | 0.0026325 | 0.00065978
25 | 0.0026451 | 0.00066291
26 | 0.0027396 | 0.00068662
27 | 0.002297 | 0.00057569
28 | 0.0030995 | 0.0007768
29 | 0.0040761 | 0.0010216
30 | 0.0062654 | 0.0015703

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1