## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1322-3_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1322-3_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1322-3_0_5_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_1322-3_0_5_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_1322-3_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1322-3_0_5_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1322-3_0_5_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_1322-3_0_5_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1322-3_0_5_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1322-3_0_5_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1322-3_0_5_node_37 | 0.4 | n |  | TRUE
11 | bus_LV_1322-3_0_5_node_30 | 0.4 | n |  | TRUE
12 | bus_LV_1322-3_0_5_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_1322-3_0_5_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_1322-3_0_5_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_1322-3_0_5_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1322-3_0_5_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_1322-3_0_5_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1322-3_0_5_node_36 | 0.4 | n |  | TRUE
19 | bus_LV_1322-3_0_5_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1322-3_0_5_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_1322-3_0_5_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_1322-3_0_5_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_1322-3_0_5_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_1322-3_0_5_node_33 | 0.4 | n |  | TRUE
25 | bus_LV_1322-3_0_5_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_1322-3_0_5_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_1322-3_0_5_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1322-3_0_5_node_43 | 0.4 | n |  | TRUE
29 | bus_LV_1322-3_0_5_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_1322-3_0_5_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_1322-3_0_5_node_38 | 0.4 | n |  | TRUE
32 | bus_LV_1322-3_0_5_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_1322-3_0_5_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_1322-3_0_5_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_1322-3_0_5_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_1322-3_0_5_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_1322-3_0_5_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_1322-3_0_5_node_41 | 0.4 | n |  | TRUE
39 | bus_LV_1322-3_0_5_node_42 | 0.4 | n |  | TRUE
40 | bus_LV_1322-3_0_5_node_40 | 0.4 | n |  | TRUE
41 | bus_MV_16_0_node_99 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1322-3_0_5_load_0 | 0 | 0.084841 | 0.021263 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1322-3_0_5_load_22 | 6 | 0.017051 | 0.0042734 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1322-3_0_5_load_37 | 10 | 0.001337 | 0.00033508 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1322-3_0_5_load_30 | 11 | 0.00931 | 0.0023333 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1322-3_0_5_load_29 | 12 | 0.024967 | 0.0062573 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1322-3_0_5_load_35 | 13 | 0.0056406 | 0.0014137 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1322-3_0_5_load_24 | 14 | 0.015473 | 0.0038778 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1322-3_0_5_load_36 | 18 | 0.011088 | 0.0027789 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1322-3_0_5_load_34 | 20 | 0.0067139 | 0.0016827 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1322-3_0_5_load_27 | 23 | 0.0056504 | 0.0014161 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1322-3_0_5_load_33 | 24 | 0.009466 | 0.0023724 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1322-3_0_5_load_32 | 26 | 0.0043444 | 0.0010888 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1322-3_0_5_load_43 | 28 | 0.00031312 | 7.8475e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1322-3_0_5_load_18 | 30 | 0.0092536 | 0.0023192 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1322-3_0_5_load_38 | 31 | 0.0011707 | 0.00029342 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1322-3_0_5_load_28 | 33 | 0.070153 | 0.017582 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1322-3_0_5_load_26 | 34 | 0.01731 | 0.0043382 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1322-3_0_5_load_31 | 35 | 0.070838 | 0.017754 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1322-3_0_5_load_19 | 36 | 0.060878 | 0.015258 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1322-3_0_5_load_41 | 38 | 0.076097 | 0.019072 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1322-3_0_5_load_40 | 40 | 0.054195 | 0.013583 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1322-3_0_5_line_0 |  | 0 | 1 | 0.016539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1322-3_0_5_line_1 |  | 1 | 2 | 0.018455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1322-3_0_5_line_2 |  | 2 | 3 | 0.18939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1322-3_0_5_line_3 |  | 3 | 13 | 0.022067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1322-3_0_5_line_4 |  | 3 | 5 | 0.14964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1322-3_0_5_line_5 |  | 4 | 5 | 0.1251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_1322-3_0_5_line_6 |  | 4 | 6 | 0.031645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_1322-3_0_5_line_7 |  | 5 | 11 | 0.019357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1322-3_0_5_line_8 |  | 5 | 12 | 0.03582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_1322-3_0_5_line_9 |  | 6 | 8 | 0.05271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_1322-3_0_5_line_10 |  | 7 | 8 | 0.039577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_1322-3_0_5_line_11 |  | 7 | 9 | 0.075731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_1322-3_0_5_line_12 |  | 7 | 10 | 0.018044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1322-3_0_5_line_13 |  | 9 | 14 | 0.025091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_1322-3_0_5_line_14 |  | 10 | 31 | 0.00741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1322-3_0_5_line_15 |  | 11 | 32 | 0.05174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1322-3_0_5_line_16 |  | 13 | 20 | 0.028793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1322-3_0_5_line_17 |  | 14 | 15 | 0.038925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_1322-3_0_5_line_18 |  | 15 | 16 | 0.027605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_1322-3_0_5_line_19 |  | 16 | 33 | 0.021004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1322-3_0_5_line_20 |  | 16 | 34 | 0.0057499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_1322-3_0_5_line_21 |  | 17 | 18 | 0.034973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1322-3_0_5_line_22 |  | 17 | 19 | 0.15563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1322-3_0_5_line_23 |  | 17 | 20 | 0.036805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1322-3_0_5_line_24 |  | 19 | 27 | 0.047711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1322-3_0_5_line_25 |  | 19 | 28 | 0.017957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1322-3_0_5_line_26 |  | 21 | 22 | 0.012728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_1322-3_0_5_line_27 |  | 21 | 23 | 0.014188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_1322-3_0_5_line_28 |  | 22 | 24 | 0.018203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_1322-3_0_5_line_29 |  | 23 | 34 | 0.017103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_1322-3_0_5_line_30 |  | 24 | 25 | 0.0056798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_1322-3_0_5_line_31 |  | 25 | 26 | 0.019406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_1322-3_0_5_line_32 |  | 26 | 35 | 0.031401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1322-3_0_5_line_33 |  | 27 | 29 | 0.10294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1322-3_0_5_line_34 |  | 29 | 30 | 0.16036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1322-3_0_5_line_35 |  | 31 | 40 | 0.015558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1322-3_0_5_line_36 |  | 32 | 37 | 0.077035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1322-3_0_5_line_37 |  | 36 | 37 | 0.046122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1322-3_0_5_line_38 |  | 38 | 39 | 0.040843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1322-3_0_5_line_39 |  | 39 | 40 | 0.021679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1322-3_0_5_trafo_29 | 0.63 MVA 20/0.4 kV | 41 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2702470.7281 | 1228491.2527 | 2702454.3618 | 1228488.869
1 | 2702470.7281 | 1228491.2527 | 2702471.2831 | 1228493.3527 | 2702466.2266 | 1228508.8326
2 | 2702444.196 | 1228615.6876 | 2702416.3575 | 1228613.6734 | 2702422.5783 | 1228606.6976 | 2702435.6468 | 1228588.9095 | 2702439.6641 | 1228583.5858 | 2702443.5638 | 1228579.3721 | 2702446.8464 | 1228576.2263 | 2702450.4152 | 1228573.1855 | 2702454.2281 | 1228570.4937 | 2702458.573 | 1228567.7109 | 2702463.3058 | 1228565.2906 | 2702468.1254 | 1228563.1054 | 2702472.9065 | 1228561.3976 | 2702479.8558 | 1228559.6493 | 2702485.0686 | 1228558.8385 | 2702490.0235 | 1228558.4792 | 2702494.0518 | 1228534.0639 | 2702484.506 | 1228528.1729 | 2702477.9826 | 1228522.801 | 2702468.5023 | 1228519.702 | 2702466.2266 | 1228508.8326
3 | 2702444.196 | 1228615.6876 | 2702464.9616 | 1228608.2225
4 | 2702338.7712 | 1228682.2888 | 2702340.721 | 1228679.9651 | 2702342.8 | 1228674.9749 | 2702343.7446 | 1228670.2877 | 2702344.2535 | 1228664.0586 | 2702344.3956 | 1228655.3657 | 2702343.6577 | 1228641.4427 | 2702356.4679 | 1228640.3957 | 2702364.83 | 1228639.3277 | 2702371.6017 | 1228637.7653 | 2702380.4848 | 1228635.0495 | 2702388.8965 | 1228631.9809 | 2702400.6258 | 1228625.9339 | 2702408.7997 | 1228619.9591 | 2702416.3575 | 1228613.6734 | 2702444.196 | 1228615.6876
5 | 2702268.3709 | 1228666.333 | 2702275.2954 | 1228658.524 | 2702289.0638 | 1228648.4756 | 2702293.1764 | 1228646.4114 | 2702297.6204 | 1228644.909 | 2702305.5492 | 1228643.4776 | 2702343.6577 | 1228641.4427 | 2702344.3956 | 1228655.3657 | 2702344.2535 | 1228664.0586 | 2702343.7446 | 1228670.2877 | 2702342.8 | 1228674.9749 | 2702340.721 | 1228679.9651 | 2702338.7712 | 1228682.2888
6 | 2702268.3709 | 1228666.333 | 2702260.0076 | 1228674.9622 | 2702258.2182 | 1228677.6557 | 2702256.8067 | 1228680.856 | 2702255.9419 | 1228684.4327 | 2702255.0809 | 1228693.6095
7 | 2702338.7712 | 1228682.2888 | 2702336.0699 | 1228683.8101 | 2702332.9978 | 1228684.858 | 2702328.8708 | 1228685.1206 | 2702320.0264 | 1228684.3817
8 | 2702338.7712 | 1228682.2888 | 2702347.7852 | 1228687.8146 | 2702372.9149 | 1228690.2435
9 | 2702248.4456 | 1228745.7491 | 2702249.5859 | 1228742.8999 | 2702250.5699 | 1228739.0028 | 2702251.1641 | 1228734.8544 | 2702252.5455 | 1228720.6343 | 2702255.0809 | 1228693.6095
10 | 2702248.4456 | 1228745.7491 | 2702247.126 | 1228747.5722 | 2702245.3293 | 1228750.2544 | 2702243.4368 | 1228752.3345 | 2702240.7756 | 1228754.6127 | 2702237.5142 | 1228756.5358 | 2702234.3689 | 1228757.8827 | 2702230.5694 | 1228758.9293 | 2702246.8491 | 1228762.345
11 | 2702246.8491 | 1228762.345 | 2702266.2195 | 1228768.9161 | 2702274.4022 | 1228770.3356 | 2702282.6068 | 1228771.3664 | 2702287.1986 | 1228771.8346 | 2702321.1589 | 1228774.7652
12 | 2702246.8491 | 1228762.345 | 2702245.7119 | 1228774.2676 | 2702245.1645 | 1228780.3101
13 | 2702321.1589 | 1228774.7652 | 2702346.1288 | 1228777.2291
14 | 2702244.4959 | 1228787.6899 | 2702245.1645 | 1228780.3101
15 | 2702276.1736 | 1228698.6576 | 2702277.214 | 1228695.0062 | 2702278.8964 | 1228691.4769 | 2702281.4987 | 1228688.664 | 2702284.023 | 1228686.4169 | 2702287.3523 | 1228684.5172 | 2702291.0844 | 1228683.425 | 2702294.8495 | 1228682.6225 | 2702298.8661 | 1228682.6138 | 2702320.0264 | 1228684.3817
16 | 2702493.1284 | 1228607.4113 | 2702484.9282 | 1228606.538 | 2702473.1504 | 1228605.2786 | 2702464.9616 | 1228608.2225
17 | 2702384.8946 | 1228775.8849 | 2702364.8902 | 1228777.9755 | 2702358.0349 | 1228778.2467 | 2702352.4187 | 1228777.8497 | 2702346.1288 | 1228777.2291
18 | 2702412.1869 | 1228780.5248 | 2702384.8946 | 1228775.8849
19 | 2702412.1869 | 1228780.5248 | 2702410.8905 | 1228787.1519 | 2702414.0292 | 1228788.3957 | 2702417.0319 | 1228790.4934 | 2702418.68 | 1228793.3572 | 2702420.4333 | 1228796.8496
20 | 2702412.1869 | 1228780.5248 | 2702412.3303 | 1228779.6822 | 2702413.1712 | 1228774.8598 | 2702413.1712 | 1228774.8598
21 | 2702519.3219 | 1228627.8908 | 2702504.0811 | 1228634.9668 | 2702486.0367 | 1228632.8329
22 | 2702519.3219 | 1228627.8908 | 2702532.4228 | 1228628.4504 | 2702546.2681 | 1228629.79 | 2702547.6199 | 1228620.3953 | 2702552.5138 | 1228587.989 | 2702552.3017 | 1228585.3501 | 2702551.5595 | 1228584.003 | 2702556.3083 | 1228581.0938 | 2702570.5632 | 1228579.7831 | 2702579.1989 | 1228576.9187 | 2702587.5361 | 1228577.3072 | 2702605.2797 | 1228578.9145 | 2702609.3895 | 1228579.2189 | 2702610.3961 | 1228570.9524 | 2702611.3692 | 1228562.8743 | 2702614.6108 | 1228559.9169 | 2702614.8503 | 1228557.8973
23 | 2702519.3219 | 1228627.8908 | 2702507.5535 | 1228608.9518 | 2702501.3734 | 1228608.2893 | 2702493.1284 | 1228607.4113
24 | 2702603.2937 | 1228533.2798 | 2702603.454 | 1228536.2848 | 2702604.4079 | 1228538.5363 | 2702606.0131 | 1228540.3764 | 2702608.1061 | 1228541.6134 | 2702610.7113 | 1228542.1588 | 2702616.5717 | 1228542.9049 | 2702616.1791 | 1228546.3339 | 2702615.9206 | 1228548.5756 | 2702615.0285 | 1228548.449 | 2702611.6718 | 1228547.9796 | 2702609.2524 | 1228547.6488 | 2702608.6363 | 1228551.73 | 2702611.1773 | 1228552.0408 | 2702614.4819 | 1228552.4536 | 2702615.4949 | 1228552.6046 | 2702615.1985 | 1228554.8455 | 2702615.0731 | 1228555.9664 | 2702614.8503 | 1228557.8973
25 | 2702614.8503 | 1228557.8973 | 2702597.0422 | 1228555.5917
26 | 2702444.2986 | 1228775.5074 | 2702449.2033 | 1228775.414 | 2702450.2139 | 1228783.1705
27 | 2702444.2986 | 1228775.5074 | 2702430.1763 | 1228774.1439
28 | 2702450.2139 | 1228783.1705 | 2702460.4184 | 1228783.3575 | 2702464.0902 | 1228783.5653 | 2702468.3955 | 1228783.9133
29 | 2702430.1763 | 1228774.1439 | 2702425.2334 | 1228773.6666 | 2702416.1801 | 1228774.8338 | 2702413.1712 | 1228774.8598
30 | 2702474.0568 | 1228784.371 | 2702468.3955 | 1228783.9133
31 | 2702474.0568 | 1228784.371 | 2702493.4204 | 1228785.6477
32 | 2702493.4204 | 1228785.6477 | 2702509.4519 | 1228786.7047 | 2702524.769 | 1228787.4313
33 | 2702603.2937 | 1228533.2798 | 2702603.8246 | 1228531.4988 | 2702605.1109 | 1228529.4194 | 2702606.9796 | 1228527.8505 | 2702609.246 | 1228526.9445 | 2702611.6284 | 1228526.7855 | 2702614.6376 | 1228527.1932 | 2702642.8243 | 1228531.0045 | 2702670.4381 | 1228534.6393 | 2702674.3668 | 1228535.341 | 2702676.866 | 1228536.3182 | 2702678.9879 | 1228537.1999 | 2702681.3982 | 1228538.9316 | 2702690.3786 | 1228549.0275 | 2702694.3121 | 1228543.747
34 | 2702694.3121 | 1228543.747 | 2702685.1982 | 1228530.4132 | 2702681.8183 | 1228526.8967 | 2702677.3862 | 1228523.7512 | 2702610.4012 | 1228485.923 | 2702560.086 | 1228459.2134
35 | 2702244.4959 | 1228787.6899 | 2702243.3036 | 1228799.2891 | 2702243.5411 | 1228803.1793
36 | 2702276.1736 | 1228698.6576 | 2702276.4793 | 1228702.9105 | 2702277.4089 | 1228706.1399 | 2702279.2329 | 1228710.241 | 2702281.6789 | 1228712.9851 | 2702284.5926 | 1228715.4148 | 2702288.3476 | 1228716.9582 | 2702293.2946 | 1228717.4881 | 2702303.4658 | 1228718.297 | 2702305.6568 | 1228719.1242 | 2702307.5463 | 1228720.302 | 2702309.079 | 1228721.9518 | 2702310.0825 | 1228723.9705 | 2702310.3086 | 1228726.2428 | 2702307.4618 | 1228752.9469
37 | 2702307.4618 | 1228752.9469 | 2702329.3551 | 1228754.7136 | 2702353.395 | 1228757.0925
38 | 2702245.6225 | 1228824.403 | 2702243.8866 | 1228827.5199 | 2702235.3676 | 1228836.4023 | 2702233.6909 | 1228837.3964 | 2702231.6491 | 1228838.0285 | 2702229.5151 | 1228838.292 | 2702227.6524 | 1228838.2044 | 2702225.8802 | 1228837.7069 | 2702224.553 | 1228836.8835 | 2702213.5667 | 1228829.0998
39 | 2702245.6225 | 1228824.403 | 2702246.299 | 1228822.0796 | 2702246.5689 | 1228819.6046 | 2702246.2505 | 1228817.4087 | 2702243.8594 | 1228808.3942 | 2702243.5411 | 1228803.1793

## bus_geodata
| x | y | coords
0 | 2702454.3618 | 1228488.869
1 | 2702470.7281 | 1228491.2527
2 | 2702466.2266 | 1228508.8326
3 | 2702444.196 | 1228615.6876
4 | 2702268.3709 | 1228666.333
5 | 2702338.7712 | 1228682.2888
6 | 2702255.0809 | 1228693.6095
7 | 2702246.8491 | 1228762.345
8 | 2702248.4456 | 1228745.7491
9 | 2702321.1589 | 1228774.7652
10 | 2702245.1645 | 1228780.3101
11 | 2702320.0264 | 1228684.3817
12 | 2702372.9149 | 1228690.2435
13 | 2702464.9616 | 1228608.2225
14 | 2702346.1288 | 1228777.2291
15 | 2702384.8946 | 1228775.8849
16 | 2702412.1869 | 1228780.5248
17 | 2702519.3219 | 1228627.8908
18 | 2702486.0367 | 1228632.8329
19 | 2702614.8503 | 1228557.8973
20 | 2702493.1284 | 1228607.4113
21 | 2702444.2986 | 1228775.5074
22 | 2702450.2139 | 1228783.1705
23 | 2702430.1763 | 1228774.1439
24 | 2702468.3955 | 1228783.9133
25 | 2702474.0568 | 1228784.371
26 | 2702493.4204 | 1228785.6477
27 | 2702603.2937 | 1228533.2798
28 | 2702597.0422 | 1228555.5917
29 | 2702694.3121 | 1228543.747
30 | 2702560.086 | 1228459.2134
31 | 2702244.4959 | 1228787.6899
32 | 2702276.1736 | 1228698.6576
33 | 2702420.4333 | 1228796.8496
34 | 2702413.1712 | 1228774.8598
35 | 2702524.769 | 1228787.4313
36 | 2702353.395 | 1228757.0925
37 | 2702307.4618 | 1228752.9469
38 | 2702213.5667 | 1228829.0998
39 | 2702245.6225 | 1228824.403
40 | 2702243.5411 | 1228803.1793
41 | 2702338.7712 | 1228682.2888

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97044 | -0.56868 | 0.084841 | 0.021263
1 | 0.97175 | -0.54274 | 0 | 0
2 | 0.97321 | -0.51389 | 0 | 0
3 | 0.98824 | -0.22268 | 0 | 0
4 | 0.98845 | -0.21851 | 0 | 0
5 | 0.99646 | -0.066571 | 0 | 0
6 | 0.98642 | -0.25733 | 0.017051 | 0.0042734
7 | 0.98081 | -0.36576 | 0 | 0
8 | 0.98322 | -0.31911 | 0 | 0
9 | 0.97809 | -0.41894 | 0 | 0
10 | 0.97858 | -0.40927 | 0.001337 | 0.00033508
11 | 0.99521 | -0.090451 | 0.00931 | 0.0023333
12 | 1 | 0 | -0.54486 | -0.1408
13 | 0.98757 | -0.2357 | 0.0056406 | 0.0014137
14 | 0.97718 | -0.43663 | 0.015473 | 0.0038778
15 | 0.97589 | -0.46193 | 0 | 0
16 | 0.97498 | -0.47991 | 0 | 0
17 | 0.98614 | -0.26343 | 0 | 0
18 | 0.98578 | -0.27038 | 0.011088 | 0.0027789
19 | 0.98477 | -0.29019 | 0 | 0
20 | 0.98684 | -0.2498 | 0.0067139 | 0.0016827
21 | 0.97435 | -0.49225 | 0 | 0
22 | 0.97415 | -0.49621 | 0 | 0
23 | 0.97457 | -0.48784 | 0.0056504 | 0.0014161
24 | 0.97386 | -0.50187 | 0.009466 | 0.0023724
25 | 0.97378 | -0.50344 | 0 | 0
26 | 0.97351 | -0.50881 | 0.0043444 | 0.0010888
27 | 0.98436 | -0.29813 | 0 | 0
28 | 0.98476 | -0.29029 | 0.00031312 | 7.8475e-05
29 | 0.98348 | -0.3153 | 0 | 0
30 | 0.98211 | -0.34208 | 0.0092536 | 0.0023192
31 | 0.97767 | -0.42702 | 0.0011707 | 0.00029342
32 | 0.99231 | -0.14605 | 0 | 0
33 | 0.9736 | -0.50696 | 0.070153 | 0.017582
34 | 0.97486 | -0.48218 | 0.01731 | 0.0043382
35 | 0.97143 | -0.5498 | 0.070838 | 0.017754
36 | 0.98541 | -0.27969 | 0.060878 | 0.015258
37 | 0.98799 | -0.22943 | 0 | 0
38 | 0.97134 | -0.55155 | 0.076097 | 0.019072
39 | 0.97424 | -0.4943 | 0 | 0
40 | 0.97578 | -0.46405 | 0.054195 | 0.013583
41 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.084841 | -0.021263 | 0.084945 | 0.02133 | 0.00010496 | 6.6971e-05 | 0.13009 | 0.13009 | 0.13009 | 0.97044 | -0.56868 | 0.97175 | -0.54274 | 35.739
1 | -0.084945 | -0.02133 | 0.085063 | 0.021405 | 0.00011712 | 7.4728e-05 | 0.13009 | 0.13009 | 0.13009 | 0.97175 | -0.54274 | 0.97321 | -0.51389 | 35.739
2 | -0.085063 | -0.021405 | 0.086264 | 0.022172 | 0.0012019 | 0.00076683 | 0.13009 | 0.13009 | 0.13009 | 0.97321 | -0.51389 | 0.98824 | -0.22268 | 35.739
3 | 0.0331 | 0.0083236 | -0.03308 | -0.0083107 | 2.0564e-05 | 1.2878e-05 | 0.04985 | 0.04985 | 0.04985 | 0.98824 | -0.22268 | 0.98757 | -0.2357 | 13.6951
4 | -0.11936 | -0.030495 | 0.12027 | 0.031073 | 0.00090847 | 0.00057755 | 0.17994 | 0.17994 | 0.17994 | 0.98824 | -0.22268 | 0.99646 | -0.066571 | 24.7168
5 | -0.34778 | -0.08896 | 0.35035 | 0.090602 | 0.0025781 | 0.0016419 | 0.52419 | 0.52418 | 0.52419 | 0.98845 | -0.21851 | 0.99646 | -0.066571 | 28.8015
6 | 0.34778 | 0.08896 | -0.34712 | -0.088545 | 0.00065215 | 0.00041535 | 0.52419 | 0.52419 | 0.52419 | 0.98845 | -0.21851 | 0.98642 | -0.25733 | 28.8016
7 | 0.070824 | 0.017995 | -0.070743 | -0.017943 | 8.1327e-05 | 5.1798e-05 | 0.10585 | 0.10585 | 0.10585 | 0.99646 | -0.066571 | 0.99521 | -0.090451 | 29.0794
8 | -0.54145 | -0.13967 | 0.54321 | 0.1408 | 0.0017625 | 0.0011256 | 0.80997 | 0.80997 | 0.80997 | 0.99646 | -0.066571 | 1 | 0 | 44.5038
9 | 0.33007 | 0.084272 | -0.32909 | -0.083646 | 0.00098226 | 0.00062529 | 0.49847 | 0.49847 | 0.49847 | 0.98642 | -0.25733 | 0.98322 | -0.31911 | 27.3884
10 | -0.32835 | -0.083177 | 0.32909 | 0.083646 | 0.00073754 | 0.00046952 | 0.49847 | 0.49847 | 0.49847 | 0.98081 | -0.36576 | 0.98322 | -0.31911 | 27.3884
11 | 0.19461 | 0.049293 | -0.19412 | -0.04898 | 0.00049575 | 0.00031251 | 0.29544 | 0.29544 | 0.29544 | 0.98081 | -0.36576 | 0.97809 | -0.41894 | 16.2328
12 | 0.13374 | 0.033884 | -0.13346 | -0.033706 | 0.00027893 | 0.00017829 | 0.20303 | 0.20303 | 0.20303 | 0.98081 | -0.36576 | 0.97858 | -0.40927 | 55.7786
13 | 0.19412 | 0.04898 | -0.19395 | -0.048877 | 0.00016425 | 0.00010355 | 0.29544 | 0.29544 | 0.29544 | 0.97809 | -0.41894 | 0.97718 | -0.43663 | 16.2328
14 | 0.13213 | 0.033371 | -0.13201 | -0.033299 | 0.00011227 | 7.1757e-05 | 0.201 | 0.201 | 0.201 | 0.97858 | -0.40927 | 0.97767 | -0.42702 | 55.2201
15 | 0.061433 | 0.01561 | -0.061269 | -0.015506 | 0.00016397 | 0.00010427 | 0.091929 | 0.091929 | 0.091929 | 0.99521 | -0.090451 | 0.99231 | -0.14605 | 25.2552
16 | 0.027439 | 0.006897 | -0.027421 | -0.0068856 | 1.8463e-05 | 1.1448e-05 | 0.041351 | 0.041351 | 0.041351 | 0.98757 | -0.2357 | 0.98684 | -0.2498 | 11.3602
17 | 0.17848 | 0.044999 | -0.17826 | -0.044863 | 0.00021579 | 0.00013567 | 0.27188 | 0.27188 | 0.27188 | 0.97718 | -0.43663 | 0.97589 | -0.46193 | 14.9383
18 | 0.17826 | 0.044863 | -0.17811 | -0.044767 | 0.00015304 | 9.6221e-05 | 0.27188 | 0.27188 | 0.27188 | 0.97589 | -0.46193 | 0.97498 | -0.47991 | 14.9384
19 | 0.070244 | 0.01764 | -0.070153 | -0.017582 | 9.0546e-05 | 5.7688e-05 | 0.10722 | 0.10722 | 0.10722 | 0.97498 | -0.47991 | 0.9736 | -0.50696 | 29.4558
20 | 0.10787 | 0.027127 | -0.10785 | -0.02712 | 1.1692e-05 | 7.1245e-06 | 0.16466 | 0.16466 | 0.16466 | 0.97498 | -0.47991 | 0.97486 | -0.48218 | 9.0472
21 | 0.011091 | 0.0027808 | -0.011088 | -0.0027789 | 3.6737e-06 | 1.9051e-06 | 0.016737 | 0.016737 | 0.016737 | 0.98614 | -0.26343 | 0.98578 | -0.27038 | 4.598
22 | 0.0096019 | 0.002414 | -0.0095897 | -0.0024081 | 1.2256e-05 | 5.8611e-06 | 0.014491 | 0.014492 | 0.014492 | 0.98614 | -0.26343 | 0.98477 | -0.29019 | 3.9813
23 | -0.020693 | -0.0051948 | 0.020707 | 0.0052029 | 1.3459e-05 | 8.1439e-06 | 0.031228 | 0.031228 | 0.031228 | 0.98614 | -0.26343 | 0.98684 | -0.2498 | 8.5791
24 | 0.0092765 | 0.0023299 | -0.009273 | -0.0023283 | 3.5163e-06 | 1.6437e-06 | 0.014019 | 0.014019 | 0.014019 | 0.98477 | -0.29019 | 0.98436 | -0.29813 | 3.8514
25 | 0.00031312 | 7.8248e-05 | -0.00031312 | -7.8475e-05 | 1.5071e-09 | -2.2749e-07 | 0.00047305 | 0.00047314 | 0.00047314 | 0.98477 | -0.29019 | 0.98476 | -0.29029 | 0.12998
26 | 0.084852 | 0.021341 | -0.084835 | -0.021331 | 1.6036e-05 | 9.4706e-06 | 0.12961 | 0.12961 | 0.12961 | 0.97435 | -0.49225 | 0.97415 | -0.49621 | 7.1215
27 | -0.084852 | -0.021341 | 0.084869 | 0.021351 | 1.7876e-05 | 1.0557e-05 | 0.12961 | 0.12961 | 0.12961 | 0.97435 | -0.49225 | 0.97457 | -0.48784 | 7.1215
28 | 0.084835 | 0.021331 | -0.084813 | -0.021318 | 2.2935e-05 | 1.3546e-05 | 0.12961 | 0.12961 | 0.12961 | 0.97415 | -0.49621 | 0.97386 | -0.50187 | 7.1215
29 | -0.09052 | -0.022767 | 0.090544 | 0.022782 | 2.4513e-05 | 1.4622e-05 | 0.13824 | 0.13824 | 0.13824 | 0.97457 | -0.48784 | 0.97486 | -0.48218 | 7.5955
30 | 0.075347 | 0.018945 | -0.075341 | -0.018942 | 5.6482e-06 | 3.2615e-06 | 0.11515 | 0.11515 | 0.11515 | 0.97386 | -0.50187 | 0.97378 | -0.50344 | 6.3268
31 | 0.075341 | 0.018942 | -0.075322 | -0.018931 | 1.9298e-05 | 1.1144e-05 | 0.11515 | 0.11515 | 0.11515 | 0.97378 | -0.50344 | 0.97351 | -0.50881 | 6.3269
32 | 0.070977 | 0.017842 | -0.070838 | -0.017754 | 0.00013864 | 8.8342e-05 | 0.10851 | 0.10851 | 0.10851 | 0.97351 | -0.50881 | 0.97143 | -0.5498 | 29.8101
33 | 0.009273 | 0.0023283 | -0.0092654 | -0.0023247 | 7.5871e-06 | 3.5483e-06 | 0.014019 | 0.01402 | 0.01402 | 0.98436 | -0.29813 | 0.98348 | -0.3153 | 3.8515
34 | 0.0092654 | 0.0023247 | -0.0092536 | -0.0023192 | 1.182e-05 | 5.5327e-06 | 0.01402 | 0.01402 | 0.01402 | 0.98348 | -0.3153 | 0.98211 | -0.34208 | 3.8517
35 | 0.13084 | 0.033006 | -0.13061 | -0.032858 | 0.00023155 | 0.000148 | 0.19922 | 0.19922 | 0.19922 | 0.97767 | -0.42702 | 0.97578 | -0.46405 | 54.7306
36 | 0.061269 | 0.015506 | -0.061025 | -0.015351 | 0.00024413 | 0.00015525 | 0.091929 | 0.091929 | 0.091929 | 0.99231 | -0.14605 | 0.98799 | -0.22943 | 25.2553
37 | -0.060878 | -0.015258 | 0.061025 | 0.015351 | 0.00014617 | 9.2957e-05 | 0.09193 | 0.091929 | 0.09193 | 0.98541 | -0.27969 | 0.98799 | -0.22943 | 25.2554
38 | -0.076097 | -0.019072 | 0.076305 | 0.019204 | 0.00020814 | 0.0001327 | 0.11657 | 0.11657 | 0.11657 | 0.97134 | -0.55155 | 0.97424 | -0.4943 | 32.0261
39 | -0.076305 | -0.019204 | 0.076416 | 0.019275 | 0.00011048 | 7.0437e-05 | 0.11657 | 0.11657 | 0.11657 | 0.97424 | -0.4943 | 0.97578 | -0.46405 | 32.026

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.56983 | 0.14705

## res_load
| p_mw | q_mvar
0 | 0.084841 | 0.021263
1 | 0.017051 | 0.0042734
2 | 0.001337 | 0.00033508
3 | 0.00931 | 0.0023333
4 | 0.024967 | 0.0062573
5 | 0.0056406 | 0.0014137
6 | 0.015473 | 0.0038778
7 | 0.011088 | 0.0027789
8 | 0.0067139 | 0.0016827
9 | 0.0056504 | 0.0014161
10 | 0.009466 | 0.0023724
11 | 0.0043444 | 0.0010888
12 | 0.00031312 | 7.8475e-05
13 | 0.0092536 | 0.0023192
14 | 0.0011707 | 0.00029342
15 | 0.070153 | 0.017582
16 | 0.01731 | 0.0043382
17 | 0.070838 | 0.017754
18 | 0.060878 | 0.015258
19 | 0.076097 | 0.019072
20 | 0.054195 | 0.013583

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1