## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1322-7_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1322-7_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1322-7_0_4_node_10 | 0.4 | n |  | TRUE
3 | bus_LV_1322-7_0_4_node_9 | 0.4 | n |  | TRUE
4 | bus_LV_1322-7_0_4_node_29 | 0.4 | n |  | TRUE
5 | bus_LV_1322-7_0_4_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_1322-7_0_4_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_1322-7_0_4_node_20 | 0.4 | n |  | TRUE
8 | bus_LV_1322-7_0_4_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_1322-7_0_4_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_1322-7_0_4_node_2 | 0.4 | n |  | TRUE
11 | bus_LV_1322-7_0_4_node_3 | 0.4 | n |  | TRUE
12 | bus_LV_1322-7_0_4_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_1322-7_0_4_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1322-7_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1322-7_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1322-7_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_1322-7_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1322-7_0_4_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1322-7_0_4_node_28 | 0.4 | n |  | TRUE
20 | bus_LV_1322-7_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1322-7_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1322-7_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1322-7_0_4_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_1322-7_0_4_node_33 | 0.4 | n |  | TRUE
25 | bus_LV_1322-7_0_4_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_1322-7_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1322-7_0_4_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_1322-7_0_4_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_1322-7_0_4_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_1322-7_0_4_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_1322-7_0_4_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_1322-7_0_4_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1322-7_0_4_node_35 | 0.4 | n |  | TRUE
34 | bus_MV_16_0_node_35 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1322-7_0_4_load_0 | 0 | 0.0010987 | 0.00027536 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1322-7_0_4_load_1 | 1 | 0.0013686 | 0.000343 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1322-7_0_4_load_10 | 2 | 0.0033818 | 0.00084757 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1322-7_0_4_load_9 | 3 | 0.00071213 | 0.00017848 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1322-7_0_4_load_29 | 4 | 0.0109 | 0.0027318 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1322-7_0_4_load_25 | 5 | 0.0057735 | 0.001447 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1322-7_0_4_load_26 | 6 | 0.0063743 | 0.0015976 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1322-7_0_4_load_20 | 7 | 0.0021206 | 0.00053148 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1322-7_0_4_load_19 | 8 | 0.004224 | 0.0010586 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1322-7_0_4_load_17 | 9 | 0.0039136 | 0.00098083 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1322-7_0_4_load_2 | 10 | 0.041389 | 0.010373 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1322-7_0_4_load_3 | 11 | 0.0064228 | 0.0016097 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1322-7_0_4_load_5 | 12 | 0.0058968 | 0.0014779 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1322-7_0_4_load_6 | 13 | 0.0068507 | 0.001717 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1322-7_0_4_load_7 | 14 | 0.0036609 | 0.0009175 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1322-7_0_4_load_8 | 15 | 0.0036632 | 0.00091809 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1322-7_0_4_load_15 | 17 | 0.070277 | 0.017613 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1322-7_0_4_load_28 | 19 | 0.0037909 | 0.00095008 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1322-7_0_4_load_11 | 20 | 0.037255 | 0.009337 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1322-7_0_4_load_33 | 24 | 0.0030927 | 0.0007751 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1322-7_0_4_load_24 | 25 | 0.015044 | 0.0037704 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1322-7_0_4_load_22 | 26 | 0.038475 | 0.0096427 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1322-7_0_4_load_32 | 27 | 0.022191 | 0.0055617 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1322-7_0_4_load_18 | 29 | 0.0040204 | 0.0010076 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1322-7_0_4_load_30 | 30 | 0.0044618 | 0.0011182 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1322-7_0_4_load_31 | 31 | 0.004542 | 0.0011383 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1322-7_0_4_load_27 | 32 | 0.0049577 | 0.0012425 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1322-7_0_4_load_35 | 33 | 0.0070325 | 0.0017625 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1322-7_0_4_line_0 |  | 0 | 1 | 0.042035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1322-7_0_4_line_1 |  | 0 | 2 | 0.10646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1322-7_0_4_line_2 |  | 2 | 3 | 0.0044194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1322-7_0_4_line_3 |  | 3 | 4 | 0.13067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1322-7_0_4_line_4 |  | 4 | 19 | 0.014797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1322-7_0_4_line_5 |  | 5 | 6 | 0.014033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1322-7_0_4_line_6 |  | 5 | 7 | 0.015587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1322-7_0_4_line_7 |  | 6 | 32 | 0.015863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1322-7_0_4_line_8 |  | 7 | 8 | 0.011315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1322-7_0_4_line_9 |  | 8 | 9 | 0.021919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1322-7_0_4_line_10 |  | 9 | 29 | 0.03755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1322-7_0_4_line_11 |  | 10 | 11 | 0.0090816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1322-7_0_4_line_12 |  | 11 | 12 | 0.048936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1322-7_0_4_line_13 |  | 12 | 13 | 0.012841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1322-7_0_4_line_14 |  | 13 | 14 | 0.0083616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1322-7_0_4_line_15 |  | 14 | 15 | 0.0098779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1322-7_0_4_line_16 |  | 15 | 16 | 0.024527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1322-7_0_4_line_17 |  | 16 | 17 | 0.036393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_1322-7_0_4_line_18 |  | 16 | 18 | 0.070418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1322-7_0_4_line_19 |  | 17 | 28 | 0.01687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1322-7_0_4_line_20 |  | 18 | 29 | 0.068319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1322-7_0_4_line_21 |  | 19 | 32 | 0.010503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1322-7_0_4_line_22 |  | 20 | 21 | 0.033421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1322-7_0_4_line_23 |  | 21 | 22 | 0.043524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1322-7_0_4_line_24 |  | 22 | 23 | 0.037125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1322-7_0_4_line_25 |  | 22 | 24 | 0.0048772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1322-7_0_4_line_26 |  | 23 | 25 | 0.06124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1322-7_0_4_line_27 |  | 23 | 26 | 0.061935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1322-7_0_4_line_28 |  | 24 | 27 | 0.011617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1322-7_0_4_line_29 |  | 25 | 30 | 0.047351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1322-7_0_4_line_30 |  | 26 | 28 | 0.019852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1322-7_0_4_line_31 |  | 30 | 31 | 0.029239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1322-7_0_4_line_32 |  | 31 | 33 | 0.030572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1322-7_0_4_trafo_14 | 0.63 MVA 20/0.4 kV | 34 | 16 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2702930.3256 | 1229116.5338 | 2702927.3955 | 1229115.721 | 2702916.4545 | 1229107.7702 | 2702923.7872 | 1229083.3786
1 | 2702930.3256 | 1229116.5338 | 2702893.5149 | 1229216.4316
2 | 2702893.5149 | 1229216.4316 | 2702890.8023 | 1229219.9206
3 | 2702769.6176 | 1229171.0561 | 2702890.8023 | 1229219.9206
4 | 2702769.6176 | 1229171.0561 | 2702770.097 | 1229156.2665
5 | 2702771.4059 | 1229115.8893 | 2702770.9512 | 1229129.9145
6 | 2702771.4059 | 1229115.8893 | 2702771.9108 | 1229100.3108
7 | 2702770.9512 | 1229129.9145 | 2702770.4373 | 1229145.7688
8 | 2702772.2774 | 1229089.0021 | 2702771.9108 | 1229100.3108
9 | 2702772.2774 | 1229089.0021 | 2702772.622 | 1229078.3727 | 2702770.183 | 1229067.3557
10 | 2702738.5033 | 1229051.5564 | 2702753.2591 | 1229052.608 | 2702762.9689 | 1229058.5913 | 2702770.183 | 1229067.3557 | 2702770.183 | 1229067.3557
11 | 2702597.3094 | 1229161.1441 | 2702605.1366 | 1229156.5387
12 | 2702605.1366 | 1229156.5387 | 2702617.6389 | 1229149.1827 | 2702629.2036 | 1229142.5328 | 2702632.4797 | 1229129.6576 | 2702628.7462 | 1229122.8036
13 | 2702622.6035 | 1229111.5266 | 2702628.7462 | 1229122.8036
14 | 2702618.6037 | 1229104.1837 | 2702622.6035 | 1229111.5266
15 | 2702618.6037 | 1229104.1837 | 2702613.8787 | 1229095.5092
16 | 2702602.145 | 1229073.9708 | 2702610.3641 | 1229089.0571 | 2702613.8787 | 1229095.5092
17 | 2702602.145 | 1229073.9708 | 2702580.2943 | 1229044.8672
18 | 2702670.8466 | 1229057.6553 | 2702602.145 | 1229073.9708
19 | 2702573.8027 | 1229029.7048 | 2702575.841 | 1229038.9357 | 2702580.2943 | 1229044.8672
20 | 2702670.8466 | 1229057.6553 | 2702691.6817 | 1229053.4897 | 2702719.0647 | 1229050.1711 | 2702738.5033 | 1229051.5564
21 | 2702770.4373 | 1229145.7688 | 2702770.097 | 1229156.2665
22 | 2702515.1608 | 1228935.0684 | 2702499.9748 | 1228954.8324 | 2702495.9067 | 1228962.292
23 | 2702551.2177 | 1228913.0514 | 2702531.515 | 1228918.7604 | 2702523.3238 | 1228927.0698 | 2702515.1608 | 1228935.0684
24 | 2702551.2177 | 1228913.0514 | 2702556.1679 | 1228949.8417
25 | 2702551.2177 | 1228913.0514 | 2702550.6527 | 1228908.207
26 | 2702556.1679 | 1228949.8417 | 2702572.14 | 1228953.0417 | 2702616.9594 | 1228949.6173
27 | 2702556.1679 | 1228949.8417 | 2702563.2177 | 1228981.7646 | 2702569.5226 | 1229010.32
28 | 2702549.3069 | 1228896.6684 | 2702550.6527 | 1228908.207
29 | 2702616.9594 | 1228949.6173 | 2702637.6694 | 1228948.035 | 2702664.0896 | 1228945.1159
30 | 2702573.8027 | 1229029.7048 | 2702569.5226 | 1229010.32
31 | 2702693.1513 | 1228941.9049 | 2702664.0896 | 1228945.1159
32 | 2702723.5388 | 1228938.5474 | 2702693.1513 | 1228941.9049

## bus_geodata
| x | y | coords
0 | 2702930.3256 | 1229116.5338
1 | 2702923.7872 | 1229083.3786
2 | 2702893.5149 | 1229216.4316
3 | 2702890.8023 | 1229219.9206
4 | 2702769.6176 | 1229171.0561
5 | 2702771.4059 | 1229115.8893
6 | 2702770.9512 | 1229129.9145
7 | 2702771.9108 | 1229100.3108
8 | 2702772.2774 | 1229089.0021
9 | 2702770.183 | 1229067.3557
10 | 2702597.3094 | 1229161.1441
11 | 2702605.1366 | 1229156.5387
12 | 2702628.7462 | 1229122.8036
13 | 2702622.6035 | 1229111.5266
14 | 2702618.6037 | 1229104.1837
15 | 2702613.8787 | 1229095.5092
16 | 2702602.145 | 1229073.9708
17 | 2702580.2943 | 1229044.8672
18 | 2702670.8466 | 1229057.6553
19 | 2702770.097 | 1229156.2665
20 | 2702495.9067 | 1228962.292
21 | 2702515.1608 | 1228935.0684
22 | 2702551.2177 | 1228913.0514
23 | 2702556.1679 | 1228949.8417
24 | 2702550.6527 | 1228908.207
25 | 2702616.9594 | 1228949.6173
26 | 2702569.5226 | 1229010.32
27 | 2702549.3069 | 1228896.6684
28 | 2702573.8027 | 1229029.7048
29 | 2702738.5033 | 1229051.5564
30 | 2702664.0896 | 1228945.1159
31 | 2702693.1513 | 1228941.9049
32 | 2702770.4373 | 1229145.7688
33 | 2702723.5388 | 1228938.5474
34 | 2702573.8027 | 1229029.7048

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98747 | -0.24127 | 0.0010987 | 0.00027536
1 | 0.98742 | -0.2423 | 0.0013686 | 0.000343
2 | 0.98771 | -0.23657 | 0.0033818 | 0.00084757
3 | 0.98774 | -0.23611 | 0.00071213 | 0.00017848
4 | 0.98852 | -0.22079 | 0.0109 | 0.0027318
5 | 0.98977 | -0.19665 | 0.0057735 | 0.001447
6 | 0.98935 | -0.20479 | 0.0063743 | 0.0015976
7 | 0.99031 | -0.18601 | 0.0021206 | 0.00053148
8 | 0.99073 | -0.17788 | 0.004224 | 0.0010586
9 | 0.99163 | -0.16049 | 0.0039136 | 0.00098083
10 | 0.99434 | -0.10888 | 0.041389 | 0.010373
11 | 0.99468 | -0.10225 | 0.0064228 | 0.0016097
12 | 0.99681 | -0.061121 | 0.0058968 | 0.0014779
13 | 0.99744 | -0.04903 | 0.0068507 | 0.001717
14 | 0.9979 | -0.040162 | 0.0036609 | 0.0009175
15 | 0.99848 | -0.029065 | 0.0036632 | 0.00091809
16 | 1 | 0 | -0.32728 | -0.082661
17 | 0.99662 | -0.064406 | 0.070277 | 0.017613
18 | 0.9966 | -0.064844 | 0 | 0
19 | 0.98876 | -0.21618 | 0.0037909 | 0.00095008
20 | 0.98202 | -0.34647 | 0.037255 | 0.009337
21 | 0.98317 | -0.32399 | 0 | 0
22 | 0.98467 | -0.2948 | 0 | 0
23 | 0.98681 | -0.25315 | 0 | 0
24 | 0.98456 | -0.29702 | 0.0030927 | 0.0007751
25 | 0.98506 | -0.28728 | 0.015044 | 0.0037704
26 | 0.99216 | -0.14992 | 0.038475 | 0.0096427
27 | 0.98432 | -0.30165 | 0.022191 | 0.0055617
28 | 0.99457 | -0.10359 | 0 | 0
29 | 0.9933 | -0.12818 | 0.0040204 | 0.0010076
30 | 0.98436 | -0.30093 | 0.0044618 | 0.0011182
31 | 0.98405 | -0.30702 | 0.004542 | 0.0011383
32 | 0.98896 | -0.2122 | 0.0049577 | 0.0012425
33 | 0.98385 | -0.31089 | 0.0070325 | 0.0017625
34 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0013686 | 0.0003425 | -0.0013686 | -0.000343 | 6.7043e-08 | -4.9481e-07 | 0.0020622 | 0.0020624 | 0.0020624 | 0.98747 | -0.24127 | 0.98742 | -0.2423 | 0.56659
1 | -0.0024673 | -0.00061786 | 0.0024679 | 0.00061685 | 5.5178e-07 | -1.0091e-06 | 0.0037179 | 0.0037174 | 0.0037179 | 0.98747 | -0.24127 | 0.98771 | -0.23657 | 1.0214
2 | -0.0058497 | -0.0014644 | 0.0058499 | 0.0014644 | 1.287e-07 | 2.58e-08 | 0.0088122 | 0.0088122 | 0.0088122 | 0.98771 | -0.23657 | 0.98774 | -0.23611 | 2.4209
3 | -0.006562 | -0.0016429 | 0.0065668 | 0.0016443 | 4.7876e-06 | 1.3903e-06 | 0.009885 | 0.0098844 | 0.009885 | 0.98774 | -0.23611 | 0.98852 | -0.22079 | 2.7157
4 | -0.017467 | -0.0043761 | 0.01747 | 0.0043783 | 3.8358e-06 | 2.2652e-06 | 0.026292 | 0.026292 | 0.026292 | 0.98852 | -0.22079 | 0.98876 | -0.21618 | 7.223
5 | 0.032619 | 0.0081846 | -0.032607 | -0.0081766 | 1.2657e-05 | 7.9202e-06 | 0.049043 | 0.049043 | 0.049043 | 0.98977 | -0.19665 | 0.98935 | -0.20479 | 13.4734
6 | -0.038393 | -0.0096315 | 0.038412 | 0.0096438 | 1.9475e-05 | 1.2264e-05 | 0.057723 | 0.057723 | 0.057723 | 0.98977 | -0.19665 | 0.99031 | -0.18601 | 15.858
7 | 0.026232 | 0.0065791 | -0.026223 | -0.0065734 | 9.2605e-06 | 5.7231e-06 | 0.039456 | 0.039456 | 0.039456 | 0.98935 | -0.20479 | 0.98896 | -0.2122 | 10.8396
8 | -0.040533 | -0.010175 | 0.040549 | 0.010185 | 1.5741e-05 | 9.9288e-06 | 0.060909 | 0.060909 | 0.060909 | 0.99031 | -0.18601 | 0.99073 | -0.17788 | 16.7333
9 | -0.044773 | -0.011244 | 0.04481 | 0.011267 | 3.7177e-05 | 2.3511e-05 | 0.067253 | 0.067253 | 0.067253 | 0.99073 | -0.17788 | 0.99163 | -0.16049 | 18.4762
10 | -0.048723 | -0.012248 | 0.048799 | 0.012296 | 7.5298e-05 | 4.7706e-05 | 0.073126 | 0.073126 | 0.073126 | 0.99163 | -0.16049 | 0.9933 | -0.12818 | 20.0896
11 | -0.041389 | -0.010373 | 0.041402 | 0.010381 | 1.3065e-05 | 8.2439e-06 | 0.061939 | 0.061939 | 0.061939 | 0.99434 | -0.10888 | 0.99468 | -0.10225 | 17.0161
12 | -0.047825 | -0.011991 | 0.047919 | 0.012051 | 9.3938e-05 | 5.9484e-05 | 0.071547 | 0.071547 | 0.071547 | 0.99468 | -0.10225 | 0.99681 | -0.061121 | 19.6557
13 | -0.053816 | -0.013528 | 0.053847 | 0.013548 | 3.1089e-05 | 1.973e-05 | 0.080349 | 0.080349 | 0.080349 | 0.99681 | -0.061121 | 0.99744 | -0.04903 | 22.0739
14 | -0.060698 | -0.015265 | 0.060723 | 0.015281 | 2.5721e-05 | 1.6352e-05 | 0.090569 | 0.090569 | 0.090569 | 0.99744 | -0.04903 | 0.9979 | -0.040162 | 24.8817
15 | -0.064384 | -0.016199 | 0.064418 | 0.016221 | 3.4158e-05 | 2.1732e-05 | 0.096028 | 0.096028 | 0.096028 | 0.9979 | -0.040162 | 0.99848 | -0.029065 | 26.3813
16 | -0.068082 | -0.017139 | 0.068176 | 0.017199 | 9.4733e-05 | 6.0308e-05 | 0.10149 | 0.10149 | 0.10149 | 0.99848 | -0.029065 | 1 | 0 | 27.8811
17 | 0.20431 | 0.051951 | -0.20367 | -0.051548 | 0.00063177 | 0.00040338 | 0.30428 | 0.30428 | 0.30428 | 1 | 0 | 0.99662 | -0.064406 | 41.7961
18 | 0.053145 | 0.01351 | -0.052979 | -0.013405 | 0.00016542 | 0.00010495 | 0.079148 | 0.079148 | 0.079148 | 1 | 0 | 0.9966 | -0.064844 | 21.744
19 | 0.1334 | 0.033935 | -0.13315 | -0.033774 | 0.00025141 | 0.00016068 | 0.19935 | 0.19935 | 0.19935 | 0.99662 | -0.064406 | 0.99457 | -0.10359 | 54.766
20 | 0.052979 | 0.013405 | -0.052819 | -0.013303 | 0.00016049 | 0.00010183 | 0.079148 | 0.079148 | 0.079148 | 0.9966 | -0.064844 | 0.9933 | -0.12818 | 21.7441
21 | -0.021261 | -0.0053284 | 0.021265 | 0.0053309 | 4.0324e-06 | 2.446e-06 | 0.031997 | 0.031997 | 0.031997 | 0.98876 | -0.21618 | 0.98896 | -0.2122 | 8.7903
22 | -0.037255 | -0.009337 | 0.037295 | 0.0093621 | 3.9939e-05 | 2.5137e-05 | 0.056451 | 0.056451 | 0.056451 | 0.98202 | -0.34647 | 0.98317 | -0.32399 | 15.5084
23 | -0.037295 | -0.0093621 | 0.037347 | 0.0093948 | 5.2011e-05 | 3.2734e-05 | 0.056451 | 0.05645 | 0.056451 | 0.98317 | -0.32399 | 0.98467 | -0.2948 | 15.5084
24 | -0.062638 | -0.015736 | 0.062763 | 0.015816 | 0.00012478 | 7.9384e-05 | 0.094672 | 0.094672 | 0.094672 | 0.98467 | -0.2948 | 0.98681 | -0.25315 | 26.0087
25 | 0.025292 | 0.0063414 | -0.025289 | -0.0063398 | 2.6718e-06 | 1.648e-06 | 0.038221 | 0.038221 | 0.038221 | 0.98467 | -0.2948 | 0.98456 | -0.29702 | 10.5004
26 | 0.031146 | 0.0078294 | -0.031095 | -0.0077978 | 5.0673e-05 | 3.165e-05 | 0.046974 | 0.046974 | 0.046974 | 0.98681 | -0.25315 | 0.98506 | -0.28728 | 12.9049
27 | -0.093909 | -0.023645 | 0.094375 | 0.023942 | 0.00046599 | 0.00029744 | 0.14165 | 0.14164 | 0.14165 | 0.98681 | -0.25315 | 0.99216 | -0.14992 | 38.9135
28 | 0.022196 | 0.0055647 | -0.022191 | -0.0055617 | 4.9027e-06 | 2.99e-06 | 0.033547 | 0.033547 | 0.033547 | 0.98456 | -0.29702 | 0.98432 | -0.30165 | 9.2163
29 | 0.016051 | 0.0040274 | -0.016041 | -0.0040213 | 1.0441e-05 | 6.0799e-06 | 0.024249 | 0.024249 | 0.024249 | 0.98506 | -0.28728 | 0.98436 | -0.30093 | 6.6618
30 | -0.13285 | -0.033585 | 0.13315 | 0.033774 | 0.00029584 | 0.00018908 | 0.19935 | 0.19935 | 0.19935 | 0.99216 | -0.14992 | 0.99457 | -0.10359 | 54.766
31 | 0.011579 | 0.0029031 | -0.011576 | -0.0029013 | 3.3595e-06 | 1.7785e-06 | 0.017504 | 0.017504 | 0.017504 | 0.98436 | -0.30093 | 0.98405 | -0.30702 | 4.8089
32 | 0.0070338 | 0.001763 | -0.0070325 | -0.0017625 | 1.297e-06 | 4.4175e-07 | 0.010636 | 0.010636 | 0.010636 | 0.98405 | -0.30702 | 0.98385 | -0.31089 | 2.9221

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32728 | 0.082661

## res_load
| p_mw | q_mvar
0 | 0.0010987 | 0.00027536
1 | 0.0013686 | 0.000343
2 | 0.0033818 | 0.00084757
3 | 0.00071213 | 0.00017848
4 | 0.0109 | 0.0027318
5 | 0.0057735 | 0.001447
6 | 0.0063743 | 0.0015976
7 | 0.0021206 | 0.00053148
8 | 0.004224 | 0.0010586
9 | 0.0039136 | 0.00098083
10 | 0.041389 | 0.010373
11 | 0.0064228 | 0.0016097
12 | 0.0058968 | 0.0014779
13 | 0.0068507 | 0.001717
14 | 0.0036609 | 0.0009175
15 | 0.0036632 | 0.00091809
16 | 0.070277 | 0.017613
17 | 0.0037909 | 0.00095008
18 | 0.037255 | 0.009337
19 | 0.0030927 | 0.0007751
20 | 0.015044 | 0.0037704
21 | 0.038475 | 0.0096427
22 | 0.022191 | 0.0055617
23 | 0.0040204 | 0.0010076
24 | 0.0044618 | 0.0011182
25 | 0.004542 | 0.0011383
26 | 0.0049577 | 0.0012425
27 | 0.0070325 | 0.0017625

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1