## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1322-9_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1322-9_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1322-9_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1322-9_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1322-9_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1322-9_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1322-9_0_3_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_1322-9_0_3_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_1322-9_0_3_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1322-9_0_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_1322-9_0_3_node_39 | 0.4 | n |  | TRUE
11 | bus_LV_1322-9_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1322-9_0_3_node_42 | 0.4 | n |  | TRUE
13 | bus_LV_1322-9_0_3_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_1322-9_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1322-9_0_3_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_1322-9_0_3_node_49 | 0.4 | n |  | TRUE
17 | bus_LV_1322-9_0_3_node_38 | 0.4 | n |  | TRUE
18 | bus_LV_1322-9_0_3_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_1322-9_0_3_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_1322-9_0_3_node_50 | 0.4 | n |  | TRUE
21 | bus_LV_1322-9_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1322-9_0_3_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1322-9_0_3_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1322-9_0_3_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_1322-9_0_3_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1322-9_0_3_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_1322-9_0_3_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_1322-9_0_3_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_1322-9_0_3_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_1322-9_0_3_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_1322-9_0_3_node_41 | 0.4 | n |  | TRUE
32 | bus_LV_1322-9_0_3_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1322-9_0_3_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_1322-9_0_3_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_1322-9_0_3_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_1322-9_0_3_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_1322-9_0_3_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_1322-9_0_3_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_1322-9_0_3_node_48 | 0.4 | n |  | TRUE
40 | bus_LV_1322-9_0_3_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_1322-9_0_3_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_1322-9_0_3_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_1322-9_0_3_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_1322-9_0_3_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_1322-9_0_3_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_1322-9_0_3_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_1322-9_0_3_node_46 | 0.4 | n |  | TRUE
48 | bus_LV_1322-9_0_3_node_47 | 0.4 | n |  | TRUE
49 | bus_MV_16_0_node_136 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1322-9_0_3_load_0 | 0 | 0.0081203 | 0.0020351 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1322-9_0_3_load_9 | 7 | 0.010438 | 0.0026159 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1322-9_0_3_load_11 | 8 | 0.010843 | 0.0027174 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1322-9_0_3_load_39 | 10 | 0.0053422 | 0.0013389 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1322-9_0_3_load_42 | 12 | 0.0067743 | 0.0016978 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1322-9_0_3_load_23 | 13 | 0.0069848 | 0.0017506 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1322-9_0_3_load_10 | 14 | 0.0073024 | 0.0018301 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1322-9_0_3_load_20 | 15 | 0.0049088 | 0.0012303 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1322-9_0_3_load_49 | 16 | 0.0027816 | 0.00069712 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1322-9_0_3_load_38 | 17 | 0.0049657 | 0.0012445 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1322-9_0_3_load_24 | 18 | 0.036898 | 0.0092474 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1322-9_0_3_load_50 | 20 | 0.002503 | 0.0006273 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1322-9_0_3_load_13 | 21 | 0.003378 | 0.0008466 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1322-9_0_3_load_14 | 22 | 0.0034254 | 0.00085848 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1322-9_0_3_load_25 | 24 | 0.0057967 | 0.0014528 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1322-9_0_3_load_18 | 27 | 0.0055278 | 0.0013854 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1322-9_0_3_load_19 | 28 | 0.0099263 | 0.0024878 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1322-9_0_3_load_36 | 30 | 0.026075 | 0.006535 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1322-9_0_3_load_26 | 32 | 0.011029 | 0.0027642 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1322-9_0_3_load_27 | 33 | 0.0013828 | 0.00034655 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1322-9_0_3_load_28 | 34 | 0.0040246 | 0.0010087 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1322-9_0_3_load_30 | 36 | 0.00041382 | 0.00010371 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1322-9_0_3_load_31 | 37 | 0.0011919 | 0.00029872 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1322-9_0_3_load_32 | 38 | 0.0072628 | 0.0018202 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1322-9_0_3_load_48 | 39 | 0.0027989 | 0.00070148 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1322-9_0_3_load_33 | 41 | 0.00093105 | 0.00023334 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1322-9_0_3_load_44 | 44 | 0.0037473 | 0.00093916 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1322-9_0_3_load_45 | 45 | 0.0014399 | 0.00036087 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1322-9_0_3_load_40 | 46 | 0.085376 | 0.021397 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1322-9_0_3_load_46 | 47 | 0.001385 | 0.00034711 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1322-9_0_3_load_47 | 48 | 0.0082506 | 0.0020678 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1322-9_0_3_line_0 |  | 0 | 1 | 0.025854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1322-9_0_3_line_1 |  | 0 | 2 | 0.016712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1322-9_0_3_line_2 |  | 1 | 3 | 0.04734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1322-9_0_3_line_3 |  | 2 | 4 | 0.006518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1322-9_0_3_line_4 |  | 2 | 5 | 0.028665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1322-9_0_3_line_5 |  | 3 | 6 | 0.040033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1322-9_0_3_line_6 |  | 3 | 7 | 0.014861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1322-9_0_3_line_7 |  | 4 | 8 | 0.043823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1322-9_0_3_line_8 |  | 4 | 9 | 0.081342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1322-9_0_3_line_9 |  | 5 | 10 | 0.028784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1322-9_0_3_line_10 |  | 6 | 13 | 0.021937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1322-9_0_3_line_11 |  | 6 | 14 | 0.017072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1322-9_0_3_line_12 |  | 7 | 15 | 0.0079038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1322-9_0_3_line_13 |  | 8 | 11 | 0.017494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1322-9_0_3_line_14 |  | 9 | 16 | 0.022654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1322-9_0_3_line_15 |  | 10 | 17 | 0.017652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1322-9_0_3_line_16 |  | 11 | 12 | 0.013372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1322-9_0_3_line_17 |  | 13 | 18 | 0.008203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1322-9_0_3_line_18 |  | 15 | 19 | 0.043024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1322-9_0_3_line_19 |  | 16 | 20 | 0.10503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1322-9_0_3_line_20 |  | 17 | 46 | 0.010038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1322-9_0_3_line_21 |  | 18 | 24 | 0.01283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1322-9_0_3_line_22 |  | 19 | 28 | 0.0060894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_1322-9_0_3_line_23 |  | 21 | 22 | 0.036655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1322-9_0_3_line_24 |  | 21 | 23 | 0.076328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1322-9_0_3_line_25 |  | 23 | 24 | 0.081895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1322-9_0_3_line_26 |  | 24 | 25 | 0.0083408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1322-9_0_3_line_27 |  | 25 | 30 | 0.016037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1322-9_0_3_line_28 |  | 26 | 27 | 0.023654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1322-9_0_3_line_29 |  | 26 | 28 | 0.024587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1322-9_0_3_line_30 |  | 27 | 29 | 0.0053297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1322-9_0_3_line_31 |  | 29 | 31 | 0.015408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1322-9_0_3_line_32 |  | 31 | 43 | 0.036812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1322-9_0_3_line_33 |  | 32 | 33 | 0.032612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1322-9_0_3_line_34 |  | 33 | 34 | 0.040775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1322-9_0_3_line_35 |  | 33 | 35 | 0.019396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1322-9_0_3_line_36 |  | 34 | 36 | 0.020479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1322-9_0_3_line_37 |  | 35 | 37 | 0.0033464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1322-9_0_3_line_38 |  | 35 | 38 | 0.018097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1322-9_0_3_line_39 |  | 37 | 39 | 0.011741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1322-9_0_3_line_40 |  | 38 | 40 | 0.032457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1322-9_0_3_line_41 |  | 39 | 43 | 0.0040824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1322-9_0_3_line_42 |  | 40 | 44 | 0.02828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1322-9_0_3_line_43 |  | 40 | 42 | 0.007471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1322-9_0_3_line_44 |  | 41 | 42 | 0.05185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1322-9_0_3_line_45 |  | 44 | 45 | 0.053344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1322-9_0_3_line_46 |  | 45 | 47 | 0.036894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1322-9_0_3_line_47 |  | 47 | 48 | 0.0035587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1322-9_0_3_trafo_19 | 0.63 MVA 20/0.4 kV | 49 | 28 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2701226.6715 | 1229235.4341 | 2701235.9425 | 1229233.8796 | 2701236.8246 | 1229228.802 | 2701247.8292 | 1229226.2376
1 | 2701264.4628 | 1229225.0697 | 2701250.2979 | 1229225.6624 | 2701247.8292 | 1229226.2376
2 | 2701226.6715 | 1229235.4341 | 2701220.0366 | 1229206.3331 | 2701216.1518 | 1229189.2767
3 | 2701264.2079 | 1229231.5813 | 2701264.4628 | 1229225.0697
4 | 2701264.4628 | 1229225.0697 | 2701264.8662 | 1229214.2909 | 2701265.3753 | 1229196.4197
5 | 2701216.1518 | 1229189.2767 | 2701181.659 | 1229168.7858
6 | 2701216.1518 | 1229189.2767 | 2701225.2158 | 1229177.5004
7 | 2701264.2079 | 1229231.5813 | 2701307.9436 | 1229234.3503
8 | 2701264.2079 | 1229231.5813 | 2701263.4189 | 1229248.0911 | 2701268.4358 | 1229251.6125 | 2701274.0632 | 1229310.0291
9 | 2701265.3753 | 1229196.4197 | 2701265.9923 | 1229180.6631 | 2701263.8202 | 1229172.9426 | 2701264.4451 | 1229167.9863
10 | 2701181.659 | 1229168.7858 | 2701162.8 | 1229157.5797
11 | 2701181.659 | 1229168.7858 | 2701174.4604 | 1229184.2659
12 | 2701227.5712 | 1229170.7029 | 2701228.2403 | 1229173.5708 | 2701225.2158 | 1229177.5004
13 | 2701309.0141 | 1229216.889 | 2701307.9436 | 1229234.3503
14 | 2701274.0632 | 1229310.0291 | 2701296.5784 | 1229312.5366 | 2701296.5784 | 1229312.5366
15 | 2701266.653 | 1229150.4727 | 2701264.4451 | 1229167.9863
16 | 2701309.0141 | 1229216.889 | 2701309.8371 | 1229203.5424
17 | 2701155.748 | 1229153.3894 | 2701155.748 | 1229153.3894 | 2701162.8 | 1229157.5797
18 | 2701217.7954 | 1229128.8046 | 2701227.5712 | 1229170.7029
19 | 2701296.5784 | 1229312.5366 | 2701301.0769 | 1229324.244 | 2701305.4636 | 1229333.6145 | 2701304.9639 | 1229349.1508 | 2701371.4269 | 1229353.4001
20 | 2701266.653 | 1229150.4727 | 2701267.9087 | 1229140.5132
21 | 2701155.748 | 1229153.3894 | 2701162.6322 | 1229142.5633
22 | 2701217.7954 | 1229128.8046 | 2701220.8112 | 1229123.5144
23 | 2701066.5647 | 1229165.4734 | 2701064.3387 | 1229169.0248 | 2701059.5025 | 1229201.1258
24 | 2701095.4485 | 1229095.7329 | 2701092.7441 | 1229110.3866 | 2701083.2891 | 1229138.7913 | 2701066.5647 | 1229165.4734
25 | 2701162.6322 | 1229142.5633 | 2701095.4485 | 1229095.7329
26 | 2701167.1078 | 1229135.525 | 2701162.6322 | 1229142.5633
27 | 2701167.1078 | 1229135.525 | 2701177.9467 | 1229123.7054
28 | 2701232.9878 | 1229102.1546 | 2701250.9568 | 1229093.5652 | 2701254.2118 | 1229091.7276
29 | 2701232.9878 | 1229102.1546 | 2701220.8112 | 1229123.5144
30 | 2701258.8529 | 1229089.1075 | 2701254.2118 | 1229091.7276
31 | 2701258.8529 | 1229089.1075 | 2701266.0987 | 1229085.0167 | 2701272.0605 | 1229081.1264
32 | 2701278.7404 | 1229046.6481 | 2701280.8148 | 1229059.2149 | 2701280.4489 | 1229063.7898 | 2701279.4165 | 1229067.8975 | 2701277.7196 | 1229072.7611 | 2701275.1251 | 1229076.9311 | 2701272.0605 | 1229081.1264
33 | 2701256.8754 | 1229024.1482 | 2701255.323 | 1229028.0914 | 2701252.0239 | 1229034.4843 | 2701245.9881 | 1229046.7239 | 2701239.2054 | 1229043.4469
34 | 2701256.8754 | 1229024.1482 | 2701251.3291 | 1229021.8855 | 2701249.0818 | 1229020.802 | 2701220.3976 | 1229005.974
35 | 2701275.668 | 1229027.7263 | 2701267.5489 | 1229027.9216 | 2701260.435 | 1229025.5988 | 2701256.8754 | 1229024.1482
36 | 2701220.3976 | 1229005.974 | 2701202.2055 | 1228996.5698
37 | 2701275.668 | 1229027.7263 | 2701276.1839 | 1229031.0327
38 | 2701275.668 | 1229027.7263 | 2701275.0814 | 1229022.5681 | 2701274.8083 | 1229015.4693 | 2701275.0881 | 1229009.6747
39 | 2701278.0762 | 1229042.6201 | 2701276.5083 | 1229033.1113 | 2701276.1839 | 1229031.0327
40 | 2701278.8435 | 1228977.4434 | 2701275.2299 | 1229006.7368 | 2701275.0881 | 1229009.6747
41 | 2701278.7404 | 1229046.6481 | 2701278.0762 | 1229042.6201
42 | 2701278.8435 | 1228977.4434 | 2701288.0779 | 1228979.4021 | 2701291.5029 | 1228960.8756
43 | 2701279.8714 | 1228970.0443 | 2701278.8435 | 1228977.4434
44 | 2701279.8714 | 1228970.0443 | 2701232.1301 | 1228949.8151
45 | 2701325.0789 | 1228931.3564 | 2701318.8431 | 1228931.8799 | 2701305.4034 | 1228933.0074 | 2701302.0798 | 1228934.1628 | 2701299.6839 | 1228935.5675 | 2701297.2819 | 1228937.7837 | 2701295.762 | 1228939.8149 | 2701294.5554 | 1228944.3644 | 2701291.5029 | 1228960.8756
46 | 2701325.0789 | 1228931.3564 | 2701347.2478 | 1228929.4954 | 2701361.8607 | 1228928.4896
47 | 2701365.411 | 1228928.2453 | 2701361.8607 | 1228928.4896

## bus_geodata
| x | y | coords
0 | 2701247.8292 | 1229226.2376
1 | 2701226.6715 | 1229235.4341
2 | 2701264.4628 | 1229225.0697
3 | 2701216.1518 | 1229189.2767
4 | 2701264.2079 | 1229231.5813
5 | 2701265.3753 | 1229196.4197
6 | 2701181.659 | 1229168.7858
7 | 2701225.2158 | 1229177.5004
8 | 2701307.9436 | 1229234.3503
9 | 2701274.0632 | 1229310.0291
10 | 2701264.4451 | 1229167.9863
11 | 2701309.0141 | 1229216.889
12 | 2701309.8371 | 1229203.5424
13 | 2701162.8 | 1229157.5797
14 | 2701174.4604 | 1229184.2659
15 | 2701227.5712 | 1229170.7029
16 | 2701296.5784 | 1229312.5366
17 | 2701266.653 | 1229150.4727
18 | 2701155.748 | 1229153.3894
19 | 2701217.7954 | 1229128.8046
20 | 2701371.4269 | 1229353.4001
21 | 2701066.5647 | 1229165.4734
22 | 2701059.5025 | 1229201.1258
23 | 2701095.4485 | 1229095.7329
24 | 2701162.6322 | 1229142.5633
25 | 2701167.1078 | 1229135.525
26 | 2701232.9878 | 1229102.1546
27 | 2701254.2118 | 1229091.7276
28 | 2701220.8112 | 1229123.5144
29 | 2701258.8529 | 1229089.1075
30 | 2701177.9467 | 1229123.7054
31 | 2701272.0605 | 1229081.1264
32 | 2701239.2054 | 1229043.4469
33 | 2701256.8754 | 1229024.1482
34 | 2701220.3976 | 1229005.974
35 | 2701275.668 | 1229027.7263
36 | 2701202.2055 | 1228996.5698
37 | 2701276.1839 | 1229031.0327
38 | 2701275.0881 | 1229009.6747
39 | 2701278.0762 | 1229042.6201
40 | 2701278.8435 | 1228977.4434
41 | 2701232.1301 | 1228949.8151
42 | 2701279.8714 | 1228970.0443
43 | 2701278.7404 | 1229046.6481
44 | 2701291.5029 | 1228960.8756
45 | 2701325.0789 | 1228931.3564
46 | 2701267.9087 | 1229140.5132
47 | 2701361.8607 | 1228928.4896
48 | 2701365.411 | 1228928.2453
49 | 2701217.7954 | 1229128.8046

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98379 | -0.30963 | 0.0081203 | 0.0020351
1 | 0.98683 | -0.25082 | 0 | 0
2 | 0.98195 | -0.34539 | 0 | 0
3 | 0.99241 | -0.14405 | 0 | 0
4 | 0.98181 | -0.34809 | 0 | 0
5 | 0.97939 | -0.3951 | 0 | 0
6 | 0.9891 | -0.20793 | 0 | 0
7 | 0.9939 | -0.11561 | 0.010438 | 0.0026159
8 | 0.9811 | -0.36206 | 0.010843 | 0.0027174
9 | 0.98141 | -0.35587 | 0 | 0
10 | 0.97683 | -0.44528 | 0.0053422 | 0.0013389
11 | 0.98099 | -0.36421 | 0 | 0
12 | 0.9809 | -0.36585 | 0.0067743 | 0.0016978
13 | 0.98744 | -0.24026 | 0.0069848 | 0.0017506
14 | 0.98899 | -0.21016 | 0.0073024 | 0.0018301
15 | 0.99473 | -0.099798 | 0.0049088 | 0.0012303
16 | 0.9813 | -0.35804 | 0.0027816 | 0.00069712
17 | 0.97535 | -0.47445 | 0.0049657 | 0.0012445
18 | 0.98687 | -0.25135 | 0.036898 | 0.0092474
19 | 0.99935 | -0.012317 | 0 | 0
20 | 0.98106 | -0.36281 | 0.002503 | 0.0006273
21 | 0.98542 | -0.27954 | 0.003378 | 0.0008466
22 | 0.98531 | -0.2818 | 0.0034254 | 0.00085848
23 | 0.9859 | -0.27022 | 0 | 0
24 | 0.98641 | -0.26023 | 0.0057967 | 0.0014528
25 | 0.98621 | -0.26413 | 0 | 0
26 | 0.99889 | -0.021193 | 0 | 0
27 | 0.99783 | -0.041627 | 0.0055278 | 0.0013854
28 | 1 | 0 | -0.2872 | -0.073202
29 | 0.99761 | -0.045721 | 0 | 0
30 | 0.98583 | -0.27163 | 0.026075 | 0.006535
31 | 0.997 | -0.057567 | 0 | 0
32 | 0.99417 | -0.11201 | 0.011029 | 0.0027642
33 | 0.9945 | -0.10567 | 0.0013828 | 0.00034655
34 | 0.99434 | -0.10886 | 0.0040246 | 0.0010087
35 | 0.9948 | -0.099914 | 0 | 0
36 | 0.99433 | -0.10901 | 0.00041382 | 0.00010371
37 | 0.99492 | -0.097563 | 0.0011919 | 0.00029872
38 | 0.99442 | -0.10725 | 0.0072628 | 0.0018202
39 | 0.99536 | -0.089077 | 0.0027989 | 0.00070148
40 | 0.99395 | -0.11627 | 0 | 0
41 | 0.9939 | -0.11725 | 0.00093105 | 0.00023334
42 | 0.99395 | -0.1164 | 0 | 0
43 | 0.99552 | -0.085926 | 0 | 0
44 | 0.99357 | -0.12368 | 0.0037473 | 0.00093916
45 | 0.99303 | -0.13411 | 0.0014399 | 0.00036087
46 | 0.97455 | -0.49017 | 0.085376 | 0.021397
47 | 0.99271 | -0.1404 | 0.001385 | 0.00034711
48 | 0.99268 | -0.14092 | 0.0082506 | 0.0020678
49 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.12758 | -0.032309 | 0.12794 | 0.03254 | 0.00036146 | 0.00023101 | 0.19309 | 0.19309 | 0.19309 | 0.98379 | -0.30963 | 0.98683 | -0.25082 | 53.0461
1 | 0.11946 | 0.030274 | -0.11925 | -0.030143 | 0.00020487 | 0.00013091 | 0.18081 | 0.18081 | 0.18081 | 0.98379 | -0.30963 | 0.98195 | -0.34539 | 49.6719
2 | -0.12794 | -0.03254 | 0.1286 | 0.032963 | 0.00066186 | 0.00042298 | 0.19309 | 0.19309 | 0.19309 | 0.98683 | -0.25082 | 0.99241 | -0.14405 | 53.0461
3 | 0.02292 | 0.0057481 | -0.022917 | -0.0057463 | 2.9489e-06 | 1.8049e-06 | 0.034734 | 0.034734 | 0.034734 | 0.98195 | -0.34539 | 0.98181 | -0.34809 | 9.5424
4 | 0.096333 | 0.024395 | -0.096104 | -0.024249 | 0.00022936 | 0.00014643 | 0.14607 | 0.14607 | 0.14607 | 0.98195 | -0.34539 | 0.97939 | -0.3951 | 40.1296
5 | 0.090341 | 0.022825 | -0.090065 | -0.022649 | 0.00027572 | 0.00017595 | 0.13552 | 0.13552 | 0.13552 | 0.99241 | -0.14405 | 0.9891 | -0.20793 | 37.2314
6 | -0.21894 | -0.055788 | 0.21924 | 0.055981 | 0.00030088 | 0.00019218 | 0.32861 | 0.32861 | 0.32861 | 0.99241 | -0.14405 | 0.9939 | -0.11561 | 45.1386
7 | 0.01763 | 0.0044226 | -0.017618 | -0.0044156 | 1.1734e-05 | 6.9559e-06 | 0.026721 | 0.026721 | 0.026721 | 0.98181 | -0.34809 | 0.9811 | -0.36206 | 7.341
8 | 0.0052876 | 0.0013237 | -0.0052856 | -0.0013235 | 1.9588e-06 | 2.2536e-07 | 0.0080133 | 0.0080136 | 0.0080136 | 0.98181 | -0.34809 | 0.98141 | -0.35587 | 2.2015
9 | 0.096104 | 0.024249 | -0.095874 | -0.024102 | 0.00023031 | 0.00014704 | 0.14607 | 0.14607 | 0.14607 | 0.97939 | -0.3951 | 0.97683 | -0.44528 | 40.1296
10 | 0.082762 | 0.020819 | -0.082635 | -0.020737 | 0.00012758 | 8.1373e-05 | 0.12454 | 0.12454 | 0.12454 | 0.9891 | -0.20793 | 0.98744 | -0.24026 | 34.213
11 | 0.0073032 | 0.0018304 | -0.0073024 | -0.0018301 | 7.7281e-07 | 2.755e-07 | 0.010987 | 0.010987 | 0.010987 | 0.9891 | -0.20793 | 0.98899 | -0.21016 | 3.0184
12 | -0.22968 | -0.058596 | 0.22986 | 0.058709 | 0.00017561 | 0.00011218 | 0.34424 | 0.34424 | 0.34424 | 0.9939 | -0.11561 | 0.99473 | -0.099798 | 47.2851
13 | 0.0067755 | 0.0016982 | -0.0067748 | -0.001698 | 6.9279e-07 | 2.2249e-07 | 0.010276 | 0.010276 | 0.010276 | 0.9811 | -0.36206 | 0.98099 | -0.36421 | 2.8232
14 | 0.0052856 | 0.0013235 | -0.0052851 | -0.0013235 | 5.4557e-07 | 6.2932e-08 | 0.0080136 | 0.0080137 | 0.0080137 | 0.98141 | -0.35587 | 0.9813 | -0.35804 | 2.2016
15 | 0.090532 | 0.022763 | -0.090406 | -0.022683 | 0.00012594 | 8.0383e-05 | 0.13793 | 0.13793 | 0.13793 | 0.97683 | -0.44528 | 0.97535 | -0.47445 | 37.8939
16 | 0.0067748 | 0.001698 | -0.0067743 | -0.0016978 | 5.2956e-07 | 1.7011e-07 | 0.010276 | 0.010276 | 0.010276 | 0.98099 | -0.36421 | 0.9809 | -0.36585 | 2.8232
17 | 0.07565 | 0.018987 | -0.07561 | -0.018961 | 3.9984e-05 | 2.5485e-05 | 0.11401 | 0.11401 | 0.11401 | 0.98744 | -0.24026 | 0.98687 | -0.25135 | 31.3213
18 | -0.23477 | -0.059939 | 0.23576 | 0.060576 | 0.00099713 | 0.00063704 | 0.35158 | 0.35158 | 0.35158 | 0.99473 | -0.099798 | 0.99935 | -0.012317 | 48.2937
19 | 0.0025035 | 0.00062634 | -0.002503 | -0.0006273 | 5.6758e-07 | -9.6331e-07 | 0.0037959 | 0.0037963 | 0.0037963 | 0.9813 | -0.35804 | 0.98106 | -0.36281 | 1.043
20 | 0.08544 | 0.021438 | -0.085376 | -0.021397 | 6.3969e-05 | 4.0815e-05 | 0.13036 | 0.13036 | 0.13036 | 0.97535 | -0.47445 | 0.97455 | -0.49017 | 35.8127
21 | 0.038712 | 0.0097137 | -0.038696 | -0.0097034 | 1.6394e-05 | 1.0328e-05 | 0.058375 | 0.058375 | 0.058375 | 0.98687 | -0.25135 | 0.98641 | -0.26023 | 16.0371
22 | -0.23576 | -0.060576 | 0.2359 | 0.060666 | 0.00014113 | 9.0164e-05 | 0.35158 | 0.35158 | 0.35158 | 0.99935 | -0.012317 | 1 | 0 | 48.2937
23 | 0.0034257 | 0.00085825 | -0.0034254 | -0.00085848 | 3.6782e-07 | -2.3151e-07 | 0.0051728 | 0.005173 | 0.005173 | 0.98542 | -0.27954 | 0.98531 | -0.2818 | 1.4212
24 | -0.0068037 | -0.0017048 | 0.0068067 | 0.0017058 | 3.021e-06 | 9.6058e-07 | 0.010274 | 0.010273 | 0.010274 | 0.98542 | -0.27954 | 0.9859 | -0.27022 | 2.8224
25 | -0.0068067 | -0.0017058 | 0.0068099 | 0.0017068 | 3.2411e-06 | 1.0294e-06 | 0.010273 | 0.010273 | 0.010273 | 0.9859 | -0.27022 | 0.98641 | -0.26023 | 2.8223
26 | 0.026089 | 0.0065437 | -0.026084 | -0.0065407 | 4.845e-06 | 2.9944e-06 | 0.039358 | 0.039358 | 0.039358 | 0.98641 | -0.26023 | 0.98621 | -0.26413 | 10.8125
27 | 0.026084 | 0.0065407 | -0.026075 | -0.006535 | 9.3156e-06 | 5.7574e-06 | 0.039358 | 0.039358 | 0.039358 | 0.98621 | -0.26413 | 0.98583 | -0.27163 | 10.8125
28 | 0.049592 | 0.012504 | -0.049544 | -0.012473 | 4.8446e-05 | 3.0696e-05 | 0.073902 | 0.073902 | 0.073902 | 0.99889 | -0.021193 | 0.99783 | -0.041627 | 20.3029
29 | -0.049592 | -0.012504 | 0.049643 | 0.012536 | 5.0356e-05 | 3.1905e-05 | 0.073902 | 0.073902 | 0.073902 | 0.99889 | -0.021193 | 1 | 0 | 20.3028
30 | 0.044016 | 0.011088 | -0.044007 | -0.011082 | 8.6164e-06 | 5.4449e-06 | 0.065659 | 0.065659 | 0.065659 | 0.99783 | -0.041627 | 0.99761 | -0.045721 | 18.0382
31 | 0.044007 | 0.011082 | -0.043983 | -0.011066 | 2.491e-05 | 1.5741e-05 | 0.065659 | 0.065659 | 0.065659 | 0.99761 | -0.045721 | 0.997 | -0.057567 | 18.0382
32 | 0.043983 | 0.011066 | -0.043923 | -0.011029 | 5.9513e-05 | 3.7609e-05 | 0.065659 | 0.065659 | 0.065659 | 0.997 | -0.057567 | 0.99552 | -0.085926 | 18.0383
33 | -0.011029 | -0.0027642 | 0.011033 | 0.0027659 | 3.3326e-06 | 1.7099e-06 | 0.016508 | 0.016508 | 0.016508 | 0.99417 | -0.11201 | 0.9945 | -0.10567 | 4.5351
34 | 0.0044391 | 0.001112 | -0.0044384 | -0.0011121 | 6.7454e-07 | -9.7278e-08 | 0.0066418 | 0.006642 | 0.006642 | 0.9945 | -0.10567 | 0.99434 | -0.10886 | 1.8247
35 | -0.016854 | -0.0042245 | 0.016859 | 0.0042272 | 4.6257e-06 | 2.7087e-06 | 0.025219 | 0.025218 | 0.025219 | 0.9945 | -0.10567 | 0.9948 | -0.099914 | 6.9282
36 | 0.00041382 | 0.00010345 | -0.00041382 | -0.00010371 | 2.9448e-09 | -2.6375e-07 | 0.00061919 | 0.00061929 | 0.00061929 | 0.99434 | -0.10886 | 0.99433 | -0.10901 | 0.17013
37 | -0.039905 | -0.010011 | 0.039909 | 0.010014 | 4.4714e-06 | 2.8182e-06 | 0.059693 | 0.059693 | 0.059693 | 0.9948 | -0.099914 | 0.99492 | -0.097563 | 16.3991
38 | 0.023045 | 0.0057839 | -0.023037 | -0.005779 | 8.0653e-06 | 4.9269e-06 | 0.034474 | 0.034474 | 0.034474 | 0.9948 | -0.099914 | 0.99442 | -0.10725 | 9.4709
39 | -0.041101 | -0.010313 | 0.041118 | 0.010323 | 1.6639e-05 | 1.0497e-05 | 0.061475 | 0.061475 | 0.061475 | 0.99492 | -0.097563 | 0.99536 | -0.089077 | 16.8888
40 | 0.015775 | 0.0039587 | -0.015768 | -0.0039548 | 6.7826e-06 | 3.92e-06 | 0.023606 | 0.023606 | 0.023606 | 0.99442 | -0.10725 | 0.99395 | -0.11627 | 6.4853
41 | -0.043916 | -0.011025 | 0.043923 | 0.011029 | 6.6e-06 | 4.1709e-06 | 0.065659 | 0.065659 | 0.065659 | 0.99536 | -0.089077 | 0.99552 | -0.085926 | 18.0383
42 | 0.014837 | 0.0037222 | -0.014831 | -0.0037192 | 5.2327e-06 | 2.9825e-06 | 0.022213 | 0.022213 | 0.022213 | 0.99395 | -0.11627 | 0.99357 | -0.12368 | 6.1025
43 | 0.00093109 | 0.0002326 | -0.00093109 | -0.0002327 | 5.4416e-09 | -9.3349e-08 | 0.0013936 | 0.0013937 | 0.0013937 | 0.99395 | -0.11627 | 0.99395 | -0.1164 | 0.38288
44 | -0.00093105 | -0.00023334 | 0.00093109 | 0.0002327 | 3.7773e-08 | -6.4782e-07 | 0.0013939 | 0.0013937 | 0.0013939 | 0.9939 | -0.11725 | 0.99395 | -0.1164 | 0.38294
45 | 0.011084 | 0.0027801 | -0.011079 | -0.0027772 | 5.5129e-06 | 2.8378e-06 | 0.016601 | 0.016601 | 0.016601 | 0.99357 | -0.12368 | 0.99303 | -0.13411 | 4.5607
46 | 0.0096387 | 0.0024164 | -0.0096358 | -0.002415 | 2.8863e-06 | 1.3701e-06 | 0.014443 | 0.014444 | 0.014444 | 0.99303 | -0.13411 | 0.99271 | -0.1404 | 3.968
47 | 0.0082508 | 0.0020679 | -0.0082506 | -0.0020678 | 2.0413e-07 | 8.4632e-08 | 0.012368 | 0.012368 | 0.012368 | 0.99271 | -0.1404 | 0.99268 | -0.14092 | 3.3977

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.29712 | 0.07569

## res_load
| p_mw | q_mvar
0 | 0.0081203 | 0.0020351
1 | 0.010438 | 0.0026159
2 | 0.010843 | 0.0027174
3 | 0.0053422 | 0.0013389
4 | 0.0067743 | 0.0016978
5 | 0.0069848 | 0.0017506
6 | 0.0073024 | 0.0018301
7 | 0.0049088 | 0.0012303
8 | 0.0027816 | 0.00069712
9 | 0.0049657 | 0.0012445
10 | 0.036898 | 0.0092474
11 | 0.002503 | 0.0006273
12 | 0.003378 | 0.0008466
13 | 0.0034254 | 0.00085848
14 | 0.0057967 | 0.0014528
15 | 0.0055278 | 0.0013854
16 | 0.0099263 | 0.0024878
17 | 0.026075 | 0.006535
18 | 0.011029 | 0.0027642
19 | 0.0013828 | 0.00034655
20 | 0.0040246 | 0.0010087
21 | 0.00041382 | 0.00010371
22 | 0.0011919 | 0.00029872
23 | 0.0072628 | 0.0018202
24 | 0.0027989 | 0.00070148
25 | 0.00093105 | 0.00023334
26 | 0.0037473 | 0.00093916
27 | 0.0014399 | 0.00036087
28 | 0.085376 | 0.021397
29 | 0.001385 | 0.00034711
30 | 0.0082506 | 0.0020678

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1