## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1323-24_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1323-24_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1323-24_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1323-24_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1323-24_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1323-24_0_2_node_72 | 0.4 | n |  | TRUE
6 | bus_LV_1323-24_0_2_node_73 | 0.4 | n |  | TRUE
7 | bus_LV_1323-24_0_2_node_71 | 0.4 | n |  | TRUE
8 | bus_LV_1323-24_0_2_node_39 | 0.4 | n |  | TRUE
9 | bus_LV_1323-24_0_2_node_74 | 0.4 | n |  | TRUE
10 | bus_LV_1323-24_0_2_node_75 | 0.4 | n |  | TRUE
11 | bus_LV_1323-24_0_2_node_38 | 0.4 | n |  | TRUE
12 | bus_LV_1323-24_0_2_node_69 | 0.4 | n |  | TRUE
13 | bus_LV_1323-24_0_2_node_68 | 0.4 | n |  | TRUE
14 | bus_LV_1323-24_0_2_node_37 | 0.4 | n |  | TRUE
15 | bus_LV_1323-24_0_2_node_77 | 0.4 | n |  | TRUE
16 | bus_LV_1323-24_0_2_node_78 | 0.4 | n |  | TRUE
17 | bus_LV_1323-24_0_2_node_76 | 0.4 | n |  | TRUE
18 | bus_LV_1323-24_0_2_node_30 | 0.4 | n |  | TRUE
19 | bus_LV_1323-24_0_2_node_67 | 0.4 | n |  | TRUE
20 | bus_LV_1323-24_0_2_node_5 | 0.4 | n |  | TRUE
21 | bus_LV_1323-24_0_2_node_6 | 0.4 | n |  | TRUE
22 | bus_LV_1323-24_0_2_node_7 | 0.4 | n |  | TRUE
23 | bus_LV_1323-24_0_2_node_8 | 0.4 | n |  | TRUE
24 | bus_LV_1323-24_0_2_node_41 | 0.4 | n |  | TRUE
25 | bus_LV_1323-24_0_2_node_42 | 0.4 | n |  | TRUE
26 | bus_LV_1323-24_0_2_node_66 | 0.4 | n |  | TRUE
27 | bus_LV_1323-24_0_2_node_40 | 0.4 | n |  | TRUE
28 | bus_LV_1323-24_0_2_node_43 | 0.4 | n |  | TRUE
29 | bus_LV_1323-24_0_2_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_1323-24_0_2_node_33 | 0.4 | n |  | TRUE
31 | bus_LV_1323-24_0_2_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_1323-24_0_2_node_70 | 0.4 | n |  | TRUE
33 | bus_LV_1323-24_0_2_node_9 | 0.4 | n |  | TRUE
34 | bus_LV_1323-24_0_2_node_10 | 0.4 | n |  | TRUE
35 | bus_LV_1323-24_0_2_node_11 | 0.4 | n |  | TRUE
36 | bus_LV_1323-24_0_2_node_12 | 0.4 | n |  | TRUE
37 | bus_LV_1323-24_0_2_node_13 | 0.4 | n |  | TRUE
38 | bus_LV_1323-24_0_2_node_17 | 0.4 | n |  | TRUE
39 | bus_LV_1323-24_0_2_node_15 | 0.4 | n |  | TRUE
40 | bus_LV_1323-24_0_2_node_19 | 0.4 | n |  | TRUE
41 | bus_LV_1323-24_0_2_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_1323-24_0_2_node_20 | 0.4 | n |  | TRUE
43 | bus_LV_1323-24_0_2_node_23 | 0.4 | n |  | TRUE
44 | bus_LV_1323-24_0_2_node_14 | 0.4 | n |  | TRUE
45 | bus_LV_1323-24_0_2_node_16 | 0.4 | n |  | TRUE
46 | bus_LV_1323-24_0_2_node_18 | 0.4 | n |  | TRUE
47 | bus_LV_1323-24_0_2_node_24 | 0.4 | n |  | TRUE
48 | bus_LV_1323-24_0_2_node_25 | 0.4 | n |  | TRUE
49 | bus_LV_1323-24_0_2_node_26 | 0.4 | n |  | TRUE
50 | bus_LV_1323-24_0_2_node_27 | 0.4 | n |  | TRUE
51 | bus_LV_1323-24_0_2_node_28 | 0.4 | n |  | TRUE
52 | bus_LV_1323-24_0_2_node_29 | 0.4 | n |  | TRUE
53 | bus_LV_1323-24_0_2_node_21 | 0.4 | n |  | TRUE
54 | bus_LV_1323-24_0_2_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_1323-24_0_2_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_1323-24_0_2_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_1323-24_0_2_node_58 | 0.4 | n |  | TRUE
58 | bus_LV_1323-24_0_2_node_57 | 0.4 | n |  | TRUE
59 | bus_LV_1323-24_0_2_node_59 | 0.4 | n |  | TRUE
60 | bus_LV_1323-24_0_2_node_60 | 0.4 | n |  | TRUE
61 | bus_LV_1323-24_0_2_node_65 | 0.4 | n |  | TRUE
62 | bus_LV_1323-24_0_2_node_79 | 0.4 | n |  | TRUE
63 | bus_LV_1323-24_0_2_node_44 | 0.4 | n |  | TRUE
64 | bus_LV_1323-24_0_2_node_53 | 0.4 | n |  | TRUE
65 | bus_LV_1323-24_0_2_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_1323-24_0_2_node_45 | 0.4 | n |  | TRUE
67 | bus_LV_1323-24_0_2_node_46 | 0.4 | n |  | TRUE
68 | bus_LV_1323-24_0_2_node_47 | 0.4 | n |  | TRUE
69 | bus_LV_1323-24_0_2_node_48 | 0.4 | n |  | TRUE
70 | bus_LV_1323-24_0_2_node_49 | 0.4 | n |  | TRUE
71 | bus_LV_1323-24_0_2_node_54 | 0.4 | n |  | TRUE
72 | bus_LV_1323-24_0_2_node_52 | 0.4 | n |  | TRUE
73 | bus_LV_1323-24_0_2_node_62 | 0.4 | n |  | TRUE
74 | bus_LV_1323-24_0_2_node_55 | 0.4 | n |  | TRUE
75 | bus_LV_1323-24_0_2_node_50 | 0.4 | n |  | TRUE
76 | bus_LV_1323-24_0_2_node_61 | 0.4 | n |  | TRUE
77 | bus_LV_1323-24_0_2_node_56 | 0.4 | n |  | TRUE
78 | bus_LV_1323-24_0_2_node_64 | 0.4 | n |  | TRUE
79 | bus_MV_15_0_node_121 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1323-24_0_2_load_0 | 0 | 0.0033851 | 0.00084838 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1323-24_0_2_load_1 | 1 | 0.0057407 | 0.0014388 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1323-24_0_2_load_2 | 2 | 0.0053945 | 0.001352 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1323-24_0_2_load_3 | 3 | 0.0044365 | 0.0011119 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1323-24_0_2_load_4 | 4 | 0.0035259 | 0.00088367 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1323-24_0_2_load_72 | 5 | 0.0019575 | 0.00049059 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1323-24_0_2_load_73 | 6 | 0.0023259 | 0.00058292 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1323-24_0_2_load_71 | 7 | 0.002327 | 0.0005832 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1323-24_0_2_load_39 | 8 | 0.0038299 | 0.00095988 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1323-24_0_2_load_74 | 9 | 0.0018989 | 0.00047591 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1323-24_0_2_load_75 | 10 | 0.0020202 | 0.00050631 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1323-24_0_2_load_38 | 11 | 0.002951 | 0.0007396 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1323-24_0_2_load_69 | 12 | 0.0019574 | 0.00049056 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1323-24_0_2_load_68 | 13 | 0.002095 | 0.00052507 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1323-24_0_2_load_37 | 14 | 0.0047051 | 0.0011792 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1323-24_0_2_load_77 | 15 | 0.0020223 | 0.00050684 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1323-24_0_2_load_78 | 16 | 0.0020165 | 0.00050539 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1323-24_0_2_load_76 | 17 | 0.0019001 | 0.0004762 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1323-24_0_2_load_30 | 18 | 0.0027998 | 0.00070169 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1323-24_0_2_load_67 | 19 | 0.0019312 | 0.000484 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1323-24_0_2_load_5 | 20 | 0.0038687 | 0.00096958 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1323-24_0_2_load_8 | 23 | 0.0022034 | 0.00055222 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1323-24_0_2_load_41 | 24 | 0.0024553 | 0.00061535 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1323-24_0_2_load_42 | 25 | 0.0033394 | 0.00083692 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1323-24_0_2_load_66 | 26 | 0.002204 | 0.00055238 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1323-24_0_2_load_40 | 27 | 0.0098484 | 0.0024682 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1323-24_0_2_load_43 | 28 | 0.0040423 | 0.0010131 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1323-24_0_2_load_33 | 30 | 0.0025868 | 0.00064831 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1323-24_0_2_load_31 | 31 | 0.0039664 | 0.00099407 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1323-24_0_2_load_70 | 32 | 0.0026469 | 0.00066337 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1323-24_0_2_load_9 | 33 | 0.0029123 | 0.0007299 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1323-24_0_2_load_10 | 34 | 0.0020222 | 0.00050681 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1323-24_0_2_load_11 | 35 | 0.001393 | 0.00034913 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1323-24_0_2_load_12 | 36 | 0.0013911 | 0.00034864 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1323-24_0_2_load_13 | 37 | 0.0020229 | 0.00050698 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1323-24_0_2_load_17 | 38 | 0.0050702 | 0.0012707 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1323-24_0_2_load_15 | 39 | 0.0064423 | 0.0016146 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1323-24_0_2_load_19 | 40 | 0.0013267 | 0.0003325 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1323-24_0_2_load_22 | 41 | 0.0029887 | 0.00074904 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1323-24_0_2_load_20 | 42 | 0.0048496 | 0.0012154 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1323-24_0_2_load_23 | 43 | 0.0017125 | 0.00042919 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1323-24_0_2_load_14 | 44 | 0.0034668 | 0.00086887 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1323-24_0_2_load_16 | 45 | 0.0019312 | 0.000484 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1323-24_0_2_load_18 | 46 | 0.0018123 | 0.0004542 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1323-24_0_2_load_24 | 47 | 0.0013466 | 0.0003375 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1323-24_0_2_load_25 | 48 | 0.001406 | 0.00035238 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1323-24_0_2_load_26 | 49 | 0.0017141 | 0.00042958 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1323-24_0_2_load_27 | 50 | 0.0013479 | 0.00033783 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1323-24_0_2_load_28 | 51 | 0.0026983 | 0.00067625 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1323-24_0_2_load_29 | 52 | 0.0014642 | 0.00036697 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1323-24_0_2_load_21 | 53 | 0.0027437 | 0.00068765 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1323-24_0_2_load_34 | 54 | 0.0034064 | 0.00085373 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1323-24_0_2_load_35 | 55 | 0.0094877 | 0.0023778 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1323-24_0_2_load_58 | 57 | 0.0077549 | 0.0019436 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1323-24_0_2_load_57 | 58 | 0.0061414 | 0.0015392 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1323-24_0_2_load_59 | 59 | 0.002867 | 0.00071855 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1323-24_0_2_load_60 | 60 | 0.0020585 | 0.0005159 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1323-24_0_2_load_65 | 61 | 0.0020595 | 0.00051615 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1323-24_0_2_load_79 | 62 | 0.0020155 | 0.00050513 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1323-24_0_2_load_44 | 63 | 0.011412 | 0.0028601 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1323-24_0_2_load_51 | 65 | 0.012595 | 0.0031566 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1323-24_0_2_load_45 | 66 | 0.0024674 | 0.0006184 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1323-24_0_2_load_46 | 67 | 0.0024697 | 0.00061896 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1323-24_0_2_load_47 | 68 | 0.002503 | 0.0006273 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1323-24_0_2_load_48 | 69 | 0.0030767 | 0.00077109 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1323-24_0_2_load_54 | 71 | 0.0039071 | 0.00097921 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1323-24_0_2_load_52 | 72 | 0.0026431 | 0.00066243 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1323-24_0_2_load_55 | 74 | 0.015692 | 0.0039328 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1323-24_0_2_load_50 | 75 | 0.0052185 | 0.0013079 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1323-24_0_2_load_61 | 76 | 0.0075733 | 0.0018981 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1323-24_0_2_load_56 | 77 | 0.0049855 | 0.0012495 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1323-24_0_2_load_64 | 78 | 0.01131 | 0.0028344 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1323-24_0_2_line_0 |  | 0 | 1 | 0.013699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1323-24_0_2_line_1 |  | 0 | 2 | 0.0060577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1323-24_0_2_line_2 |  | 1 | 3 | 0.016913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1323-24_0_2_line_3 |  | 2 | 4 | 0.013082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1323-24_0_2_line_4 |  | 3 | 8 | 0.01397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1323-24_0_2_line_5 |  | 4 | 11 | 0.0096125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1323-24_0_2_line_6 |  | 5 | 6 | 0.001948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1323-24_0_2_line_7 |  | 5 | 7 | 0.0055026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1323-24_0_2_line_8 |  | 6 | 9 | 0.016836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1323-24_0_2_line_9 |  | 7 | 12 | 0.0014465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1323-24_0_2_line_10 |  | 8 | 14 | 0.011996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1323-24_0_2_line_11 |  | 9 | 10 | 0.0033702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1323-24_0_2_line_12 |  | 10 | 17 | 0.0035074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1323-24_0_2_line_13 |  | 11 | 18 | 0.0010203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1323-24_0_2_line_14 |  | 12 | 13 | 0.018675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1323-24_0_2_line_15 |  | 13 | 19 | 0.0035456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1323-24_0_2_line_16 |  | 14 | 55 | 0.011699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1323-24_0_2_line_17 |  | 15 | 16 | 0.01452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1323-24_0_2_line_18 |  | 15 | 17 | 0.0036429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1323-24_0_2_line_19 |  | 16 | 62 | 0.0073429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1323-24_0_2_line_20 |  | 18 | 52 | 0.014337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1323-24_0_2_line_21 |  | 19 | 46 | 0.003975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1323-24_0_2_line_22 |  | 20 | 21 | 0.040967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1323-24_0_2_line_23 |  | 21 | 22 | 0.051122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1323-24_0_2_line_24 |  | 21 | 23 | 0.012793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1323-24_0_2_line_25 |  | 22 | 24 | 0.040536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1323-24_0_2_line_26 |  | 22 | 25 | 0.024408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1323-24_0_2_line_27 |  | 23 | 26 | 0.0070292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1323-24_0_2_line_28 |  | 24 | 27 | 0.0010044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1323-24_0_2_line_29 |  | 25 | 28 | 0.0034882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1323-24_0_2_line_30 |  | 27 | 38 | 0.0067693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1323-24_0_2_line_31 |  | 28 | 63 | 0.044051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1323-24_0_2_line_32 |  | 29 | 30 | 0.0056628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1323-24_0_2_line_33 |  | 29 | 31 | 0.014287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1323-24_0_2_line_34 |  | 30 | 32 | 0.0078512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1323-24_0_2_line_35 |  | 31 | 53 | 0.003092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1323-24_0_2_line_36 |  | 33 | 34 | 0.0046785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1323-24_0_2_line_37 |  | 33 | 35 | 0.0030412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1323-24_0_2_line_38 |  | 34 | 36 | 0.00059449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1323-24_0_2_line_39 |  | 35 | 37 | 0.0012899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1323-24_0_2_line_40 |  | 36 | 40 | 0.011501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1323-24_0_2_line_41 |  | 37 | 41 | 0.011619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1323-24_0_2_line_42 |  | 38 | 39 | 0.013735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1323-24_0_2_line_43 |  | 39 | 44 | 0.007387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1323-24_0_2_line_44 |  | 40 | 42 | 0.011543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1323-24_0_2_line_45 |  | 41 | 43 | 0.004885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1323-24_0_2_line_46 |  | 42 | 53 | 0.0029479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1323-24_0_2_line_47 |  | 43 | 47 | 0.00044118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1323-24_0_2_line_48 |  | 44 | 45 | 0.013119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1323-24_0_2_line_49 |  | 45 | 46 | 0.0031562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1323-24_0_2_line_50 |  | 47 | 48 | 0.00089171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1323-24_0_2_line_51 |  | 48 | 49 | 0.0068897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1323-24_0_2_line_52 |  | 49 | 50 | 0.00065971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1323-24_0_2_line_53 |  | 50 | 51 | 0.0058517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1323-24_0_2_line_54 |  | 51 | 52 | 0.0014003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1323-24_0_2_line_55 |  | 54 | 55 | 0.017738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1323-24_0_2_line_56 |  | 54 | 56 | 0.030281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1323-24_0_2_line_57 |  | 56 | 57 | 0.056703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1323-24_0_2_line_58 |  | 57 | 58 | 0.024136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1323-24_0_2_line_59 |  | 58 | 59 | 0.0024564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1323-24_0_2_line_60 |  | 59 | 60 | 0.018114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1323-24_0_2_line_61 |  | 60 | 61 | 0.006982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1323-24_0_2_line_62 |  | 61 | 62 | 0.0021028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1323-24_0_2_line_63 |  | 63 | 64 | 0.010307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1323-24_0_2_line_64 |  | 64 | 65 | 0.017188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1323-24_0_2_line_65 |  | 65 | 75 | 0.013843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1323-24_0_2_line_66 |  | 66 | 67 | 0.0080513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1323-24_0_2_line_67 |  | 66 | 68 | 0.0080814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1323-24_0_2_line_68 |  | 67 | 69 | 0.0087436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1323-24_0_2_line_69 |  | 68 | 70 | 0.019638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1323-24_0_2_line_70 |  | 69 | 71 | 0.011339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1323-24_0_2_line_71 |  | 70 | 72 | 0.014164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1323-24_0_2_line_72 |  | 70 | 73 | 0.052307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1323-24_0_2_line_73 |  | 71 | 74 | 0.0074151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1323-24_0_2_line_74 |  | 72 | 75 | 0.019424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1323-24_0_2_line_75 |  | 73 | 76 | 0.00639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1323-24_0_2_line_76 |  | 74 | 77 | 0.015716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1323-24_0_2_line_77 |  | 77 | 78 | 0.0081591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1323-24_0_2_trafo_71 | 0.63 MVA 20/0.4 kV | 79 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2696624.8894 | 1227833.3254 | 2696636.6101 | 1227834.0678 | 2696638.562 | 1227834.1714
1 | 2696624.8894 | 1227833.3254 | 2696618.8438 | 1227832.9425
2 | 2696655.4515 | 1227835.0679 | 2696638.562 | 1227834.1714
3 | 2696618.8438 | 1227832.9425 | 2696605.7876 | 1227832.1155
4 | 2696655.4515 | 1227835.0679 | 2696669.402 | 1227835.8084
5 | 2696596.1943 | 1227831.5079 | 2696605.7876 | 1227832.1155
6 | 2696628.7621 | 1227900.6118 | 2696626.8143 | 1227900.642
7 | 2696621.3123 | 1227900.7276 | 2696626.8143 | 1227900.642
8 | 2696628.7621 | 1227900.6118 | 2696645.5962 | 1227900.35
9 | 2696621.3123 | 1227900.7276 | 2696619.866 | 1227900.7501
10 | 2696681.3816 | 1227836.4443 | 2696669.402 | 1227835.8084
11 | 2696648.9661 | 1227900.2976 | 2696645.5962 | 1227900.35
12 | 2696648.9661 | 1227900.2976 | 2696652.473 | 1227900.2431
13 | 2696595.1761 | 1227831.4434 | 2696596.1943 | 1227831.5079
14 | 2696601.1928 | 1227901.0404 | 2696619.866 | 1227900.7501
15 | 2696597.6477 | 1227901.0956 | 2696601.1928 | 1227901.0404
16 | 2696681.3816 | 1227836.4443 | 2696693.0646 | 1227837.0644
17 | 2696656.1155 | 1227900.1864 | 2696670.6338 | 1227899.9607
18 | 2696656.1155 | 1227900.1864 | 2696652.473 | 1227900.2431
19 | 2696670.6338 | 1227899.9607 | 2696677.9758 | 1227899.8465
20 | 2696580.8676 | 1227830.5371 | 2696595.1761 | 1227831.4434
21 | 2696593.6732 | 1227901.1574 | 2696597.6477 | 1227901.0956
22 | 2696475.4672 | 1227917.4348 | 2696468.0905 | 1227925.521 | 2696447.2834 | 1227934.101 | 2696439.7714 | 1227933.9025
23 | 2696523.1132 | 1227936.299 | 2696510.1609 | 1227931.6188 | 2696503.2343 | 1227928.7822 | 2696475.4672 | 1227917.4348
24 | 2696475.4672 | 1227917.4348 | 2696463.4903 | 1227912.9374
25 | 2696523.1132 | 1227936.299 | 2696532.7518 | 1227919.143 | 2696548.8526 | 1227905.8836
26 | 2696523.1132 | 1227936.299 | 2696545.7728 | 1227945.3711
27 | 2696463.4903 | 1227912.9374 | 2696456.9097 | 1227910.4664
28 | 2696549.8449 | 1227905.7281 | 2696548.8526 | 1227905.8836 | 2696548.8526 | 1227905.8836
29 | 2696545.7728 | 1227945.3711 | 2696549.0111 | 1227946.6676
30 | 2696549.8449 | 1227905.7281 | 2696556.5326 | 1227904.6802
31 | 2696589.9062 | 1227963.0406 | 2696549.0111 | 1227946.6676
32 | 2696495.4069 | 1227833.4199 | 2696489.7943 | 1227834.1721
33 | 2696495.4069 | 1227833.4199 | 2696509.6595 | 1227832.4358
34 | 2696482.0126 | 1227835.2149 | 2696489.7943 | 1227834.1721
35 | 2696512.7442 | 1227832.2229 | 2696509.6595 | 1227832.4358
36 | 2696543.9349 | 1227830.0693 | 2696539.2675 | 1227830.3916
37 | 2696543.9349 | 1227830.0693 | 2696546.9688 | 1227829.8598
38 | 2696538.6744 | 1227830.4325 | 2696539.2675 | 1227830.3916
39 | 2696548.2557 | 1227829.771 | 2696546.9688 | 1227829.8598
40 | 2696527.201 | 1227831.2247 | 2696538.6744 | 1227830.4325
41 | 2696559.864 | 1227829.7835 | 2696551.4717 | 1227829.5489 | 2696548.2557 | 1227829.771
42 | 2696556.5326 | 1227904.6802 | 2696570.1016 | 1227902.554
43 | 2696577.3996 | 1227901.4104 | 2696570.1016 | 1227902.554
44 | 2696515.6851 | 1227832.0198 | 2696527.201 | 1227831.2247
45 | 2696559.864 | 1227829.7835 | 2696564.7472 | 1227829.92
46 | 2696515.6851 | 1227832.0198 | 2696512.7442 | 1227832.2229
47 | 2696564.7472 | 1227829.92 | 2696565.1882 | 1227829.9323
48 | 2696577.3996 | 1227901.4104 | 2696577.3996 | 1227901.4104 | 2696590.5174 | 1227901.2064
49 | 2696593.6732 | 1227901.1574 | 2696590.5174 | 1227901.2064
50 | 2696565.1882 | 1227829.9323 | 2696566.0795 | 1227829.9572
51 | 2696566.0795 | 1227829.9572 | 2696572.9666 | 1227830.1497
52 | 2696572.9666 | 1227830.1497 | 2696573.626 | 1227830.1682
53 | 2696573.626 | 1227830.1682 | 2696576.1608 | 1227830.239 | 2696579.4701 | 1227830.4486
54 | 2696580.8676 | 1227830.5371 | 2696579.4701 | 1227830.4486
55 | 2696693.0646 | 1227837.0644 | 2696695.4944 | 1227837.1934 | 2696710.7275 | 1227838.6731
56 | 2696740.8669 | 1227841.6008 | 2696710.7275 | 1227838.6731
57 | 2696731.6688 | 1227897.553 | 2696740.8669 | 1227841.6008
58 | 2696707.6273 | 1227899.3855 | 2696716.1914 | 1227899.2523 | 2696731.6688 | 1227897.553
59 | 2696707.6273 | 1227899.3855 | 2696705.1712 | 1227899.4237
60 | 2696705.1712 | 1227899.4237 | 2696687.0595 | 1227899.7053
61 | 2696680.0783 | 1227899.8138 | 2696687.0595 | 1227899.7053
62 | 2696680.0783 | 1227899.8138 | 2696677.9758 | 1227899.8465
63 | 2696599.4747 | 1227966.8715 | 2696589.9062 | 1227963.0406
64 | 2696599.4747 | 1227966.8715 | 2696615.613 | 1227972.785
65 | 2696628.6113 | 1227977.548 | 2696615.613 | 1227972.785
66 | 2696673.7836 | 1227962.017 | 2696677.5125 | 1227954.8813
67 | 2696673.7836 | 1227962.017 | 2696670.0406 | 1227969.1794
68 | 2696677.5125 | 1227954.8813 | 2696681.5621 | 1227947.1321
69 | 2696660.9452 | 1227986.5841 | 2696670.0406 | 1227969.1794
70 | 2696692.2255 | 1227947.4536 | 2696682.0734 | 1227946.1538 | 2696681.5621 | 1227947.1321
71 | 2696660.9452 | 1227986.5841 | 2696647.2615 | 1227982.9286
72 | 2696660.9452 | 1227986.5841 | 2696711.5608 | 1228000.3388
73 | 2696692.2255 | 1227947.4536 | 2696699.5806 | 1227948.3952
74 | 2696628.6113 | 1227977.548 | 2696632.6246 | 1227979.0186 | 2696647.2615 | 1227982.9286
75 | 2696711.5608 | 1228000.3388 | 2696717.7269 | 1228002.0154
76 | 2696715.1695 | 1227950.391 | 2696699.5806 | 1227948.3952
77 | 2696723.2626 | 1227951.4271 | 2696715.1695 | 1227950.391

## bus_geodata
| x | y | coords
0 | 2696624.8894 | 1227833.3254
1 | 2696638.562 | 1227834.1714
2 | 2696618.8438 | 1227832.9425
3 | 2696655.4515 | 1227835.0679
4 | 2696605.7876 | 1227832.1155
5 | 2696626.8143 | 1227900.642
6 | 2696628.7621 | 1227900.6118
7 | 2696621.3123 | 1227900.7276
8 | 2696669.402 | 1227835.8084
9 | 2696645.5962 | 1227900.35
10 | 2696648.9661 | 1227900.2976
11 | 2696596.1943 | 1227831.5079
12 | 2696619.866 | 1227900.7501
13 | 2696601.1928 | 1227901.0404
14 | 2696681.3816 | 1227836.4443
15 | 2696656.1155 | 1227900.1864
16 | 2696670.6338 | 1227899.9607
17 | 2696652.473 | 1227900.2431
18 | 2696595.1761 | 1227831.4434
19 | 2696597.6477 | 1227901.0956
20 | 2696439.7714 | 1227933.9025
21 | 2696475.4672 | 1227917.4348
22 | 2696523.1132 | 1227936.299
23 | 2696463.4903 | 1227912.9374
24 | 2696548.8526 | 1227905.8836
25 | 2696545.7728 | 1227945.3711
26 | 2696456.9097 | 1227910.4664
27 | 2696549.8449 | 1227905.7281
28 | 2696549.0111 | 1227946.6676
29 | 2696495.4069 | 1227833.4199
30 | 2696489.7943 | 1227834.1721
31 | 2696509.6595 | 1227832.4358
32 | 2696482.0126 | 1227835.2149
33 | 2696543.9349 | 1227830.0693
34 | 2696539.2675 | 1227830.3916
35 | 2696546.9688 | 1227829.8598
36 | 2696538.6744 | 1227830.4325
37 | 2696548.2557 | 1227829.771
38 | 2696556.5325 | 1227904.6802
39 | 2696570.1016 | 1227902.554
40 | 2696527.201 | 1227831.2247
41 | 2696559.864 | 1227829.7835
42 | 2696515.6851 | 1227832.0198
43 | 2696564.7472 | 1227829.92
44 | 2696577.3996 | 1227901.4104
45 | 2696590.5174 | 1227901.2064
46 | 2696593.6732 | 1227901.1574
47 | 2696565.1882 | 1227829.9323
48 | 2696566.0795 | 1227829.9572
49 | 2696572.9666 | 1227830.1497
50 | 2696573.626 | 1227830.1682
51 | 2696579.4701 | 1227830.4486
52 | 2696580.8676 | 1227830.5371
53 | 2696512.7442 | 1227832.2229
54 | 2696710.7275 | 1227838.6731
55 | 2696693.0646 | 1227837.0644
56 | 2696740.8669 | 1227841.6008
57 | 2696731.6688 | 1227897.553
58 | 2696707.6273 | 1227899.3855
59 | 2696705.1712 | 1227899.4237
60 | 2696687.0595 | 1227899.7053
61 | 2696680.0783 | 1227899.8138
62 | 2696677.9758 | 1227899.8465
63 | 2696589.9062 | 1227963.0406
64 | 2696599.4747 | 1227966.8715
65 | 2696615.613 | 1227972.785
66 | 2696673.7836 | 1227962.017
67 | 2696677.5125 | 1227954.8813
68 | 2696670.0406 | 1227969.1794
69 | 2696681.5621 | 1227947.1321
70 | 2696660.9452 | 1227986.5841
71 | 2696692.2255 | 1227947.4536
72 | 2696647.2615 | 1227982.9286
73 | 2696711.5608 | 1228000.3388
74 | 2696699.5806 | 1227948.3952
75 | 2696628.6113 | 1227977.548
76 | 2696717.7269 | 1228002.0154
77 | 2696715.1695 | 1227950.391
78 | 2696723.2626 | 1227951.4271
79 | 2696523.1132 | 1227936.299

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97497 | -0.48093 | 0.0033851 | 0.00084838
1 | 0.97575 | -0.46573 | 0.0057407 | 0.0014388
2 | 0.97465 | -0.48729 | 0.0053945 | 0.001352
3 | 0.97679 | -0.44521 | 0.0044365 | 0.0011119
4 | 0.97402 | -0.49974 | 0.0035259 | 0.00088367
5 | 0.99934 | -0.012405 | 0.0019575 | 0.00049059
6 | 0.99911 | -0.016733 | 0.0023259 | 0.00058292
7 | 1 | 0 | -0.27411 | -0.070102
8 | 0.97771 | -0.42716 | 0.0038299 | 0.00095988
9 | 0.99716 | -0.053543 | 0.0018989 | 0.00047591
10 | 0.99677 | -0.060816 | 0.0020202 | 0.00050631
11 | 0.97358 | -0.50827 | 0.002951 | 0.0007396
12 | 0.99981 | -0.0034934 | 0.0019574 | 0.00049056
13 | 0.99746 | -0.048072 | 0.002095 | 0.00052507
14 | 0.97855 | -0.41085 | 0.0047051 | 0.0011792
15 | 0.99598 | -0.075891 | 0.0020223 | 0.00050684
16 | 0.9944 | -0.10582 | 0.0020165 | 0.00050539
17 | 0.99638 | -0.068267 | 0.0019001 | 0.0004762
18 | 0.97354 | -0.50912 | 0.0027998 | 0.00070169
19 | 0.99702 | -0.056429 | 0.0019312 | 0.000484
20 | 0.98705 | -0.24701 | 0.0038687 | 0.00096958
21 | 0.9872 | -0.24417 | 0 | 0
22 | 0.98759 | -0.2366 | 0 | 0
23 | 0.98715 | -0.24518 | 0.0022034 | 0.00055222
24 | 0.9914 | -0.16334 | 0.0024553 | 0.00061535
25 | 0.98548 | -0.27736 | 0.0033394 | 0.00083692
26 | 0.98713 | -0.24546 | 0.002204 | 0.00055238
27 | 0.9915 | -0.16149 | 0.0098484 | 0.0024682
28 | 0.98518 | -0.28299 | 0.0040423 | 0.0010131
29 | 0.97126 | -0.55409 | 0 | 0
30 | 0.97124 | -0.55464 | 0.0025868 | 0.00064831
31 | 0.97133 | -0.55271 | 0.0039664 | 0.00099407
32 | 0.97122 | -0.55502 | 0.0026469 | 0.00066337
33 | 0.97187 | -0.54203 | 0.0029123 | 0.0007299
34 | 0.97178 | -0.54389 | 0.0020222 | 0.00050681
35 | 0.97194 | -0.54066 | 0.001393 | 0.00034913
36 | 0.97177 | -0.54411 | 0.0013911 | 0.00034864
37 | 0.97197 | -0.54005 | 0.0020229 | 0.00050698
38 | 0.99222 | -0.14784 | 0.0050702 | 0.0012707
39 | 0.99373 | -0.11897 | 0.0064423 | 0.0016146
40 | 0.97157 | -0.54795 | 0.0013267 | 0.0003325
41 | 0.97228 | -0.53408 | 0.0029887 | 0.00074904
42 | 0.97139 | -0.55153 | 0.0048496 | 0.0012154
43 | 0.97242 | -0.5313 | 0.0017125 | 0.00042919
44 | 0.99458 | -0.10265 | 0.0034668 | 0.00086887
45 | 0.99615 | -0.072917 | 0.0019312 | 0.000484
46 | 0.99653 | -0.065672 | 0.0018123 | 0.0004542
47 | 0.97243 | -0.53103 | 0.0013466 | 0.0003375
48 | 0.97246 | -0.53047 | 0.001406 | 0.00035238
49 | 0.97269 | -0.52599 | 0.0017141 | 0.00042958
50 | 0.97271 | -0.52554 | 0.0013479 | 0.00033783
51 | 0.97292 | -0.5214 | 0.0026983 | 0.00067625
52 | 0.97297 | -0.52035 | 0.0014642 | 0.00036697
53 | 0.97136 | -0.55218 | 0.0027437 | 0.00068765
54 | 0.98088 | -0.3654 | 0.0034064 | 0.00085373
55 | 0.97941 | -0.39398 | 0.0094877 | 0.0023778
56 | 0.98348 | -0.31495 | 0 | 0
57 | 0.98835 | -0.22119 | 0.0077549 | 0.0019436
58 | 0.99059 | -0.17824 | 0.0061414 | 0.0015392
59 | 0.99084 | -0.17361 | 0.002867 | 0.00071855
60 | 0.99267 | -0.13863 | 0.0020585 | 0.0005159
61 | 0.99339 | -0.12493 | 0.0020595 | 0.00051615
62 | 0.99361 | -0.12073 | 0.0020155 | 0.00050513
63 | 0.98167 | -0.35116 | 0.011412 | 0.0028601
64 | 0.98096 | -0.36504 | 0 | 0
65 | 0.97977 | -0.38825 | 0.012595 | 0.0031566
66 | 0.97606 | -0.46092 | 0.0024674 | 0.0006184
67 | 0.97575 | -0.46703 | 0.0024697 | 0.00061896
68 | 0.97639 | -0.45443 | 0.002503 | 0.0006273
69 | 0.97544 | -0.47327 | 0.0030767 | 0.00077109
70 | 0.97724 | -0.43778 | 0 | 0
71 | 0.97506 | -0.48072 | 0.0039071 | 0.00097921
72 | 0.97795 | -0.42383 | 0.0026431 | 0.00066243
73 | 0.97687 | -0.44501 | 0 | 0
74 | 0.97484 | -0.48507 | 0.015692 | 0.0039328
75 | 0.97898 | -0.40381 | 0.0052185 | 0.0013079
76 | 0.97683 | -0.4459 | 0.0075733 | 0.0018981
77 | 0.9746 | -0.48977 | 0.0049855 | 0.0012495
78 | 0.97451 | -0.49146 | 0.01131 | 0.0028344
79 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.060732 | -0.015272 | 0.060776 | 0.0153 | 4.4152e-05 | 2.8087e-05 | 0.092708 | 0.092708 | 0.092708 | 0.97497 | -0.48093 | 0.97575 | -0.46573 | 25.4693
1 | 0.057347 | 0.014424 | -0.057329 | -0.014412 | 1.7409e-05 | 1.1066e-05 | 0.087542 | 0.087542 | 0.087542 | 0.97497 | -0.48093 | 0.97465 | -0.48729 | 24.05
2 | -0.066517 | -0.016739 | 0.066582 | 0.01678 | 6.5294e-05 | 4.1577e-05 | 0.10146 | 0.10146 | 0.10146 | 0.97575 | -0.46573 | 0.97679 | -0.44521 | 27.8744
3 | 0.051935 | 0.01306 | -0.051904 | -0.013041 | 3.0855e-05 | 1.9584e-05 | 0.079306 | 0.079306 | 0.079306 | 0.97465 | -0.48729 | 0.97402 | -0.49974 | 21.7874
4 | -0.071019 | -0.017892 | 0.07108 | 0.017931 | 6.1356e-05 | 3.9093e-05 | 0.10822 | 0.10822 | 0.10822 | 0.97679 | -0.44521 | 0.97771 | -0.42716 | 29.7311
5 | 0.048378 | 0.012157 | -0.048358 | -0.012145 | 1.9696e-05 | 1.2486e-05 | 0.07392 | 0.07392 | 0.07392 | 0.97402 | -0.49974 | 0.97358 | -0.50827 | 20.3076
6 | 0.12965 | 0.033408 | -0.12962 | -0.033391 | 2.7316e-05 | 1.7456e-05 | 0.19337 | 0.19337 | 0.19337 | 0.99934 | -0.012405 | 0.99911 | -0.016733 | 53.1238
7 | -0.13161 | -0.033899 | 0.13168 | 0.033949 | 7.9502e-05 | 5.0809e-05 | 0.19629 | 0.19629 | 0.19629 | 0.99934 | -0.012405 | 1 | 0 | 53.9245
8 | 0.12729 | 0.032808 | -0.12707 | -0.032662 | 0.0002277 | 0.00014551 | 0.18991 | 0.18991 | 0.18991 | 0.99911 | -0.016733 | 0.99716 | -0.053543 | 52.1722
9 | 0.14077 | 0.036152 | -0.14075 | -0.036137 | 2.3872e-05 | 1.5259e-05 | 0.20978 | 0.20978 | 0.20978 | 1 | 0 | 0.99981 | -0.0034934 | 57.6329
10 | -0.07491 | -0.018891 | 0.074968 | 0.018929 | 5.8516e-05 | 3.73e-05 | 0.11405 | 0.11405 | 0.11405 | 0.97771 | -0.42716 | 0.97855 | -0.41085 | 31.3324
11 | 0.12517 | 0.032186 | -0.12512 | -0.032158 | 4.423e-05 | 2.8263e-05 | 0.18707 | 0.18707 | 0.18707 | 0.99716 | -0.053543 | 0.99677 | -0.060816 | 51.3937
12 | 0.1231 | 0.031652 | -0.12306 | -0.031623 | 4.4557e-05 | 2.8471e-05 | 0.18406 | 0.18406 | 0.18406 | 0.99677 | -0.060816 | 0.99638 | -0.068267 | 50.5652
13 | 0.045407 | 0.011405 | -0.045406 | -0.011404 | 1.8433e-06 | 1.167e-06 | 0.069409 | 0.069409 | 0.069409 | 0.97358 | -0.50827 | 0.97354 | -0.50912 | 19.0685
14 | 0.13879 | 0.035646 | -0.13849 | -0.035455 | 0.00029971 | 0.00019157 | 0.20687 | 0.20687 | 0.20687 | 0.99981 | -0.0034934 | 0.99746 | -0.048072 | 56.8326
15 | 0.1364 | 0.03493 | -0.13634 | -0.034895 | 5.5194e-05 | 3.5278e-05 | 0.20375 | 0.20375 | 0.20375 | 0.99746 | -0.048072 | 0.99702 | -0.056429 | 55.974
16 | -0.079674 | -0.020108 | 0.079738 | 0.020149 | 6.4452e-05 | 4.1102e-05 | 0.1212 | 0.1212 | 0.1212 | 0.97855 | -0.41085 | 0.97941 | -0.39398 | 33.298
17 | 0.11909 | 0.030611 | -0.11892 | -0.030501 | 0.0001729 | 0.00011047 | 0.1782 | 0.1782 | 0.1782 | 0.99598 | -0.075891 | 0.9944 | -0.10582 | 48.9557
18 | -0.12111 | -0.031118 | 0.12116 | 0.031147 | 4.4864e-05 | 2.8665e-05 | 0.18122 | 0.18122 | 0.18122 | 0.99598 | -0.075891 | 0.99638 | -0.068267 | 49.7857
19 | 0.1169 | 0.029996 | -0.11682 | -0.029942 | 8.4503e-05 | 5.3987e-05 | 0.17518 | 0.17518 | 0.17518 | 0.9944 | -0.10582 | 0.99361 | -0.12073 | 48.1267
20 | 0.042606 | 0.010702 | -0.042583 | -0.010688 | 2.2806e-05 | 1.4418e-05 | 0.06513 | 0.06513 | 0.06513 | 0.97354 | -0.50912 | 0.97297 | -0.52035 | 17.8929
21 | 0.13441 | 0.034411 | -0.13435 | -0.034372 | 6.014e-05 | 3.8438e-05 | 0.20086 | 0.20086 | 0.20086 | 0.99702 | -0.056429 | 0.99653 | -0.065672 | 55.1822
22 | -0.0038687 | -0.00096958 | 0.0038692 | 0.00096939 | 5.2253e-07 | -1.8929e-07 | 0.0058322 | 0.005832 | 0.0058322 | 0.98705 | -0.24701 | 0.9872 | -0.24417 | 1.6022
23 | -0.0082768 | -0.0020739 | 0.0082798 | 0.0020751 | 2.9837e-06 | 1.2557e-06 | 0.012476 | 0.012475 | 0.012476 | 0.9872 | -0.24417 | 0.98759 | -0.2366 | 3.4274
24 | 0.0044076 | 0.0011045 | -0.0044074 | -0.0011045 | 2.1175e-07 | -2.804e-08 | 0.0066436 | 0.0066437 | 0.0066437 | 0.9872 | -0.24417 | 0.98715 | -0.24518 | 1.8252
25 | -0.10238 | -0.02599 | 0.10274 | 0.026221 | 0.00036224 | 0.00023131 | 0.15437 | 0.15437 | 0.15437 | 0.98759 | -0.2366 | 0.9914 | -0.16334 | 42.4094
26 | 0.094096 | 0.023915 | -0.093912 | -0.023797 | 0.00018429 | 0.00011763 | 0.1419 | 0.1419 | 0.1419 | 0.98759 | -0.2366 | 0.98548 | -0.27736 | 38.9822
27 | 0.002204 | 0.0005523 | -0.002204 | -0.00055238 | 2.9095e-08 | -7.1241e-08 | 0.0033223 | 0.0033223 | 0.0033223 | 0.98715 | -0.24518 | 0.98713 | -0.24546 | 0.91273
28 | -0.10519 | -0.026836 | 0.1052 | 0.026842 | 9.4089e-06 | 6.0088e-06 | 0.15806 | 0.15806 | 0.15806 | 0.9914 | -0.16334 | 0.9915 | -0.16149 | 43.4218
29 | 0.090572 | 0.02296 | -0.090548 | -0.022944 | 2.4498e-05 | 1.5635e-05 | 0.13685 | 0.13685 | 0.13685 | 0.98548 | -0.27736 | 0.98518 | -0.28299 | 37.597
30 | -0.11505 | -0.029311 | 0.11513 | 0.029359 | 7.5829e-05 | 4.8443e-05 | 0.17284 | 0.17284 | 0.17284 | 0.9915 | -0.16149 | 0.99222 | -0.14784 | 47.4822
31 | 0.086506 | 0.021931 | -0.086223 | -0.021751 | 0.00028239 | 0.00018017 | 0.13075 | 0.13075 | 0.13075 | 0.98518 | -0.28299 | 0.98167 | -0.35116 | 35.9197
32 | 0.0052338 | 0.0013116 | -0.0052337 | -0.0013116 | 1.3653e-07 | 1.73e-08 | 0.0080184 | 0.0080184 | 0.0080184 | 0.97126 | -0.55409 | 0.97124 | -0.55464 | 2.2029
33 | -0.0052338 | -0.0013116 | 0.0052342 | 0.0013117 | 3.4445e-07 | 4.3625e-08 | 0.0080184 | 0.0080183 | 0.0080184 | 0.97126 | -0.55409 | 0.97133 | -0.55271 | 2.2029
34 | 0.0026469 | 0.0006633 | -0.0026469 | -0.00066337 | 4.8418e-08 | -6.6173e-08 | 0.0040553 | 0.0040553 | 0.0040553 | 0.97124 | -0.55464 | 0.97122 | -0.55502 | 1.1141
35 | -0.0092006 | -0.0023057 | 0.0092008 | 0.0023059 | 2.3034e-07 | 1.0915e-07 | 0.014095 | 0.014095 | 0.014095 | 0.97133 | -0.55271 | 0.97136 | -0.55218 | 3.8721
36 | 0.021543 | 0.005402 | -0.021541 | -0.0054009 | 1.9088e-06 | 1.1637e-06 | 0.032985 | 0.032985 | 0.032985 | 0.97187 | -0.54203 | 0.97178 | -0.54389 | 9.0618
37 | -0.024455 | -0.0061319 | 0.024457 | 0.0061329 | 1.5989e-06 | 9.8563e-07 | 0.037444 | 0.037444 | 0.037444 | 0.97187 | -0.54203 | 0.97194 | -0.54066 | 10.2867
38 | 0.019519 | 0.0048941 | -0.019518 | -0.0048939 | 1.9915e-07 | 1.2009e-07 | 0.029888 | 0.029888 | 0.029888 | 0.97178 | -0.54389 | 0.97177 | -0.54411 | 8.2111
39 | -0.02585 | -0.006482 | 0.02585 | 0.0064825 | 7.5766e-07 | 4.6891e-07 | 0.039576 | 0.039576 | 0.039576 | 0.97194 | -0.54066 | 0.97197 | -0.54005 | 10.8727
40 | 0.018127 | 0.0045453 | -0.018124 | -0.0045433 | 3.3231e-06 | 1.9843e-06 | 0.027758 | 0.027758 | 0.027758 | 0.97177 | -0.54411 | 0.97157 | -0.54795 | 7.6259
41 | -0.027873 | -0.0069895 | 0.027881 | 0.0069944 | 7.9345e-06 | 4.9341e-06 | 0.042673 | 0.042673 | 0.042673 | 0.97197 | -0.54005 | 0.97228 | -0.53408 | 11.7234
42 | -0.1202 | -0.03063 | 0.12037 | 0.030737 | 0.00016769 | 0.00010714 | 0.18044 | 0.18044 | 0.18044 | 0.99222 | -0.14784 | 0.99373 | -0.11897 | 49.5712
43 | -0.12681 | -0.032351 | 0.12691 | 0.032415 | 0.00010009 | 6.3963e-05 | 0.19009 | 0.19009 | 0.19009 | 0.99373 | -0.11897 | 0.99458 | -0.10265 | 52.2213
44 | 0.016797 | 0.0042108 | -0.016795 | -0.0042091 | 2.865e-06 | 1.6906e-06 | 0.025726 | 0.025726 | 0.025726 | 0.97157 | -0.54795 | 0.97139 | -0.55153 | 7.0677
45 | -0.03087 | -0.0077435 | 0.030874 | 0.007746 | 4.0893e-06 | 2.5566e-06 | 0.047247 | 0.047247 | 0.047247 | 0.97228 | -0.53408 | 0.97242 | -0.5313 | 12.98
46 | 0.011945 | 0.0029937 | -0.011945 | -0.0029935 | 3.7012e-07 | 2.0038e-07 | 0.018298 | 0.018298 | 0.018298 | 0.97139 | -0.55153 | 0.97136 | -0.55218 | 5.0268
47 | -0.032587 | -0.0081752 | 0.032587 | 0.0081755 | 4.1142e-07 | 2.5784e-07 | 0.049868 | 0.049868 | 0.049868 | 0.97242 | -0.5313 | 0.97243 | -0.53103 | 13.6999
48 | -0.13037 | -0.033284 | 0.13056 | 0.033404 | 0.0001876 | 0.00011989 | 0.19527 | 0.19527 | 0.19527 | 0.99458 | -0.10265 | 0.99615 | -0.072917 | 53.6462
49 | -0.13249 | -0.033888 | 0.13254 | 0.033918 | 4.6474e-05 | 2.9703e-05 | 0.19816 | 0.19816 | 0.19816 | 0.99615 | -0.072917 | 0.99653 | -0.065672 | 54.4387
50 | -0.033934 | -0.008513 | 0.033935 | 0.0085135 | 9.017e-07 | 5.6603e-07 | 0.051928 | 0.051928 | 0.051928 | 0.97243 | -0.53103 | 0.97246 | -0.53047 | 14.266
51 | -0.035341 | -0.0088659 | 0.035348 | 0.0088707 | 7.5562e-06 | 4.7505e-06 | 0.05408 | 0.05408 | 0.05408 | 0.97246 | -0.53047 | 0.97269 | -0.52599 | 14.8571
52 | -0.037062 | -0.0093002 | 0.037063 | 0.0093007 | 7.9539e-07 | 5.0086e-07 | 0.056702 | 0.056702 | 0.056702 | 0.97269 | -0.52599 | 0.97271 | -0.52554 | 15.5774
53 | -0.038411 | -0.0096386 | 0.038418 | 0.0096433 | 7.5776e-06 | 4.777e-06 | 0.058764 | 0.058764 | 0.058764 | 0.97271 | -0.52554 | 0.97292 | -0.5214 | 16.1439
54 | -0.041117 | -0.01032 | 0.041119 | 0.010321 | 2.077e-06 | 1.3119e-06 | 0.062891 | 0.062891 | 0.062891 | 0.97292 | -0.5214 | 0.97297 | -0.52035 | 17.2777
55 | 0.089348 | 0.022605 | -0.089226 | -0.022527 | 0.00012234 | 7.8076e-05 | 0.13562 | 0.13562 | 0.13562 | 0.98088 | -0.3654 | 0.97941 | -0.39398 | 37.2581
56 | -0.092754 | -0.023458 | 0.09298 | 0.023602 | 0.00022508 | 0.00014367 | 0.14079 | 0.14079 | 0.14079 | 0.98088 | -0.3654 | 0.98348 | -0.31495 | 38.6777
57 | -0.09298 | -0.023602 | 0.093401 | 0.023871 | 0.00042147 | 0.00026901 | 0.14079 | 0.14079 | 0.14079 | 0.98348 | -0.31495 | 0.98835 | -0.22119 | 38.6777
58 | -0.10116 | -0.025815 | 0.10137 | 0.025949 | 0.00021038 | 0.00013434 | 0.15246 | 0.15246 | 0.15246 | 0.98835 | -0.22119 | 0.99059 | -0.17824 | 41.8851
59 | -0.10751 | -0.027488 | 0.10753 | 0.027504 | 2.4081e-05 | 1.538e-05 | 0.16169 | 0.16169 | 0.16169 | 0.99059 | -0.17824 | 0.99084 | -0.17361 | 44.4195
60 | -0.1104 | -0.028222 | 0.11059 | 0.028342 | 0.00018716 | 0.00011955 | 0.16599 | 0.16599 | 0.16599 | 0.99084 | -0.17361 | 0.99267 | -0.13863 | 45.6023
61 | -0.11264 | -0.028858 | 0.11272 | 0.028905 | 7.4849e-05 | 4.7813e-05 | 0.16908 | 0.16908 | 0.16908 | 0.99267 | -0.13863 | 0.99339 | -0.12493 | 46.45
62 | -0.11478 | -0.029422 | 0.1148 | 0.029437 | 2.3372e-05 | 1.4931e-05 | 0.17216 | 0.17216 | 0.17216 | 0.99339 | -0.12493 | 0.99361 | -0.12073 | 47.2975
63 | 0.074811 | 0.018891 | -0.074762 | -0.018859 | 4.9747e-05 | 3.1708e-05 | 0.11345 | 0.11345 | 0.11345 | 0.98167 | -0.35116 | 0.98096 | -0.36504 | 31.1675
64 | 0.074762 | 0.018859 | -0.074679 | -0.018806 | 8.2957e-05 | 5.2876e-05 | 0.11345 | 0.11345 | 0.11345 | 0.98096 | -0.36504 | 0.97977 | -0.38825 | 31.1675
65 | 0.062084 | 0.01565 | -0.062037 | -0.01562 | 4.6184e-05 | 2.9384e-05 | 0.094321 | 0.094321 | 0.094321 | 0.97977 | -0.38825 | 0.97898 | -0.40381 | 25.9124
66 | 0.041488 | 0.010416 | -0.041476 | -0.010408 | 1.2081e-05 | 7.6311e-06 | 0.063255 | 0.063255 | 0.063255 | 0.97606 | -0.46092 | 0.97575 | -0.46703 | 17.3779
67 | -0.043956 | -0.011034 | 0.043969 | 0.011043 | 1.3611e-05 | 8.61e-06 | 0.067017 | 0.067017 | 0.067017 | 0.97606 | -0.46092 | 0.97639 | -0.45443 | 18.4113
68 | 0.039006 | 0.0097891 | -0.038995 | -0.0097818 | 1.1604e-05 | 7.3172e-06 | 0.059489 | 0.059489 | 0.059489 | 0.97575 | -0.46703 | 0.97544 | -0.47327 | 16.3432
69 | -0.046472 | -0.01167 | 0.046509 | 0.011693 | 3.6947e-05 | 2.34e-05 | 0.070832 | 0.070831 | 0.070832 | 0.97639 | -0.45443 | 0.97724 | -0.43778 | 19.4592
70 | 0.035918 | 0.0090107 | -0.035905 | -0.0090027 | 1.2767e-05 | 8.0295e-06 | 0.054796 | 0.054796 | 0.054796 | 0.97544 | -0.47327 | 0.97506 | -0.48072 | 15.0538
71 | -0.054085 | -0.013593 | 0.054121 | 0.013616 | 3.6035e-05 | 2.2885e-05 | 0.082368 | 0.082368 | 0.082368 | 0.97724 | -0.43778 | 0.97795 | -0.42383 | 22.6285
72 | 0.0075763 | 0.0018992 | -0.0075737 | -0.0018982 | 2.6106e-06 | 1.0157e-06 | 0.011536 | 0.011537 | 0.011537 | 0.97724 | -0.43778 | 0.97687 | -0.44501 | 3.1694
73 | 0.031998 | 0.0080235 | -0.031992 | -0.0080193 | 6.631e-06 | 4.1514e-06 | 0.048833 | 0.048833 | 0.048833 | 0.97506 | -0.48072 | 0.97484 | -0.48507 | 13.4157
74 | -0.056765 | -0.014278 | 0.056819 | 0.014313 | 5.4363e-05 | 3.4548e-05 | 0.086389 | 0.086389 | 0.086389 | 0.97795 | -0.42383 | 0.97898 | -0.40381 | 23.7333
75 | 0.0075737 | 0.0018982 | -0.0075733 | -0.0018981 | 3.1892e-07 | 1.2411e-07 | 0.011537 | 0.011537 | 0.011537 | 0.97687 | -0.44501 | 0.97683 | -0.4459 | 3.1694
76 | 0.0163 | 0.0040865 | -0.016296 | -0.0040844 | 3.6484e-06 | 2.1391e-06 | 0.024881 | 0.024881 | 0.024881 | 0.97484 | -0.48507 | 0.9746 | -0.48977 | 6.8354
77 | 0.01131 | 0.0028349 | -0.01131 | -0.0028344 | 9.1244e-07 | 4.823e-07 | 0.017269 | 0.017269 | 0.017269 | 0.9746 | -0.48977 | 0.97451 | -0.49146 | 4.7442

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27644 | 0.070685

## res_load
| p_mw | q_mvar
0 | 0.0033851 | 0.00084838
1 | 0.0057407 | 0.0014388
2 | 0.0053945 | 0.001352
3 | 0.0044365 | 0.0011119
4 | 0.0035259 | 0.00088367
5 | 0.0019575 | 0.00049059
6 | 0.0023259 | 0.00058292
7 | 0.002327 | 0.0005832
8 | 0.0038299 | 0.00095988
9 | 0.0018989 | 0.00047591
10 | 0.0020202 | 0.00050631
11 | 0.002951 | 0.0007396
12 | 0.0019574 | 0.00049056
13 | 0.002095 | 0.00052507
14 | 0.0047051 | 0.0011792
15 | 0.0020223 | 0.00050684
16 | 0.0020165 | 0.00050539
17 | 0.0019001 | 0.0004762
18 | 0.0027998 | 0.00070169
19 | 0.0019312 | 0.000484
20 | 0.0038687 | 0.00096958
21 | 0.0022034 | 0.00055222
22 | 0.0024553 | 0.00061535
23 | 0.0033394 | 0.00083692
24 | 0.002204 | 0.00055238
25 | 0.0098484 | 0.0024682
26 | 0.0040423 | 0.0010131
27 | 0.0025868 | 0.00064831
28 | 0.0039664 | 0.00099407
29 | 0.0026469 | 0.00066337
30 | 0.0029123 | 0.0007299
31 | 0.0020222 | 0.00050681
32 | 0.001393 | 0.00034913
33 | 0.0013911 | 0.00034864
34 | 0.0020229 | 0.00050698
35 | 0.0050702 | 0.0012707
36 | 0.0064423 | 0.0016146
37 | 0.0013267 | 0.0003325
38 | 0.0029887 | 0.00074904
39 | 0.0048496 | 0.0012154
40 | 0.0017125 | 0.00042919
41 | 0.0034668 | 0.00086887
42 | 0.0019312 | 0.000484
43 | 0.0018123 | 0.0004542
44 | 0.0013466 | 0.0003375
45 | 0.001406 | 0.00035238
46 | 0.0017141 | 0.00042958
47 | 0.0013479 | 0.00033783
48 | 0.0026983 | 0.00067625
49 | 0.0014642 | 0.00036697
50 | 0.0027437 | 0.00068765
51 | 0.0034064 | 0.00085373
52 | 0.0094877 | 0.0023778
53 | 0.0077549 | 0.0019436
54 | 0.0061414 | 0.0015392
55 | 0.002867 | 0.00071855
56 | 0.0020585 | 0.0005159
57 | 0.0020595 | 0.00051615
58 | 0.0020155 | 0.00050513
59 | 0.011412 | 0.0028601
60 | 0.012595 | 0.0031566
61 | 0.0024674 | 0.0006184
62 | 0.0024697 | 0.00061896
63 | 0.002503 | 0.0006273
64 | 0.0030767 | 0.00077109
65 | 0.0039071 | 0.00097921
66 | 0.0026431 | 0.00066243
67 | 0.015692 | 0.0039328
68 | 0.0052185 | 0.0013079
69 | 0.0075733 | 0.0018981
70 | 0.0049855 | 0.0012495
71 | 0.01131 | 0.0028344

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1