## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1341-10_1_3_node_6 | 0.4 | n |  | TRUE
1 | bus_LV_1341-10_1_3_node_7 | 0.4 | n |  | TRUE
2 | bus_LV_1341-10_1_3_node_8 | 0.4 | n |  | TRUE
3 | bus_LV_1341-10_1_3_node_13 | 0.4 | n |  | TRUE
4 | bus_LV_1341-10_1_3_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_1341-10_1_3_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_1341-10_1_3_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_1341-10_1_3_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_1341-10_1_3_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_1341-10_1_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_1341-10_1_3_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_1341-10_1_3_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_1341-10_1_3_node_71 | 0.4 | n |  | TRUE
13 | bus_LV_1341-10_1_3_node_72 | 0.4 | n |  | TRUE
14 | bus_LV_1341-10_1_3_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_1341-10_1_3_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_1341-10_1_3_node_74 | 0.4 | n |  | TRUE
17 | bus_LV_1341-10_1_3_node_75 | 0.4 | n |  | TRUE
18 | bus_LV_1341-10_1_3_node_33 | 0.4 | n |  | TRUE
19 | bus_LV_1341-10_1_3_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_1341-10_1_3_node_35 | 0.4 | n |  | TRUE
21 | bus_LV_1341-10_1_3_node_36 | 0.4 | n |  | TRUE
22 | bus_LV_1341-10_1_3_node_38 | 0.4 | n |  | TRUE
23 | bus_LV_1341-10_1_3_node_37 | 0.4 | n |  | TRUE
24 | bus_LV_1341-10_1_3_node_47 | 0.4 | n |  | TRUE
25 | bus_LV_1341-10_1_3_node_44 | 0.4 | n |  | TRUE
26 | bus_LV_1341-10_1_3_node_81 | 0.4 | n |  | TRUE
27 | bus_LV_1341-10_1_3_node_41 | 0.4 | n |  | TRUE
28 | bus_LV_1341-10_1_3_node_39 | 0.4 | n |  | TRUE
29 | bus_LV_1341-10_1_3_node_49 | 0.4 | n |  | TRUE
30 | bus_LV_1341-10_1_3_node_45 | 0.4 | n |  | TRUE
31 | bus_LV_1341-10_1_3_node_82 | 0.4 | n |  | TRUE
32 | bus_LV_1341-10_1_3_node_40 | 0.4 | n |  | TRUE
33 | bus_LV_1341-10_1_3_node_42 | 0.4 | n |  | TRUE
34 | bus_LV_1341-10_1_3_node_43 | 0.4 | n |  | TRUE
35 | bus_LV_1341-10_1_3_node_77 | 0.4 | n |  | TRUE
36 | bus_LV_1341-10_1_3_node_80 | 0.4 | n |  | TRUE
37 | bus_LV_1341-10_1_3_node_48 | 0.4 | n |  | TRUE
38 | bus_LV_1341-10_1_3_node_46 | 0.4 | n |  | TRUE
39 | bus_LV_1341-10_1_3_node_68 | 0.4 | n |  | TRUE
40 | bus_LV_1341-10_1_3_node_69 | 0.4 | n |  | TRUE
41 | bus_LV_1341-10_1_3_node_66 | 0.4 | n |  | TRUE
42 | bus_LV_1341-10_1_3_node_67 | 0.4 | n |  | TRUE
43 | bus_LV_1341-10_1_3_node_70 | 0.4 | n |  | TRUE
44 | bus_LV_1341-10_1_3_node_76 | 0.4 | n |  | TRUE
45 | bus_LV_1341-10_1_3_node_78 | 0.4 | n |  | TRUE
46 | bus_LV_1341-10_1_3_node_79 | 0.4 | n |  | TRUE
47 | bus_MV_223_0_node_67 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1341-10_1_3_load_6 | 0 | 0.00064061 | 0.00016055 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1341-10_1_3_load_7 | 1 | 0.00056877 | 0.00014255 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1341-10_1_3_load_8 | 2 | 0.00082162 | 0.00020592 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1341-10_1_3_load_13 | 3 | 0.0065176 | 0.0016335 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1341-10_1_3_load_9 | 4 | 0.00080829 | 0.00020258 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1341-10_1_3_load_11 | 5 | 0.0066035 | 0.001655 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1341-10_1_3_load_10 | 6 | 0.00051069 | 0.00012799 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1341-10_1_3_load_16 | 7 | 0.0012935 | 0.00032419 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1341-10_1_3_load_17 | 8 | 0.00083338 | 0.00020887 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1341-10_1_3_load_12 | 9 | 0.0015999 | 0.00040096 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1341-10_1_3_load_14 | 10 | 0.0046182 | 0.0011574 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1341-10_1_3_load_15 | 11 | 0.0043812 | 0.001098 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1341-10_1_3_load_71 | 12 | 0.0012613 | 0.00031611 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1341-10_1_3_load_20 | 14 | 0.00077882 | 0.00019519 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1341-10_1_3_load_21 | 15 | 0.008443 | 0.002116 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1341-10_1_3_load_74 | 16 | 0.026918 | 0.0067464 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1341-10_1_3_load_33 | 18 | 0.0015478 | 0.00038792 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1341-10_1_3_load_38 | 22 | 0.015402 | 0.0038602 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1341-10_1_3_load_47 | 24 | 0.0027159 | 0.00068067 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1341-10_1_3_load_44 | 25 | 0.017193 | 0.0043091 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1341-10_1_3_load_81 | 26 | 0.00050903 | 0.00012757 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1341-10_1_3_load_41 | 27 | 0.040215 | 0.010079 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1341-10_1_3_load_39 | 28 | 0.00447 | 0.0011203 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1341-10_1_3_load_49 | 29 | 0.00322 | 0.000807 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1341-10_1_3_load_45 | 30 | 0.0040221 | 0.001008 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1341-10_1_3_load_82 | 31 | 0.0055346 | 0.0013871 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1341-10_1_3_load_40 | 32 | 0.014537 | 0.0036432 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1341-10_1_3_load_42 | 33 | 0.011307 | 0.0028338 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1341-10_1_3_load_77 | 35 | 0.0084902 | 0.0021278 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1341-10_1_3_load_80 | 36 | 0.005225 | 0.0013095 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1341-10_1_3_load_48 | 37 | 0.008046 | 0.0020165 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1341-10_1_3_load_46 | 38 | 0.0040221 | 0.001008 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1341-10_1_3_load_69 | 40 | 0.0037245 | 0.00093346 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1341-10_1_3_load_66 | 41 | 0.0032228 | 0.00080772 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1341-10_1_3_load_67 | 42 | 0.0046699 | 0.0011704 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1341-10_1_3_load_70 | 43 | 0.0052883 | 0.0013254 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1341-10_1_3_load_76 | 44 | 0.011288 | 0.0028292 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1341-10_1_3_load_78 | 45 | 0.0035169 | 0.00088141 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1341-10_1_3_load_79 | 46 | 0.0020716 | 0.00051918 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1341-10_1_3_line_0 |  | 0 | 1 | 0.016251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1341-10_1_3_line_1 |  | 0 | 2 | 0.018186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1341-10_1_3_line_2 |  | 1 | 3 | 0.048118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1341-10_1_3_line_3 |  | 2 | 4 | 0.016562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1341-10_1_3_line_4 |  | 3 | 5 | 0.062536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1341-10_1_3_line_5 |  | 4 | 6 | 0.026051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1341-10_1_3_line_6 |  | 5 | 9 | 0.050544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1341-10_1_3_line_7 |  | 6 | 7 | 0.0094314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1341-10_1_3_line_8 |  | 7 | 8 | 0.03924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1341-10_1_3_line_9 |  | 9 | 10 | 0.0051281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1341-10_1_3_line_10 |  | 10 | 11 | 0.0065862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1341-10_1_3_line_11 |  | 11 | 12 | 0.0065646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1341-10_1_3_line_12 |  | 12 | 13 | 0.037408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1341-10_1_3_line_13 |  | 13 | 37 | 0.027279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1341-10_1_3_line_14 |  | 13 | 34 | 0.025575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1341-10_1_3_line_15 |  | 14 | 15 | 0.019618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1341-10_1_3_line_16 |  | 15 | 16 | 0.025052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1341-10_1_3_line_17 |  | 16 | 17 | 0.016087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1341-10_1_3_line_18 |  | 17 | 44 | 0.030353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1341-10_1_3_line_19 |  | 18 | 19 | 0.024615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1341-10_1_3_line_20 |  | 19 | 20 | 0.01378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1341-10_1_3_line_21 |  | 20 | 21 | 0.010971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1341-10_1_3_line_22 |  | 20 | 22 | 0.058395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1341-10_1_3_line_23 |  | 21 | 23 | 0.03139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1341-10_1_3_line_24 |  | 22 | 26 | 0.007773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1341-10_1_3_line_25 |  | 23 | 24 | 0.011478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1341-10_1_3_line_26 |  | 23 | 25 | 0.023994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1341-10_1_3_line_27 |  | 24 | 29 | 0.030949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1341-10_1_3_line_28 |  | 25 | 30 | 0.0043156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1341-10_1_3_line_29 |  | 26 | 31 | 0.10796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1341-10_1_3_line_30 |  | 27 | 28 | 0.022625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1341-10_1_3_line_31 |  | 28 | 32 | 0.011938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1341-10_1_3_line_32 |  | 29 | 39 | 0.0024379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1341-10_1_3_line_33 |  | 30 | 38 | 0.01223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1341-10_1_3_line_34 |  | 32 | 33 | 0.0016244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1341-10_1_3_line_35 |  | 33 | 34 | 0.025279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1341-10_1_3_line_36 |  | 34 | 35 | 0.00023684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1341-10_1_3_line_37 |  | 35 | 36 | 0.0011853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1341-10_1_3_line_38 |  | 36 | 46 | 0.013226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1341-10_1_3_line_39 |  | 37 | 38 | 0.020085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1341-10_1_3_line_40 |  | 39 | 40 | 0.026194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1341-10_1_3_line_41 |  | 39 | 41 | 0.027792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1341-10_1_3_line_42 |  | 40 | 43 | 0.012669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1341-10_1_3_line_43 |  | 41 | 42 | 0.0031937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1341-10_1_3_line_44 |  | 44 | 45 | 0.049526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1341-10_1_3_line_45 |  | 45 | 46 | 0.0031881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1341-10_1_3_trafo_72 | 0.63 MVA 20/0.4 kV | 47 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2706232.1128 | 1227631.0047 | 2706248.2813 | 1227629.3708
1 | 2706232.1128 | 1227631.0047 | 2706225.4113 | 1227631.682 | 2706214.2641 | 1227634.2972
2 | 2706296.0362 | 1227635.2682 | 2706248.2813 | 1227629.3708
3 | 2706198.1394 | 1227638.0803 | 2706214.2641 | 1227634.2972
4 | 2706296.0362 | 1227635.2682 | 2706297.6705 | 1227602.3617 | 2706306.1683 | 1227594.6856 | 2706324.0891 | 1227597.4845
5 | 2706198.1394 | 1227638.0803 | 2706184.4529 | 1227641.2913 | 2706175.9108 | 1227638.7259 | 2706174.2906 | 1227636.1136
6 | 2706324.0891 | 1227597.4845 | 2706374.0281 | 1227605.2841
7 | 2706169.3194 | 1227628.0987 | 2706174.2906 | 1227636.1136
8 | 2706169.3194 | 1227628.0987 | 2706148.6366 | 1227594.7521
9 | 2706379.0947 | 1227606.0754 | 2706379.0947 | 1227606.0754 | 2706374.0281 | 1227605.2841
10 | 2706379.0947 | 1227606.0754 | 2706384.4613 | 1227602.2574 | 2706384.4613 | 1227602.2574
11 | 2706385.6597 | 1227595.8031 | 2706384.4613 | 1227602.2574
12 | 2706392.4889 | 1227559.0242 | 2706385.6597 | 1227595.8031
13 | 2706392.4889 | 1227559.0242 | 2706418.4031 | 1227567.5444
14 | 2706392.4889 | 1227559.0242 | 2706396.6394 | 1227533.7906
15 | 2706242.5696 | 1227512.7512 | 2706262.0129 | 1227515.3663
16 | 2706262.0129 | 1227515.3663 | 2706286.8413 | 1227518.7058
17 | 2706299.1013 | 1227529.1215 | 2706286.8413 | 1227518.7058
18 | 2706299.1013 | 1227529.1215 | 2706329.4473 | 1227529.7706
19 | 2706503.7977 | 1227565.4649 | 2706527.4888 | 1227572.1466
20 | 2706497.9094 | 1227554.8182 | 2706500.484 | 1227555.8095 | 2706502.5662 | 1227557.6259 | 2706503.9025 | 1227560.0405 | 2706504.3313 | 1227562.7613 | 2706503.7977 | 1227565.4649
21 | 2706497.9094 | 1227554.8182 | 2706495.159 | 1227554.7578 | 2706492.551 | 1227555.634 | 2706490.398 | 1227557.3412 | 2706488.954 | 1227559.6726
22 | 2706497.9094 | 1227554.8182 | 2706498.8695 | 1227538.879 | 2706509.0355 | 1227499.0312 | 2706509.6926 | 1227497.9067
23 | 2706475.7103 | 1227583.4645 | 2706491.2781 | 1227568.721 | 2706489.6288 | 1227566.8568 | 2706488.6388 | 1227564.5707 | 2706488.4103 | 1227562.0981 | 2706488.954 | 1227559.6726
24 | 2706509.6926 | 1227497.9067 | 2706513.614 | 1227491.1954
25 | 2706475.7103 | 1227583.4645 | 2706470.7142 | 1227593.798
26 | 2706475.7103 | 1227583.4645 | 2706452.8848 | 1227576.067
27 | 2706457.2426 | 1227621.6615 | 2706470.7142 | 1227593.798
28 | 2706452.8848 | 1227576.067 | 2706448.7794 | 1227574.7364
29 | 2706513.614 | 1227491.1954 | 2706616.5044 | 1227458.4934
30 | 2706434.4743 | 1227542.1664 | 2706456.0142 | 1227549.0879
31 | 2706434.4743 | 1227542.1664 | 2706423.1089 | 1227538.5143
32 | 2706456.1814 | 1227623.8564 | 2706457.2426 | 1227621.6615
33 | 2706448.7794 | 1227574.7364 | 2706440.4111 | 1227572.0243 | 2706437.4835 | 1227573.8178
34 | 2706423.1089 | 1227538.5143 | 2706421.5623 | 1227538.0173
35 | 2706396.6394 | 1227533.7906 | 2706421.5623 | 1227538.0173
36 | 2706396.4045 | 1227533.7605 | 2706396.6394 | 1227533.7906
37 | 2706395.2288 | 1227533.6098 | 2706396.4045 | 1227533.7605
38 | 2706395.2288 | 1227533.6098 | 2706383.3293 | 1227532.0847 | 2706382.1022 | 1227532.006
39 | 2706437.4835 | 1227573.8178 | 2706437.4835 | 1227573.8178 | 2706418.4031 | 1227567.5444
40 | 2706456.1814 | 1227623.8564 | 2706473.9673 | 1227632.1141 | 2706477.7747 | 1227637.4863
41 | 2706456.1814 | 1227623.8564 | 2706440.4876 | 1227646.7933
42 | 2706489.5639 | 1227642.1263 | 2706477.7747 | 1227637.4863
43 | 2706438.6842 | 1227649.4291 | 2706440.4876 | 1227646.7933
44 | 2706329.4473 | 1227529.7706 | 2706356.1562 | 1227530.342 | 2706378.9207 | 1227531.8019
45 | 2706378.9207 | 1227531.8019 | 2706382.1022 | 1227532.006

## bus_geodata
| x | y | coords
0 | 2706232.1128 | 1227631.0047
1 | 2706248.2813 | 1227629.3708
2 | 2706214.2641 | 1227634.2972
3 | 2706296.0362 | 1227635.2682
4 | 2706198.1394 | 1227638.0803
5 | 2706324.0891 | 1227597.4845
6 | 2706174.2906 | 1227636.1136
7 | 2706169.3194 | 1227628.0987
8 | 2706148.6366 | 1227594.7521
9 | 2706374.0281 | 1227605.2841
10 | 2706379.0947 | 1227606.0754
11 | 2706384.4613 | 1227602.2574
12 | 2706385.6597 | 1227595.8031
13 | 2706392.4889 | 1227559.0242
14 | 2706242.5696 | 1227512.7512
15 | 2706262.0129 | 1227515.3663
16 | 2706286.8413 | 1227518.7058
17 | 2706299.1013 | 1227529.1215
18 | 2706527.4888 | 1227572.1466
19 | 2706503.7977 | 1227565.4649
20 | 2706497.9094 | 1227554.8182
21 | 2706488.954 | 1227559.6726
22 | 2706509.6926 | 1227497.9067
23 | 2706475.7103 | 1227583.4645
24 | 2706470.7142 | 1227593.798
25 | 2706452.8848 | 1227576.067
26 | 2706513.614 | 1227491.1954
27 | 2706456.0142 | 1227549.0879
28 | 2706434.4743 | 1227542.1664
29 | 2706457.2426 | 1227621.6615
30 | 2706448.7794 | 1227574.7364
31 | 2706616.5044 | 1227458.4934
32 | 2706423.1089 | 1227538.5143
33 | 2706421.5623 | 1227538.0173
34 | 2706396.6394 | 1227533.7906
35 | 2706396.4045 | 1227533.7605
36 | 2706395.2288 | 1227533.6098
37 | 2706418.4031 | 1227567.5444
38 | 2706437.4835 | 1227573.8178
39 | 2706456.1814 | 1227623.8564
40 | 2706477.7747 | 1227637.4863
41 | 2706440.4876 | 1227646.7933
42 | 2706438.6842 | 1227649.4291
43 | 2706489.5639 | 1227642.1263
44 | 2706329.4473 | 1227529.7706
45 | 2706378.9207 | 1227531.8019
46 | 2706382.1022 | 1227532.006
47 | 2706396.6394 | 1227533.7906

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9967 | -0.063535 | 0.00064061 | 0.00016055
1 | 0.99677 | -0.062135 | 0.00056877 | 0.00014255
2 | 0.99663 | -0.064898 | 0.00082162 | 0.00020592
3 | 0.99701 | -0.057508 | 0.0065176 | 0.0016335
4 | 0.99658 | -0.0659 | 0.00080829 | 0.00020258
5 | 0.99769 | -0.044358 | 0.0066035 | 0.001655
6 | 0.99651 | -0.067107 | 0.00051069 | 0.00012799
7 | 0.9965 | -0.067459 | 0.0012935 | 0.00032419
8 | 0.99647 | -0.068034 | 0.00083338 | 0.00020887
9 | 0.99855 | -0.027904 | 0.0015999 | 0.00040096
10 | 0.99864 | -0.026093 | 0.0046182 | 0.0011574
11 | 0.99879 | -0.023236 | 0.0043812 | 0.001098
12 | 0.99896 | -0.019886 | 0.0012613 | 0.00031611
13 | 1 | 0 | -0.2497 | -0.062627
14 | 0.99203 | -0.15344 | 0.00077882 | 0.00019519
15 | 0.99204 | -0.15317 | 0.008443 | 0.002116
16 | 0.99225 | -0.14908 | 0.026918 | 0.0067464
17 | 0.99278 | -0.13879 | 0 | 0
18 | 0.99379 | -0.11948 | 0.0015478 | 0.00038792
19 | 0.99382 | -0.11881 | 0 | 0
20 | 0.99384 | -0.11843 | 0 | 0
21 | 0.99407 | -0.11398 | 0 | 0
22 | 0.9927 | -0.14056 | 0.015402 | 0.0038602
23 | 0.99473 | -0.10126 | 0 | 0
24 | 0.99449 | -0.10588 | 0.0027159 | 0.00068067
25 | 0.99573 | -0.081897 | 0.017193 | 0.0043091
26 | 0.99265 | -0.14139 | 0.00050903 | 0.00012757
27 | 0.99377 | -0.11984 | 0.040215 | 0.010079
28 | 0.9946 | -0.1038 | 0.00447 | 0.0011203
29 | 0.99392 | -0.11686 | 0.00322 | 0.000807
30 | 0.99598 | -0.077116 | 0.0040221 | 0.001008
31 | 0.99211 | -0.15197 | 0.0055346 | 0.0013871
32 | 0.99508 | -0.094405 | 0.014537 | 0.0036432
33 | 0.99517 | -0.092711 | 0.011307 | 0.0028338
34 | 0.9968 | -0.061385 | 0 | 0
35 | 0.99678 | -0.061662 | 0.0084902 | 0.0021278
36 | 0.99672 | -0.062874 | 0.005225 | 0.0013095
37 | 0.99803 | -0.037699 | 0.008046 | 0.0020165
38 | 0.99673 | -0.062715 | 0.0040221 | 0.001008
39 | 0.99388 | -0.11759 | 0 | 0
40 | 0.99367 | -0.12175 | 0.0037245 | 0.00093346
41 | 0.99368 | -0.12146 | 0.0032228 | 0.00080772
42 | 0.99367 | -0.12172 | 0.0046699 | 0.0011704
43 | 0.99361 | -0.12294 | 0.0052883 | 0.0013254
44 | 0.99378 | -0.11941 | 0.011288 | 0.0028292
45 | 0.99593 | -0.078039 | 0.0035169 | 0.00088141
46 | 0.99608 | -0.075185 | 0.0020716 | 0.00051918
47 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0049088 | -0.0012291 | 0.0049091 | 0.0012291 | 3.2726e-07 | -2.3646e-09 | 0.0073281 | 0.0073281 | 0.0073281 | 0.9967 | -0.063535 | 0.99677 | -0.062135 | 2.0132
1 | 0.0042682 | 0.0010685 | -0.0042679 | -0.0010686 | 2.7687e-07 | -5.9794e-08 | 0.0063717 | 0.0063718 | 0.0063718 | 0.9967 | -0.063535 | 0.99663 | -0.064898 | 1.7505
2 | -0.0054779 | -0.0013716 | 0.0054791 | 0.0013718 | 1.2065e-06 | 1.4481e-07 | 0.0081771 | 0.0081769 | 0.0081771 | 0.99677 | -0.062135 | 0.99701 | -0.057508 | 2.2465
3 | 0.0034463 | 0.00086268 | -0.0034461 | -0.00086279 | 1.6442e-07 | -1.1059e-07 | 0.0051451 | 0.0051452 | 0.0051452 | 0.99663 | -0.064898 | 0.99658 | -0.0659 | 1.4135
4 | -0.011997 | -0.0030052 | 0.012004 | 0.0030092 | 7.5175e-06 | 3.9951e-06 | 0.017904 | 0.017904 | 0.017904 | 0.99701 | -0.057508 | 0.99769 | -0.044358 | 4.9188
5 | 0.0026378 | 0.00066021 | -0.0026377 | -0.00066045 | 1.5153e-07 | -2.4244e-07 | 0.0039383 | 0.0039384 | 0.0039384 | 0.99658 | -0.0659 | 0.99651 | -0.067107 | 1.082
6 | -0.018608 | -0.0046642 | 0.018622 | 0.0046729 | 1.4599e-05 | 8.6825e-06 | 0.027753 | 0.027753 | 0.027753 | 0.99769 | -0.044358 | 0.99855 | -0.027904 | 7.6244
7 | 0.002127 | 0.00053246 | -0.002127 | -0.00053256 | 3.5672e-08 | -1.0004e-07 | 0.0031759 | 0.0031759 | 0.0031759 | 0.99651 | -0.067107 | 0.9965 | -0.067459 | 0.8725
8 | 0.00083341 | 0.00020837 | -0.00083338 | -0.00020887 | 2.2786e-08 | -4.966e-07 | 0.0012443 | 0.0012445 | 0.0012445 | 0.9965 | -0.067459 | 0.99647 | -0.068034 | 0.34189
9 | -0.020222 | -0.0050739 | 0.020224 | 0.0050749 | 1.7465e-06 | 1.0507e-06 | 0.030137 | 0.030137 | 0.030137 | 0.99855 | -0.027904 | 0.99864 | -0.026093 | 8.2793
10 | -0.024842 | -0.0062323 | 0.024845 | 0.0062344 | 3.3845e-06 | 2.0799e-06 | 0.037018 | 0.037018 | 0.037018 | 0.99864 | -0.026093 | 0.99879 | -0.023236 | 10.1698
11 | -0.029227 | -0.0073325 | 0.029231 | 0.0073354 | 4.6678e-06 | 2.9015e-06 | 0.043545 | 0.043545 | 0.043545 | 0.99879 | -0.023236 | 0.99896 | -0.019886 | 11.9629
12 | -0.030493 | -0.0076515 | 0.030522 | 0.0076695 | 2.8944e-05 | 1.8034e-05 | 0.045424 | 0.045424 | 0.045424 | 0.99896 | -0.019886 | 1 | 0 | 12.4791
13 | 0.079515 | 0.020077 | -0.079372 | -0.019985 | 0.00014334 | 9.1378e-05 | 0.11837 | 0.11837 | 0.11837 | 1 | 0 | 0.99803 | -0.037699 | 32.5198
14 | 0.13802 | 0.034881 | -0.13761 | -0.034622 | 0.00040491 | 0.00025881 | 0.20547 | 0.20547 | 0.20547 | 1 | 0 | 0.9968 | -0.061385 | 56.4487
15 | -0.00077882 | -0.00019519 | 0.00077883 | 0.00019494 | 1.0039e-08 | -2.4687e-07 | 0.0011682 | 0.0011681 | 0.0011682 | 0.99203 | -0.15344 | 0.99204 | -0.15317 | 0.32094
16 | -0.0092218 | -0.002311 | 0.0092236 | 0.0023118 | 1.7975e-06 | 8.2685e-07 | 0.013832 | 0.013832 | 0.013832 | 0.99204 | -0.15317 | 0.99225 | -0.14908 | 3.8001
17 | -0.036142 | -0.0090582 | 0.03616 | 0.0090693 | 1.7722e-05 | 1.1134e-05 | 0.0542 | 0.0542 | 0.0542 | 0.99225 | -0.14908 | 0.99278 | -0.13879 | 14.8901
18 | -0.03616 | -0.0090693 | 0.036193 | 0.0090903 | 3.3437e-05 | 2.1007e-05 | 0.0542 | 0.0542 | 0.0542 | 0.99278 | -0.13879 | 0.99378 | -0.11941 | 14.8901
19 | -0.0015478 | -0.00038792 | 0.0015479 | 0.00038763 | 4.9577e-08 | -2.8721e-07 | 0.0023176 | 0.0023175 | 0.0023176 | 0.99379 | -0.11948 | 0.99382 | -0.11881 | 0.6367
20 | -0.0015479 | -0.00038763 | 0.0015479 | 0.00038747 | 2.7752e-08 | -1.608e-07 | 0.0023175 | 0.0023174 | 0.0023175 | 0.99382 | -0.11881 | 0.99384 | -0.11843 | 0.63667
21 | -0.02302 | -0.0057765 | 0.023024 | 0.0057795 | 4.8879e-06 | 2.986e-06 | 0.034468 | 0.034468 | 0.034468 | 0.99384 | -0.11843 | 0.99407 | -0.11398 | 9.4693
22 | 0.021472 | 0.0053891 | -0.021449 | -0.0053753 | 2.2636e-05 | 1.3731e-05 | 0.032151 | 0.032151 | 0.032151 | 0.99384 | -0.11843 | 0.9927 | -0.14056 | 8.8328
23 | -0.023024 | -0.0057795 | 0.023038 | 0.0057881 | 1.3985e-05 | 8.5433e-06 | 0.034468 | 0.034468 | 0.034468 | 0.99407 | -0.11398 | 0.99473 | -0.10126 | 9.4693
24 | 0.0060467 | 0.0015151 | -0.0060465 | -0.0015151 | 2.3946e-07 | 5.2765e-08 | 0.0090637 | 0.0090637 | 0.0090637 | 0.9927 | -0.14056 | 0.99265 | -0.14139 | 2.49
25 | 0.022861 | 0.0057358 | -0.022856 | -0.0057327 | 5.0345e-06 | 3.0731e-06 | 0.0342 | 0.0342 | 0.0342 | 0.99473 | -0.10126 | 0.99449 | -0.10588 | 9.3957
26 | -0.0459 | -0.011524 | 0.045942 | 0.011551 | 4.2428e-05 | 2.6842e-05 | 0.068669 | 0.068668 | 0.068669 | 0.99473 | -0.10126 | 0.99573 | -0.081897 | 18.865
27 | 0.02014 | 0.005052 | -0.02013 | -0.0050457 | 1.0541e-05 | 6.3448e-06 | 0.030137 | 0.030137 | 0.030137 | 0.99449 | -0.10588 | 0.99392 | -0.11686 | 8.2794
28 | -0.063136 | -0.01586 | 0.06315 | 0.015869 | 1.441e-05 | 9.1664e-06 | 0.094362 | 0.094362 | 0.094362 | 0.99573 | -0.081897 | 0.99598 | -0.077116 | 25.9237
29 | 0.0055374 | 0.0013875 | -0.0055346 | -0.0013871 | 2.7897e-06 | 3.9051e-07 | 0.0083007 | 0.0083012 | 0.0083012 | 0.99265 | -0.14139 | 0.99211 | -0.15197 | 2.2805
30 | -0.040215 | -0.010079 | 0.040246 | 0.010098 | 3.0764e-05 | 1.9395e-05 | 0.060216 | 0.060216 | 0.060216 | 0.99377 | -0.11984 | 0.9946 | -0.1038 | 16.5429
31 | -0.044716 | -0.011219 | 0.044736 | 0.011231 | 2.0038e-05 | 1.2669e-05 | 0.066904 | 0.066904 | 0.066904 | 0.9946 | -0.1038 | 0.99508 | -0.094405 | 18.3801
32 | 0.01691 | 0.0042387 | -0.016909 | -0.0042383 | 5.8593e-07 | 3.434e-07 | 0.025316 | 0.025316 | 0.025316 | 0.99392 | -0.11686 | 0.99388 | -0.11759 | 6.955
33 | -0.067172 | -0.016877 | 0.067218 | 0.016906 | 4.6204e-05 | 2.9411e-05 | 0.10037 | 0.10037 | 0.10037 | 0.99598 | -0.077116 | 0.99673 | -0.062715 | 27.5745
34 | -0.059273 | -0.014874 | 0.059277 | 0.014877 | 4.7864e-06 | 3.0422e-06 | 0.088641 | 0.088641 | 0.088641 | 0.99508 | -0.094405 | 0.99517 | -0.092711 | 24.3519
35 | -0.070584 | -0.017711 | 0.07069 | 0.017778 | 0.0001056 | 6.7258e-05 | 0.10555 | 0.10555 | 0.10555 | 0.99517 | -0.092711 | 0.9968 | -0.061385 | 28.9966
36 | 0.066922 | 0.016844 | -0.066921 | -0.016843 | 8.8684e-07 | 5.6449e-07 | 0.099926 | 0.099926 | 0.099926 | 0.9968 | -0.061385 | 0.99678 | -0.061662 | 27.4522
37 | 0.058431 | 0.014715 | -0.058427 | -0.014713 | 3.3838e-06 | 2.1502e-06 | 0.087252 | 0.087252 | 0.087252 | 0.99678 | -0.061662 | 0.99672 | -0.062874 | 23.9702
38 | 0.053202 | 0.013404 | -0.053171 | -0.013384 | 3.1309e-05 | 1.9866e-05 | 0.079451 | 0.079451 | 0.079451 | 0.99672 | -0.062874 | 0.99608 | -0.075185 | 21.8272
39 | 0.071326 | 0.017969 | -0.07124 | -0.017914 | 8.523e-05 | 5.4285e-05 | 0.10638 | 0.10638 | 0.10638 | 0.99803 | -0.037699 | 0.99673 | -0.062715 | 29.2241
40 | 0.0090149 | 0.0022597 | -0.0090132 | -0.0022589 | 1.7894e-06 | 8.0585e-07 | 0.013497 | 0.013497 | 0.013497 | 0.99388 | -0.11759 | 0.99367 | -0.12175 | 3.708
41 | 0.0078943 | 0.0019787 | -0.0078928 | -0.0019781 | 1.4559e-06 | 5.7168e-07 | 0.011819 | 0.011819 | 0.011819 | 0.99388 | -0.11759 | 0.99368 | -0.12146 | 3.2471
42 | 0.0052886 | 0.0013254 | -0.0052883 | -0.0013254 | 2.9799e-07 | 2.6609e-08 | 0.0079197 | 0.0079197 | 0.0079197 | 0.99367 | -0.12175 | 0.99361 | -0.12294 | 2.1757
43 | 0.00467 | 0.0011704 | -0.0046699 | -0.0011704 | 5.857e-08 | -3.8863e-09 | 0.0069932 | 0.0069932 | 0.0069932 | 0.99368 | -0.12146 | 0.99367 | -0.12172 | 1.9212
44 | -0.047482 | -0.011919 | 0.047576 | 0.011979 | 9.3893e-05 | 5.9448e-05 | 0.071102 | 0.071102 | 0.071102 | 0.99378 | -0.11941 | 0.99593 | -0.078039 | 19.5336
45 | -0.051092 | -0.01286 | 0.051099 | 0.012865 | 6.9704e-06 | 4.4195e-06 | 0.076357 | 0.076357 | 0.076357 | 0.99593 | -0.078039 | 0.99608 | -0.075185 | 20.9771

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.2497 | 0.062627

## res_load
| p_mw | q_mvar
0 | 0.00064061 | 0.00016055
1 | 0.00056877 | 0.00014255
2 | 0.00082162 | 0.00020592
3 | 0.0065176 | 0.0016335
4 | 0.00080829 | 0.00020258
5 | 0.0066035 | 0.001655
6 | 0.00051069 | 0.00012799
7 | 0.0012935 | 0.00032419
8 | 0.00083338 | 0.00020887
9 | 0.0015999 | 0.00040096
10 | 0.0046182 | 0.0011574
11 | 0.0043812 | 0.001098
12 | 0.0012613 | 0.00031611
13 | 0.00077882 | 0.00019519
14 | 0.008443 | 0.002116
15 | 0.026918 | 0.0067464
16 | 0.0015478 | 0.00038792
17 | 0.015402 | 0.0038602
18 | 0.0027159 | 0.00068067
19 | 0.017193 | 0.0043091
20 | 0.00050903 | 0.00012757
21 | 0.040215 | 0.010079
22 | 0.00447 | 0.0011203
23 | 0.00322 | 0.000807
24 | 0.0040221 | 0.001008
25 | 0.0055346 | 0.0013871
26 | 0.014537 | 0.0036432
27 | 0.011307 | 0.0028338
28 | 0.0084902 | 0.0021278
29 | 0.005225 | 0.0013095
30 | 0.008046 | 0.0020165
31 | 0.0040221 | 0.001008
32 | 0.0037245 | 0.00093346
33 | 0.0032228 | 0.00080772
34 | 0.0046699 | 0.0011704
35 | 0.0052883 | 0.0013254
36 | 0.011288 | 0.0028292
37 | 0.0035169 | 0.00088141
38 | 0.0020716 | 0.00051918

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1