## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1341-13_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1341-13_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1341-13_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1341-13_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1341-13_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1341-13_0_3_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_1341-13_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1341-13_0_3_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_1341-13_0_3_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_1341-13_0_3_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_1341-13_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1341-13_0_3_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_1341-13_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1341-13_0_3_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1341-13_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1341-13_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1341-13_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1341-13_0_3_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1341-13_0_3_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_1341-13_0_3_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_1341-13_0_3_node_26 | 0.4 | n |  | TRUE
21 | bus_LV_1341-13_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1341-13_0_3_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_1341-13_0_3_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1341-13_0_3_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1341-13_0_3_node_25 | 0.4 | n |  | TRUE
26 | bus_MV_223_0_node_18 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1341-13_0_3_load_0 | 0 | 0.0087697 | 0.0021979 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1341-13_0_3_load_1 | 1 | 0.012128 | 0.0030394 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1341-13_0_3_load_3 | 3 | 0.0078872 | 0.0019767 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1341-13_0_3_load_18 | 5 | 0.0028271 | 0.00070854 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1341-13_0_3_load_14 | 7 | 0.083549 | 0.020939 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1341-13_0_3_load_10 | 8 | 0.011335 | 0.0028407 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1341-13_0_3_load_19 | 9 | 0.029059 | 0.0072829 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1341-13_0_3_load_7 | 10 | 0.087229 | 0.021862 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1341-13_0_3_load_6 | 13 | 0.014526 | 0.0036406 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1341-13_0_3_load_9 | 14 | 0.014533 | 0.0036422 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1341-13_0_3_load_11 | 15 | 0.014531 | 0.0036417 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1341-13_0_3_load_13 | 17 | 0.011449 | 0.0028694 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1341-13_0_3_load_22 | 18 | 0.0029886 | 0.00074902 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1341-13_0_3_load_26 | 20 | 0.030817 | 0.0077236 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1341-13_0_3_load_15 | 21 | 0.026543 | 0.0066524 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1341-13_0_3_load_20 | 23 | 0.001136 | 0.00028471 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1341-13_0_3_load_25 | 25 | 0.010042 | 0.0025167 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1341-13_0_3_line_0 |  | 0 | 1 | 0.041109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1341-13_0_3_line_1 |  | 0 | 2 | 0.0093865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1341-13_0_3_line_2 |  | 1 | 3 | 0.034827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1341-13_0_3_line_3 |  | 2 | 4 | 0.014042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1341-13_0_3_line_4 |  | 3 | 5 | 0.019961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1341-13_0_3_line_5 |  | 4 | 9 | 0.009221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1341-13_0_3_line_6 |  | 4 | 10 | 0.020743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1341-13_0_3_line_7 |  | 5 | 11 | 0.016287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1341-13_0_3_line_8 |  | 6 | 7 | 0.03695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1341-13_0_3_line_9 |  | 6 | 8 | 0.0053291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1341-13_0_3_line_10 |  | 8 | 12 | 0.025463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1341-13_0_3_line_11 |  | 10 | 13 | 0.0087695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1341-13_0_3_line_12 |  | 11 | 21 | 0.024177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1341-13_0_3_line_13 |  | 12 | 14 | 0.0017659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1341-13_0_3_line_14 |  | 12 | 13 | 0.015766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_1341-13_0_3_line_15 |  | 14 | 15 | 0.016798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1341-13_0_3_line_16 |  | 15 | 16 | 0.036795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1341-13_0_3_line_17 |  | 16 | 17 | 0.071449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1341-13_0_3_line_18 |  | 17 | 18 | 0.036808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1341-13_0_3_line_19 |  | 18 | 19 | 0.024223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1341-13_0_3_line_20 |  | 18 | 20 | 0.02601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1341-13_0_3_line_21 |  | 19 | 24 | 0.064461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1341-13_0_3_line_22 |  | 21 | 22 | 0.035693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1341-13_0_3_line_23 |  | 22 | 23 | 0.12287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1341-13_0_3_line_24 |  | 24 | 25 | 0.065706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1341-13_0_3_trafo_7 | 0.63 MVA 20/0.4 kV | 26 | 10 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2705017.3662 | 1227798.147 | 2705058.452 | 1227796.7713
1 | 2705007.9849 | 1227798.4611 | 2705017.3662 | 1227798.147
2 | 2705093.2598 | 1227795.6058 | 2705058.452 | 1227796.7713
3 | 2704993.9092 | 1227798.9241 | 2705007.9849 | 1227798.4611
4 | 2705093.2598 | 1227795.6058 | 2705113.2099 | 1227794.9378
5 | 2704993.9092 | 1227798.9241 | 2704993.8371 | 1227789.7049
6 | 2704993.9092 | 1227798.9241 | 2704973.1693 | 1227799.2965
7 | 2705129.4882 | 1227794.3927 | 2705113.2099 | 1227794.9378
8 | 2704951.3629 | 1227830.408 | 2704953.7464 | 1227857.2589 | 2704955.2531 | 1227867.1382
9 | 2704951.3629 | 1227830.408 | 2704950.8919 | 1227825.0998
10 | 2704948.6376 | 1227799.7371 | 2704950.3451 | 1227818.937 | 2704950.8919 | 1227825.0998
11 | 2704973.1693 | 1227799.2965 | 2704964.4012 | 1227799.454
12 | 2705129.4882 | 1227794.3927 | 2705153.6578 | 1227793.7875
13 | 2704948.6376 | 1227799.7371 | 2704946.872 | 1227799.769
14 | 2704948.6376 | 1227799.7371 | 2704964.4012 | 1227799.454
15 | 2704946.872 | 1227799.769 | 2704939.926 | 1227799.8946 | 2704930.0863 | 1227800.3667
16 | 2704893.3332 | 1227802.1302 | 2704930.0863 | 1227800.3667
17 | 2704893.3332 | 1227802.1302 | 2704892.1774 | 1227790.7458 | 2704893.3007 | 1227782.4928 | 2704906.0695 | 1227760.3126 | 2704909.3837 | 1227750.7528 | 2704910.244 | 1227740.6604 | 2704907.9462 | 1227735.2947
18 | 2704907.9462 | 1227735.2947 | 2704906.444 | 1227731.7868 | 2704894.4709 | 1227708.8698 | 2704892.4621 | 1227702.023
19 | 2704893.2964 | 1227678.3486 | 2704890.6899 | 1227688.1767 | 2704891.0605 | 1227697.2455 | 2704892.4621 | 1227702.023
20 | 2704892.4621 | 1227702.023 | 2704918.4473 | 1227703.1661
21 | 2704893.2964 | 1227678.3486 | 2704954.5245 | 1227658.1912
22 | 2705189.3399 | 1227792.894 | 2705153.6578 | 1227793.7875
23 | 2705189.3399 | 1227792.894 | 2705188.9305 | 1227915.7622
24 | 2704954.5245 | 1227658.1912 | 2704950.613 | 1227661.647 | 2704949.9871 | 1227665.3276 | 2704951.3012 | 1227669.0313 | 2704954.9203 | 1227673.5541 | 2704957.6747 | 1227674.6702 | 2704963.0507 | 1227675.8436 | 2704967.511 | 1227676.0781 | 2704977.2095 | 1227676.7052 | 2704989.541 | 1227676.3114 | 2704998.3258 | 1227676.3109 | 2705001.7182 | 1227676.0706

## bus_geodata
| x | y | coords
0 | 2705017.3662 | 1227798.147
1 | 2705058.452 | 1227796.7713
2 | 2705007.9849 | 1227798.4611
3 | 2705093.2598 | 1227795.6058
4 | 2704993.9092 | 1227798.9241
5 | 2705113.2099 | 1227794.9378
6 | 2704951.3629 | 1227830.408
7 | 2704955.2531 | 1227867.1382
8 | 2704950.8919 | 1227825.0998
9 | 2704993.8371 | 1227789.7049
10 | 2704973.1693 | 1227799.2965
11 | 2705129.4882 | 1227794.3927
12 | 2704948.6376 | 1227799.7371
13 | 2704964.4012 | 1227799.454
14 | 2704946.872 | 1227799.769
15 | 2704930.0863 | 1227800.3667
16 | 2704893.3332 | 1227802.1302
17 | 2704907.9462 | 1227735.2947
18 | 2704892.4621 | 1227702.023
19 | 2704893.2964 | 1227678.3486
20 | 2704918.4473 | 1227703.1661
21 | 2705153.6578 | 1227793.7875
22 | 2705189.3399 | 1227792.894
23 | 2705188.9305 | 1227915.7622
24 | 2704954.5245 | 1227658.1912
25 | 2705001.7182 | 1227676.0706
26 | 2704993.9092 | 1227798.9241

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99706 | -0.056327 | 0.0087697 | 0.0021979
1 | 0.99517 | -0.092815 | 0.012128 | 0.0030394
2 | 0.99757 | -0.046573 | 0 | 0
3 | 0.99395 | -0.11638 | 0.0078872 | 0.0019767
4 | 0.99833 | -0.032 | 0 | 0
5 | 0.99339 | -0.12713 | 0.0028271 | 0.00070854
6 | 0.99532 | -0.08973 | 0 | 0
7 | 0.9925 | -0.1442 | 0.083549 | 0.020939
8 | 0.99573 | -0.081899 | 0.011335 | 0.0028407
9 | 0.99809 | -0.036687 | 0.029059 | 0.0072829
10 | 1 | 0 | -0.2854 | -0.071741
11 | 0.99298 | -0.1351 | 0 | 0
12 | 0.99793 | -0.039521 | 0 | 0
13 | 0.99922 | -0.014821 | 0.014526 | 0.0036406
14 | 0.9978 | -0.042129 | 0.014533 | 0.0036422
15 | 0.99672 | -0.062689 | 0.014531 | 0.0036417
16 | 0.99486 | -0.098459 | 0 | 0
17 | 0.99124 | -0.1683 | 0.011449 | 0.0028694
18 | 0.98976 | -0.19698 | 0.0029886 | 0.00074902
19 | 0.98953 | -0.20131 | 0 | 0
20 | 0.98902 | -0.21125 | 0.030817 | 0.0077236
21 | 0.99237 | -0.14694 | 0.026543 | 0.0066524
22 | 0.99233 | -0.14766 | 0 | 0
23 | 0.9922 | -0.15014 | 0.001136 | 0.00028471
24 | 0.98894 | -0.21284 | 0 | 0
25 | 0.98833 | -0.22461 | 0.010042 | 0.0025167
26 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.050695 | 0.012769 | -0.050607 | -0.012713 | 8.8292e-05 | 5.5972e-05 | 0.075679 | 0.07568 | 0.07568 | 0.99706 | -0.056327 | 0.99517 | -0.092815 | 20.7911
1 | -0.059465 | -0.014967 | 0.059492 | 0.014985 | 2.7736e-05 | 1.7629e-05 | 0.088767 | 0.088767 | 0.088767 | 0.99706 | -0.056327 | 0.99757 | -0.046573 | 24.3866
2 | 0.038479 | 0.0096736 | -0.038436 | -0.0096464 | 4.325e-05 | 2.7228e-05 | 0.057546 | 0.057546 | 0.057546 | 0.99517 | -0.092815 | 0.99395 | -0.11638 | 15.8094
3 | -0.059492 | -0.014985 | 0.059534 | 0.015011 | 4.1492e-05 | 2.6372e-05 | 0.088767 | 0.088767 | 0.088767 | 0.99757 | -0.046573 | 0.99833 | -0.032 | 24.3866
4 | 0.030549 | 0.0076697 | -0.030533 | -0.0076599 | 1.566e-05 | 9.7636e-06 | 0.045738 | 0.045738 | 0.045738 | 0.99395 | -0.11638 | 0.99339 | -0.12713 | 12.5655
5 | 0.029065 | 0.0072869 | -0.029059 | -0.0072829 | 6.49e-06 | 4.0331e-06 | 0.043323 | 0.043323 | 0.043323 | 0.99833 | -0.032 | 0.99809 | -0.036687 | 11.9019
6 | -0.088599 | -0.022298 | 0.088735 | 0.022384 | 0.00013572 | 8.659e-05 | 0.13209 | 0.13209 | 0.13209 | 0.99833 | -0.032 | 1 | 0 | 36.2885
7 | 0.027706 | 0.0069514 | -0.027695 | -0.0069449 | 1.0521e-05 | 6.5227e-06 | 0.041504 | 0.041504 | 0.041504 | 0.99339 | -0.12713 | 0.99298 | -0.1351 | 11.4021
8 | 0.083766 | 0.021078 | -0.083549 | -0.020939 | 0.00021741 | 0.00013866 | 0.12526 | 0.12526 | 0.12526 | 0.99532 | -0.08973 | 0.9925 | -0.1442 | 34.4126
9 | -0.083766 | -0.021078 | 0.083798 | 0.021098 | 3.1356e-05 | 1.9998e-05 | 0.12526 | 0.12526 | 0.12526 | 0.99532 | -0.08973 | 0.99573 | -0.081899 | 34.4126
10 | -0.095132 | -0.023939 | 0.095325 | 0.024062 | 0.00019308 | 0.00012324 | 0.1422 | 0.1422 | 0.1422 | 0.99573 | -0.081899 | 0.99793 | -0.039521 | 39.066
11 | 0.19502 | 0.049357 | -0.19488 | -0.049268 | 0.00013863 | 8.8492e-05 | 0.29036 | 0.29036 | 0.29036 | 1 | 0 | 0.99922 | -0.014821 | 39.8847
12 | 0.027695 | 0.0069449 | -0.02768 | -0.0069352 | 1.5618e-05 | 9.6827e-06 | 0.041504 | 0.041504 | 0.041504 | 0.99298 | -0.1351 | 0.99237 | -0.14694 | 11.4022
13 | 0.084815 | 0.021429 | -0.084805 | -0.021423 | 1.0602e-05 | 6.762e-06 | 0.12653 | 0.12653 | 0.12653 | 0.99793 | -0.039521 | 0.9978 | -0.042129 | 34.7606
14 | -0.18014 | -0.045491 | 0.18035 | 0.045628 | 0.00021348 | 0.00013621 | 0.26873 | 0.26873 | 0.26873 | 0.99793 | -0.039521 | 0.99922 | -0.014821 | 36.9133
15 | 0.070272 | 0.01778 | -0.070203 | -0.017736 | 6.926e-05 | 4.4107e-05 | 0.10486 | 0.10486 | 0.10486 | 0.9978 | -0.042129 | 0.99672 | -0.062689 | 28.8067
16 | 0.055672 | 0.014095 | -0.055577 | -0.014034 | 9.5432e-05 | 6.0597e-05 | 0.083164 | 0.083164 | 0.083164 | 0.99672 | -0.062689 | 0.99486 | -0.098459 | 22.8472
17 | 0.055577 | 0.014034 | -0.055391 | -0.013916 | 0.00018531 | 0.00011767 | 0.083164 | 0.083164 | 0.083164 | 0.99486 | -0.098459 | 0.99124 | -0.1683 | 22.8473
18 | 0.043942 | 0.011047 | -0.043882 | -0.011009 | 6.0084e-05 | 3.798e-05 | 0.065977 | 0.065977 | 0.065977 | 0.99124 | -0.1683 | 0.98976 | -0.19698 | 18.1256
19 | 0.010055 | 0.0025232 | -0.010053 | -0.0025222 | 2.0762e-06 | 1.0175e-06 | 0.015118 | 0.015118 | 0.015118 | 0.98976 | -0.19698 | 0.98953 | -0.20131 | 4.1534
20 | 0.030838 | 0.0077367 | -0.030817 | -0.0077236 | 2.0969e-05 | 1.3086e-05 | 0.046366 | 0.046366 | 0.046366 | 0.98976 | -0.19698 | 0.98902 | -0.21125 | 12.7379
21 | 0.010053 | 0.0025222 | -0.010047 | -0.0025195 | 5.5251e-06 | 2.7085e-06 | 0.015118 | 0.015119 | 0.015119 | 0.98953 | -0.20131 | 0.98894 | -0.21284 | 4.1534
22 | 0.0011362 | 0.00028277 | -0.0011361 | -0.00028321 | 3.8821e-08 | -4.3628e-07 | 0.001703 | 0.0017031 | 0.0017031 | 0.99237 | -0.14694 | 0.99233 | -0.14766 | 0.46789
23 | 0.0011361 | 0.00028321 | -0.001136 | -0.00028471 | 1.3369e-07 | -1.5015e-06 | 0.0017031 | 0.0017037 | 0.0017037 | 0.99233 | -0.14766 | 0.9922 | -0.15014 | 0.46805
24 | 0.010047 | 0.0025195 | -0.010042 | -0.0025167 | 5.632e-06 | 2.762e-06 | 0.015119 | 0.015119 | 0.015119 | 0.98894 | -0.21284 | 0.98833 | -0.22461 | 4.1535

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37263 | 0.093603

## res_load
| p_mw | q_mvar
0 | 0.0087697 | 0.0021979
1 | 0.012128 | 0.0030394
2 | 0.0078872 | 0.0019767
3 | 0.0028271 | 0.00070854
4 | 0.083549 | 0.020939
5 | 0.011335 | 0.0028407
6 | 0.029059 | 0.0072829
7 | 0.087229 | 0.021862
8 | 0.014526 | 0.0036406
9 | 0.014533 | 0.0036422
10 | 0.014531 | 0.0036417
11 | 0.011449 | 0.0028694
12 | 0.0029886 | 0.00074902
13 | 0.030817 | 0.0077236
14 | 0.026543 | 0.0066524
15 | 0.001136 | 0.00028471
16 | 0.010042 | 0.0025167

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1