## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1341-16_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1341-16_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1341-16_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1341-16_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1341-16_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1341-16_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1341-16_0_4_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_1341-16_0_4_node_22 | 0.4 | n |  | TRUE
8 | bus_LV_1341-16_0_4_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_1341-16_0_4_node_91 | 0.4 | n |  | TRUE
10 | bus_LV_1341-16_0_4_node_23 | 0.4 | n |  | TRUE
11 | bus_LV_1341-16_0_4_node_83 | 0.4 | n |  | TRUE
12 | bus_LV_1341-16_0_4_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_1341-16_0_4_node_92 | 0.4 | n |  | TRUE
14 | bus_LV_1341-16_0_4_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_1341-16_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_1341-16_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1341-16_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1341-16_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1341-16_0_4_node_39 | 0.4 | n |  | TRUE
20 | bus_LV_1341-16_0_4_node_42 | 0.4 | n |  | TRUE
21 | bus_LV_1341-16_0_4_node_43 | 0.4 | n |  | TRUE
22 | bus_LV_1341-16_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1341-16_0_4_node_41 | 0.4 | n |  | TRUE
24 | bus_LV_1341-16_0_4_node_44 | 0.4 | n |  | TRUE
25 | bus_LV_1341-16_0_4_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_1341-16_0_4_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_1341-16_0_4_node_120 | 0.4 | n |  | TRUE
28 | bus_LV_1341-16_0_4_node_101 | 0.4 | n |  | TRUE
29 | bus_LV_1341-16_0_4_node_102 | 0.4 | n |  | TRUE
30 | bus_LV_1341-16_0_4_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_1341-16_0_4_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_1341-16_0_4_node_119 | 0.4 | n |  | TRUE
33 | bus_LV_1341-16_0_4_node_14 | 0.4 | n |  | TRUE
34 | bus_LV_1341-16_0_4_node_15 | 0.4 | n |  | TRUE
35 | bus_LV_1341-16_0_4_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_1341-16_0_4_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_1341-16_0_4_node_50 | 0.4 | n |  | TRUE
38 | bus_LV_1341-16_0_4_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_1341-16_0_4_node_51 | 0.4 | n |  | TRUE
40 | bus_LV_1341-16_0_4_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_1341-16_0_4_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_1341-16_0_4_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_1341-16_0_4_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_1341-16_0_4_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_1341-16_0_4_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_1341-16_0_4_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_1341-16_0_4_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_1341-16_0_4_node_70 | 0.4 | n |  | TRUE
49 | bus_LV_1341-16_0_4_node_116 | 0.4 | n |  | TRUE
50 | bus_LV_1341-16_0_4_node_117 | 0.4 | n |  | TRUE
51 | bus_LV_1341-16_0_4_node_115 | 0.4 | n |  | TRUE
52 | bus_LV_1341-16_0_4_node_118 | 0.4 | n |  | TRUE
53 | bus_LV_1341-16_0_4_node_68 | 0.4 | n |  | TRUE
54 | bus_LV_1341-16_0_4_node_88 | 0.4 | n |  | TRUE
55 | bus_LV_1341-16_0_4_node_89 | 0.4 | n |  | TRUE
56 | bus_LV_1341-16_0_4_node_33 | 0.4 | n |  | TRUE
57 | bus_LV_1341-16_0_4_node_35 | 0.4 | n |  | TRUE
58 | bus_LV_1341-16_0_4_node_37 | 0.4 | n |  | TRUE
59 | bus_LV_1341-16_0_4_node_73 | 0.4 | n |  | TRUE
60 | bus_LV_1341-16_0_4_node_77 | 0.4 | n |  | TRUE
61 | bus_LV_1341-16_0_4_node_38 | 0.4 | n |  | TRUE
62 | bus_LV_1341-16_0_4_node_74 | 0.4 | n |  | TRUE
63 | bus_LV_1341-16_0_4_node_127 | 0.4 | n |  | TRUE
64 | bus_LV_1341-16_0_4_node_76 | 0.4 | n |  | TRUE
65 | bus_LV_1341-16_0_4_node_100 | 0.4 | n |  | TRUE
66 | bus_LV_1341-16_0_4_node_126 | 0.4 | n |  | TRUE
67 | bus_LV_1341-16_0_4_node_40 | 0.4 | n |  | TRUE
68 | bus_LV_1341-16_0_4_node_45 | 0.4 | n |  | TRUE
69 | bus_LV_1341-16_0_4_node_46 | 0.4 | n |  | TRUE
70 | bus_LV_1341-16_0_4_node_47 | 0.4 | n |  | TRUE
71 | bus_LV_1341-16_0_4_node_48 | 0.4 | n |  | TRUE
72 | bus_LV_1341-16_0_4_node_49 | 0.4 | n |  | TRUE
73 | bus_LV_1341-16_0_4_node_57 | 0.4 | n |  | TRUE
74 | bus_LV_1341-16_0_4_node_58 | 0.4 | n |  | TRUE
75 | bus_LV_1341-16_0_4_node_52 | 0.4 | n |  | TRUE
76 | bus_LV_1341-16_0_4_node_53 | 0.4 | n |  | TRUE
77 | bus_LV_1341-16_0_4_node_54 | 0.4 | n |  | TRUE
78 | bus_LV_1341-16_0_4_node_55 | 0.4 | n |  | TRUE
79 | bus_LV_1341-16_0_4_node_56 | 0.4 | n |  | TRUE
80 | bus_LV_1341-16_0_4_node_59 | 0.4 | n |  | TRUE
81 | bus_LV_1341-16_0_4_node_60 | 0.4 | n |  | TRUE
82 | bus_LV_1341-16_0_4_node_67 | 0.4 | n |  | TRUE
83 | bus_LV_1341-16_0_4_node_61 | 0.4 | n |  | TRUE
84 | bus_LV_1341-16_0_4_node_62 | 0.4 | n |  | TRUE
85 | bus_LV_1341-16_0_4_node_63 | 0.4 | n |  | TRUE
86 | bus_LV_1341-16_0_4_node_64 | 0.4 | n |  | TRUE
87 | bus_LV_1341-16_0_4_node_65 | 0.4 | n |  | TRUE
88 | bus_LV_1341-16_0_4_node_66 | 0.4 | n |  | TRUE
89 | bus_LV_1341-16_0_4_node_71 | 0.4 | n |  | TRUE
90 | bus_LV_1341-16_0_4_node_72 | 0.4 | n |  | TRUE
91 | bus_LV_1341-16_0_4_node_69 | 0.4 | n |  | TRUE
92 | bus_LV_1341-16_0_4_node_109 | 0.4 | n |  | TRUE
93 | bus_LV_1341-16_0_4_node_106 | 0.4 | n |  | TRUE
94 | bus_LV_1341-16_0_4_node_79 | 0.4 | n |  | TRUE
95 | bus_LV_1341-16_0_4_node_107 | 0.4 | n |  | TRUE
96 | bus_LV_1341-16_0_4_node_90 | 0.4 | n |  | TRUE
97 | bus_LV_1341-16_0_4_node_81 | 0.4 | n |  | TRUE
98 | bus_LV_1341-16_0_4_node_80 | 0.4 | n |  | TRUE
99 | bus_LV_1341-16_0_4_node_75 | 0.4 | n |  | TRUE
100 | bus_LV_1341-16_0_4_node_78 | 0.4 | n |  | TRUE
101 | bus_LV_1341-16_0_4_node_84 | 0.4 | n |  | TRUE
102 | bus_LV_1341-16_0_4_node_85 | 0.4 | n |  | TRUE
103 | bus_LV_1341-16_0_4_node_86 | 0.4 | n |  | TRUE
104 | bus_LV_1341-16_0_4_node_87 | 0.4 | n |  | TRUE
105 | bus_LV_1341-16_0_4_node_93 | 0.4 | n |  | TRUE
106 | bus_LV_1341-16_0_4_node_94 | 0.4 | n |  | TRUE
107 | bus_LV_1341-16_0_4_node_95 | 0.4 | n |  | TRUE
108 | bus_LV_1341-16_0_4_node_96 | 0.4 | n |  | TRUE
109 | bus_LV_1341-16_0_4_node_97 | 0.4 | n |  | TRUE
110 | bus_LV_1341-16_0_4_node_98 | 0.4 | n |  | TRUE
111 | bus_LV_1341-16_0_4_node_99 | 0.4 | n |  | TRUE
112 | bus_LV_1341-16_0_4_node_121 | 0.4 | n |  | TRUE
113 | bus_LV_1341-16_0_4_node_123 | 0.4 | n |  | TRUE
114 | bus_LV_1341-16_0_4_node_103 | 0.4 | n |  | TRUE
115 | bus_LV_1341-16_0_4_node_112 | 0.4 | n |  | TRUE
116 | bus_LV_1341-16_0_4_node_113 | 0.4 | n |  | TRUE
117 | bus_LV_1341-16_0_4_node_111 | 0.4 | n |  | TRUE
118 | bus_LV_1341-16_0_4_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_1341-16_0_4_node_105 | 0.4 | n |  | TRUE
120 | bus_LV_1341-16_0_4_node_114 | 0.4 | n |  | TRUE
121 | bus_LV_1341-16_0_4_node_108 | 0.4 | n |  | TRUE
122 | bus_LV_1341-16_0_4_node_110 | 0.4 | n |  | TRUE
123 | bus_LV_1341-16_0_4_node_124 | 0.4 | n |  | TRUE
124 | bus_LV_1341-16_0_4_node_125 | 0.4 | n |  | TRUE
125 | bus_MV_16_0_node_137 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1341-16_0_4_load_0 | 0 | 0.0096916 | 0.0024289 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1341-16_0_4_load_1 | 1 | 0.00089676 | 0.00022475 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1341-16_0_4_load_5 | 5 | 0.0014445 | 0.00036202 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1341-16_0_4_load_13 | 6 | 0.0027156 | 0.0006806 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1341-16_0_4_load_22 | 7 | 0.0014457 | 0.00036232 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1341-16_0_4_load_19 | 8 | 0.00095966 | 0.00024051 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1341-16_0_4_load_91 | 9 | 0.0011955 | 0.00029963 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1341-16_0_4_load_23 | 10 | 0.0035254 | 0.00088355 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1341-16_0_4_load_83 | 11 | 0.00037524 | 9.4043e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1341-16_0_4_load_20 | 12 | 0.0040599 | 0.0010175 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1341-16_0_4_load_92 | 13 | 0.001543 | 0.00038672 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1341-16_0_4_load_6 | 14 | 0.005117 | 0.0012824 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1341-16_0_4_load_7 | 15 | 0.012126 | 0.0030391 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1341-16_0_4_load_9 | 17 | 0.0021628 | 0.00054205 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1341-16_0_4_load_39 | 19 | 0.0021612 | 0.00054165 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1341-16_0_4_load_43 | 21 | 0.0021638 | 0.00054229 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1341-16_0_4_load_16 | 22 | 0.0021604 | 0.00054146 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1341-16_0_4_load_44 | 24 | 0.0021628 | 0.00054205 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1341-16_0_4_load_11 | 25 | 0.001985 | 0.00049749 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1341-16_0_4_load_12 | 26 | 0.0092253 | 0.0023121 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1341-16_0_4_load_120 | 27 | 0.0077024 | 0.0019304 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1341-16_0_4_load_101 | 28 | 0.0018992 | 0.00047599 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1341-16_0_4_load_102 | 29 | 0.0017718 | 0.00044405 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1341-16_0_4_load_29 | 30 | 0.0067976 | 0.0017036 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1341-16_0_4_load_30 | 31 | 0.0060901 | 0.0015263 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1341-16_0_4_load_119 | 32 | 0.0022172 | 0.00055567 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1341-16_0_4_load_14 | 33 | 0.0021716 | 0.00054426 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1341-16_0_4_load_17 | 35 | 0.0022613 | 0.00056673 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1341-16_0_4_load_18 | 36 | 0.0026286 | 0.00065878 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1341-16_0_4_load_50 | 37 | 0.0021615 | 0.00054173 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1341-16_0_4_load_36 | 38 | 0.0042845 | 0.0010738 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1341-16_0_4_load_51 | 39 | 0.0042731 | 0.0010709 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1341-16_0_4_load_34 | 40 | 0.0028603 | 0.00071687 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1341-16_0_4_load_21 | 41 | 0.0012096 | 0.00030316 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1341-16_0_4_load_27 | 42 | 0.0056697 | 0.001421 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1341-16_0_4_load_25 | 43 | 0.00060056 | 0.00015051 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1341-16_0_4_load_26 | 44 | 0.00026239 | 6.5762e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1341-16_0_4_load_28 | 45 | 0.0066734 | 0.0016725 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1341-16_0_4_load_31 | 46 | 0.00026223 | 6.5721e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1341-16_0_4_load_32 | 47 | 0.00026216 | 6.5703e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1341-16_0_4_load_116 | 49 | 0.0014993 | 0.00037577 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1341-16_0_4_load_117 | 50 | 0.0022572 | 0.0005657 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1341-16_0_4_load_115 | 51 | 0.0012574 | 0.00031513 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1341-16_0_4_load_118 | 52 | 0.0022581 | 0.00056592 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1341-16_0_4_load_88 | 54 | 0.0014497 | 0.00036332 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1341-16_0_4_load_89 | 55 | 0.0014516 | 0.00036381 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1341-16_0_4_load_33 | 56 | 0.0041373 | 0.0010369 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1341-16_0_4_load_37 | 58 | 0.0057782 | 0.0014481 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1341-16_0_4_load_73 | 59 | 0.011627 | 0.0029141 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1341-16_0_4_load_77 | 60 | 0.00603 | 0.0015113 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1341-16_0_4_load_127 | 63 | 0.0067646 | 0.0016954 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1341-16_0_4_load_76 | 64 | 0.0013226 | 0.00033148 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1341-16_0_4_load_126 | 66 | 0.0040745 | 0.0010212 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1341-16_0_4_load_40 | 67 | 0.020259 | 0.0050773 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1341-16_0_4_load_45 | 68 | 0.0021636 | 0.00054225 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1341-16_0_4_load_46 | 69 | 0.0021638 | 0.00054229 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1341-16_0_4_load_47 | 70 | 0.0021628 | 0.00054205 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1341-16_0_4_load_48 | 71 | 0.0017874 | 0.00044796 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1341-16_0_4_load_49 | 72 | 0.0017863 | 0.00044769 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1341-16_0_4_load_57 | 73 | 0.0034594 | 0.00086702 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1341-16_0_4_load_58 | 74 | 0.0034294 | 0.00085949 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1341-16_0_4_load_52 | 75 | 0.0022597 | 0.00056634 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1341-16_0_4_load_53 | 76 | 0.0021636 | 0.00054225 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1341-16_0_4_load_54 | 77 | 0.0021628 | 0.00054206 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1341-16_0_4_load_55 | 78 | 0.0018651 | 0.00046744 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1341-16_0_4_load_56 | 79 | 0.0033738 | 0.00084554 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1341-16_0_4_load_59 | 80 | 0.0017854 | 0.00044747 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1341-16_0_4_load_60 | 81 | 0.0017848 | 0.0004473 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1341-16_0_4_load_67 | 82 | 0.0010197 | 0.00025556 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1341-16_0_4_load_61 | 83 | 0.0018656 | 0.00046757 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1341-16_0_4_load_62 | 84 | 0.0028037 | 0.00070268 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1341-16_0_4_load_63 | 85 | 0.0017848 | 0.0004473 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1341-16_0_4_load_64 | 86 | 0.0017848 | 0.0004473 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1341-16_0_4_load_65 | 87 | 0.0018681 | 0.00046818 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1341-16_0_4_load_66 | 88 | 0.003505 | 0.00087844 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1341-16_0_4_load_71 | 89 | 0.0073037 | 0.0018305 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1341-16_0_4_load_72 | 90 | 0.004472 | 0.0011208 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1341-16_0_4_load_109 | 92 | 0.013282 | 0.0033288 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1341-16_0_4_load_106 | 93 | 0.0057311 | 0.0014364 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1341-16_0_4_load_79 | 94 | 0.014262 | 0.0035745 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1341-16_0_4_load_107 | 95 | 0.0059932 | 0.001502 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1341-16_0_4_load_90 | 96 | 0.0014507 | 0.00036359 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1341-16_0_4_load_81 | 97 | 0.0045483 | 0.0011399 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1341-16_0_4_load_80 | 98 | 0.0040231 | 0.0010083 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1341-16_0_4_load_75 | 99 | 0.0019657 | 0.00049265 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1341-16_0_4_load_78 | 100 | 0.013274 | 0.0033267 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1341-16_0_4_load_84 | 101 | 0.0014533 | 0.00036422 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1341-16_0_4_load_85 | 102 | 0.0015011 | 0.00037621 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1341-16_0_4_load_86 | 103 | 0.0015686 | 0.00039314 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1341-16_0_4_load_87 | 104 | 0.0016079 | 0.00040297 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1341-16_0_4_load_93 | 105 | 0.001501 | 0.00037619 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1341-16_0_4_load_94 | 106 | 0.00097084 | 0.00024332 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1341-16_0_4_load_95 | 107 | 0.0015608 | 0.00039117 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1341-16_0_4_load_96 | 108 | 0.0015904 | 0.0003986 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1341-16_0_4_load_97 | 109 | 0.00073617 | 0.0001845 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1341-16_0_4_load_98 | 110 | 0.00083288 | 0.00020874 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1341-16_0_4_load_99 | 111 | 0.0020157 | 0.00050518 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1341-16_0_4_load_121 | 112 | 0.0011593 | 0.00029054 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1341-16_0_4_load_123 | 113 | 0.0017437 | 0.00043701 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1341-16_0_4_load_103 | 114 | 0.0010637 | 0.00026659 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1341-16_0_4_load_113 | 116 | 0.010534 | 0.00264 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1341-16_0_4_load_111 | 117 | 0.0058534 | 0.001467 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1341-16_0_4_load_105 | 119 | 0.0027911 | 0.00069952 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1341-16_0_4_load_114 | 120 | 0.0027911 | 0.00069952 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1341-16_0_4_load_108 | 121 | 0.0057187 | 0.0014332 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1341-16_0_4_load_110 | 122 | 0.0032738 | 0.0008205 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1341-16_0_4_load_124 | 123 | 0.0014298 | 0.00035833 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1341-16_0_4_load_125 | 124 | 0.00061012 | 0.00015291 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 86 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1341-16_0_4_line_0 |  | 0 | 1 | 0.021822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1341-16_0_4_line_1 |  | 0 | 2 | 0.058235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1341-16_0_4_line_2 |  | 1 | 3 | 0.027482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1341-16_0_4_line_3 |  | 2 | 4 | 0.003952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1341-16_0_4_line_4 |  | 2 | 5 | 0.01506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1341-16_0_4_line_5 |  | 3 | 6 | 0.042766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1341-16_0_4_line_6 |  | 4 | 7 | 0.014758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1341-16_0_4_line_7 |  | 4 | 8 | 0.013946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1341-16_0_4_line_8 |  | 5 | 9 | 0.008504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1341-16_0_4_line_9 |  | 6 | 10 | 0.03695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1341-16_0_4_line_10 |  | 7 | 11 | 0.00051838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1341-16_0_4_line_11 |  | 8 | 12 | 0.013091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1341-16_0_4_line_12 |  | 9 | 13 | 0.0088006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1341-16_0_4_line_13 |  | 11 | 20 | 0.034383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1341-16_0_4_line_14 |  | 12 | 41 | 0.010612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1341-16_0_4_line_15 |  | 13 | 105 | 0.0064989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1341-16_0_4_line_16 |  | 14 | 15 | 0.050073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1341-16_0_4_line_17 |  | 14 | 16 | 0.039507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1341-16_0_4_line_18 |  | 16 | 17 | 0.0020381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1341-16_0_4_line_19 |  | 16 | 18 | 0.01537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1341-16_0_4_line_20 |  | 17 | 19 | 0.020582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_1341-16_0_4_line_21 |  | 18 | 20 | 0.019951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1341-16_0_4_line_22 |  | 18 | 21 | 0.026251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_1341-16_0_4_line_23 |  | 19 | 22 | 0.0096365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_1341-16_0_4_line_24 |  | 20 | 23 | 0.056313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1341-16_0_4_line_25 |  | 21 | 24 | 0.015026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1341-16_0_4_line_26 |  | 22 | 34 | 0.025523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1341-16_0_4_line_27 |  | 23 | 67 | 0.034258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1341-16_0_4_line_28 |  | 24 | 68 | 0.0094416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1341-16_0_4_line_29 |  | 25 | 26 | 0.034136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1341-16_0_4_line_30 |  | 26 | 27 | 0.060457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1341-16_0_4_line_31 |  | 27 | 32 | 0.0084784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1341-16_0_4_line_32 |  | 27 | 30 | 0.054908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1341-16_0_4_line_33 |  | 28 | 29 | 0.0081352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1341-16_0_4_line_34 |  | 29 | 114 | 0.027273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1341-16_0_4_line_35 |  | 30 | 31 | 0.030767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1341-16_0_4_line_36 |  | 31 | 48 | 0.016755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1341-16_0_4_line_37 |  | 32 | 52 | 0.0085339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1341-16_0_4_line_38 |  | 33 | 34 | 0.05766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1341-16_0_4_line_39 |  | 34 | 35 | 0.014108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_1341-16_0_4_line_40 |  | 34 | 36 | 0.053017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1341-16_0_4_line_41 |  | 35 | 37 | 0.0066096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_1341-16_0_4_line_42 |  | 36 | 38 | 0.024926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1341-16_0_4_line_43 |  | 37 | 39 | 0.010441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_1341-16_0_4_line_44 |  | 38 | 40 | 0.017323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1341-16_0_4_line_45 |  | 39 | 75 | 0.0055781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_1341-16_0_4_line_46 |  | 40 | 56 | 0.022493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1341-16_0_4_line_47 |  | 41 | 42 | 0.013678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1341-16_0_4_line_48 |  | 42 | 43 | 0.0042299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1341-16_0_4_line_49 |  | 43 | 44 | 0.019649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1341-16_0_4_line_50 |  | 44 | 45 | 0.0020357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1341-16_0_4_line_51 |  | 45 | 46 | 0.0072658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1341-16_0_4_line_52 |  | 46 | 47 | 0.0093052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1341-16_0_4_line_53 |  | 47 | 54 | 0.0093061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1341-16_0_4_line_54 |  | 48 | 53 | 0.019017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_1341-16_0_4_line_55 |  | 49 | 50 | 0.0050289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1341-16_0_4_line_56 |  | 49 | 51 | 0.01452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1341-16_0_4_line_57 |  | 50 | 52 | 0.0075988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1341-16_0_4_line_58 |  | 51 | 120 | 0.00066767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1341-16_0_4_line_59 |  | 53 | 91 | 0.014736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1341-16_0_4_line_60 |  | 53 | 82 | 0.034123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_1341-16_0_4_line_61 |  | 54 | 55 | 0.0093847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1341-16_0_4_line_62 |  | 55 | 96 | 0.0093051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1341-16_0_4_line_63 |  | 56 | 57 | 0.0025251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1341-16_0_4_line_64 |  | 57 | 58 | 0.020519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1341-16_0_4_line_65 |  | 58 | 59 | 0.022732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1341-16_0_4_line_66 |  | 58 | 60 | 0.036711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1341-16_0_4_line_67 |  | 59 | 62 | 0.021703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1341-16_0_4_line_68 |  | 60 | 64 | 0.017522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1341-16_0_4_line_69 |  | 61 | 62 | 0.044541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1341-16_0_4_line_70 |  | 61 | 63 | 0.086227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1341-16_0_4_line_71 |  | 63 | 65 | 0.10057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1341-16_0_4_line_72 |  | 63 | 66 | 0.053801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1341-16_0_4_line_73 |  | 64 | 97 | 0.03335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1341-16_0_4_line_74 |  | 64 | 99 | 0.018668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1341-16_0_4_line_75 |  | 65 | 108 | 0.011609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1341-16_0_4_line_76 |  | 66 | 124 | 0.008341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1341-16_0_4_line_77 |  | 68 | 69 | 0.016455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_1341-16_0_4_line_78 |  | 69 | 70 | 0.0094414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_1341-16_0_4_line_79 |  | 70 | 71 | 0.017903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_1341-16_0_4_line_80 |  | 71 | 72 | 0.0094422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_1341-16_0_4_line_81 |  | 72 | 73 | 0.027066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_1341-16_0_4_line_82 |  | 73 | 74 | 0.020082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_1341-16_0_4_line_83 |  | 74 | 82 | 0.0052711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_1341-16_0_4_line_84 |  | 75 | 76 | 0.00077219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_1341-16_0_4_line_85 |  | 76 | 77 | 0.0094416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_1341-16_0_4_line_86 |  | 77 | 78 | 0.012668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_1341-16_0_4_line_87 |  | 78 | 79 | 0.0020065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_1341-16_0_4_line_88 |  | 79 | 80 | 0.0025932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_1341-16_0_4_line_89 |  | 80 | 81 | 0.0094416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_1341-16_0_4_line_90 |  | 81 | 83 | 0.0094054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_1341-16_0_4_line_91 |  | 83 | 84 | 0.0012169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
92 | LV_1341-16_0_4_line_92 |  | 84 | 85 | 0.0056011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_1341-16_0_4_line_93 |  | 85 | 86 | 0.0094396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_1341-16_0_4_line_94 |  | 86 | 87 | 0.0057948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1341-16_0_4_line_95 |  | 87 | 88 | 0.023894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1341-16_0_4_line_96 |  | 88 | 89 | 0.0035493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1341-16_0_4_line_97 |  | 89 | 90 | 0.004585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1341-16_0_4_line_98 |  | 91 | 92 | 0.033022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1341-16_0_4_line_99 |  | 91 | 93 | 0.0076455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1341-16_0_4_line_100 |  | 92 | 94 | 0.054875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1341-16_0_4_line_101 |  | 93 | 95 | 0.031121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1341-16_0_4_line_102 |  | 94 | 100 | 0.0013374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1341-16_0_4_line_103 |  | 95 | 121 | 0.0067305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1341-16_0_4_line_104 |  | 97 | 98 | 0.02938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1341-16_0_4_line_105 |  | 101 | 102 | 0.007679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1341-16_0_4_line_106 |  | 101 | 103 | 0.0088108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1341-16_0_4_line_107 |  | 103 | 104 | 0.0078778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1341-16_0_4_line_108 |  | 104 | 105 | 0.0086404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1341-16_0_4_line_109 |  | 106 | 107 | 0.024148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1341-16_0_4_line_110 |  | 107 | 108 | 0.016674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1341-16_0_4_line_111 |  | 107 | 109 | 0.13897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1341-16_0_4_line_112 |  | 109 | 112 | 0.20465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1341-16_0_4_line_113 |  | 109 | 110 | 0.010908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1341-16_0_4_line_114 |  | 110 | 111 | 0.018277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1341-16_0_4_line_115 |  | 112 | 113 | 0.13666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1341-16_0_4_line_116 |  | 114 | 118 | 0.016104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1341-16_0_4_line_117 |  | 115 | 116 | 0.026235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1341-16_0_4_line_118 |  | 115 | 117 | 0.0081439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1341-16_0_4_line_119 |  | 117 | 122 | 0.031395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1341-16_0_4_line_120 |  | 118 | 119 | 0.030439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1341-16_0_4_line_121 |  | 119 | 120 | 0.0083604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1341-16_0_4_line_122 |  | 121 | 122 | 0.0020123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1341-16_0_4_line_123 |  | 123 | 124 | 0.0027046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1341-16_0_4_trafo_64 | 0.63 MVA 20/0.4 kV | 125 | 86 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2704114.9369 | 1227956.9945 | 2704114.9369 | 1227956.9945 | 2704101.662 | 1227960.2312 | 2704094.5861 | 1227964.2915
1 | 2704096.0603 | 1227922.1717 | 2704098.0062 | 1227930.5119 | 2704106.8 | 1227935.1692 | 2704122.5508 | 1227939.4369 | 2704125.3875 | 1227946.2472 | 2704122.3049 | 1227953.4764 | 2704114.9369 | 1227956.9945
2 | 2704086.4151 | 1227989.9532 | 2704092.8803 | 1227965.2702 | 2704094.5861 | 1227964.2915
3 | 2704092.26 | 1227921.0488 | 2704096.0603 | 1227922.1717
4 | 2704096.0603 | 1227922.1717 | 2704108.5248 | 1227925.8369 | 2704110.4357 | 1227926.6282
5 | 2704086.4151 | 1227989.9532 | 2704089.6601 | 1227990.755 | 2704125.3333 | 1228007.5357
6 | 2704092.26 | 1227921.0488 | 2704094.1151 | 1227914.6654 | 2704096.3403 | 1227906.8662
7 | 2704092.26 | 1227921.0488 | 2704078.7892 | 1227917.4405
8 | 2704110.4357 | 1227926.6282 | 2704118.2928 | 1227929.8814
9 | 2704157.9468 | 1228024.8134 | 2704142.1834 | 1228015.4592 | 2704137.7331 | 1228013.3686 | 2704125.3333 | 1228007.5357
10 | 2704096.3403 | 1227906.8662 | 2704096.4826 | 1227906.3677
11 | 2704078.7892 | 1227917.4405 | 2704066.1437 | 1227914.0532
12 | 2704118.2928 | 1227929.8814 | 2704126.4239 | 1227933.2482
13 | 2704102.6891 | 1227873.0068 | 2704103.457 | 1227877.6347 | 2704103.3204 | 1227882.4025 | 2704096.4826 | 1227906.3677
14 | 2704055.8144 | 1227911.768 | 2704058.3274 | 1227911.9596 | 2704066.1437 | 1227914.0532
15 | 2704126.4239 | 1227933.2482 | 2704128.2095 | 1227933.9875 | 2704132.2113 | 1227936.1869
16 | 2704100.8262 | 1227832.7678 | 2704101.6208 | 1227831.435 | 2704116.0932 | 1227798.3526 | 2704118.4356 | 1227786.1643
17 | 2704075.9193 | 1227862.5862 | 2704089.3064 | 1227852.0904 | 2704100.8262 | 1227832.7678
18 | 2704075.9193 | 1227862.5862 | 2704074.9878 | 1227860.7735
19 | 2704082.9485 | 1227876.2638 | 2704075.9193 | 1227862.5862
20 | 2704065.5811 | 1227842.4674 | 2704074.9878 | 1227860.7735
21 | 2704082.9485 | 1227876.2638 | 2704102.6891 | 1227873.0068
22 | 2704082.9485 | 1227876.2638 | 2704071.2069 | 1227877.6261 | 2704056.8186 | 1227878.7342
23 | 2704065.5811 | 1227842.4674 | 2704061.1767 | 1227833.8963
24 | 2704102.6891 | 1227873.0068 | 2704130.7182 | 1227861.7222 | 2704152.9645 | 1227847.8347
25 | 2704056.8186 | 1227878.7342 | 2704041.8367 | 1227879.8881
26 | 2704047.9477 | 1227812.1262 | 2704056.195 | 1227824.2017 | 2704061.1767 | 1227833.8963
27 | 2704152.9645 | 1227847.8347 | 2704154.9484 | 1227850.9717 | 2704155.6325 | 1227855.1868 | 2704153.6561 | 1227863.7364 | 2704148.9517 | 1227879.1766 | 2704149.1581 | 1227880.5209
28 | 2704041.8367 | 1227879.8881 | 2704032.423 | 1227880.6132
29 | 2703864.1578 | 1228049.1711 | 2703857.4437 | 1228057.3793 | 2703855.5853 | 1228064.4077 | 2703857.5215 | 1228070.7128 | 2703865.3346 | 1228076.4034
30 | 2703861.6059 | 1227988.7678 | 2703864.1578 | 1228049.1711
31 | 2703861.6059 | 1227988.7678 | 2703853.1674 | 1227989.59
32 | 2703905.6221 | 1227955.9434 | 2703861.6059 | 1227988.7678
33 | 2703782.9436 | 1228048.1864 | 2703782.2219 | 1228040.0833
34 | 2703779.8022 | 1228012.9179 | 2703782.2219 | 1228040.0833
35 | 2703898.558 | 1227926.0516 | 2703903.7552 | 1227950.9647 | 2703905.6221 | 1227955.9434
36 | 2703895.6033 | 1227909.5694 | 2703896.531 | 1227916.3351 | 2703898.558 | 1227926.0516
37 | 2703853.1674 | 1227989.59 | 2703844.6737 | 1227990.4175
38 | 2704047.9477 | 1227812.1262 | 2704058.193 | 1227804.4553 | 2704068.0217 | 1227791.1396 | 2704079.6776 | 1227771.7291 | 2704079.1625 | 1227766.0825
39 | 2704047.9477 | 1227812.1262 | 2704033.8761 | 1227813.1395
40 | 2704047.9477 | 1227812.1262 | 2704036.2494 | 1227794.9867 | 2704022.6747 | 1227780.2496 | 2704013.33 | 1227772.3605
41 | 2704027.2835 | 1227813.6142 | 2704033.8761 | 1227813.1395
42 | 2704013.33 | 1227772.3605 | 2704007.221 | 1227767.2031 | 2703992.3126 | 1227759.1776
43 | 2704027.2835 | 1227813.6142 | 2704016.8694 | 1227814.3641
44 | 2703992.3126 | 1227759.1776 | 2703985.7008 | 1227755.6183 | 2703976.7575 | 1227751.5764
45 | 2704011.3057 | 1227814.7647 | 2704016.8694 | 1227814.3641
46 | 2703957.6699 | 1227739.8809 | 2703969.0137 | 1227748.0766 | 2703976.7575 | 1227751.5764
47 | 2704055.8144 | 1227911.768 | 2704043.5598 | 1227910.8338 | 2704042.1725 | 1227910.8246
48 | 2704042.1725 | 1227910.8246 | 2704037.9427 | 1227910.7967
49 | 2704018.2942 | 1227910.6671 | 2704037.9427 | 1227910.7967
50 | 2704016.2586 | 1227910.6537 | 2704018.2942 | 1227910.6671
51 | 2704016.2586 | 1227910.6537 | 2704008.9929 | 1227910.6058
52 | 2704008.9929 | 1227910.6058 | 2703999.6879 | 1227910.5444
53 | 2703999.6879 | 1227910.5444 | 2703990.3821 | 1227910.483
54 | 2703893.0069 | 1227890.7323 | 2703895.6033 | 1227909.5694
55 | 2703832.1055 | 1227991.6419 | 2703837.1107 | 1227991.1543
56 | 2703817.6543 | 1227993.0499 | 2703832.1055 | 1227991.6419
57 | 2703844.6737 | 1227990.4175 | 2703837.1107 | 1227991.1543
58 | 2703817.6543 | 1227993.0499 | 2703816.9897 | 1227993.1146
59 | 2703893.0069 | 1227890.7323 | 2703878.2395 | 1227891.3305
60 | 2703893.0069 | 1227890.7323 | 2703927.0559 | 1227888.4897
61 | 2703990.3821 | 1227910.483 | 2703980.9975 | 1227910.4211
62 | 2703980.9975 | 1227910.4211 | 2703971.6926 | 1227910.3597
63 | 2703955.6231 | 1227738.4022 | 2703957.6699 | 1227739.8809
64 | 2703955.6231 | 1227738.4022 | 2703953.4523 | 1227745.0803 | 2703940.2316 | 1227747.7958
65 | 2703925.9893 | 1227730.0788 | 2703940.2316 | 1227747.7958 | 2703940.2316 | 1227747.7958
66 | 2703940.2316 | 1227747.7958 | 2703907.0834 | 1227763.5729
67 | 2703913.0053 | 1227712.7053 | 2703919.0081 | 1227721.3943 | 2703925.9893 | 1227730.0788
68 | 2703907.0834 | 1227763.5729 | 2703889.5914 | 1227764.5989
69 | 2703931.6911 | 1227680.0631 | 2703924.7004 | 1227678.8956 | 2703918.9129 | 1227684.7767 | 2703918.0943 | 1227692.5793 | 2703917.881 | 1227703.9173 | 2703913.0053 | 1227712.7053
70 | 2703931.6911 | 1227680.0631 | 2703898.5271 | 1227632.9712 | 2703887.2856 | 1227606.6409
71 | 2703887.2856 | 1227606.6409 | 2703936.704 | 1227519.0537
72 | 2703848.534 | 1227572.3024 | 2703854.2734 | 1227573.2988 | 2703882.7623 | 1227596.0463 | 2703887.2856 | 1227606.6409
73 | 2703882.4316 | 1227732.0262 | 2703889.5914 | 1227764.5989
74 | 2703870.9551 | 1227765.692 | 2703889.5914 | 1227764.5989
75 | 2703936.704 | 1227519.0537 | 2703946.6996 | 1227524.9585
76 | 2703840.3159 | 1227570.8756 | 2703848.534 | 1227572.3024
77 | 2704032.423 | 1227880.6132 | 2704016.0163 | 1227881.8768
78 | 2704016.0163 | 1227881.8768 | 2704006.6027 | 1227882.6018
79 | 2704006.6027 | 1227882.6018 | 2703988.7523 | 1227883.9767
80 | 2703988.7523 | 1227883.9767 | 2703979.3379 | 1227884.7018
81 | 2703979.3379 | 1227884.7018 | 2703953.0902 | 1227886.7233 | 2703952.3514 | 1227886.7799
82 | 2703932.3156 | 1227888.1433 | 2703948.2405 | 1227887.0944 | 2703952.3514 | 1227886.7799
83 | 2703927.0559 | 1227888.4897 | 2703932.3156 | 1227888.1433
84 | 2704010.5355 | 1227814.8202 | 2704011.3057 | 1227814.7647
85 | 2704010.5355 | 1227814.8202 | 2704001.1182 | 1227815.4983
86 | 2704001.1182 | 1227815.4983 | 2703988.4831 | 1227816.4081
87 | 2703988.4831 | 1227816.4081 | 2703986.4817 | 1227816.5522
88 | 2703983.8952 | 1227816.7384 | 2703986.4817 | 1227816.5522
89 | 2703983.8952 | 1227816.7384 | 2703974.4779 | 1227817.4165
90 | 2703974.4779 | 1227817.4165 | 2703965.0968 | 1227818.092
91 | 2703965.0968 | 1227818.092 | 2703963.8831 | 1227818.1794
92 | 2703958.2965 | 1227818.5817 | 2703963.8831 | 1227818.1794
93 | 2703958.2965 | 1227818.5817 | 2703948.8813 | 1227819.2597
94 | 2703948.8813 | 1227819.2597 | 2703943.1015 | 1227819.6759
95 | 2703943.1015 | 1227819.6759 | 2703919.2694 | 1227821.3919
96 | 2703919.2694 | 1227821.3919 | 2703915.7292 | 1227821.6468
97 | 2703911.1561 | 1227821.9761 | 2703915.7292 | 1227821.6468
98 | 2703878.2395 | 1227891.3305 | 2703873.0234 | 1227868.4224 | 2703867.8181 | 1227860.4422
99 | 2703878.2395 | 1227891.3305 | 2703870.6861 | 1227892.5139
100 | 2703822.8696 | 1227835.5594 | 2703830.2999 | 1227835.7969 | 2703848.9328 | 1227839.5472 | 2703861.0504 | 1227850.0665 | 2703867.8181 | 1227860.4422
101 | 2703870.6861 | 1227892.5139 | 2703866.6188 | 1227893.1512 | 2703840.8569 | 1227901.2484
102 | 2703821.5329 | 1227835.5167 | 2703822.8696 | 1227835.5594
103 | 2703834.4361 | 1227903.2665 | 2703840.8569 | 1227901.2484
104 | 2703853.1919 | 1227734.895 | 2703882.4316 | 1227732.0262
105 | 2704154.4087 | 1227948.3866 | 2704161.1384 | 1227952.0852
106 | 2704154.4087 | 1227948.3866 | 2704146.6873 | 1227944.1429
107 | 2704139.7835 | 1227940.3485 | 2704146.6873 | 1227944.1429
108 | 2704132.2113 | 1227936.1869 | 2704139.7835 | 1227940.3485
109 | 2703981.3196 | 1227546.4948 | 2703975.6335 | 1227542.0509 | 2703961.0559 | 1227533.4393
110 | 2703961.0559 | 1227533.4393 | 2703946.6996 | 1227524.9585
111 | 2703961.0559 | 1227533.4393 | 2704040.0395 | 1227419.0949
112 | 2704040.0395 | 1227419.0949 | 2704071.4546 | 1227216.8747
113 | 2704040.0395 | 1227419.0949 | 2704044.8765 | 1227419.8153 | 2704049.9955 | 1227422.9786
114 | 2704065.5433 | 1227432.5862 | 2704049.9955 | 1227422.9786
115 | 2704071.4546 | 1227216.8747 | 2704045.0893 | 1227082.7808
116 | 2703778.3734 | 1227996.8769 | 2703779.8022 | 1228012.9179
117 | 2703794.7971 | 1227915.7255 | 2703788.4745 | 1227890.2635
118 | 2703794.7971 | 1227915.7255 | 2703802.5662 | 1227913.2836
119 | 2703832.5163 | 1227903.8699 | 2703802.5662 | 1227913.2836
120 | 2703778.3734 | 1227996.8769 | 2703808.6687 | 1227993.9253
121 | 2703816.9897 | 1227993.1146 | 2703808.6687 | 1227993.9253
122 | 2703832.5163 | 1227903.8699 | 2703834.4361 | 1227903.2665
123 | 2703837.6786 | 1227571.4752 | 2703840.3159 | 1227570.8756 | 2703840.3159 | 1227570.8756

## bus_geodata
| x | y | coords
0 | 2704114.9369 | 1227956.9945
1 | 2704094.5861 | 1227964.2915
2 | 2704096.0603 | 1227922.1717
3 | 2704086.4151 | 1227989.9532
4 | 2704092.26 | 1227921.0488
5 | 2704110.4357 | 1227926.6282
6 | 2704125.3333 | 1228007.5357
7 | 2704096.3403 | 1227906.8662
8 | 2704078.7892 | 1227917.4405
9 | 2704118.2928 | 1227929.8814
10 | 2704157.9468 | 1228024.8134
11 | 2704096.4826 | 1227906.3677
12 | 2704066.1437 | 1227914.0532
13 | 2704126.4239 | 1227933.2482
14 | 2704100.8262 | 1227832.7678
15 | 2704118.4356 | 1227786.1643
16 | 2704075.9193 | 1227862.5862
17 | 2704074.9878 | 1227860.7735
18 | 2704082.9485 | 1227876.2638
19 | 2704065.581 | 1227842.4674
20 | 2704102.6891 | 1227873.0068
21 | 2704056.8186 | 1227878.7342
22 | 2704061.1767 | 1227833.8963
23 | 2704152.9645 | 1227847.8347
24 | 2704041.8367 | 1227879.8881
25 | 2703865.3346 | 1228076.4034
26 | 2703864.1578 | 1228049.1711
27 | 2703861.6059 | 1227988.7678
28 | 2703782.9436 | 1228048.1864
29 | 2703782.2219 | 1228040.0833
30 | 2703905.6221 | 1227955.9434
31 | 2703898.558 | 1227926.0516
32 | 2703853.1674 | 1227989.59
33 | 2704079.1625 | 1227766.0825
34 | 2704047.9477 | 1227812.1262
35 | 2704033.8761 | 1227813.1395
36 | 2704013.33 | 1227772.3605
37 | 2704027.2835 | 1227813.6142
38 | 2703992.3126 | 1227759.1776
39 | 2704016.8694 | 1227814.3641
40 | 2703976.7575 | 1227751.5764
41 | 2704055.8144 | 1227911.768
42 | 2704042.1725 | 1227910.8246
43 | 2704037.9427 | 1227910.7967
44 | 2704018.2942 | 1227910.6671
45 | 2704016.2586 | 1227910.6537
46 | 2704008.9929 | 1227910.6058
47 | 2703999.6879 | 1227910.5444
48 | 2703895.6033 | 1227909.5694
49 | 2703832.1055 | 1227991.6419
50 | 2703837.1107 | 1227991.1543
51 | 2703817.6543 | 1227993.0499
52 | 2703844.6737 | 1227990.4175
53 | 2703893.0069 | 1227890.7323
54 | 2703990.382 | 1227910.483
55 | 2703980.9975 | 1227910.4211
56 | 2703957.6699 | 1227739.8809
57 | 2703955.6231 | 1227738.4022
58 | 2703940.2316 | 1227747.7958
59 | 2703925.9893 | 1227730.0788
60 | 2703907.0834 | 1227763.5729
61 | 2703931.6911 | 1227680.0631
62 | 2703913.0053 | 1227712.7053
63 | 2703887.2856 | 1227606.6409
64 | 2703889.5914 | 1227764.5989
65 | 2703936.704 | 1227519.0537
66 | 2703848.534 | 1227572.3024
67 | 2704149.1581 | 1227880.5209
68 | 2704032.423 | 1227880.6132
69 | 2704016.0163 | 1227881.8768
70 | 2704006.6027 | 1227882.6018
71 | 2703988.7523 | 1227883.9767
72 | 2703979.3379 | 1227884.7018
73 | 2703952.3514 | 1227886.7799
74 | 2703932.3156 | 1227888.1433
75 | 2704011.3057 | 1227814.7647
76 | 2704010.5355 | 1227814.8202
77 | 2704001.1182 | 1227815.4983
78 | 2703988.4831 | 1227816.4081
79 | 2703986.4817 | 1227816.5522
80 | 2703983.8952 | 1227816.7384
81 | 2703974.4779 | 1227817.4165
82 | 2703927.0559 | 1227888.4897
83 | 2703965.0968 | 1227818.092
84 | 2703963.8831 | 1227818.1794
85 | 2703958.2965 | 1227818.5817
86 | 2703948.8813 | 1227819.2597
87 | 2703943.1015 | 1227819.6759
88 | 2703919.2694 | 1227821.3919
89 | 2703915.7292 | 1227821.6468
90 | 2703911.1561 | 1227821.9761
91 | 2703878.2395 | 1227891.3305
92 | 2703867.8181 | 1227860.4422
93 | 2703870.6861 | 1227892.5139
94 | 2703822.8696 | 1227835.5594
95 | 2703840.8569 | 1227901.2484
96 | 2703971.6926 | 1227910.3597
97 | 2703882.4316 | 1227732.0262
98 | 2703853.1919 | 1227734.895
99 | 2703870.9551 | 1227765.692
100 | 2703821.5329 | 1227835.5167
101 | 2704154.4087 | 1227948.3866
102 | 2704161.1384 | 1227952.0852
103 | 2704146.6873 | 1227944.1429
104 | 2704139.7835 | 1227940.3485
105 | 2704132.2113 | 1227936.1869
106 | 2703981.3196 | 1227546.4948
107 | 2703961.0559 | 1227533.4393
108 | 2703946.6996 | 1227524.9585
109 | 2704040.0395 | 1227419.0949
110 | 2704049.9955 | 1227422.9786
111 | 2704065.5433 | 1227432.5862
112 | 2704071.4546 | 1227216.8747
113 | 2704045.0893 | 1227082.7808
114 | 2703779.8022 | 1228012.9179
115 | 2703794.797 | 1227915.7255
116 | 2703788.4745 | 1227890.2635
117 | 2703802.5662 | 1227913.2836
118 | 2703778.3734 | 1227996.8769
119 | 2703808.6687 | 1227993.9253
120 | 2703816.9897 | 1227993.1146
121 | 2703834.4361 | 1227903.2665
122 | 2703832.5163 | 1227903.8699
123 | 2703837.6786 | 1227571.4752
124 | 2703840.3159 | 1227570.8756
125 | 2703911.1561 | 1227821.9761

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97912 | -0.4004 | 0.0096916 | 0.0024289
1 | 0.97898 | -0.40324 | 0.00089676 | 0.00022475
2 | 0.98003 | -0.3826 | 0 | 0
3 | 0.97882 | -0.40636 | 0 | 0
4 | 0.98013 | -0.38054 | 0 | 0
5 | 0.97987 | -0.38583 | 0.0014445 | 0.00036202
6 | 0.97857 | -0.41122 | 0.0027156 | 0.0006806
7 | 0.98086 | -0.36637 | 0.0014457 | 0.00036232
8 | 0.97982 | -0.38669 | 0.00095966 | 0.00024051
9 | 0.97978 | -0.38743 | 0.0011955 | 0.00029963
10 | 0.97845 | -0.41359 | 0.0035254 | 0.00088355
11 | 0.98088 | -0.36586 | 0.00037524 | 9.4043e-05
12 | 0.97954 | -0.39225 | 0.0040599 | 0.0010175
13 | 0.97971 | -0.38889 | 0.001543 | 0.00038672
14 | 0.98447 | -0.29614 | 0.005117 | 0.0012824
15 | 0.98391 | -0.30707 | 0.012126 | 0.0030391
16 | 0.9851 | -0.2839 | 0 | 0
17 | 0.98525 | -0.28092 | 0.0021628 | 0.00054205
18 | 0.98401 | -0.3048 | 0 | 0
19 | 0.98682 | -0.25062 | 0.0021612 | 0.00054165
20 | 0.98263 | -0.33179 | 0 | 0
21 | 0.98278 | -0.32875 | 0.0021638 | 0.00054229
22 | 0.98756 | -0.23635 | 0.0021604 | 0.00054146
23 | 0.98157 | -0.35241 | 0 | 0
24 | 0.98208 | -0.34229 | 0.0021628 | 0.00054205
25 | 0.97045 | -0.57017 | 0.001985 | 0.00049749
26 | 0.97051 | -0.56892 | 0.0092253 | 0.0023121
27 | 0.97115 | -0.55638 | 0.0077024 | 0.0019304
28 | 0.97014 | -0.57626 | 0.0018992 | 0.00047599
29 | 0.97016 | -0.57597 | 0.0017718 | 0.00044405
30 | 0.97313 | -0.51717 | 0.0067976 | 0.0017036
31 | 0.97444 | -0.49142 | 0.0060901 | 0.0015263
32 | 0.97099 | -0.55949 | 0.0022172 | 0.00055567
33 | 0.98943 | -0.20054 | 0.0021716 | 0.00054426
34 | 0.98954 | -0.19831 | 0 | 0
35 | 0.99097 | -0.1711 | 0.0022613 | 0.00056673
36 | 0.98597 | -0.2672 | 0.0026286 | 0.00065878
37 | 0.99164 | -0.15829 | 0.0021615 | 0.00054173
38 | 0.98436 | -0.29858 | 0.0042845 | 0.0010738
39 | 0.9927 | -0.13796 | 0.0042731 | 0.0010709
40 | 0.9833 | -0.31911 | 0.0028603 | 0.00071687
41 | 0.97935 | -0.39597 | 0.0012096 | 0.00030316
42 | 0.97912 | -0.40046 | 0.0056697 | 0.001421
43 | 0.97907 | -0.40142 | 0.00060056 | 0.00015051
44 | 0.97886 | -0.40564 | 0.00026239 | 6.5762e-05
45 | 0.97883 | -0.40607 | 0.0066734 | 0.0016725
46 | 0.9788 | -0.40671 | 0.00026223 | 6.5721e-05
47 | 0.97876 | -0.40749 | 0.00026216 | 6.5703e-05
48 | 0.97525 | -0.47556 | 0 | 0
49 | 0.97068 | -0.56564 | 0.0014993 | 0.00037577
50 | 0.97074 | -0.56442 | 0.0022572 | 0.0005657
51 | 0.97052 | -0.56875 | 0.0012574 | 0.00031513
52 | 0.97085 | -0.56226 | 0.0022581 | 0.00056592
53 | 0.9757 | -0.46657 | 0 | 0
54 | 0.97872 | -0.40823 | 0.0014497 | 0.00036332
55 | 0.9787 | -0.40873 | 0.0014516 | 0.00036381
56 | 0.98199 | -0.34467 | 0.0041373 | 0.0010369
57 | 0.98185 | -0.34735 | 0 | 0
58 | 0.98073 | -0.3692 | 0.0057782 | 0.0014481
59 | 0.97999 | -0.38369 | 0.011627 | 0.0029141
60 | 0.98013 | -0.38111 | 0.00603 | 0.0015113
61 | 0.97855 | -0.412 | 0 | 0
62 | 0.97952 | -0.39295 | 0 | 0
63 | 0.97666 | -0.44898 | 0.0067646 | 0.0016954
64 | 0.97993 | -0.38488 | 0.0013226 | 0.00033148
65 | 0.97567 | -0.46853 | 0 | 0
66 | 0.97636 | -0.45499 | 0.0040745 | 0.0010212
67 | 0.98093 | -0.36497 | 0.020259 | 0.0050773
68 | 0.98164 | -0.35069 | 0.0021636 | 0.00054225
69 | 0.9809 | -0.36512 | 0.0021638 | 0.00054229
70 | 0.98048 | -0.37329 | 0.0021628 | 0.00054205
71 | 0.9797 | -0.38856 | 0.0017874 | 0.00044796
72 | 0.97929 | -0.39652 | 0.0017863 | 0.00044769
73 | 0.97813 | -0.41909 | 0.0034594 | 0.00086702
74 | 0.97729 | -0.43544 | 0.0034294 | 0.00085949
75 | 0.99328 | -0.12697 | 0.0022597 | 0.00056634
76 | 0.99336 | -0.12544 | 0.0021636 | 0.00054225
77 | 0.99435 | -0.10663 | 0.0021628 | 0.00054206
78 | 0.99569 | -0.081295 | 0.0018651 | 0.00046744
79 | 0.9959 | -0.077265 | 0.0033738 | 0.00084554
80 | 0.99618 | -0.07201 | 0.0017854 | 0.00044747
81 | 0.9972 | -0.0528 | 0.0017848 | 0.0004473
82 | 0.97708 | -0.43963 | 0.0010197 | 0.00025556
83 | 0.99821 | -0.033606 | 0.0018656 | 0.00046757
84 | 0.99835 | -0.031112 | 0.0028037 | 0.00070268
85 | 0.99896 | -0.01955 | 0.0017848 | 0.0004473
86 | 1 | 0 | -0.38194 | -0.098043
87 | 0.99991 | -0.0017323 | 0.0018681 | 0.00046818
88 | 0.99958 | -0.0080996 | 0.003505 | 0.00087844
89 | 0.99954 | -0.0088287 | 0.0073037 | 0.0018305
90 | 0.99952 | -0.0091864 | 0.004472 | 0.0011208
91 | 0.97463 | -0.48762 | 0 | 0
92 | 0.97338 | -0.51238 | 0.013282 | 0.0033288
93 | 0.97437 | -0.49282 | 0.0057311 | 0.0014364
94 | 0.97197 | -0.54022 | 0.014262 | 0.0035745
95 | 0.97346 | -0.51077 | 0.0059932 | 0.001502
96 | 0.97869 | -0.40897 | 0.0014507 | 0.00036359
97 | 0.97967 | -0.39007 | 0.0045483 | 0.0011399
98 | 0.97956 | -0.39222 | 0.0040231 | 0.0010083
99 | 0.9799 | -0.38555 | 0.0019657 | 0.00049265
100 | 0.97195 | -0.54055 | 0.013274 | 0.0033267
101 | 0.97956 | -0.39188 | 0.0014533 | 0.00036422
102 | 0.97955 | -0.39209 | 0.0015011 | 0.00037621
103 | 0.97958 | -0.3914 | 0.0015686 | 0.00039314
104 | 0.97961 | -0.39076 | 0.0016079 | 0.00040297
105 | 0.97966 | -0.38979 | 0.001501 | 0.00037619
106 | 0.9754 | -0.47398 | 0.00097084 | 0.00024332
107 | 0.97542 | -0.47355 | 0.0015608 | 0.00039117
108 | 0.97556 | -0.47079 | 0.0015904 | 0.0003986
109 | 0.97458 | -0.49011 | 0.00073617 | 0.0001845
110 | 0.97455 | -0.49068 | 0.00083288 | 0.00020874
111 | 0.97452 | -0.49136 | 0.0020157 | 0.00050518
112 | 0.97403 | -0.50105 | 0.0011593 | 0.00029054
113 | 0.9738 | -0.50543 | 0.0017437 | 0.00043701
114 | 0.97025 | -0.57412 | 0.0010637 | 0.00026659
115 | 0.9727 | -0.52569 | 0 | 0
116 | 0.97245 | -0.53078 | 0.010534 | 0.00264
117 | 0.97278 | -0.52411 | 0.0058534 | 0.001467
118 | 0.97032 | -0.57271 | 0 | 0
119 | 0.97046 | -0.57004 | 0.0027911 | 0.00069952
120 | 0.97052 | -0.56887 | 0.0027911 | 0.00069952
121 | 0.9733 | -0.51391 | 0.0057187 | 0.0014332
122 | 0.97326 | -0.51464 | 0.0032738 | 0.0008205
123 | 0.97634 | -0.45537 | 0.0014298 | 0.00035833
124 | 0.97634 | -0.4553 | 0.00061012 | 0.00015291
125 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0071415 | 0.0017897 | -0.0071406 | -0.0017893 | 9.6393e-07 | 3.425e-07 | 0.010853 | 0.010853 | 0.010853 | 0.97912 | -0.4004 | 0.97898 | -0.40324 | 2.9817
1 | -0.016833 | -0.0042186 | 0.016847 | 0.004227 | 1.4292e-05 | 8.4135e-06 | 0.025582 | 0.025582 | 0.025582 | 0.97912 | -0.4004 | 0.98003 | -0.3826 | 7.028
2 | 0.0062438 | 0.0015646 | -0.0062429 | -0.0015643 | 9.2821e-07 | 2.4856e-07 | 0.0094903 | 0.0094904 | 0.0094904 | 0.97898 | -0.40324 | 0.97882 | -0.40636 | 2.6073
3 | -0.028666 | -0.0071898 | 0.028669 | 0.0071916 | 2.8078e-06 | 1.7472e-06 | 0.043527 | 0.043527 | 0.043527 | 0.98003 | -0.3826 | 0.98013 | -0.38054 | 11.958
4 | 0.011819 | 0.0029628 | -0.011817 | -0.0029618 | 1.8188e-06 | 9.7428e-07 | 0.017945 | 0.017946 | 0.017946 | 0.98003 | -0.3826 | 0.97987 | -0.38583 | 4.9301
5 | 0.0062429 | 0.0015643 | -0.0062414 | -0.0015639 | 1.4445e-06 | 3.8705e-07 | 0.0094904 | 0.0094906 | 0.0094906 | 0.97882 | -0.40636 | 0.97857 | -0.41122 | 2.6073
6 | -0.053005 | -0.013299 | 0.053041 | 0.013321 | 3.5842e-05 | 2.2753e-05 | 0.080476 | 0.080476 | 0.080476 | 0.98013 | -0.38054 | 0.98086 | -0.36637 | 22.1089
7 | 0.024336 | 0.0061071 | -0.024329 | -0.0061027 | 7.1398e-06 | 4.3937e-06 | 0.036949 | 0.036949 | 0.036949 | 0.98013 | -0.38054 | 0.97982 | -0.38669 | 10.1509
8 | 0.010373 | 0.0025998 | -0.010372 | -0.0025994 | 7.9127e-07 | 3.993e-07 | 0.015752 | 0.015752 | 0.015752 | 0.97987 | -0.38583 | 0.97978 | -0.38743 | 4.3275
9 | 0.0035258 | 0.00088334 | -0.0035254 | -0.00088355 | 3.9828e-07 | -2.0925e-07 | 0.0053612 | 0.0053614 | 0.0053614 | 0.97857 | -0.41122 | 0.97845 | -0.41359 | 1.4729
10 | -0.054487 | -0.013684 | 0.054488 | 0.013685 | 1.3285e-06 | 8.4372e-07 | 0.082669 | 0.082669 | 0.082669 | 0.98086 | -0.36637 | 0.98088 | -0.36586 | 22.7114
11 | 0.023369 | 0.0058622 | -0.023363 | -0.0058584 | 6.184e-06 | 3.7929e-06 | 0.035492 | 0.035492 | 0.035492 | 0.97982 | -0.38669 | 0.97954 | -0.39225 | 9.7505
12 | 0.0091763 | 0.0022998 | -0.0091757 | -0.0022995 | 6.4097e-07 | 2.9939e-07 | 0.013936 | 0.013936 | 0.013936 | 0.97978 | -0.38743 | 0.97971 | -0.38889 | 3.8287
13 | -0.054863 | -0.013779 | 0.054953 | 0.013835 | 8.9335e-05 | 5.6739e-05 | 0.083239 | 0.083239 | 0.083239 | 0.98088 | -0.36586 | 0.98263 | -0.33179 | 22.8678
14 | 0.019303 | 0.0048409 | -0.0193 | -0.0048389 | 3.4221e-06 | 2.0566e-06 | 0.029325 | 0.029325 | 0.029325 | 0.97954 | -0.39225 | 0.97935 | -0.39597 | 8.0562
15 | 0.0076327 | 0.0019128 | -0.0076323 | -0.0019126 | 3.2752e-07 | 1.2778e-07 | 0.011593 | 0.011593 | 0.011593 | 0.97971 | -0.38889 | 0.97966 | -0.38979 | 3.1848
16 | 0.012132 | 0.0030425 | -0.012126 | -0.0030391 | 6.3149e-06 | 3.4052e-06 | 0.018338 | 0.018339 | 0.018339 | 0.98447 | -0.29614 | 0.98391 | -0.30707 | 5.0381
17 | -0.017249 | -0.0043249 | 0.017259 | 0.0043308 | 1.0071e-05 | 5.9429e-06 | 0.026073 | 0.026073 | 0.026073 | 0.98447 | -0.29614 | 0.9851 | -0.2839 | 7.1629
18 | -0.24618 | -0.062483 | 0.24622 | 0.062506 | 3.5282e-05 | 2.2503e-05 | 0.37214 | 0.37214 | 0.37214 | 0.9851 | -0.2839 | 0.98525 | -0.28092 | 34.0791
19 | 0.22892 | 0.058153 | -0.22869 | -0.058006 | 0.0002301 | 0.00014668 | 0.34607 | 0.34607 | 0.34607 | 0.9851 | -0.2839 | 0.98401 | -0.3048 | 31.6916
20 | -0.24838 | -0.063048 | 0.24874 | 0.063279 | 0.00036258 | 0.00023126 | 0.37541 | 0.37541 | 0.37541 | 0.98525 | -0.28092 | 0.98682 | -0.25062 | 34.3783
21 | 0.07534 | 0.018994 | -0.075243 | -0.018932 | 9.7178e-05 | 6.1941e-05 | 0.11397 | 0.11397 | 0.11397 | 0.98401 | -0.3048 | 0.98263 | -0.33179 | 31.3102
22 | 0.15335 | 0.039012 | -0.15317 | -0.0389 | 0.00017678 | 0.00011214 | 0.2321 | 0.2321 | 0.2321 | 0.98401 | -0.3048 | 0.98278 | -0.32875 | 21.2549
23 | -0.2509 | -0.063821 | 0.25108 | 0.063931 | 0.00017272 | 0.00011017 | 0.37867 | 0.37867 | 0.37867 | 0.98682 | -0.25062 | 0.98756 | -0.23635 | 34.6767
24 | 0.020291 | 0.0050967 | -0.020271 | -0.0050846 | 1.9943e-05 | 1.2051e-05 | 0.030731 | 0.030731 | 0.030731 | 0.98263 | -0.33179 | 0.98157 | -0.35241 | 8.4426
25 | 0.15101 | 0.038357 | -0.15091 | -0.038295 | 9.8351e-05 | 6.2374e-05 | 0.22883 | 0.22883 | 0.22883 | 0.98278 | -0.32875 | 0.98208 | -0.34229 | 20.9549
26 | -0.25324 | -0.064473 | 0.2537 | 0.064769 | 0.00046536 | 0.00029685 | 0.38192 | 0.38192 | 0.38192 | 0.98756 | -0.23635 | 0.98954 | -0.19831 | 34.9748
27 | 0.020271 | 0.0050846 | -0.020259 | -0.0050773 | 1.2132e-05 | 7.332e-06 | 0.030731 | 0.030731 | 0.030731 | 0.98157 | -0.35241 | 0.98093 | -0.36497 | 8.4426
28 | 0.14875 | 0.037753 | -0.14869 | -0.037715 | 6.004e-05 | 3.8067e-05 | 0.22555 | 0.22555 | 0.22555 | 0.98208 | -0.34229 | 0.98164 | -0.35069 | 20.6548
29 | -0.001985 | -0.00049749 | 0.0019851 | 0.00049714 | 1.1858e-07 | -3.459e-07 | 0.0030437 | 0.0030435 | 0.0030437 | 0.97045 | -0.57017 | 0.97051 | -0.56892 | 0.83617
30 | -0.01121 | -0.0028092 | 0.011217 | 0.0028128 | 6.6976e-06 | 3.5389e-06 | 0.017188 | 0.017188 | 0.017188 | 0.97051 | -0.56892 | 0.97115 | -0.55638 | 4.722
31 | 0.019817 | 0.0049693 | -0.019814 | -0.0049675 | 2.9316e-06 | 1.7713e-06 | 0.030365 | 0.030365 | 0.030365 | 0.97115 | -0.55638 | 0.97099 | -0.55949 | 8.3421
32 | -0.038737 | -0.0097124 | 0.038809 | 0.0097582 | 7.254e-05 | 4.5745e-05 | 0.059355 | 0.059355 | 0.059355 | 0.97115 | -0.55638 | 0.97313 | -0.51717 | 16.3063
33 | -0.0018992 | -0.00047599 | 0.0018993 | 0.00047591 | 2.5888e-08 | -8.3884e-08 | 0.0029131 | 0.002913 | 0.0029131 | 0.97014 | -0.57626 | 0.97016 | -0.57597 | 0.80029
34 | -0.003671 | -0.00091996 | 0.0036714 | 0.00091983 | 3.2423e-07 | -1.2929e-07 | 0.0056306 | 0.0056304 | 0.0056306 | 0.97016 | -0.57597 | 0.97025 | -0.57412 | 1.5469
35 | -0.045607 | -0.011462 | 0.045663 | 0.011497 | 5.6129e-05 | 3.554e-05 | 0.069749 | 0.069749 | 0.069749 | 0.97313 | -0.51717 | 0.97444 | -0.49142 | 19.1618
36 | -0.051753 | -0.013024 | 0.051792 | 0.013049 | 3.926e-05 | 2.4918e-05 | 0.079048 | 0.079048 | 0.079048 | 0.97444 | -0.49142 | 0.97525 | -0.47556 | 21.7166
37 | 0.017597 | 0.0044118 | -0.017595 | -0.0044105 | 2.3274e-06 | 1.384e-06 | 0.026968 | 0.026968 | 0.026968 | 0.97099 | -0.55949 | 0.97085 | -0.56226 | 7.4087
38 | -0.0021716 | -0.00054426 | 0.0021718 | 0.00054367 | 2.3061e-07 | -5.9305e-07 | 0.0032659 | 0.0032657 | 0.0032659 | 0.98943 | -0.20054 | 0.98954 | -0.19831 | 0.89723
39 | -0.32926 | -0.083961 | 0.32969 | 0.084238 | 0.00043322 | 0.00027671 | 0.49564 | 0.49564 | 0.49564 | 0.98954 | -0.19831 | 0.99097 | -0.1711 | 45.3881
40 | 0.073388 | 0.018648 | -0.073146 | -0.018494 | 0.00024253 | 0.00015454 | 0.11045 | 0.11045 | 0.11045 | 0.98954 | -0.19831 | 0.98597 | -0.2672 | 30.3429
41 | -0.33196 | -0.084805 | 0.33216 | 0.084936 | 0.00020575 | 0.00013143 | 0.49903 | 0.49903 | 0.49903 | 0.99097 | -0.1711 | 0.99164 | -0.15829 | 45.699
42 | 0.070517 | 0.017835 | -0.070411 | -0.017767 | 0.00010598 | 6.7512e-05 | 0.10648 | 0.10648 | 0.10648 | 0.98597 | -0.2672 | 0.98436 | -0.29858 | 29.2531
43 | -0.33432 | -0.085478 | 0.33465 | 0.085688 | 0.00032926 | 0.00021032 | 0.50228 | 0.50228 | 0.50228 | 0.99164 | -0.15829 | 0.9927 | -0.13796 | 45.996
44 | 0.066127 | 0.016694 | -0.066062 | -0.016652 | 6.4968e-05 | 4.136e-05 | 0.1 | 0.1 | 0.1 | 0.98436 | -0.29858 | 0.9833 | -0.31911 | 27.4738
45 | -0.33893 | -0.086759 | 0.33911 | 0.086874 | 0.00018042 | 0.00011525 | 0.50868 | 0.50868 | 0.50868 | 0.9927 | -0.13796 | 0.99328 | -0.12697 | 46.5825
46 | 0.063201 | 0.015935 | -0.063124 | -0.015886 | 7.7211e-05 | 4.913e-05 | 0.095676 | 0.095676 | 0.095676 | 0.9833 | -0.31911 | 0.98199 | -0.34467 | 26.2847
47 | 0.01809 | 0.0045357 | -0.018086 | -0.0045334 | 3.8751e-06 | 2.308e-06 | 0.027487 | 0.027487 | 0.027487 | 0.97935 | -0.39597 | 0.97912 | -0.40046 | 7.5513
48 | 0.012417 | 0.0031124 | -0.012416 | -0.0031121 | 5.6482e-07 | 3.0829e-07 | 0.01887 | 0.01887 | 0.01887 | 0.97912 | -0.40046 | 0.97907 | -0.40142 | 5.1841
49 | 0.011815 | 0.0029616 | -0.011813 | -0.0029603 | 2.3761e-06 | 1.2737e-06 | 0.017957 | 0.017958 | 0.017958 | 0.97907 | -0.40142 | 0.97886 | -0.40564 | 4.9334
50 | 0.011551 | 0.0028946 | -0.01155 | -0.0028945 | 2.3535e-07 | 1.2504e-07 | 0.017559 | 0.017559 | 0.017559 | 0.97886 | -0.40564 | 0.97883 | -0.40607 | 4.8238
51 | 0.004877 | 0.0012219 | -0.0048768 | -0.0012219 | 1.4976e-07 | 4.5217e-09 | 0.0074138 | 0.0074139 | 0.0074139 | 0.97883 | -0.40607 | 0.9788 | -0.40671 | 2.0368
52 | 0.0046146 | 0.0011562 | -0.0046144 | -0.0011562 | 1.7173e-07 | -7.0454e-09 | 0.0070152 | 0.0070153 | 0.0070153 | 0.9788 | -0.40671 | 0.97876 | -0.40749 | 1.9273
53 | 0.0043523 | 0.0010905 | -0.0043521 | -0.0010905 | 1.5279e-07 | -1.917e-08 | 0.0066167 | 0.0066168 | 0.0066168 | 0.97876 | -0.40749 | 0.97872 | -0.40823 | 1.8178
54 | -0.051792 | -0.013049 | 0.051815 | 0.013062 | 2.2281e-05 | 1.3785e-05 | 0.079048 | 0.079048 | 0.079048 | 0.97525 | -0.47556 | 0.9757 | -0.46657 | 10.8583
55 | -0.013077 | -0.0032775 | 0.013078 | 0.0032779 | 7.5787e-07 | 4.2287e-07 | 0.020047 | 0.020047 | 0.020047 | 0.97068 | -0.56564 | 0.97074 | -0.56442 | 5.5074
56 | 0.011578 | 0.0029017 | -0.011576 | -0.0029008 | 1.7152e-06 | 9.1826e-07 | 0.017748 | 0.017748 | 0.017748 | 0.97068 | -0.56564 | 0.97052 | -0.56875 | 4.876
57 | -0.015335 | -0.0038436 | 0.015337 | 0.0038445 | 1.5746e-06 | 9.1377e-07 | 0.023507 | 0.023507 | 0.023507 | 0.97074 | -0.56442 | 0.97085 | -0.56226 | 6.4579
58 | 0.010319 | 0.0025857 | -0.010319 | -0.0025856 | 6.2668e-08 | 3.1857e-08 | 0.015821 | 0.015821 | 0.015821 | 0.97052 | -0.56875 | 0.97052 | -0.56887 | 4.3463
59 | 0.078137 | 0.019664 | -0.078059 | -0.019614 | 7.8508e-05 | 5.0062e-05 | 0.11919 | 0.11919 | 0.11919 | 0.9757 | -0.46657 | 0.97463 | -0.48762 | 32.7455
60 | -0.12995 | -0.032726 | 0.13012 | 0.032832 | 0.00016763 | 0.000106 | 0.19824 | 0.19824 | 0.19824 | 0.9757 | -0.46657 | 0.97708 | -0.43963 | 18.154
61 | 0.0029025 | 0.00072722 | -0.0029024 | -0.0007273 | 6.8528e-08 | -7.4077e-08 | 0.0044127 | 0.0044128 | 0.0044128 | 0.97872 | -0.40823 | 0.9787 | -0.40873 | 1.2123
62 | 0.0014508 | 0.00036348 | -0.0014507 | -0.00036359 | 1.6977e-08 | -1.0606e-07 | 0.0022057 | 0.0022057 | 0.0022057 | 0.9787 | -0.40873 | 0.97869 | -0.40897 | 0.60597
63 | 0.058987 | 0.014849 | -0.058979 | -0.014844 | 7.5693e-06 | 4.8124e-06 | 0.089407 | 0.089407 | 0.089407 | 0.98199 | -0.34467 | 0.98185 | -0.34735 | 24.5624
64 | 0.058979 | 0.014844 | -0.058918 | -0.014805 | 6.1507e-05 | 3.9105e-05 | 0.089407 | 0.089407 | 0.089407 | 0.98185 | -0.34735 | 0.98073 | -0.3692 | 24.5624
65 | 0.035235 | 0.0088657 | -0.035211 | -0.0088504 | 2.4374e-05 | 1.5313e-05 | 0.053473 | 0.053473 | 0.053473 | 0.98073 | -0.3692 | 0.97999 | -0.38369 | 14.6904
66 | 0.017905 | 0.0044914 | -0.017895 | -0.0044854 | 1.0161e-05 | 6.0399e-06 | 0.027167 | 0.027168 | 0.027168 | 0.98073 | -0.3692 | 0.98013 | -0.38111 | 7.4636
67 | 0.023583 | 0.0059363 | -0.023573 | -0.0059299 | 1.0441e-05 | 6.4092e-06 | 0.035818 | 0.035818 | 0.035818 | 0.97999 | -0.38369 | 0.97952 | -0.39295 | 9.8401
68 | 0.011864 | 0.0029741 | -0.011862 | -0.002973 | 2.132e-06 | 1.1437e-06 | 0.018013 | 0.018013 | 0.018013 | 0.98013 | -0.38111 | 0.97993 | -0.38488 | 4.9486
69 | -0.023551 | -0.0059168 | 0.023573 | 0.0059299 | 2.1429e-05 | 1.3154e-05 | 0.035818 | 0.035818 | 0.035818 | 0.97855 | -0.412 | 0.97952 | -0.39295 | 9.8402
70 | 0.023551 | 0.0059168 | -0.02351 | -0.0058913 | 4.1485e-05 | 2.5469e-05 | 0.035818 | 0.035819 | 0.035819 | 0.97855 | -0.412 | 0.97666 | -0.44898 | 9.8403
71 | 0.010629 | 0.0026632 | -0.010619 | -0.0026581 | 9.8902e-06 | 5.0725e-06 | 0.016194 | 0.016194 | 0.016194 | 0.97666 | -0.44898 | 0.97567 | -0.46853 | 4.449
72 | 0.0061161 | 0.0015327 | -0.0061144 | -0.0015323 | 1.7519e-06 | 4.4814e-07 | 0.0093183 | 0.0093185 | 0.0093185 | 0.97666 | -0.44898 | 0.97636 | -0.45499 | 2.56
73 | 0.008574 | 0.002149 | -0.0085719 | -0.0021481 | 2.12e-06 | 9.3674e-07 | 0.01302 | 0.01302 | 0.01302 | 0.97993 | -0.38488 | 0.97967 | -0.39007 | 3.5768
74 | 0.0019658 | 0.00049246 | -0.0019657 | -0.00049265 | 6.2375e-08 | -1.9526e-07 | 0.0029849 | 0.002985 | 0.002985 | 0.97993 | -0.38488 | 0.9799 | -0.38555 | 0.82005
75 | 0.010619 | 0.0026581 | -0.010618 | -0.0026575 | 1.1418e-06 | 5.8576e-07 | 0.016194 | 0.016194 | 0.016194 | 0.97567 | -0.46853 | 0.97556 | -0.47079 | 4.449
76 | 0.0020399 | 0.00051112 | -0.0020399 | -0.00051121 | 3.0231e-08 | -8.4965e-08 | 0.0031089 | 0.0031089 | 0.0031089 | 0.97636 | -0.45499 | 0.97634 | -0.4553 | 0.85409
77 | 0.14653 | 0.037173 | -0.14642 | -0.037108 | 0.00010162 | 6.4414e-05 | 0.22227 | 0.22227 | 0.22227 | 0.98164 | -0.35069 | 0.9809 | -0.36512 | 20.3545
78 | 0.14426 | 0.036566 | -0.1442 | -0.03653 | 5.6597e-05 | 3.5865e-05 | 0.21899 | 0.21899 | 0.21899 | 0.9809 | -0.36512 | 0.98048 | -0.37329 | 20.0539
79 | 0.14204 | 0.035988 | -0.14194 | -0.035922 | 0.00010413 | 6.5965e-05 | 0.21571 | 0.21571 | 0.21571 | 0.98048 | -0.37329 | 0.9797 | -0.38856 | 19.7534
80 | 0.14015 | 0.035474 | -0.1401 | -0.03544 | 5.3544e-05 | 3.3912e-05 | 0.21299 | 0.21299 | 0.21299 | 0.9797 | -0.38856 | 0.97929 | -0.39652 | 19.5048
81 | 0.13831 | 0.034993 | -0.13816 | -0.034898 | 0.0001496 | 9.4723e-05 | 0.21028 | 0.21028 | 0.21028 | 0.97929 | -0.39652 | 0.97813 | -0.41909 | 19.2562
82 | 0.1347 | 0.034031 | -0.13459 | -0.033964 | 0.00010551 | 6.6771e-05 | 0.20502 | 0.20502 | 0.20502 | 0.97813 | -0.41909 | 0.97729 | -0.43544 | 18.7743
83 | 0.13117 | 0.033105 | -0.13114 | -0.033088 | 2.6301e-05 | 1.6635e-05 | 0.19979 | 0.19979 | 0.19979 | 0.97729 | -0.43544 | 0.97708 | -0.43963 | 18.2962
84 | -0.34137 | -0.087441 | 0.34139 | 0.087457 | 2.531e-05 | 1.6168e-05 | 0.51207 | 0.51207 | 0.51207 | 0.99328 | -0.12697 | 0.99336 | -0.12544 | 46.8925
85 | -0.34355 | -0.087999 | 0.34387 | 0.088199 | 0.00031339 | 0.0002002 | 0.51531 | 0.51531 | 0.51531 | 0.99336 | -0.12544 | 0.99435 | -0.10663 | 47.1893
86 | -0.34603 | -0.088741 | 0.34646 | 0.089013 | 0.00042578 | 0.000272 | 0.51854 | 0.51854 | 0.51854 | 0.99435 | -0.10663 | 0.99569 | -0.081295 | 47.4857
87 | -0.34832 | -0.089481 | 0.34839 | 0.089524 | 6.8168e-05 | 4.3549e-05 | 0.52133 | 0.52133 | 0.52133 | 0.99569 | -0.081295 | 0.9959 | -0.077265 | 47.7409
88 | -0.35176 | -0.09037 | 0.35185 | 0.090427 | 8.9813e-05 | 5.7379e-05 | 0.52637 | 0.52637 | 0.52637 | 0.9959 | -0.077265 | 0.99618 | -0.07201 | 48.2025
89 | -0.35364 | -0.090875 | 0.35397 | 0.091086 | 0.00033032 | 0.00021103 | 0.52904 | 0.52904 | 0.52904 | 0.99618 | -0.07201 | 0.9972 | -0.0528 | 48.4467
90 | -0.35575 | -0.091533 | 0.35609 | 0.091745 | 0.00033237 | 0.00021235 | 0.5317 | 0.5317 | 0.5317 | 0.9972 | -0.0528 | 0.99821 | -0.033606 | 48.6906
91 | -0.35795 | -0.092213 | 0.358 | 0.092241 | 4.3453e-05 | 2.7762e-05 | 0.53448 | 0.53448 | 0.53448 | 0.99821 | -0.033606 | 0.99835 | -0.031112 | 48.9453
92 | -0.3608 | -0.092943 | 0.361 | 0.093073 | 0.00020315 | 0.00012979 | 0.53866 | 0.53866 | 0.53866 | 0.99835 | -0.031112 | 0.99896 | -0.01955 | 49.3279
93 | -0.36279 | -0.09352 | 0.36313 | 0.093741 | 0.00034576 | 0.00022091 | 0.54132 | 0.54132 | 0.54132 | 0.99896 | -0.01955 | 1 | 0 | 49.5714
94 | 0.017155 | 0.0043016 | -0.017154 | -0.0043008 | 1.4161e-06 | 8.3031e-07 | 0.025528 | 0.025528 | 0.025528 | 1 | 0 | 0.99991 | -0.0017323 | 7.0132
95 | 0.015286 | 0.0038326 | -0.015281 | -0.0038299 | 4.6367e-06 | 2.6542e-06 | 0.022748 | 0.022748 | 0.022748 | 0.99991 | -0.0017323 | 0.99958 | -0.0080996 | 6.2495
96 | 0.011776 | 0.0029515 | -0.011776 | -0.0029513 | 4.0904e-07 | 2.1526e-07 | 0.017531 | 0.017531 | 0.017531 | 0.99958 | -0.0080996 | 0.99954 | -0.0088287 | 4.8161
97 | 0.0044721 | 0.0011208 | -0.004472 | -0.0011208 | 7.6208e-08 | -1.1323e-08 | 0.0066575 | 0.0066576 | 0.0066576 | 0.99954 | -0.0088287 | 0.99952 | -0.0091864 | 1.829
98 | 0.040903 | 0.010283 | -0.040855 | -0.010253 | 4.8311e-05 | 3.0508e-05 | 0.06246 | 0.062461 | 0.062461 | 0.97463 | -0.48762 | 0.97338 | -0.51238 | 17.1595
99 | 0.037155 | 0.0093306 | -0.037146 | -0.0093247 | 9.2281e-06 | 5.8107e-06 | 0.056733 | 0.056733 | 0.056733 | 0.97463 | -0.48762 | 0.97437 | -0.49282 | 15.586
100 | 0.027573 | 0.0069241 | -0.027537 | -0.0069014 | 3.6571e-05 | 2.2724e-05 | 0.042156 | 0.042157 | 0.042157 | 0.97338 | -0.51238 | 0.97197 | -0.54022 | 11.5815
101 | 0.031415 | 0.0078884 | -0.031388 | -0.0078716 | 2.6867e-05 | 1.6808e-05 | 0.047981 | 0.047981 | 0.047981 | 0.97437 | -0.49282 | 0.97346 | -0.51077 | 13.1816
102 | 0.013274 | 0.0033269 | -0.013274 | -0.0033267 | 2.0712e-07 | 1.1598e-07 | 0.020322 | 0.020322 | 0.020322 | 0.97197 | -0.54022 | 0.97195 | -0.54055 | 5.5829
103 | 0.025395 | 0.0063696 | -0.025391 | -0.0063672 | 3.8035e-06 | 2.3506e-06 | 0.03882 | 0.03882 | 0.03882 | 0.97346 | -0.51077 | 0.9733 | -0.51391 | 10.6648
104 | 0.0040235 | 0.0010082 | -0.0040231 | -0.0010083 | 4.1149e-07 | -1.0654e-07 | 0.0061113 | 0.0061114 | 0.0061114 | 0.97967 | -0.39007 | 0.97956 | -0.39222 | 1.679
105 | 0.0015011 | 0.00037612 | -0.0015011 | -0.00037621 | 1.4973e-08 | -8.7083e-08 | 0.0022802 | 0.0022803 | 0.0022803 | 0.97956 | -0.39188 | 0.97955 | -0.39209 | 0.62645
106 | -0.0029544 | -0.00074034 | 0.0029544 | 0.00074027 | 6.6545e-08 | -6.8327e-08 | 0.0044878 | 0.0044878 | 0.0044878 | 0.97956 | -0.39188 | 0.97958 | -0.3914 | 1.2329
107 | -0.004523 | -0.0011334 | 0.0045232 | 0.0011334 | 1.3945e-07 | -9.928e-09 | 0.0068706 | 0.0068706 | 0.0068706 | 0.97958 | -0.3914 | 0.97961 | -0.39076 | 1.8875
108 | -0.006131 | -0.0015364 | 0.0061313 | 0.0015364 | 2.8102e-07 | 7.1064e-08 | 0.0093129 | 0.0093128 | 0.0093129 | 0.97961 | -0.39076 | 0.97966 | -0.38979 | 2.5585
109 | -0.00097084 | -0.00024332 | 0.00097086 | 0.00024303 | 1.9862e-08 | -2.887e-07 | 0.0014811 | 0.001481 | 0.0014811 | 0.9754 | -0.47398 | 0.97542 | -0.47355 | 0.40689
110 | -0.0090265 | -0.0022584 | 0.0090277 | 0.0022589 | 1.1854e-06 | 5.5048e-07 | 0.013769 | 0.013769 | 0.013769 | 0.97542 | -0.47355 | 0.97556 | -0.47079 | 3.7826
111 | 0.0064948 | 0.0016242 | -0.0064897 | -0.0016227 | 5.115e-06 | 1.5404e-06 | 0.0099067 | 0.0099073 | 0.0099073 | 0.97542 | -0.47355 | 0.97458 | -0.49011 | 2.7218
112 | 0.0029048 | 0.0007245 | -0.0029033 | -0.00072608 | 1.509e-06 | -1.5828e-06 | 0.0044339 | 0.0044348 | 0.0044348 | 0.97458 | -0.49011 | 0.97403 | -0.50105 | 1.2184
113 | 0.0028487 | 0.00071365 | -0.0028487 | -0.00071374 | 7.7381e-08 | -8.6392e-08 | 0.0043494 | 0.0043495 | 0.0043495 | 0.97458 | -0.49011 | 0.97455 | -0.49068 | 1.1949
114 | 0.0020158 | 0.000505 | -0.0020157 | -0.00050518 | 6.4925e-08 | -1.8617e-07 | 0.0030778 | 0.0030778 | 0.0030778 | 0.97455 | -0.49068 | 0.97452 | -0.49136 | 0.84556
115 | 0.0017441 | 0.00043554 | -0.0017437 | -0.00043701 | 3.6374e-07 | -1.4678e-06 | 0.0026638 | 0.0026644 | 0.0026644 | 0.97403 | -0.50105 | 0.9738 | -0.50543 | 0.73199
116 | -0.0047351 | -0.0011864 | 0.0047354 | 0.0011864 | 3.1847e-07 | 4.9085e-09 | 0.0072618 | 0.0072617 | 0.0072618 | 0.97025 | -0.57412 | 0.97032 | -0.57271 | 1.995
117 | 0.010536 | 0.0026413 | -0.010534 | -0.00264 | 2.556e-06 | 1.3102e-06 | 0.016118 | 0.016118 | 0.016118 | 0.9727 | -0.52569 | 0.97245 | -0.53078 | 4.4281
118 | -0.010536 | -0.0026413 | 0.010537 | 0.0026417 | 7.9341e-07 | 4.0668e-07 | 0.016118 | 0.016118 | 0.016118 | 0.9727 | -0.52569 | 0.97278 | -0.52411 | 4.4281
119 | -0.01639 | -0.0041087 | 0.016398 | 0.004113 | 7.4004e-06 | 4.3463e-06 | 0.025072 | 0.025072 | 0.025072 | 0.97278 | -0.52411 | 0.97326 | -0.51464 | 6.8879
120 | -0.0047354 | -0.0011864 | 0.004736 | 0.0011864 | 6.0191e-07 | 9.1867e-09 | 0.0072617 | 0.0072616 | 0.0072617 | 0.97032 | -0.57271 | 0.97046 | -0.57004 | 1.995
121 | -0.0075271 | -0.001886 | 0.0075275 | 0.0018861 | 4.1761e-07 | 1.6396e-07 | 0.011541 | 0.011541 | 0.011541 | 0.97046 | -0.57004 | 0.97052 | -0.56887 | 3.1707
122 | 0.019672 | 0.004934 | -0.019672 | -0.0049335 | 6.8266e-07 | 4.1189e-07 | 0.030077 | 0.030077 | 0.030077 | 0.9733 | -0.51391 | 0.97326 | -0.51464 | 8.2629
123 | -0.0014298 | -0.00035833 | 0.0014298 | 0.0003583 | 4.8158e-09 | -3.0741e-08 | 0.0021791 | 0.002179 | 0.0021791 | 0.97634 | -0.45537 | 0.97634 | -0.4553 | 0.59864

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38372 | 0.09849

## res_load
| p_mw | q_mvar
0 | 0.0096916 | 0.0024289
1 | 0.00089676 | 0.00022475
2 | 0.0014445 | 0.00036202
3 | 0.0027156 | 0.0006806
4 | 0.0014457 | 0.00036232
5 | 0.00095966 | 0.00024051
6 | 0.0011955 | 0.00029963
7 | 0.0035254 | 0.00088355
8 | 0.00037524 | 9.4043e-05
9 | 0.0040599 | 0.0010175
10 | 0.001543 | 0.00038672
11 | 0.005117 | 0.0012824
12 | 0.012126 | 0.0030391
13 | 0.0021628 | 0.00054205
14 | 0.0021612 | 0.00054165
15 | 0.0021638 | 0.00054229
16 | 0.0021604 | 0.00054146
17 | 0.0021628 | 0.00054205
18 | 0.001985 | 0.00049749
19 | 0.0092253 | 0.0023121
20 | 0.0077024 | 0.0019304
21 | 0.0018992 | 0.00047599
22 | 0.0017718 | 0.00044405
23 | 0.0067976 | 0.0017036
24 | 0.0060901 | 0.0015263
25 | 0.0022172 | 0.00055567
26 | 0.0021716 | 0.00054426
27 | 0.0022613 | 0.00056673
28 | 0.0026286 | 0.00065878
29 | 0.0021615 | 0.00054173
30 | 0.0042845 | 0.0010738
31 | 0.0042731 | 0.0010709
32 | 0.0028603 | 0.00071687
33 | 0.0012096 | 0.00030316
34 | 0.0056697 | 0.001421
35 | 0.00060056 | 0.00015051
36 | 0.00026239 | 6.5762e-05
37 | 0.0066734 | 0.0016725
38 | 0.00026223 | 6.5721e-05
39 | 0.00026216 | 6.5703e-05
40 | 0.0014993 | 0.00037577
41 | 0.0022572 | 0.0005657
42 | 0.0012574 | 0.00031513
43 | 0.0022581 | 0.00056592
44 | 0.0014497 | 0.00036332
45 | 0.0014516 | 0.00036381
46 | 0.0041373 | 0.0010369
47 | 0.0057782 | 0.0014481
48 | 0.011627 | 0.0029141
49 | 0.00603 | 0.0015113
50 | 0.0067646 | 0.0016954
51 | 0.0013226 | 0.00033148
52 | 0.0040745 | 0.0010212
53 | 0.020259 | 0.0050773
54 | 0.0021636 | 0.00054225
55 | 0.0021638 | 0.00054229
56 | 0.0021628 | 0.00054205
57 | 0.0017874 | 0.00044796
58 | 0.0017863 | 0.00044769
59 | 0.0034594 | 0.00086702
60 | 0.0034294 | 0.00085949
61 | 0.0022597 | 0.00056634
62 | 0.0021636 | 0.00054225
63 | 0.0021628 | 0.00054206
64 | 0.0018651 | 0.00046744
65 | 0.0033738 | 0.00084554
66 | 0.0017854 | 0.00044747
67 | 0.0017848 | 0.0004473
68 | 0.0010197 | 0.00025556
69 | 0.0018656 | 0.00046757
70 | 0.0028037 | 0.00070268
71 | 0.0017848 | 0.0004473
72 | 0.0017848 | 0.0004473
73 | 0.0018681 | 0.00046818
74 | 0.003505 | 0.00087844
75 | 0.0073037 | 0.0018305
76 | 0.004472 | 0.0011208
77 | 0.013282 | 0.0033288
78 | 0.0057311 | 0.0014364
79 | 0.014262 | 0.0035745
80 | 0.0059932 | 0.001502
81 | 0.0014507 | 0.00036359
82 | 0.0045483 | 0.0011399
83 | 0.0040231 | 0.0010083
84 | 0.0019657 | 0.00049265
85 | 0.013274 | 0.0033267
86 | 0.0014533 | 0.00036422
87 | 0.0015011 | 0.00037621
88 | 0.0015686 | 0.00039314
89 | 0.0016079 | 0.00040297
90 | 0.001501 | 0.00037619
91 | 0.00097084 | 0.00024332
92 | 0.0015608 | 0.00039117
93 | 0.0015904 | 0.0003986
94 | 0.00073617 | 0.0001845
95 | 0.00083288 | 0.00020874
96 | 0.0020157 | 0.00050518
97 | 0.0011593 | 0.00029054
98 | 0.0017437 | 0.00043701
99 | 0.0010637 | 0.00026659
100 | 0.010534 | 0.00264
101 | 0.0058534 | 0.001467
102 | 0.0027911 | 0.00069952
103 | 0.0027911 | 0.00069952
104 | 0.0057187 | 0.0014332
105 | 0.0032738 | 0.0008205
106 | 0.0014298 | 0.00035833
107 | 0.00061012 | 0.00015291

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1