## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1341-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1341-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1341-1_0_4_node_21 | 0.4 | n |  | TRUE
3 | bus_LV_1341-1_0_4_node_22 | 0.4 | n |  | TRUE
4 | bus_LV_1341-1_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1341-1_0_4_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_1341-1_0_4_node_2 | 0.4 | n |  | TRUE
7 | bus_LV_1341-1_0_4_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_1341-1_0_4_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_1341-1_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1341-1_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1341-1_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1341-1_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1341-1_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1341-1_0_4_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_1341-1_0_4_node_31 | 0.4 | n |  | TRUE
16 | bus_LV_1341-1_0_4_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_1341-1_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1341-1_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1341-1_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1341-1_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1341-1_0_4_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_1341-1_0_4_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_1341-1_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1341-1_0_4_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1341-1_0_4_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1341-1_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1341-1_0_4_node_41 | 0.4 | n |  | TRUE
28 | bus_LV_1341-1_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1341-1_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1341-1_0_4_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_1341-1_0_4_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_1341-1_0_4_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_1341-1_0_4_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_1341-1_0_4_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_1341-1_0_4_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_1341-1_0_4_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_1341-1_0_4_node_37 | 0.4 | n |  | TRUE
38 | bus_LV_1341-1_0_4_node_38 | 0.4 | n |  | TRUE
39 | bus_LV_1341-1_0_4_node_39 | 0.4 | n |  | TRUE
40 | bus_LV_1341-1_0_4_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_1341-1_0_4_node_42 | 0.4 | n |  | TRUE
42 | bus_LV_1341-1_0_4_node_43 | 0.4 | n |  | TRUE
43 | bus_MV_223_0_node_66 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1341-1_0_4_load_0 | 0 | 0.0084316 | 0.0021132 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1341-1_0_4_load_22 | 3 | 0.061257 | 0.015353 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1341-1_0_4_load_18 | 5 | 0.024605 | 0.0061667 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1341-1_0_4_load_2 | 6 | 0.032134 | 0.0080535 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1341-1_0_4_load_3 | 7 | 0.032398 | 0.0081198 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1341-1_0_4_load_7 | 10 | 0.0044957 | 0.0011267 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1341-1_0_4_load_6 | 11 | 0.003071 | 0.00076967 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1341-1_0_4_load_8 | 12 | 0.0046307 | 0.0011606 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1341-1_0_4_load_31 | 15 | 0.015732 | 0.0039428 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1341-1_0_4_load_27 | 16 | 0.0065443 | 0.0016401 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1341-1_0_4_load_11 | 17 | 0.0014561 | 0.00036494 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1341-1_0_4_load_12 | 18 | 0.032305 | 0.0080964 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1341-1_0_4_load_13 | 19 | 0.00095734 | 0.00023993 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1341-1_0_4_load_28 | 21 | 0.0049517 | 0.001241 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1341-1_0_4_load_30 | 22 | 0.003693 | 0.00092556 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1341-1_0_4_load_15 | 23 | 0.047021 | 0.011785 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1341-1_0_4_load_16 | 24 | 0.044065 | 0.011044 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1341-1_0_4_load_41 | 27 | 0.058035 | 0.014545 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1341-1_0_4_load_25 | 28 | 0.0020378 | 0.00051072 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1341-1_0_4_load_23 | 29 | 0.0092212 | 0.002311 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1341-1_0_4_load_24 | 30 | 0.0029163 | 0.0007309 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1341-1_0_4_load_33 | 32 | 0.0021383 | 0.00053591 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1341-1_0_4_load_34 | 33 | 0.0067614 | 0.0016946 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1341-1_0_4_load_32 | 34 | 0.017015 | 0.0042643 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1341-1_0_4_load_35 | 35 | 0.020448 | 0.0051247 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1341-1_0_4_load_37 | 37 | 0.004866 | 0.0012195 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1341-1_0_4_load_38 | 38 | 0.0047496 | 0.0011903 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1341-1_0_4_load_39 | 39 | 0.0050285 | 0.0012603 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1341-1_0_4_load_40 | 40 | 0.0042209 | 0.0010579 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1341-1_0_4_load_42 | 41 | 0.0037502 | 0.0009399 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1341-1_0_4_load_43 | 42 | 0.0010579 | 0.00026513 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1341-1_0_4_line_0 |  | 0 | 1 | 0.076729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1341-1_0_4_line_1 |  | 1 | 2 | 0.058634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1341-1_0_4_line_2 |  | 2 | 5 | 0.083815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1341-1_0_4_line_3 |  | 3 | 4 | 0.059409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1341-1_0_4_line_4 |  | 4 | 9 | 0.014044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1341-1_0_4_line_5 |  | 4 | 8 | 0.075841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1341-1_0_4_line_6 |  | 5 | 24 | 0.035461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1341-1_0_4_line_7 |  | 6 | 7 | 0.041154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1341-1_0_4_line_8 |  | 6 | 8 | 0.061532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1341-1_0_4_line_9 |  | 9 | 10 | 0.020175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1341-1_0_4_line_10 |  | 10 | 11 | 0.038657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1341-1_0_4_line_11 |  | 11 | 12 | 0.036921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1341-1_0_4_line_12 |  | 12 | 13 | 0.012331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1341-1_0_4_line_13 |  | 13 | 14 | 0.015573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_1341-1_0_4_line_14 |  | 14 | 15 | 0.030682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1341-1_0_4_line_15 |  | 14 | 16 | 0.017711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1341-1_0_4_line_16 |  | 15 | 34 | 0.030528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1341-1_0_4_line_17 |  | 16 | 21 | 0.037392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_1341-1_0_4_line_18 |  | 17 | 18 | 0.10051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1341-1_0_4_line_19 |  | 17 | 19 | 0.035157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1341-1_0_4_line_20 |  | 18 | 20 | 0.019438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1341-1_0_4_line_21 |  | 20 | 21 | 0.079685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1341-1_0_4_line_22 |  | 21 | 22 | 0.024287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_1341-1_0_4_line_23 |  | 22 | 31 | 0.0096875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_1341-1_0_4_line_24 |  | 23 | 24 | 0.031353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1341-1_0_4_line_25 |  | 23 | 25 | 0.013666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1341-1_0_4_line_26 |  | 25 | 26 | 0.007932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1341-1_0_4_line_27 |  | 26 | 27 | 0.024522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1341-1_0_4_line_28 |  | 26 | 28 | 0.046232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_1341-1_0_4_line_29 |  | 28 | 29 | 0.0024426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_1341-1_0_4_line_30 |  | 29 | 30 | 0.011311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_1341-1_0_4_line_31 |  | 30 | 31 | 0.012241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_1341-1_0_4_line_32 |  | 31 | 32 | 0.010728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1341-1_0_4_line_33 |  | 32 | 33 | 0.018171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1341-1_0_4_line_34 |  | 33 | 35 | 0.00067086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1341-1_0_4_line_35 |  | 35 | 36 | 0.085308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1341-1_0_4_line_36 |  | 36 | 37 | 0.026408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1341-1_0_4_line_37 |  | 37 | 38 | 0.049295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1341-1_0_4_line_38 |  | 38 | 39 | 0.031364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1341-1_0_4_line_39 |  | 39 | 40 | 0.033349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1341-1_0_4_line_40 |  | 40 | 41 | 0.358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1341-1_0_4_line_41 |  | 41 | 42 | 0.042759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1341-1_0_4_trafo_10 | 0.63 MVA 20/0.4 kV | 43 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2704435.815 | 1227895.1838 | 2704445.1662 | 1227900.463 | 2704470.4031 | 1227961.4374
1 | 2704412.4373 | 1227841.4114 | 2704435.815 | 1227895.1838
2 | 2704412.4373 | 1227841.4114 | 2704404.3248 | 1227836.3764 | 2704395.0324 | 1227835.5127 | 2704354.648 | 1227849.8259 | 2704346.3501 | 1227850.6032 | 2704339.5226 | 1227847.0586 | 2704337.7918 | 1227841.249
3 | 2704320.2409 | 1227952.432 | 2704356.3861 | 1227905.2836
4 | 2704320.2409 | 1227952.432 | 2704309.7348 | 1227945.5871 | 2704308.6009 | 1227944.5554
5 | 2704320.2409 | 1227952.432 | 2704326.2406 | 1227955.6284 | 2704354.2817 | 1227969.575 | 2704358.9226 | 1227972.8922 | 2704363.6245 | 1227978.7791 | 2704347.9016 | 1227997.5506
6 | 2704327.6671 | 1227807.2644 | 2704337.7918 | 1227841.249
7 | 2704310.8354 | 1228046.6022 | 2704285.5446 | 1228079.0684
8 | 2704347.9016 | 1227997.5506 | 2704336.5766 | 1228011.0286 | 2704321.225 | 1228033.2648 | 2704310.8354 | 1228046.6022
9 | 2704308.6009 | 1227944.5554 | 2704293.7064 | 1227930.9466
10 | 2704266.6726 | 1227903.4034 | 2704278.6724 | 1227917.2104 | 2704293.7064 | 1227930.9466
11 | 2704250.42 | 1227871.315 | 2704255.5224 | 1227890.5738 | 2704266.6726 | 1227903.4034
12 | 2704247.2619 | 1227859.3948 | 2704250.42 | 1227871.315
13 | 2704242.1461 | 1227844.6832 | 2704247.2619 | 1227859.3948
14 | 2704242.1461 | 1227844.6832 | 2704215.6534 | 1227860.1588
15 | 2704242.1461 | 1227844.6832 | 2704239.2273 | 1227837.8047 | 2704233.9225 | 1227829.0468
16 | 2704215.6534 | 1227860.1588 | 2704189.2936 | 1227875.5569
17 | 2704214.5504 | 1227797.0644 | 2704233.9225 | 1227829.0468
18 | 2704152.8748 | 1227866.3007 | 2704148.9517 | 1227879.1766 | 2704149.9653 | 1227885.777 | 2704153.9537 | 1227891.3065 | 2704195.1561 | 1227927.1434 | 2704210.4659 | 1227938.3125
19 | 2704238.8677 | 1227959.0328 | 2704210.4659 | 1227938.3125
20 | 2704152.9645 | 1227847.8347 | 2704154.9484 | 1227850.9717 | 2704155.6325 | 1227855.1868 | 2704153.6561 | 1227863.7364 | 2704152.8748 | 1227866.3007
21 | 2704214.5504 | 1227797.0644 | 2704152.9645 | 1227847.8347
22 | 2704214.5504 | 1227797.0644 | 2704230.0215 | 1227788.7737 | 2704236.1679 | 1227786.0225
23 | 2704245.0101 | 1227782.0647 | 2704236.1679 | 1227786.0225
24 | 2704318.7151 | 1227777.2163 | 2704327.6671 | 1227807.2644
25 | 2704314.8138 | 1227764.1193 | 2704316.818 | 1227770.8483 | 2704318.7151 | 1227777.2163
26 | 2704312.5444 | 1227756.5183 | 2704314.8138 | 1227764.1193
27 | 2704312.5444 | 1227756.5183 | 2704335.566 | 1227748.073
28 | 2704312.5444 | 1227756.5183 | 2704269.1422 | 1227772.4435
29 | 2704269.1422 | 1227772.4435 | 2704266.8491 | 1227773.2849
30 | 2704256.2307 | 1227777.181 | 2704266.8491 | 1227773.2849
31 | 2704245.0101 | 1227782.0647 | 2704254.4983 | 1227777.8167 | 2704256.2307 | 1227777.181
32 | 2704245.0101 | 1227782.0647 | 2704239.502 | 1227772.8583
33 | 2704239.502 | 1227772.8583 | 2704232.6464 | 1227761.3994 | 2704229.258 | 1227757.9739
34 | 2704229.258 | 1227757.9739 | 2704228.7862 | 1227757.497
35 | 2704172.2336 | 1227712.7497 | 2704173.5552 | 1227719.5112 | 2704176.7676 | 1227733.4333 | 2704181.5254 | 1227743.9355 | 2704188.8954 | 1227750.7029 | 2704195.3775 | 1227751.4726 | 2704206.8546 | 1227749.2163 | 2704217.2921 | 1227750.0553 | 2704224.968 | 1227753.6369 | 2704228.7862 | 1227757.497
36 | 2704172.2336 | 1227712.7497 | 2704187.0364 | 1227690.8802
37 | 2704187.0364 | 1227690.8802 | 2704214.6682 | 1227650.0574
38 | 2704232.3976 | 1227624.2406 | 2704231.9693 | 1227624.4971 | 2704214.6682 | 1227650.0574
39 | 2704261.4318 | 1227615.4066 | 2704261.0275 | 1227618.5797 | 2704257.5735 | 1227619.7422 | 2704240.4108 | 1227619.4413 | 2704232.3976 | 1227624.2406
40 | 2704261.4318 | 1227615.4066 | 2704204.9055 | 1227261.8963
41 | 2704204.9055 | 1227261.8963 | 2704197.9602 | 1227260.2761 | 2704169.5279 | 1227238.8081

## bus_geodata
| x | y | coords
0 | 2704470.4031 | 1227961.4374
1 | 2704435.815 | 1227895.1838
2 | 2704412.4373 | 1227841.4114
3 | 2704356.3861 | 1227905.2836
4 | 2704320.2409 | 1227952.432
5 | 2704337.7918 | 1227841.249
6 | 2704310.8354 | 1228046.6022
7 | 2704285.5446 | 1228079.0684
8 | 2704347.9016 | 1227997.5506
9 | 2704308.6009 | 1227944.5554
10 | 2704293.7064 | 1227930.9466
11 | 2704266.6726 | 1227903.4034
12 | 2704250.42 | 1227871.315
13 | 2704247.2619 | 1227859.3948
14 | 2704242.1461 | 1227844.6832
15 | 2704215.6534 | 1227860.1588
16 | 2704233.9225 | 1227829.0468
17 | 2704210.4659 | 1227938.3125
18 | 2704152.8748 | 1227866.3007
19 | 2704238.8677 | 1227959.0328
20 | 2704152.9645 | 1227847.8347
21 | 2704214.5504 | 1227797.0644
22 | 2704236.1679 | 1227786.0225
23 | 2704318.7151 | 1227777.2163
24 | 2704327.6671 | 1227807.2644
25 | 2704314.8138 | 1227764.1193
26 | 2704312.5444 | 1227756.5183
27 | 2704335.566 | 1227748.073
28 | 2704269.1422 | 1227772.4435
29 | 2704266.8491 | 1227773.2849
30 | 2704256.2307 | 1227777.181
31 | 2704245.0101 | 1227782.0647
32 | 2704239.502 | 1227772.8583
33 | 2704229.258 | 1227757.9739
34 | 2704189.2936 | 1227875.5569
35 | 2704228.7862 | 1227757.4969
36 | 2704172.2336 | 1227712.7497
37 | 2704187.0364 | 1227690.8802
38 | 2704214.6682 | 1227650.0574
39 | 2704232.3976 | 1227624.2406
40 | 2704261.4318 | 1227615.4066
41 | 2704204.9055 | 1227261.8963
42 | 2704169.5279 | 1227238.8081
43 | 2704242.1461 | 1227844.6832

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97784 | -0.42786 | 0.0084316 | 0.0021132
1 | 0.97844 | -0.41607 | 0 | 0
2 | 0.97889 | -0.40707 | 0 | 0
3 | 0.98184 | -0.34806 | 0.061257 | 0.015353
4 | 0.9852 | -0.28248 | 0 | 0
5 | 0.97955 | -0.39422 | 0.024605 | 0.0061667
6 | 0.97696 | -0.44302 | 0.032134 | 0.0080535
7 | 0.97573 | -0.4674 | 0.032398 | 0.0081198
8 | 0.98065 | -0.37078 | 0 | 0
9 | 0.98684 | -0.25081 | 0 | 0
10 | 0.98919 | -0.20549 | 0.0044957 | 0.0011267
11 | 0.99386 | -0.1162 | 0.003071 | 0.00076967
12 | 0.99842 | -0.029707 | 0.0046307 | 0.0011606
13 | 1 | 0 | -0.47845 | -0.12212
14 | 0.99841 | -0.030092 | 0 | 0
15 | 0.9975 | -0.047676 | 0.015732 | 0.0039428
16 | 0.99678 | -0.061039 | 0.0065443 | 0.0016401
17 | 0.99005 | -0.19057 | 0.0014561 | 0.00036494
18 | 0.99027 | -0.18625 | 0.032305 | 0.0080964
19 | 0.99002 | -0.19117 | 0.00095734 | 0.00023993
20 | 0.99089 | -0.17426 | 0 | 0
21 | 0.99342 | -0.12527 | 0.0049517 | 0.001241
22 | 0.99153 | -0.16152 | 0.003693 | 0.00092556
23 | 0.98287 | -0.32924 | 0.047021 | 0.011785
24 | 0.98063 | -0.37296 | 0.044065 | 0.011044
25 | 0.98444 | -0.29868 | 0 | 0
26 | 0.98535 | -0.28099 | 0 | 0
27 | 0.98404 | -0.30657 | 0.058035 | 0.014545
28 | 0.98924 | -0.20569 | 0.0020378 | 0.00051072
29 | 0.98938 | -0.20302 | 0.0092212 | 0.002311
30 | 0.99005 | -0.19005 | 0.0029163 | 0.0007309
31 | 0.99079 | -0.17581 | 0 | 0
32 | 0.99027 | -0.18592 | 0.0021383 | 0.00053591
33 | 0.98942 | -0.20237 | 0.0067614 | 0.0016946
34 | 0.99703 | -0.056779 | 0.017015 | 0.0042643
35 | 0.98939 | -0.2029 | 0.020448 | 0.0051247
36 | 0.98753 | -0.23895 | 0 | 0
37 | 0.98696 | -0.25014 | 0.004866 | 0.0012195
38 | 0.98611 | -0.26676 | 0.0047496 | 0.0011903
39 | 0.9857 | -0.27467 | 0.0050285 | 0.0012603
40 | 0.98542 | -0.28008 | 0.0042209 | 0.0010579
41 | 0.98384 | -0.31108 | 0.0037502 | 0.0009399
42 | 0.9838 | -0.31189 | 0.0010579 | 0.00026513
43 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0084316 | -0.0021132 | 0.0084364 | 0.0021152 | 4.7368e-06 | 2.0685e-06 | 0.012831 | 0.01283 | 0.012831 | 0.97784 | -0.42786 | 0.97844 | -0.41607 | 3.5249
1 | -0.0084364 | -0.0021152 | 0.00844 | 0.0021168 | 3.6196e-06 | 1.5798e-06 | 0.01283 | 0.01283 | 0.01283 | 0.97844 | -0.41607 | 0.97889 | -0.40707 | 3.5249
2 | -0.00844 | -0.0021168 | 0.0084452 | 0.0021191 | 5.1738e-06 | 2.2568e-06 | 0.01283 | 0.01283 | 0.01283 | 0.97889 | -0.40707 | 0.97955 | -0.39422 | 3.5248
3 | -0.061257 | -0.015353 | 0.061449 | 0.015475 | 0.00019201 | 0.00012214 | 0.092838 | 0.092838 | 0.092838 | 0.98184 | -0.34806 | 0.9852 | -0.28248 | 25.5049
4 | -0.12652 | -0.031989 | 0.12671 | 0.032112 | 0.00019251 | 0.00012303 | 0.19119 | 0.19119 | 0.19119 | 0.9852 | -0.28248 | 0.98684 | -0.25081 | 52.5244
5 | 0.065068 | 0.016514 | -0.064793 | -0.016339 | 0.0002751 | 0.0001751 | 0.098351 | 0.098351 | 0.098351 | 0.9852 | -0.28248 | 0.98065 | -0.37078 | 27.0196
6 | -0.03305 | -0.0082857 | 0.033084 | 0.0083068 | 3.3521e-05 | 2.1006e-05 | 0.050207 | 0.050207 | 0.050207 | 0.97955 | -0.39422 | 0.98063 | -0.37296 | 13.7932
7 | 0.032436 | 0.0081434 | -0.032398 | -0.0081198 | 3.7675e-05 | 2.3597e-05 | 0.049408 | 0.049409 | 0.049409 | 0.97696 | -0.44302 | 0.97573 | -0.4674 | 13.5738
8 | -0.06457 | -0.016197 | 0.064793 | 0.016339 | 0.0002232 | 0.00014207 | 0.098352 | 0.098351 | 0.098352 | 0.97696 | -0.44302 | 0.98065 | -0.37078 | 27.0197
9 | -0.12671 | -0.032112 | 0.12699 | 0.032289 | 0.00027655 | 0.00017673 | 0.19119 | 0.19119 | 0.19119 | 0.98684 | -0.25081 | 0.98919 | -0.20549 | 52.5244
10 | -0.13148 | -0.033415 | 0.13205 | 0.033778 | 0.00056804 | 0.00036305 | 0.19795 | 0.19795 | 0.19795 | 0.98919 | -0.20549 | 0.99386 | -0.1162 | 54.3822
11 | -0.13512 | -0.034548 | 0.13569 | 0.034911 | 0.00056802 | 0.00036305 | 0.20255 | 0.20255 | 0.20255 | 0.99386 | -0.1162 | 0.99842 | -0.029707 | 55.6453
12 | -0.14032 | -0.036072 | 0.14052 | 0.036201 | 0.00020286 | 0.00012967 | 0.20945 | 0.20945 | 0.20945 | 0.99842 | -0.029707 | 1 | 0 | 57.5413
13 | 0.33627 | 0.085917 | -0.33579 | -0.085605 | 0.00048853 | 0.00031205 | 0.50096 | 0.50096 | 0.50096 | 1 | 0 | 0.99841 | -0.030092 | 45.8756
14 | 0.032781 | 0.0082286 | -0.032754 | -0.0082114 | 2.7469e-05 | 1.7179e-05 | 0.048861 | 0.048861 | 0.048861 | 0.99841 | -0.030092 | 0.9975 | -0.047676 | 13.4235
15 | 0.303 | 0.077376 | -0.30255 | -0.077087 | 0.00045251 | 0.00028892 | 0.4521 | 0.4521 | 0.4521 | 0.99841 | -0.030092 | 0.99678 | -0.061039 | 41.4012
16 | 0.017022 | 0.0042686 | -0.017015 | -0.0042643 | 7.3821e-06 | 4.3262e-06 | 0.025394 | 0.025394 | 0.025394 | 0.9975 | -0.047676 | 0.99703 | -0.056779 | 6.9763
17 | 0.29601 | 0.075447 | -0.29509 | -0.074863 | 0.0009145 | 0.00058382 | 0.44233 | 0.44233 | 0.44233 | 0.99678 | -0.061039 | 0.99342 | -0.12527 | 40.5066
18 | -0.0024135 | -0.00060444 | 0.002414 | 0.00060347 | 4.9587e-07 | -9.7549e-07 | 0.0036273 | 0.0036268 | 0.0036273 | 0.99005 | -0.19057 | 0.99027 | -0.18625 | 0.99651
19 | 0.00095737 | 0.0002395 | -0.00095734 | -0.00023993 | 2.7293e-08 | -4.3461e-07 | 0.0014387 | 0.0014389 | 0.0014389 | 0.99005 | -0.19057 | 0.99002 | -0.19117 | 0.3953
20 | -0.034719 | -0.0086999 | 0.034739 | 0.0087123 | 1.9839e-05 | 1.2446e-05 | 0.05217 | 0.05217 | 0.05217 | 0.99027 | -0.18625 | 0.99089 | -0.17426 | 14.3323
21 | -0.034739 | -0.0087123 | 0.03482 | 0.0087634 | 8.1328e-05 | 5.1021e-05 | 0.05217 | 0.052169 | 0.05217 | 0.99089 | -0.17426 | 0.99342 | -0.12527 | 14.3323
22 | 0.25532 | 0.064859 | -0.25488 | -0.064575 | 0.00044473 | 0.00028369 | 0.38275 | 0.38275 | 0.38275 | 0.99342 | -0.12527 | 0.99153 | -0.16152 | 35.05
23 | 0.25118 | 0.063649 | -0.25101 | -0.06354 | 0.0001723 | 0.00010989 | 0.3772 | 0.3772 | 0.3772 | 0.99153 | -0.16152 | 0.99079 | -0.17581 | 34.5425
24 | 0.07731 | 0.019453 | -0.077149 | -0.019351 | 0.00016114 | 0.00010274 | 0.11707 | 0.11707 | 0.11707 | 0.98287 | -0.32924 | 0.98063 | -0.37296 | 32.1625
25 | -0.12433 | -0.031238 | 0.12451 | 0.031354 | 0.00018162 | 0.00011607 | 0.18826 | 0.18826 | 0.18826 | 0.98287 | -0.32924 | 0.98444 | -0.29868 | 51.7195
26 | -0.12451 | -0.031354 | 0.12462 | 0.031421 | 0.00010542 | 6.7368e-05 | 0.18826 | 0.18826 | 0.18826 | 0.98444 | -0.29868 | 0.98535 | -0.28099 | 51.7194
27 | 0.058106 | 0.01459 | -0.058035 | -0.014545 | 7.0819e-05 | 4.5012e-05 | 0.087757 | 0.087757 | 0.087757 | 0.98535 | -0.28099 | 0.98404 | -0.30657 | 24.1092
28 | -0.18272 | -0.046011 | 0.18338 | 0.046433 | 0.0006604 | 0.00042147 | 0.27602 | 0.27602 | 0.27602 | 0.98535 | -0.28099 | 0.98924 | -0.20569 | 37.9143
29 | -0.18542 | -0.046943 | 0.18545 | 0.046958 | 2.3781e-05 | 1.5126e-05 | 0.27908 | 0.27908 | 0.27908 | 0.98924 | -0.20569 | 0.98938 | -0.20302 | 25.5568
30 | -0.19467 | -0.049269 | 0.19479 | 0.049347 | 0.00012133 | 7.7217e-05 | 0.29295 | 0.29295 | 0.29295 | 0.98938 | -0.20302 | 0.99005 | -0.19005 | 26.8269
31 | -0.1977 | -0.050078 | 0.19784 | 0.050164 | 0.00013527 | 8.6103e-05 | 0.29733 | 0.29733 | 0.29733 | 0.99005 | -0.19005 | 0.99079 | -0.17581 | 27.2282
32 | 0.053171 | 0.013376 | -0.053145 | -0.01336 | 2.5666e-05 | 1.6288e-05 | 0.079872 | 0.079872 | 0.079872 | 0.99079 | -0.17581 | 0.99027 | -0.18592 | 21.9429
33 | 0.051007 | 0.012824 | -0.050967 | -0.012798 | 4.0045e-05 | 2.5395e-05 | 0.076659 | 0.076659 | 0.076659 | 0.99027 | -0.18592 | 0.98942 | -0.20237 | 21.0602
34 | 0.044205 | 0.011104 | -0.044204 | -0.011103 | 1.1122e-06 | 7.0319e-07 | 0.06649 | 0.06649 | 0.06649 | 0.98942 | -0.20237 | 0.98939 | -0.2029 | 18.2666
35 | 0.023756 | 0.0059783 | -0.023715 | -0.0059532 | 4.0857e-05 | 2.5055e-05 | 0.035737 | 0.035738 | 0.035738 | 0.98939 | -0.2029 | 0.98753 | -0.23895 | 9.818
36 | 0.023715 | 0.0059532 | -0.023703 | -0.0059455 | 1.2648e-05 | 7.7571e-06 | 0.035738 | 0.035738 | 0.035738 | 0.98753 | -0.23895 | 0.98696 | -0.25014 | 9.8181
37 | 0.018837 | 0.0047259 | -0.018822 | -0.004717 | 1.4912e-05 | 8.9139e-06 | 0.028401 | 0.028402 | 0.028402 | 0.98696 | -0.25014 | 0.98611 | -0.26676 | 7.8027
38 | 0.014072 | 0.0035267 | -0.014067 | -0.0035237 | 5.3035e-06 | 2.9943e-06 | 0.021235 | 0.021235 | 0.021235 | 0.98611 | -0.26676 | 0.9857 | -0.27467 | 5.8338
39 | 0.0090385 | 0.0022634 | -0.0090362 | -0.0022624 | 2.3281e-06 | 1.065e-06 | 0.013644 | 0.013644 | 0.013644 | 0.9857 | -0.27467 | 0.98542 | -0.28008 | 3.7484
40 | 0.0048153 | 0.0012045 | -0.0048082 | -0.0012045 | 7.0978e-06 | -1.0877e-08 | 0.0072703 | 0.007272 | 0.007272 | 0.98542 | -0.28008 | 0.98384 | -0.31108 | 1.9978
41 | 0.0010579 | 0.00026461 | -0.0010579 | -0.00026513 | 4.1047e-08 | -5.1668e-07 | 0.0015999 | 0.0016001 | 0.0016001 | 0.98384 | -0.31108 | 0.9838 | -0.31189 | 0.43958

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47845 | 0.12212

## res_load
| p_mw | q_mvar
0 | 0.0084316 | 0.0021132
1 | 0.061257 | 0.015353
2 | 0.024605 | 0.0061667
3 | 0.032134 | 0.0080535
4 | 0.032398 | 0.0081198
5 | 0.0044957 | 0.0011267
6 | 0.003071 | 0.00076967
7 | 0.0046307 | 0.0011606
8 | 0.015732 | 0.0039428
9 | 0.0065443 | 0.0016401
10 | 0.0014561 | 0.00036494
11 | 0.032305 | 0.0080964
12 | 0.00095734 | 0.00023993
13 | 0.0049517 | 0.001241
14 | 0.003693 | 0.00092556
15 | 0.047021 | 0.011785
16 | 0.044065 | 0.011044
17 | 0.058035 | 0.014545
18 | 0.0020378 | 0.00051072
19 | 0.0092212 | 0.002311
20 | 0.0029163 | 0.0007309
21 | 0.0021383 | 0.00053591
22 | 0.0067614 | 0.0016946
23 | 0.017015 | 0.0042643
24 | 0.020448 | 0.0051247
25 | 0.004866 | 0.0012195
26 | 0.0047496 | 0.0011903
27 | 0.0050285 | 0.0012603
28 | 0.0042209 | 0.0010579
29 | 0.0037502 | 0.0009399
30 | 0.0010579 | 0.00026513

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1