## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1341-2_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1341-2_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1341-2_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1341-2_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1341-2_0_5_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1341-2_0_5_node_23 | 0.4 | n |  | TRUE
6 | bus_LV_1341-2_0_5_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_1341-2_0_5_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_1341-2_0_5_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1341-2_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1341-2_0_5_node_83 | 0.4 | n |  | TRUE
11 | bus_LV_1341-2_0_5_node_84 | 0.4 | n |  | TRUE
12 | bus_LV_1341-2_0_5_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1341-2_0_5_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_1341-2_0_5_node_46 | 0.4 | n |  | TRUE
15 | bus_LV_1341-2_0_5_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1341-2_0_5_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_1341-2_0_5_node_45 | 0.4 | n |  | TRUE
18 | bus_LV_1341-2_0_5_node_30 | 0.4 | n |  | TRUE
19 | bus_LV_1341-2_0_5_node_79 | 0.4 | n |  | TRUE
20 | bus_LV_1341-2_0_5_node_80 | 0.4 | n |  | TRUE
21 | bus_LV_1341-2_0_5_node_81 | 0.4 | n |  | TRUE
22 | bus_LV_1341-2_0_5_node_82 | 0.4 | n |  | TRUE
23 | bus_LV_1341-2_0_5_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_1341-2_0_5_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_1341-2_0_5_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_1341-2_0_5_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_1341-2_0_5_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_1341-2_0_5_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_1341-2_0_5_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_1341-2_0_5_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_1341-2_0_5_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_1341-2_0_5_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_1341-2_0_5_node_50 | 0.4 | n |  | TRUE
34 | bus_LV_1341-2_0_5_node_59 | 0.4 | n |  | TRUE
35 | bus_LV_1341-2_0_5_node_32 | 0.4 | n |  | TRUE
36 | bus_LV_1341-2_0_5_node_48 | 0.4 | n |  | TRUE
37 | bus_LV_1341-2_0_5_node_58 | 0.4 | n |  | TRUE
38 | bus_LV_1341-2_0_5_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_1341-2_0_5_node_43 | 0.4 | n |  | TRUE
40 | bus_LV_1341-2_0_5_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_1341-2_0_5_node_28 | 0.4 | n |  | TRUE
42 | bus_LV_1341-2_0_5_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_1341-2_0_5_node_44 | 0.4 | n |  | TRUE
44 | bus_LV_1341-2_0_5_node_42 | 0.4 | n |  | TRUE
45 | bus_LV_1341-2_0_5_node_40 | 0.4 | n |  | TRUE
46 | bus_LV_1341-2_0_5_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_1341-2_0_5_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_1341-2_0_5_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_1341-2_0_5_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_1341-2_0_5_node_60 | 0.4 | n |  | TRUE
51 | bus_LV_1341-2_0_5_node_61 | 0.4 | n |  | TRUE
52 | bus_LV_1341-2_0_5_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_1341-2_0_5_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_1341-2_0_5_node_52 | 0.4 | n |  | TRUE
55 | bus_LV_1341-2_0_5_node_51 | 0.4 | n |  | TRUE
56 | bus_LV_1341-2_0_5_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_1341-2_0_5_node_49 | 0.4 | n |  | TRUE
58 | bus_LV_1341-2_0_5_node_53 | 0.4 | n |  | TRUE
59 | bus_LV_1341-2_0_5_node_54 | 0.4 | n |  | TRUE
60 | bus_LV_1341-2_0_5_node_55 | 0.4 | n |  | TRUE
61 | bus_LV_1341-2_0_5_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_1341-2_0_5_node_57 | 0.4 | n |  | TRUE
63 | bus_LV_1341-2_0_5_node_62 | 0.4 | n |  | TRUE
64 | bus_LV_1341-2_0_5_node_63 | 0.4 | n |  | TRUE
65 | bus_LV_1341-2_0_5_node_65 | 0.4 | n |  | TRUE
66 | bus_LV_1341-2_0_5_node_64 | 0.4 | n |  | TRUE
67 | bus_LV_1341-2_0_5_node_76 | 0.4 | n |  | TRUE
68 | bus_LV_1341-2_0_5_node_77 | 0.4 | n |  | TRUE
69 | bus_LV_1341-2_0_5_node_66 | 0.4 | n |  | TRUE
70 | bus_LV_1341-2_0_5_node_68 | 0.4 | n |  | TRUE
71 | bus_LV_1341-2_0_5_node_69 | 0.4 | n |  | TRUE
72 | bus_LV_1341-2_0_5_node_70 | 0.4 | n |  | TRUE
73 | bus_LV_1341-2_0_5_node_73 | 0.4 | n |  | TRUE
74 | bus_LV_1341-2_0_5_node_74 | 0.4 | n |  | TRUE
75 | bus_LV_1341-2_0_5_node_75 | 0.4 | n |  | TRUE
76 | bus_LV_1341-2_0_5_node_71 | 0.4 | n |  | TRUE
77 | bus_LV_1341-2_0_5_node_72 | 0.4 | n |  | TRUE
78 | bus_LV_1341-2_0_5_node_78 | 0.4 | n |  | TRUE
79 | bus_MV_223_0_node_65 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1341-2_0_5_load_0 | 0 | 0.021569 | 0.0054057 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1341-2_0_5_load_23 | 5 | 0.0047854 | 0.0011993 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1341-2_0_5_load_9 | 6 | 0.0012825 | 0.00032142 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1341-2_0_5_load_10 | 7 | 0.021694 | 0.0054371 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1341-2_0_5_load_11 | 8 | 0.018801 | 0.0047119 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1341-2_0_5_load_83 | 10 | 0.0061028 | 0.0015295 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1341-2_0_5_load_84 | 11 | 0.017342 | 0.0043463 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1341-2_0_5_load_22 | 13 | 0.0059763 | 0.0014978 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1341-2_0_5_load_8 | 15 | 0.0024172 | 0.0006058 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1341-2_0_5_load_45 | 17 | 0.0078622 | 0.0019705 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1341-2_0_5_load_30 | 18 | 0.0018123 | 0.00045421 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1341-2_0_5_load_80 | 20 | 0.0091299 | 0.0022882 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1341-2_0_5_load_81 | 21 | 0.00088325 | 0.00022136 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1341-2_0_5_load_82 | 22 | 0.00061564 | 0.00015429 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1341-2_0_5_load_12 | 24 | 0.033497 | 0.0083952 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1341-2_0_5_load_17 | 27 | 0.032381 | 0.0081154 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1341-2_0_5_load_18 | 28 | 0.0086978 | 0.0021799 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1341-2_0_5_load_19 | 29 | 0.027555 | 0.0069061 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1341-2_0_5_load_20 | 30 | 0.0055379 | 0.0013879 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1341-2_0_5_load_21 | 31 | 0.016036 | 0.0040189 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1341-2_0_5_load_31 | 32 | 0.01937 | 0.0048546 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1341-2_0_5_load_50 | 33 | 0.027533 | 0.0069003 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1341-2_0_5_load_59 | 34 | 0.0062398 | 0.0015639 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1341-2_0_5_load_58 | 37 | 0.0039156 | 0.00098133 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1341-2_0_5_load_25 | 38 | 0.0094678 | 0.0023729 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1341-2_0_5_load_43 | 39 | 0.0017895 | 0.00044849 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1341-2_0_5_load_42 | 44 | 0.0093947 | 0.0023545 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1341-2_0_5_load_33 | 46 | 0.027557 | 0.0069064 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1341-2_0_5_load_35 | 48 | 0.016287 | 0.0040819 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1341-2_0_5_load_36 | 49 | 0.011013 | 0.0027601 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1341-2_0_5_load_61 | 51 | 0.015231 | 0.0038171 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1341-2_0_5_load_37 | 52 | 0.0087243 | 0.0021865 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1341-2_0_5_load_52 | 54 | 0.0048447 | 0.0012142 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1341-2_0_5_load_51 | 55 | 0.0041891 | 0.0010499 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1341-2_0_5_load_47 | 56 | 0.023367 | 0.0058563 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1341-2_0_5_load_49 | 57 | 0.024431 | 0.0061229 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1341-2_0_5_load_53 | 58 | 0.012768 | 0.0032 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1341-2_0_5_load_54 | 59 | 0.0085791 | 0.0021501 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1341-2_0_5_load_55 | 60 | 0.010903 | 0.0027326 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1341-2_0_5_load_56 | 61 | 0.02013 | 0.005045 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1341-2_0_5_load_57 | 62 | 0.040753 | 0.010214 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1341-2_0_5_load_62 | 63 | 0.017684 | 0.0044321 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1341-2_0_5_load_63 | 64 | 0.017698 | 0.0044356 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1341-2_0_5_load_65 | 65 | 0.0022056 | 0.00055276 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1341-2_0_5_load_64 | 66 | 0.0032123 | 0.00080508 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1341-2_0_5_load_76 | 67 | 0.0012875 | 0.00032267 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1341-2_0_5_load_77 | 68 | 0.0037291 | 0.00093461 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1341-2_0_5_load_66 | 69 | 0.0013729 | 0.00034409 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1341-2_0_5_load_70 | 72 | 0.0022375 | 0.00056076 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1341-2_0_5_load_73 | 73 | 0.00045784 | 0.00011474 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1341-2_0_5_load_74 | 74 | 0.0015 | 0.00037594 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1341-2_0_5_load_75 | 75 | 0.00054603 | 0.00013685 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1341-2_0_5_load_71 | 76 | 0.0010555 | 0.00026453 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1341-2_0_5_load_72 | 77 | 0.00049699 | 0.00012456 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1341-2_0_5_load_78 | 78 | 0.00021624 | 5.4195e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 25 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1341-2_0_5_line_0 |  | 0 | 1 | 0.038957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1341-2_0_5_line_1 |  | 0 | 2 | 0.086084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1341-2_0_5_line_2 |  | 1 | 3 | 0.016367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1341-2_0_5_line_3 |  | 1 | 4 | 0.013203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1341-2_0_5_line_4 |  | 2 | 5 | 0.08688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1341-2_0_5_line_5 |  | 3 | 6 | 0.016238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1341-2_0_5_line_6 |  | 4 | 7 | 0.058133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1341-2_0_5_line_7 |  | 4 | 8 | 0.025908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1341-2_0_5_line_8 |  | 4 | 9 | 0.060865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1341-2_0_5_line_9 |  | 6 | 15 | 0.0032755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1341-2_0_5_line_10 |  | 7 | 13 | 0.048287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1341-2_0_5_line_11 |  | 8 | 16 | 0.016165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1341-2_0_5_line_12 |  | 9 | 10 | 0.013532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1341-2_0_5_line_13 |  | 9 | 11 | 0.005429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1341-2_0_5_line_14 |  | 12 | 13 | 0.025741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1341-2_0_5_line_15 |  | 12 | 14 | 0.033248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1341-2_0_5_line_16 |  | 14 | 17 | 0.028666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1341-2_0_5_line_17 |  | 16 | 23 | 0.018832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_1341-2_0_5_line_18 |  | 17 | 43 | 0.044516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1341-2_0_5_line_19 |  | 17 | 41 | 0.027193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1341-2_0_5_line_20 |  | 18 | 19 | 0.042885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1341-2_0_5_line_21 |  | 19 | 20 | 0.051697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1341-2_0_5_line_22 |  | 19 | 21 | 0.010104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1341-2_0_5_line_23 |  | 21 | 22 | 0.013096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1341-2_0_5_line_24 |  | 22 | 42 | 0.025264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1341-2_0_5_line_25 |  | 23 | 26 | 0.020499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1341-2_0_5_line_26 |  | 23 | 24 | 0.036538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1341-2_0_5_line_27 |  | 24 | 25 | 0.031923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_1341-2_0_5_line_28 |  | 25 | 27 | 0.0027744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1341-2_0_5_line_29 |  | 25 | 28 | 0.054954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1341-2_0_5_line_30 |  | 26 | 29 | 0.019836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_1341-2_0_5_line_31 |  | 27 | 30 | 0.014459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1341-2_0_5_line_32 |  | 28 | 31 | 0.037217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1341-2_0_5_line_33 |  | 29 | 32 | 0.012164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_1341-2_0_5_line_34 |  | 30 | 33 | 0.052888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1341-2_0_5_line_35 |  | 31 | 34 | 0.0086994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1341-2_0_5_line_36 |  | 32 | 35 | 0.049866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_1341-2_0_5_line_37 |  | 33 | 36 | 0.0035057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1341-2_0_5_line_38 |  | 34 | 37 | 0.023252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1341-2_0_5_line_39 |  | 35 | 46 | 0.01969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1341-2_0_5_line_40 |  | 35 | 47 | 0.007096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_1341-2_0_5_line_41 |  | 36 | 57 | 0.04142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1341-2_0_5_line_42 |  | 36 | 56 | 0.023443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1341-2_0_5_line_43 |  | 37 | 61 | 0.013175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1341-2_0_5_line_44 |  | 38 | 39 | 0.026537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1341-2_0_5_line_45 |  | 39 | 43 | 0.046485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1341-2_0_5_line_46 |  | 39 | 44 | 0.032328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1341-2_0_5_line_47 |  | 40 | 41 | 0.015658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1341-2_0_5_line_48 |  | 40 | 42 | 0.046177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1341-2_0_5_line_49 |  | 44 | 45 | 0.044973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1341-2_0_5_line_50 |  | 45 | 53 | 0.021094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1341-2_0_5_line_51 |  | 46 | 48 | 0.034261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1341-2_0_5_line_52 |  | 47 | 49 | 0.021647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_1341-2_0_5_line_53 |  | 49 | 50 | 0.045111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_1341-2_0_5_line_54 |  | 50 | 51 | 0.1038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1341-2_0_5_line_55 |  | 51 | 63 | 0.0060685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1341-2_0_5_line_56 |  | 52 | 53 | 0.029233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1341-2_0_5_line_57 |  | 54 | 55 | 0.026052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1341-2_0_5_line_58 |  | 55 | 57 | 0.0049286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1341-2_0_5_line_59 |  | 58 | 59 | 0.01715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1341-2_0_5_line_60 |  | 58 | 60 | 0.01374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1341-2_0_5_line_61 |  | 59 | 61 | 0.016694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1341-2_0_5_line_62 |  | 60 | 62 | 0.004369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1341-2_0_5_line_63 |  | 63 | 64 | 0.027046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1341-2_0_5_line_64 |  | 64 | 65 | 0.14732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1341-2_0_5_line_65 |  | 65 | 66 | 0.0058888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1341-2_0_5_line_66 |  | 66 | 67 | 0.12961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1341-2_0_5_line_67 |  | 67 | 68 | 0.007204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1341-2_0_5_line_68 |  | 68 | 78 | 0.029388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1341-2_0_5_line_69 |  | 69 | 70 | 0.031216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1341-2_0_5_line_70 |  | 70 | 71 | 0.1061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1341-2_0_5_line_71 |  | 70 | 72 | 0.047059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1341-2_0_5_line_72 |  | 71 | 73 | 0.08831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1341-2_0_5_line_73 |  | 72 | 74 | 0.0047836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1341-2_0_5_line_74 |  | 73 | 75 | 0.014888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1341-2_0_5_line_75 |  | 75 | 76 | 0.11546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1341-2_0_5_line_76 |  | 76 | 77 | 0.0024703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1341-2_0_5_line_77 |  | 77 | 78 | 0.013047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1341-2_0_5_trafo_14 | 0.63 MVA 20/0.4 kV | 79 | 25 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2704573.5851 | 1227874.4996 | 2704575.1648 | 1227881.6438 | 2704578.0793 | 1227913.1499
1 | 2704550.6662 | 1227974.8491 | 2704548.1149 | 1227966.4981 | 2704552.6989 | 1227963.5653 | 2704557.2402 | 1227965.213 | 2704573.3119 | 1227957.6788 | 2704575.7644 | 1227953.9858 | 2704581.6286 | 1227951.5204 | 2704578.0793 | 1227913.1499
2 | 2704573.5851 | 1227874.4996 | 2704557.2151 | 1227875.7128
3 | 2704586.7905 | 1227873.5199 | 2704573.5851 | 1227874.4996
4 | 2704550.6662 | 1227974.8491 | 2704466.7073 | 1227952.5082
5 | 2704557.2151 | 1227875.7128 | 2704547.9259 | 1227876.3945 | 2704544.0785 | 1227876.6604 | 2704542.2412 | 1227876.4057 | 2704541.1357 | 1227875.9081 | 2704541.1357 | 1227875.9081
6 | 2704586.7905 | 1227873.5199 | 2704630.6368 | 1227868.8096 | 2704631.8148 | 1227882.7943
7 | 2704586.7905 | 1227873.5199 | 2704585.1655 | 1227847.6627
8 | 2704586.7905 | 1227873.5199 | 2704589.3689 | 1227912.2162 | 2704611.3987 | 1227910.6801
9 | 2704539.8923 | 1227872.9174 | 2704540.4491 | 1227874.8731 | 2704541.1357 | 1227875.9081
10 | 2704635.8679 | 1227930.9105 | 2704631.8148 | 1227882.7943
11 | 2704584.126 | 1227831.5307 | 2704584.7771 | 1227841.4829 | 2704585.1655 | 1227847.6627
12 | 2704611.3987 | 1227910.6801 | 2704612.3816 | 1227924.1741
13 | 2704611.3987 | 1227910.6801 | 2704610.8647 | 1227905.2778
14 | 2704638.0284 | 1227956.5603 | 2704635.8679 | 1227930.9105
15 | 2704671.2592 | 1227953.7984 | 2704638.0284 | 1227956.5603
16 | 2704671.2592 | 1227953.7984 | 2704682.8728 | 1227957.55 | 2704699.2632 | 1227956.0187
17 | 2704594.5782 | 1227818.1712 | 2704594.3288 | 1227822.8703 | 2704592.2308 | 1227827.0921 | 2704588.6375 | 1227830.1424 | 2704584.126 | 1227831.5307
18 | 2704743.6209 | 1227952.8157 | 2704738.7216 | 1227952.5626 | 2704722.2287 | 1227953.8732 | 2704699.2632 | 1227956.0187
19 | 2704699.2632 | 1227956.0187 | 2704696.0669 | 1227983.0233
20 | 2704655.664 | 1228056.9563 | 2704653.1205 | 1228054.1984 | 2704642.9405 | 1228045.2237 | 2704640.0146 | 1228043.5154 | 2704638.2384 | 1228041.516 | 2704637.6696 | 1228039.3822 | 2704639.6138 | 1228034.8575 | 2704643.5883 | 1228033.393 | 2704648.8748 | 1228027.2152
21 | 2704655.664 | 1228056.9563 | 2704655.0862 | 1228084.6111 | 2704676.2727 | 1228096.0702
22 | 2704655.664 | 1228056.9563 | 2704661.5237 | 1228048.7243
23 | 2704669.4751 | 1228038.3352 | 2704666.2952 | 1228042.0211 | 2704661.5237 | 1228048.7243
24 | 2704685.9784 | 1228019.206 | 2704669.4751 | 1228038.3352
25 | 2704578.9826 | 1227808.9569 | 2704584.0799 | 1227808.3016 | 2704588.9713 | 1227809.8776 | 2704592.7066 | 1227813.4015 | 2704594.5782 | 1227818.1712
26 | 2704594.5782 | 1227818.1712 | 2704604.5938 | 1227816.7018 | 2704616.4148 | 1227815.5755 | 2704630.9552 | 1227815.4382
27 | 2704662.8771 | 1227815.1368 | 2704630.9552 | 1227815.4382
28 | 2704662.8771 | 1227815.1368 | 2704665.6501 | 1227815.2244
29 | 2704662.8771 | 1227815.1368 | 2704663.5177 | 1227804.5846 | 2704670.0629 | 1227760.6875
30 | 2704578.9826 | 1227808.9569 | 2704573.1195 | 1227801.0035 | 2704566.0267 | 1227794.0181
31 | 2704680.1019 | 1227815.6813 | 2704665.6501 | 1227815.2244
32 | 2704695.3115 | 1227739.2926 | 2704689.6245 | 1227740.274 | 2704676.1337 | 1227744.9623 | 2704671.1408 | 1227753.4586 | 2704670.0629 | 1227760.6875
33 | 2704566.0267 | 1227794.0181 | 2704554.9503 | 1227788.9907
34 | 2704680.1019 | 1227815.6813 | 2704694.6402 | 1227816.1408 | 2704732.9716 | 1227817.0605
35 | 2704695.3115 | 1227739.2926 | 2704703.8841 | 1227737.8132
36 | 2704510.0048 | 1227767.3917 | 2704553.5895 | 1227788.3731 | 2704554.9503 | 1227788.9907
37 | 2704736.4763 | 1227817.1446 | 2704732.9716 | 1227817.0605
38 | 2704703.8841 | 1227737.8132 | 2704726.797 | 1227733.859
39 | 2704510.0048 | 1227767.3917 | 2704516.4116 | 1227760.3768 | 2704525.3234 | 1227755.4368
40 | 2704503.507 | 1227764.4977 | 2704510.0048 | 1227767.3917
41 | 2704736.4763 | 1227817.1446 | 2704776.8751 | 1227816.2775 | 2704777.8837 | 1227816.1987
42 | 2704736.4763 | 1227817.1446 | 2704735.0161 | 1227832.4858 | 2704729.12 | 1227837.9407
43 | 2704739.3406 | 1227737.1137 | 2704738.3149 | 1227737.3065 | 2704727.7444 | 1227733.6955 | 2704726.797 | 1227733.859
44 | 2704789.5362 | 1227945.562 | 2704777.9776 | 1227969.4495
45 | 2704743.6209 | 1227952.8157 | 2704789.5362 | 1227945.562
46 | 2704821.468 | 1227940.5174 | 2704789.5362 | 1227945.562
47 | 2704711.7635 | 1227982.5992 | 2704709.6792 | 1227982.5959 | 2704697.1217 | 1227982.9529 | 2704696.0669 | 1227983.0233
48 | 2704685.9784 | 1228019.206 | 2704686.3266 | 1228018.8007 | 2704689.0716 | 1228015.7134 | 2704711.0859 | 1227990.9491 | 2704711.7635 | 1227982.5992
49 | 2704865.8899 | 1227933.4997 | 2704821.468 | 1227940.5174
50 | 2704866.133 | 1227912.4105 | 2704865.8899 | 1227933.4997
51 | 2704525.3234 | 1227755.4368 | 2704555.2886 | 1227738.8265
52 | 2704503.507 | 1227764.4977 | 2704483.6825 | 1227755.8031
53 | 2704441.3279 | 1227740.5769 | 2704463.229 | 1227746.8328 | 2704483.6825 | 1227755.8031
54 | 2704441.3279 | 1227740.5769 | 2704444.9773 | 1227733.0354 | 2704453.7685 | 1227727.9193 | 2704475.7088 | 1227725.4805 | 2704526.6868 | 1227713.5337 | 2704531.1042 | 1227710.1755 | 2704531.5679 | 1227704.9242
55 | 2704531.5679 | 1227704.9242 | 2704531.5679 | 1227704.9242 | 2704525.9203 | 1227702.7034
56 | 2704866.133 | 1227912.4105 | 2704868.8055 | 1227883.2995
57 | 2704808.7705 | 1227813.7855 | 2704782.7973 | 1227815.8148
58 | 2704777.8837 | 1227816.1987 | 2704782.7973 | 1227815.8148
59 | 2704772.6022 | 1227730.8617 | 2704755.7471 | 1227734.0299
60 | 2704772.6022 | 1227730.8617 | 2704786.1062 | 1227728.3235
61 | 2704739.3406 | 1227737.1137 | 2704755.7471 | 1227734.0299
62 | 2704790.4 | 1227727.5164 | 2704786.1062 | 1227728.3235
63 | 2704499.2636 | 1227698.5948 | 2704502.3347 | 1227699.2397 | 2704523.6941 | 1227701.828 | 2704525.9203 | 1227702.7034
64 | 2704499.2636 | 1227698.5948 | 2704490.4156 | 1227551.543
65 | 2704490.4156 | 1227551.543 | 2704495.4915 | 1227548.5576
66 | 2704436.3242 | 1227433.2395 | 2704495.4915 | 1227548.5576
67 | 2704436.3242 | 1227433.2395 | 2704430.7994 | 1227428.6163
68 | 2704430.7994 | 1227428.6163 | 2704430.7994 | 1227428.6163 | 2704432.6843 | 1227414.9504 | 2704432.987 | 1227399.3609
69 | 2704273.6949 | 1227199.2577 | 2704242.9203 | 1227204.4862
70 | 2704379.4353 | 1227187.3918 | 2704273.6949 | 1227199.2577
71 | 2704273.6949 | 1227199.2577 | 2704274.9287 | 1227206.707 | 2704299.6275 | 1227214.7792 | 2704299.8005 | 1227220.0417 | 2704307.7019 | 1227222.444
72 | 2704379.4353 | 1227187.3918 | 2704375.7095 | 1227200.5695 | 2704367.6158 | 1227235.4312 | 2704366.2449 | 1227257.8237 | 2704380.3206 | 1227266.2249
73 | 2704307.7019 | 1227222.444 | 2704312.2786 | 1227223.8354
74 | 2704380.3206 | 1227266.2249 | 2704387.1668 | 1227270.3111 | 2704389.9035 | 1227276.6619
75 | 2704389.9035 | 1227276.6619 | 2704432.6246 | 1227383.9243
76 | 2704432.6246 | 1227383.9243 | 2704433.2403 | 1227386.3167
77 | 2704433.2403 | 1227386.3167 | 2704433.2403 | 1227386.3167 | 2704432.987 | 1227399.3609

## bus_geodata
| x | y | coords
0 | 2704578.0793 | 1227913.1499
1 | 2704573.5851 | 1227874.4996
2 | 2704550.6662 | 1227974.8491
3 | 2704557.2151 | 1227875.7128
4 | 2704586.7905 | 1227873.5199
5 | 2704466.7074 | 1227952.5082
6 | 2704541.1357 | 1227875.9081
7 | 2704631.8148 | 1227882.7943
8 | 2704585.1655 | 1227847.6627
9 | 2704611.3987 | 1227910.6801
10 | 2704612.3816 | 1227924.1741
11 | 2704610.8647 | 1227905.2778
12 | 2704638.0284 | 1227956.5603
13 | 2704635.8679 | 1227930.9105
14 | 2704671.2592 | 1227953.7984
15 | 2704539.8923 | 1227872.9174
16 | 2704584.126 | 1227831.5307
17 | 2704699.2632 | 1227956.0187
18 | 2704648.8748 | 1228027.2152
19 | 2704655.664 | 1228056.9563
20 | 2704676.2727 | 1228096.0701
21 | 2704661.5237 | 1228048.7243
22 | 2704669.4751 | 1228038.3352
23 | 2704594.5782 | 1227818.1712
24 | 2704630.9552 | 1227815.4382
25 | 2704662.8771 | 1227815.1368
26 | 2704578.9826 | 1227808.9569
27 | 2704665.6501 | 1227815.2244
28 | 2704670.0629 | 1227760.6875
29 | 2704566.0267 | 1227794.0181
30 | 2704680.1019 | 1227815.6813
31 | 2704695.3115 | 1227739.2926
32 | 2704554.9503 | 1227788.9907
33 | 2704732.9716 | 1227817.0605
34 | 2704703.8841 | 1227737.8132
35 | 2704510.0048 | 1227767.3917
36 | 2704736.4763 | 1227817.1446
37 | 2704726.797 | 1227733.859
38 | 2704777.9776 | 1227969.4495
39 | 2704789.5362 | 1227945.562
40 | 2704711.7635 | 1227982.5992
41 | 2704696.0669 | 1227983.0233
42 | 2704685.9784 | 1228019.206
43 | 2704743.6209 | 1227952.8157
44 | 2704821.468 | 1227940.5174
45 | 2704865.8899 | 1227933.4997
46 | 2704525.3234 | 1227755.4368
47 | 2704503.507 | 1227764.4977
48 | 2704555.2886 | 1227738.8265
49 | 2704483.6825 | 1227755.8031
50 | 2704441.3279 | 1227740.5769
51 | 2704531.5679 | 1227704.9242
52 | 2704868.8055 | 1227883.2995
53 | 2704866.133 | 1227912.4105
54 | 2704808.7705 | 1227813.7855
55 | 2704782.7973 | 1227815.8148
56 | 2704729.12 | 1227837.9407
57 | 2704777.8837 | 1227816.1987
58 | 2704772.6022 | 1227730.8617
59 | 2704755.7471 | 1227734.0299
60 | 2704786.1062 | 1227728.3235
61 | 2704739.3406 | 1227737.1137
62 | 2704790.4 | 1227727.5164
63 | 2704525.9203 | 1227702.7034
64 | 2704499.2636 | 1227698.5948
65 | 2704490.4156 | 1227551.543
66 | 2704495.4915 | 1227548.5576
67 | 2704436.3242 | 1227433.2395
68 | 2704430.7994 | 1227428.6163
69 | 2704242.9203 | 1227204.4862
70 | 2704273.6949 | 1227199.2577
71 | 2704379.4353 | 1227187.3918
72 | 2704307.7019 | 1227222.444
73 | 2704380.3206 | 1227266.2249
74 | 2704312.2786 | 1227223.8354
75 | 2704389.9035 | 1227276.6619
76 | 2704432.6246 | 1227383.9243
77 | 2704433.2403 | 1227386.3167
78 | 2704432.987 | 1227399.3609
79 | 2704594.5782 | 1227818.1712

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9865 | -0.25854 | 0.021569 | 0.0054057
1 | 0.98744 | -0.24017 | 0 | 0
2 | 0.98612 | -0.26593 | 0 | 0
3 | 0.98739 | -0.24125 | 0 | 0
4 | 0.98781 | -0.23308 | 0 | 0
5 | 0.98574 | -0.27339 | 0.0047854 | 0.0011993
6 | 0.98733 | -0.24233 | 0.0012825 | 0.00032142
7 | 0.98363 | -0.31376 | 0.021694 | 0.0054371
8 | 0.99094 | -0.1727 | 0.018801 | 0.0047119
9 | 0.9865 | -0.2586 | 0 | 0
10 | 0.98642 | -0.26008 | 0.0061028 | 0.0015295
11 | 0.98641 | -0.26029 | 0.017342 | 0.0043463
12 | 0.97994 | -0.3855 | 0 | 0
13 | 0.98113 | -0.36231 | 0.0059763 | 0.0014978
14 | 0.97841 | -0.41554 | 0 | 0
15 | 0.98732 | -0.24247 | 0.0024172 | 0.0006058
16 | 0.99206 | -0.15125 | 0 | 0
17 | 0.97708 | -0.44151 | 0.0078622 | 0.0019705
18 | 0.97544 | -0.4738 | 0.0018123 | 0.00045421
19 | 0.97551 | -0.47238 | 0 | 0
20 | 0.97508 | -0.48103 | 0.0091299 | 0.0022882
21 | 0.97562 | -0.47035 | 0.00088325 | 0.00022136
22 | 0.97576 | -0.46752 | 0.00061564 | 0.00015429
23 | 0.99293 | -0.13462 | 0 | 0
24 | 0.99653 | -0.065875 | 0.033497 | 0.0083952
25 | 1 | 0 | -0.61314 | -0.15607
26 | 0.99185 | -0.15527 | 0 | 0
27 | 0.99969 | -0.0059152 | 0.032381 | 0.0081154
28 | 0.99352 | -0.12343 | 0.0086978 | 0.0021799
29 | 0.99081 | -0.1753 | 0.027555 | 0.0069061
30 | 0.9985 | -0.028614 | 0.0055379 | 0.0013879
31 | 0.98943 | -0.20217 | 0.016036 | 0.0040189
32 | 0.99028 | -0.18561 | 0.01937 | 0.0048546
33 | 0.99443 | -0.10694 | 0.027533 | 0.0069003
34 | 0.9886 | -0.21818 | 0.0062398 | 0.0015639
35 | 0.98837 | -0.22226 | 0 | 0
36 | 0.99425 | -0.11045 | 0 | 0
37 | 0.98652 | -0.25851 | 0.0039156 | 0.00098133
38 | 0.97436 | -0.49506 | 0.0094678 | 0.0023729
39 | 0.97459 | -0.49045 | 0.0017895 | 0.00044849
40 | 0.97659 | -0.45125 | 0 | 0
41 | 0.97677 | -0.44769 | 0 | 0
42 | 0.97605 | -0.46176 | 0 | 0
43 | 0.97587 | -0.46542 | 0 | 0
44 | 0.97405 | -0.50121 | 0.0093947 | 0.0023545
45 | 0.97368 | -0.50842 | 0 | 0
46 | 0.98758 | -0.23768 | 0.027557 | 0.0069064
47 | 0.9882 | -0.22564 | 0 | 0
48 | 0.98707 | -0.24765 | 0.016287 | 0.0040819
49 | 0.9874 | -0.2411 | 0.011013 | 0.0027601
50 | 0.98595 | -0.26895 | 0 | 0
51 | 0.97931 | -0.39816 | 0.015231 | 0.0038171
52 | 0.97327 | -0.5165 | 0.0087243 | 0.0021865
53 | 0.97351 | -0.5118 | 0 | 0
54 | 0.99283 | -0.13794 | 0.0048447 | 0.0012142
55 | 0.99294 | -0.13571 | 0.0041891 | 0.0010499
56 | 0.99375 | -0.12011 | 0.023367 | 0.0058563
57 | 0.99299 | -0.13492 | 0.024431 | 0.0061229
58 | 0.98324 | -0.32231 | 0.012768 | 0.0032
59 | 0.98426 | -0.30241 | 0.0085791 | 0.0021501
60 | 0.98259 | -0.33512 | 0.010903 | 0.0027326
61 | 0.98538 | -0.28051 | 0.02013 | 0.005045
62 | 0.98242 | -0.33833 | 0.040753 | 0.010214
63 | 0.97901 | -0.40409 | 0.017684 | 0.0044321
64 | 0.97811 | -0.42183 | 0.017698 | 0.0044356
65 | 0.97559 | -0.47117 | 0.0022056 | 0.00055276
66 | 0.9755 | -0.47291 | 0.0032123 | 0.00080508
67 | 0.97395 | -0.50363 | 0.0012875 | 0.00032267
68 | 0.97387 | -0.50516 | 0.0037291 | 0.00093461
69 | 0.97184 | -0.54527 | 0.0013729 | 0.00034409
70 | 0.97188 | -0.54448 | 0 | 0
71 | 0.97239 | -0.53447 | 0 | 0
72 | 0.97172 | -0.54773 | 0.0022375 | 0.00056076
73 | 0.97281 | -0.52614 | 0.00045784 | 0.00011474
74 | 0.97171 | -0.54786 | 0.0015 | 0.00037594
75 | 0.97288 | -0.52461 | 0.00054603 | 0.00013685
76 | 0.97354 | -0.5116 | 0.0010555 | 0.00026453
77 | 0.97356 | -0.51127 | 0.00049699 | 0.00012456
78 | 0.97365 | -0.50943 | 0.00021624 | 5.4195e-05
79 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.026358 | -0.006605 | 0.026381 | 0.0066193 | 2.3092e-05 | 1.4281e-05 | 0.039757 | 0.039757 | 0.039757 | 0.9865 | -0.25854 | 0.98744 | -0.24017 | 10.9223
1 | 0.0047888 | 0.0011993 | -0.0047871 | -0.0011993 | 1.6843e-06 | -2.0708e-08 | 0.007223 | 0.0072234 | 0.0072234 | 0.9865 | -0.25854 | 0.98612 | -0.26593 | 1.9845
2 | 0.0037 | 0.00092701 | -0.0036999 | -0.0009271 | 1.9081e-07 | -8.7236e-08 | 0.0055756 | 0.0055757 | 0.0055757 | 0.98744 | -0.24017 | 0.98739 | -0.24125 | 1.5318
3 | -0.030081 | -0.0075463 | 0.030091 | 0.0075526 | 1.0175e-05 | 6.343e-06 | 0.045333 | 0.045333 | 0.045333 | 0.98744 | -0.24017 | 0.98781 | -0.23308 | 12.4541
4 | 0.0047871 | 0.0011993 | -0.0047854 | -0.0011993 | 1.7001e-06 | -1.9926e-08 | 0.0072234 | 0.0072238 | 0.0072238 | 0.98612 | -0.26593 | 0.98574 | -0.27339 | 1.9846
5 | 0.0036999 | 0.0009271 | -0.0036997 | -0.00092719 | 1.8931e-07 | -8.6521e-08 | 0.0055757 | 0.0055758 | 0.0055758 | 0.98739 | -0.24125 | 0.98733 | -0.24233 | 1.5318
6 | 0.078081 | 0.019845 | -0.077778 | -0.019652 | 0.00030209 | 0.0001926 | 0.11772 | 0.11772 | 0.11772 | 0.98781 | -0.23308 | 0.98363 | -0.31376 | 32.3402
7 | -0.13165 | -0.033292 | 0.13203 | 0.033536 | 0.00038249 | 0.00024446 | 0.19842 | 0.19842 | 0.19842 | 0.98781 | -0.23308 | 0.99094 | -0.1727 | 54.5101
8 | 0.023475 | 0.0058942 | -0.023447 | -0.0058767 | 2.8549e-05 | 1.7493e-05 | 0.035366 | 0.035367 | 0.035367 | 0.98781 | -0.23308 | 0.9865 | -0.2586 | 9.7161
9 | 0.0024172 | 0.00060577 | -0.0024172 | -0.0006058 | 1.6301e-08 | -3.1458e-08 | 0.003643 | 0.003643 | 0.003643 | 0.98733 | -0.24233 | 0.98732 | -0.24247 | 1.0008
10 | 0.056084 | 0.014215 | -0.055953 | -0.014132 | 0.00013052 | 8.292e-05 | 0.084899 | 0.0849 | 0.0849 | 0.98363 | -0.31376 | 0.98113 | -0.36231 | 23.3241
11 | -0.15083 | -0.038248 | 0.15099 | 0.038347 | 0.0001557 | 9.9232e-05 | 0.22665 | 0.22665 | 0.22665 | 0.99094 | -0.1727 | 0.99206 | -0.15125 | 31.1329
12 | 0.0061032 | 0.0015296 | -0.0061028 | -0.0015295 | 4.3007e-07 | 1.0249e-07 | 0.009206 | 0.009206 | 0.009206 | 0.9865 | -0.2586 | 0.98642 | -0.26008 | 2.5291
13 | 0.017343 | 0.0043471 | -0.017342 | -0.0043463 | 1.3933e-06 | 8.2241e-07 | 0.026161 | 0.026161 | 0.026161 | 0.9865 | -0.2586 | 0.98641 | -0.26029 | 7.187
14 | -0.049922 | -0.012599 | 0.049977 | 0.012634 | 5.5514e-05 | 3.5204e-05 | 0.075836 | 0.075836 | 0.075836 | 0.97994 | -0.3855 | 0.98113 | -0.36231 | 20.8341
15 | 0.049922 | 0.012599 | -0.04985 | -0.012554 | 7.1705e-05 | 4.5473e-05 | 0.075836 | 0.075836 | 0.075836 | 0.97994 | -0.3855 | 0.97841 | -0.41554 | 20.8341
16 | 0.04985 | 0.012554 | -0.049788 | -0.012514 | 6.1824e-05 | 3.9208e-05 | 0.075836 | 0.075836 | 0.075836 | 0.97841 | -0.41554 | 0.97708 | -0.44151 | 20.8342
17 | -0.15099 | -0.038347 | 0.15111 | 0.038424 | 0.00012092 | 7.6661e-05 | 0.22665 | 0.22665 | 0.22665 | 0.99206 | -0.15125 | 0.99293 | -0.13462 | 20.7553
18 | 0.029463 | 0.0074147 | -0.029429 | -0.0073937 | 3.3625e-05 | 2.0963e-05 | 0.04488 | 0.044881 | 0.044881 | 0.97708 | -0.44151 | 0.97587 | -0.46542 | 12.3299
19 | 0.012463 | 0.0031292 | -0.012459 | -0.0031272 | 3.6745e-06 | 2.0112e-06 | 0.018982 | 0.018982 | 0.018982 | 0.97708 | -0.44151 | 0.97677 | -0.44769 | 5.215
20 | -0.0018123 | -0.00045421 | 0.0018124 | 0.00045376 | 1.2291e-07 | -4.567e-07 | 0.0027647 | 0.0027645 | 0.0027647 | 0.97544 | -0.4738 | 0.97551 | -0.47238 | 0.75952
21 | 0.0091337 | 0.0022899 | -0.0091299 | -0.0022882 | 3.7632e-06 | 1.7633e-06 | 0.013933 | 0.013933 | 0.013933 | 0.97551 | -0.47238 | 0.97508 | -0.48103 | 3.8277
22 | -0.010946 | -0.0027437 | 0.010947 | 0.0027442 | 1.0564e-06 | 5.4992e-07 | 0.016697 | 0.016697 | 0.016697 | 0.97551 | -0.47238 | 0.97562 | -0.47035 | 4.5871
23 | -0.01183 | -0.0029656 | 0.011832 | 0.0029665 | 1.599e-06 | 8.5978e-07 | 0.018044 | 0.018044 | 0.018044 | 0.97562 | -0.47035 | 0.97576 | -0.46752 | 4.9572
24 | -0.012448 | -0.0031208 | 0.012451 | 0.0031226 | 3.414e-06 | 1.8693e-06 | 0.018983 | 0.018983 | 0.018983 | 0.97576 | -0.46752 | 0.97605 | -0.46176 | 5.2151
25 | 0.1721 | 0.043652 | -0.17193 | -0.043544 | 0.00017068 | 0.00010844 | 0.25809 | 0.25809 | 0.25809 | 0.99293 | -0.13462 | 0.99185 | -0.15527 | 23.6348
26 | -0.3232 | -0.082076 | 0.32428 | 0.082762 | 0.0010732 | 0.00068542 | 0.48474 | 0.48474 | 0.48474 | 0.99293 | -0.13462 | 0.99653 | -0.065875 | 44.39
27 | -0.35777 | -0.091157 | 0.35891 | 0.091886 | 0.0011411 | 0.00072906 | 0.53476 | 0.53476 | 0.53476 | 0.99653 | -0.065875 | 1 | 0 | 48.9703
28 | 0.12279 | 0.030971 | -0.12276 | -0.030949 | 3.4761e-05 | 2.221e-05 | 0.18279 | 0.18279 | 0.18279 | 1 | 0 | 0.99969 | -0.0059152 | 50.216
29 | 0.12979 | 0.033213 | -0.12902 | -0.032721 | 0.00077056 | 0.00049244 | 0.19337 | 0.19337 | 0.19337 | 1 | 0 | 0.99352 | -0.12343 | 53.1237
30 | 0.17193 | 0.043544 | -0.17176 | -0.043439 | 0.00016516 | 0.00010494 | 0.25809 | 0.25809 | 0.25809 | 0.99185 | -0.15527 | 0.99081 | -0.1753 | 23.6348
31 | 0.090377 | 0.022833 | -0.090279 | -0.022771 | 9.8216e-05 | 6.2669e-05 | 0.13459 | 0.13459 | 0.13459 | 0.99969 | -0.0059152 | 0.9985 | -0.028614 | 36.9748
32 | 0.12032 | 0.030541 | -0.11987 | -0.030251 | 0.00045391 | 0.00029002 | 0.18034 | 0.18034 | 0.18034 | 0.99352 | -0.12343 | 0.98943 | -0.20217 | 49.5449
33 | 0.1442 | 0.036533 | -0.14413 | -0.036488 | 7.1406e-05 | 4.523e-05 | 0.21671 | 0.21671 | 0.21671 | 0.99081 | -0.1753 | 0.99028 | -0.18561 | 19.8452
34 | 0.084741 | 0.021383 | -0.084424 | -0.021181 | 0.00031655 | 0.0002019 | 0.12634 | 0.12634 | 0.12634 | 0.9985 | -0.028614 | 0.99443 | -0.10694 | 34.7076
35 | 0.10383 | 0.026232 | -0.10375 | -0.026181 | 7.9622e-05 | 5.0846e-05 | 0.15623 | 0.15623 | 0.15623 | 0.98943 | -0.20217 | 0.9886 | -0.21818 | 42.9196
36 | 0.12476 | 0.031633 | -0.12454 | -0.031495 | 0.00021938 | 0.00013848 | 0.1876 | 0.1876 | 0.1876 | 0.99028 | -0.18561 | 0.98837 | -0.22226 | 17.1798
37 | 0.056892 | 0.014281 | -0.056882 | -0.014274 | 9.529e-06 | 6.0531e-06 | 0.085137 | 0.085137 | 0.085137 | 0.99443 | -0.10694 | 0.99425 | -0.11045 | 23.3894
38 | 0.097511 | 0.024617 | -0.097323 | -0.024497 | 0.00018799 | 0.00012002 | 0.14684 | 0.14684 | 0.14684 | 0.9886 | -0.21818 | 0.98652 | -0.25851 | 40.3394
39 | 0.043884 | 0.011013 | -0.043852 | -0.010993 | 3.2235e-05 | 2.0378e-05 | 0.066073 | 0.066073 | 0.066073 | 0.98837 | -0.22226 | 0.98758 | -0.23768 | 18.152
40 | 0.08066 | 0.020481 | -0.080647 | -0.020473 | 1.3101e-05 | 8.1117e-06 | 0.12153 | 0.12153 | 0.12153 | 0.98837 | -0.22226 | 0.9882 | -0.22564 | 11.1292
41 | 0.033504 | 0.0084116 | -0.033465 | -0.0083872 | 3.9062e-05 | 2.4463e-05 | 0.050149 | 0.050149 | 0.050149 | 0.99425 | -0.11045 | 0.99299 | -0.13492 | 13.7772
42 | 0.023378 | 0.0058628 | -0.023367 | -0.0058563 | 1.0762e-05 | 6.5839e-06 | 0.034989 | 0.034989 | 0.034989 | 0.99425 | -0.11045 | 0.99375 | -0.12011 | 9.6123
43 | 0.093407 | 0.023516 | -0.093309 | -0.023453 | 9.8129e-05 | 6.2634e-05 | 0.14093 | 0.14093 | 0.14093 | 0.98652 | -0.25851 | 0.98538 | -0.28051 | 38.7168
44 | -0.0094678 | -0.0023729 | 0.0094699 | 0.0023739 | 2.0804e-06 | 1.0009e-06 | 0.014459 | 0.014459 | 0.014459 | 0.97436 | -0.49506 | 0.97459 | -0.49045 | 3.9722
45 | -0.029394 | -0.0073718 | 0.029429 | 0.0073937 | 3.5113e-05 | 2.1892e-05 | 0.044881 | 0.044881 | 0.044881 | 0.97459 | -0.49045 | 0.97587 | -0.46542 | 12.3299
46 | 0.018135 | 0.0045495 | -0.018125 | -0.0045439 | 9.295e-06 | 5.5462e-06 | 0.02769 | 0.02769 | 0.02769 | 0.97459 | -0.49045 | 0.97405 | -0.50121 | 7.6071
47 | -0.012457 | -0.003126 | 0.012459 | 0.0031272 | 2.1158e-06 | 1.1582e-06 | 0.018983 | 0.018982 | 0.018983 | 0.97659 | -0.45125 | 0.97677 | -0.44769 | 5.215
48 | 0.012457 | 0.003126 | -0.012451 | -0.0031226 | 6.2398e-06 | 3.416e-06 | 0.018983 | 0.018983 | 0.018983 | 0.97659 | -0.45125 | 0.97605 | -0.46176 | 5.215
49 | 0.0087307 | 0.0021894 | -0.0087277 | -0.002188 | 3.0003e-06 | 1.3606e-06 | 0.013338 | 0.013338 | 0.013338 | 0.97405 | -0.50121 | 0.97368 | -0.50842 | 3.6643
50 | 0.0087277 | 0.002188 | -0.0087263 | -0.0021874 | 1.4073e-06 | 6.3835e-07 | 0.013338 | 0.013338 | 0.013338 | 0.97368 | -0.50842 | 0.97351 | -0.5118 | 3.6644
51 | 0.016295 | 0.0040864 | -0.016287 | -0.0040819 | 7.745e-06 | 4.5187e-06 | 0.024552 | 0.024553 | 0.024553 | 0.98758 | -0.23768 | 0.98707 | -0.24765 | 6.7452
52 | 0.080647 | 0.020473 | -0.080587 | -0.020436 | 5.9948e-05 | 3.7813e-05 | 0.12153 | 0.12153 | 0.12153 | 0.9882 | -0.22564 | 0.9874 | -0.2411 | 16.6938
53 | 0.069574 | 0.017675 | -0.069481 | -0.017617 | 9.3137e-05 | 5.8455e-05 | 0.10493 | 0.10493 | 0.10493 | 0.9874 | -0.2411 | 0.98595 | -0.26895 | 14.4141
54 | 0.069481 | 0.017617 | -0.069052 | -0.017344 | 0.00042864 | 0.00027301 | 0.10493 | 0.10494 | 0.10494 | 0.98595 | -0.26895 | 0.97931 | -0.39816 | 28.8284
55 | 0.053822 | 0.013527 | -0.053807 | -0.013517 | 1.5225e-05 | 9.6674e-06 | 0.081793 | 0.081793 | 0.081793 | 0.97931 | -0.39816 | 0.97901 | -0.40409 | 22.4707
56 | -0.0087243 | -0.0021865 | 0.0087263 | 0.0021874 | 1.9504e-06 | 8.8484e-07 | 0.013338 | 0.013338 | 0.013338 | 0.97327 | -0.5165 | 0.97351 | -0.5118 | 3.6644
57 | -0.0048447 | -0.0012142 | 0.0048452 | 0.0012142 | 5.1508e-07 | -7.2924e-09 | 0.0072611 | 0.007261 | 0.0072611 | 0.99283 | -0.13794 | 0.99294 | -0.13571 | 1.9948
58 | -0.0090343 | -0.0022641 | 0.0090346 | 0.0022642 | 3.3877e-07 | 1.5306e-07 | 0.013539 | 0.013539 | 0.013539 | 0.99294 | -0.13571 | 0.99299 | -0.13492 | 3.7194
59 | -0.064463 | -0.01617 | 0.064524 | 0.016209 | 6.1216e-05 | 3.896e-05 | 0.097562 | 0.097562 | 0.097562 | 0.98324 | -0.32231 | 0.98426 | -0.30241 | 26.8027
60 | 0.051694 | 0.01297 | -0.051663 | -0.01295 | 3.1541e-05 | 2.0012e-05 | 0.078239 | 0.078239 | 0.078239 | 0.98324 | -0.32231 | 0.98259 | -0.33512 | 21.4941
61 | -0.073103 | -0.018359 | 0.07318 | 0.018408 | 7.6482e-05 | 4.8736e-05 | 0.11053 | 0.11053 | 0.11053 | 0.98426 | -0.30241 | 0.98538 | -0.28051 | 30.3659
62 | 0.04076 | 0.010218 | -0.040753 | -0.010214 | 6.2425e-06 | 3.9399e-06 | 0.061727 | 0.061727 | 0.061727 | 0.98259 | -0.33512 | 0.98242 | -0.33833 | 16.9579
63 | 0.036122 | 0.0090851 | -0.036092 | -0.0090659 | 3.0585e-05 | 1.9235e-05 | 0.054915 | 0.054915 | 0.054915 | 0.97901 | -0.40409 | 0.97811 | -0.42183 | 15.0865
64 | 0.018394 | 0.0046302 | -0.01835 | -0.0046044 | 4.3281e-05 | 2.5856e-05 | 0.02799 | 0.027991 | 0.027991 | 0.97811 | -0.42183 | 0.97559 | -0.47117 | 7.6897
65 | 0.016145 | 0.0040516 | -0.016143 | -0.0040508 | 1.3393e-06 | 7.836e-07 | 0.024627 | 0.024627 | 0.024627 | 0.97559 | -0.47117 | 0.9755 | -0.47291 | 6.7655
66 | 0.012931 | 0.0032458 | -0.012912 | -0.0032353 | 1.8914e-05 | 1.049e-05 | 0.019727 | 0.019727 | 0.019727 | 0.9755 | -0.47291 | 0.97395 | -0.50363 | 5.4196
67 | 0.011625 | 0.0029126 | -0.011624 | -0.0029121 | 8.5211e-07 | 4.5571e-07 | 0.01776 | 0.01776 | 0.01776 | 0.97395 | -0.50363 | 0.97387 | -0.50516 | 4.8792
68 | 0.0078947 | 0.0019775 | -0.0078931 | -0.0019769 | 1.6035e-06 | 6.6063e-07 | 0.012062 | 0.012062 | 0.012062 | 0.97387 | -0.50516 | 0.97365 | -0.50943 | 3.3138
69 | -0.0013729 | -0.00034409 | 0.001373 | 0.00034373 | 5.1724e-08 | -3.537e-07 | 0.0021021 | 0.002102 | 0.0021021 | 0.97184 | -0.54527 | 0.97188 | -0.54448 | 0.57751
70 | -0.0051111 | -0.0012802 | 0.0051135 | 0.0012804 | 2.4361e-06 | 2.4365e-07 | 0.0078251 | 0.0078246 | 0.0078251 | 0.97188 | -0.54448 | 0.97239 | -0.53447 | 2.1498
71 | 0.0037381 | 0.00093644 | -0.0037375 | -0.00093665 | 5.7804e-07 | -2.1311e-07 | 0.0057231 | 0.0057233 | 0.0057233 | 0.97188 | -0.54448 | 0.97172 | -0.54773 | 1.5723
72 | -0.0051135 | -0.0012804 | 0.0051155 | 0.0012806 | 2.0274e-06 | 2.0162e-07 | 0.0078246 | 0.0078242 | 0.0078246 | 0.97239 | -0.53447 | 0.97281 | -0.52614 | 2.1496
73 | 0.0015 | 0.00037589 | -0.0015 | -0.00037594 | 9.465e-09 | -5.3199e-08 | 0.002297 | 0.002297 | 0.002297 | 0.97172 | -0.54773 | 0.97171 | -0.54786 | 0.63106
74 | -0.0055734 | -0.0013954 | 0.0055738 | 0.0013954 | 4.0571e-07 | 7.4793e-08 | 0.0085245 | 0.0085245 | 0.0085245 | 0.97281 | -0.52614 | 0.97288 | -0.52461 | 2.3419
75 | -0.0061198 | -0.0015323 | 0.0061236 | 0.0015333 | 3.7927e-06 | 9.9265e-07 | 0.0093596 | 0.0093591 | 0.0093596 | 0.97288 | -0.52461 | 0.97354 | -0.5116 | 2.5713
76 | -0.0071791 | -0.0017978 | 0.0071792 | 0.0017978 | 1.1153e-07 | 4.0661e-08 | 0.010972 | 0.010972 | 0.010972 | 0.97354 | -0.5116 | 0.97356 | -0.51127 | 3.0144
77 | -0.0076762 | -0.0019224 | 0.0076768 | 0.0019227 | 6.7339e-07 | 2.6873e-07 | 0.011732 | 0.011732 | 0.011732 | 0.97356 | -0.51127 | 0.97365 | -0.50943 | 3.2231

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.61314 | 0.15607

## res_load
| p_mw | q_mvar
0 | 0.021569 | 0.0054057
1 | 0.0047854 | 0.0011993
2 | 0.0012825 | 0.00032142
3 | 0.021694 | 0.0054371
4 | 0.018801 | 0.0047119
5 | 0.0061028 | 0.0015295
6 | 0.017342 | 0.0043463
7 | 0.0059763 | 0.0014978
8 | 0.0024172 | 0.0006058
9 | 0.0078622 | 0.0019705
10 | 0.0018123 | 0.00045421
11 | 0.0091299 | 0.0022882
12 | 0.00088325 | 0.00022136
13 | 0.00061564 | 0.00015429
14 | 0.033497 | 0.0083952
15 | 0.032381 | 0.0081154
16 | 0.0086978 | 0.0021799
17 | 0.027555 | 0.0069061
18 | 0.0055379 | 0.0013879
19 | 0.016036 | 0.0040189
20 | 0.01937 | 0.0048546
21 | 0.027533 | 0.0069003
22 | 0.0062398 | 0.0015639
23 | 0.0039156 | 0.00098133
24 | 0.0094678 | 0.0023729
25 | 0.0017895 | 0.00044849
26 | 0.0093947 | 0.0023545
27 | 0.027557 | 0.0069064
28 | 0.016287 | 0.0040819
29 | 0.011013 | 0.0027601
30 | 0.015231 | 0.0038171
31 | 0.0087243 | 0.0021865
32 | 0.0048447 | 0.0012142
33 | 0.0041891 | 0.0010499
34 | 0.023367 | 0.0058563
35 | 0.024431 | 0.0061229
36 | 0.012768 | 0.0032
37 | 0.0085791 | 0.0021501
38 | 0.010903 | 0.0027326
39 | 0.02013 | 0.005045
40 | 0.040753 | 0.010214
41 | 0.017684 | 0.0044321
42 | 0.017698 | 0.0044356
43 | 0.0022056 | 0.00055276
44 | 0.0032123 | 0.00080508
45 | 0.0012875 | 0.00032267
46 | 0.0037291 | 0.00093461
47 | 0.0013729 | 0.00034409
48 | 0.0022375 | 0.00056076
49 | 0.00045784 | 0.00011474
50 | 0.0015 | 0.00037594
51 | 0.00054603 | 0.00013685
52 | 0.0010555 | 0.00026453
53 | 0.00049699 | 0.00012456
54 | 0.00021624 | 5.4195e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1