## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1344-11_1_3_node_2 | 0.4 | n |  | TRUE
1 | bus_LV_1344-11_1_3_node_29 | 0.4 | n |  | TRUE
2 | bus_LV_1344-11_1_3_node_8 | 0.4 | n |  | TRUE
3 | bus_LV_1344-11_1_3_node_15 | 0.4 | n |  | TRUE
4 | bus_LV_1344-11_1_3_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_1344-11_1_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1344-11_1_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1344-11_1_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1344-11_1_3_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_1344-11_1_3_node_50 | 0.4 | n |  | TRUE
10 | bus_LV_1344-11_1_3_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1344-11_1_3_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_1344-11_1_3_node_31 | 0.4 | n |  | TRUE
13 | bus_LV_1344-11_1_3_node_49 | 0.4 | n |  | TRUE
14 | bus_LV_1344-11_1_3_node_34 | 0.4 | n |  | TRUE
15 | bus_LV_1344-11_1_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1344-11_1_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1344-11_1_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1344-11_1_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1344-11_1_3_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_1344-11_1_3_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1344-11_1_3_node_39 | 0.4 | n |  | TRUE
22 | bus_LV_1344-11_1_3_node_53 | 0.4 | n |  | TRUE
23 | bus_LV_1344-11_1_3_node_38 | 0.4 | n |  | TRUE
24 | bus_LV_1344-11_1_3_node_52 | 0.4 | n |  | TRUE
25 | bus_LV_1344-11_1_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1344-11_1_3_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_1344-11_1_3_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1344-11_1_3_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1344-11_1_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1344-11_1_3_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_1344-11_1_3_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_1344-11_1_3_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1344-11_1_3_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_1344-11_1_3_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_1344-11_1_3_node_37 | 0.4 | n |  | TRUE
36 | bus_LV_1344-11_1_3_node_55 | 0.4 | n |  | TRUE
37 | bus_LV_1344-11_1_3_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_1344-11_1_3_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_1344-11_1_3_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_1344-11_1_3_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_1344-11_1_3_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_1344-11_1_3_node_44 | 0.4 | n |  | TRUE
43 | bus_LV_1344-11_1_3_node_42 | 0.4 | n |  | TRUE
44 | bus_MV_18_0_node_28 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1344-11_1_3_load_2 | 0 | 0.0043681 | 0.0010947 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1344-11_1_3_load_29 | 1 | 0.0055199 | 0.0013834 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1344-11_1_3_load_15 | 3 | 0.0063365 | 0.0015881 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1344-11_1_3_load_13 | 4 | 0.018999 | 0.0047616 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1344-11_1_3_load_4 | 5 | 0.040709 | 0.010203 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1344-11_1_3_load_7 | 7 | 0.0025066 | 0.00062822 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1344-11_1_3_load_30 | 8 | 0.0019007 | 0.00047637 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1344-11_1_3_load_50 | 9 | 0.0069661 | 0.0017459 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1344-11_1_3_load_10 | 10 | 0.01759 | 0.0044086 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1344-11_1_3_load_36 | 11 | 0.0020237 | 0.00050718 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1344-11_1_3_load_31 | 12 | 0.0029647 | 0.00074303 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1344-11_1_3_load_49 | 13 | 0.012157 | 0.0030467 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1344-11_1_3_load_34 | 14 | 0.0017933 | 0.00044944 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1344-11_1_3_load_11 | 15 | 0.0037303 | 0.00093489 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1344-11_1_3_load_12 | 16 | 0.016333 | 0.0040935 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1344-11_1_3_load_14 | 17 | 0.01736 | 0.0043509 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1344-11_1_3_load_39 | 21 | 0.0029311 | 0.00073461 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1344-11_1_3_load_53 | 22 | 0.0055602 | 0.0013935 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1344-11_1_3_load_38 | 23 | 0.0083065 | 0.0020818 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1344-11_1_3_load_52 | 24 | 0.0041939 | 0.0010511 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1344-11_1_3_load_19 | 25 | 0.015215 | 0.0038133 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1344-11_1_3_load_20 | 26 | 0.0039963 | 0.0010016 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1344-11_1_3_load_22 | 28 | 0.016122 | 0.0040405 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1344-11_1_3_load_23 | 29 | 0.0036141 | 0.00090578 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1344-11_1_3_load_24 | 30 | 0.0060765 | 0.0015229 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1344-11_1_3_load_26 | 32 | 0.0052439 | 0.0013143 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1344-11_1_3_load_27 | 33 | 0.0044211 | 0.001108 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1344-11_1_3_load_28 | 34 | 0.01267 | 0.0031753 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1344-11_1_3_load_55 | 36 | 0.0082758 | 0.0020741 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1344-11_1_3_load_35 | 37 | 0.0044689 | 0.00112 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1344-11_1_3_load_32 | 38 | 0.001747 | 0.00043785 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1344-11_1_3_load_33 | 39 | 0.0039145 | 0.00098108 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1344-11_1_3_load_40 | 40 | 0.0035507 | 0.00088988 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1344-11_1_3_load_41 | 41 | 0.004102 | 0.0010281 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1344-11_1_3_load_42 | 43 | 0.0064985 | 0.0016287 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1344-11_1_3_line_0 |  | 0 | 1 | 0.023377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1344-11_1_3_line_1 |  | 1 | 2 | 0.034653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1344-11_1_3_line_2 |  | 2 | 9 | 0.030819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1344-11_1_3_line_3 |  | 3 | 4 | 0.020491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1344-11_1_3_line_4 |  | 4 | 15 | 0.046591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1344-11_1_3_line_5 |  | 5 | 6 | 0.0062885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1344-11_1_3_line_6 |  | 6 | 7 | 0.01926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1344-11_1_3_line_7 |  | 7 | 8 | 0.0070929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1344-11_1_3_line_8 |  | 8 | 12 | 0.023152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1344-11_1_3_line_9 |  | 9 | 13 | 0.001665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1344-11_1_3_line_10 |  | 10 | 11 | 0.0042735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1344-11_1_3_line_11 |  | 11 | 14 | 0.025073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1344-11_1_3_line_12 |  | 12 | 38 | 0.0044332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1344-11_1_3_line_13 |  | 13 | 28 | 0.037722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1344-11_1_3_line_14 |  | 14 | 39 | 0.028256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1344-11_1_3_line_15 |  | 15 | 16 | 0.045664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1344-11_1_3_line_16 |  | 16 | 17 | 0.069723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1344-11_1_3_line_17 |  | 17 | 18 | 0.052696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1344-11_1_3_line_18 |  | 18 | 19 | 0.026824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1344-11_1_3_line_19 |  | 18 | 20 | 0.08131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1344-11_1_3_line_20 |  | 19 | 21 | 0.04934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1344-11_1_3_line_21 |  | 20 | 22 | 0.054984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1344-11_1_3_line_22 |  | 21 | 23 | 0.011827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1344-11_1_3_line_23 |  | 22 | 24 | 0.02214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_1344-11_1_3_line_24 |  | 23 | 40 | 0.015739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1344-11_1_3_line_25 |  | 24 | 30 | 0.019082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_1344-11_1_3_line_26 |  | 25 | 26 | 0.050708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_1344-11_1_3_line_27 |  | 25 | 27 | 0.021937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_1344-11_1_3_line_28 |  | 26 | 28 | 0.0056124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_1344-11_1_3_line_29 |  | 27 | 29 | 0.014424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1344-11_1_3_line_30 |  | 27 | 30 | 0.0007805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_1344-11_1_3_line_31 |  | 29 | 31 | 0.041683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1344-11_1_3_line_32 |  | 31 | 32 | 0.05093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1344-11_1_3_line_33 |  | 31 | 33 | 0.018436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1344-11_1_3_line_34 |  | 31 | 34 | 0.032584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1344-11_1_3_line_35 |  | 32 | 35 | 0.0094249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1344-11_1_3_line_36 |  | 34 | 36 | 0.03426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1344-11_1_3_line_37 |  | 35 | 37 | 0.034393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1344-11_1_3_line_38 |  | 36 | 38 | 0.030823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1344-11_1_3_line_39 |  | 37 | 39 | 0.038351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1344-11_1_3_line_40 |  | 40 | 41 | 0.0068558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1344-11_1_3_line_41 |  | 41 | 42 | 0.025863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1344-11_1_3_line_42 |  | 42 | 43 | 0.019187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1344-11_1_3_trafo_22 | 0.63 MVA 20/0.4 kV | 44 | 28 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2707490.3595 | 1227105.8622 | 2707480.7209 | 1227084.5649
1 | 2707504.6476 | 1227137.4329 | 2707490.3595 | 1227105.8622
2 | 2707504.6476 | 1227137.4329 | 2707516.0609 | 1227166.0611
3 | 2707539.3561 | 1227126.5153 | 2707536.1467 | 1227119.2884 | 2707533.1324 | 1227107.0717
4 | 2707539.3561 | 1227126.5153 | 2707558.2657 | 1227169.0958
5 | 2707448.3087 | 1227142.519 | 2707442.0508 | 1227143.139
6 | 2707448.3087 | 1227142.519 | 2707455.3466 | 1227160.447
7 | 2707455.3466 | 1227160.447 | 2707457.9385 | 1227167.0494
8 | 2707466.3988 | 1227188.6007 | 2707457.9385 | 1227167.0494
9 | 2707516.6775 | 1227167.6077 | 2707516.0609 | 1227166.0611
10 | 2707395.9089 | 1227173.0709 | 2707394.8293 | 1227168.936
11 | 2707402.8585 | 1227197.1576 | 2707397.7996 | 1227180.3132 | 2707395.9089 | 1227173.0709
12 | 2707468.0188 | 1227192.7273 | 2707466.3988 | 1227188.6007
13 | 2707530.647 | 1227202.6478 | 2707516.6775 | 1227167.6077
14 | 2707402.8585 | 1227197.1576 | 2707408.2891 | 1227215.2399 | 2707412.3694 | 1227223.6808
15 | 2707558.2657 | 1227169.0958 | 2707560.3798 | 1227173.8563 | 2707580.6488 | 1227208.867
16 | 2707580.6488 | 1227208.867 | 2707599.2573 | 1227241.0096 | 2707619.3268 | 1227266.6776
17 | 2707651.4012 | 1227308.4812 | 2707642.7173 | 1227296.5929 | 2707619.3268 | 1227266.6776
18 | 2707673.5366 | 1227293.3593 | 2707666.3538 | 1227297.7771 | 2707664.3341 | 1227299.2194 | 2707654.4914 | 1227306.1131 | 2707651.4012 | 1227308.4812
19 | 2707593.933 | 1227365.996 | 2707644.414 | 1227315.082 | 2707651.4012 | 1227308.4812
20 | 2707673.5366 | 1227293.3593 | 2707664.9418 | 1227283.6631 | 2707659.1285 | 1227273.1501 | 2707654.937 | 1227249.1437
21 | 2707593.933 | 1227365.996 | 2707588.823 | 1227355.5735 | 2707573.9906 | 1227314.8118
22 | 2707654.937 | 1227249.1437 | 2707652.9028 | 1227237.4928
23 | 2707566.4198 | 1227294.0063 | 2707573.9906 | 1227314.8118
24 | 2707650.1957 | 1227221.9886 | 2707652.9028 | 1227237.4928
25 | 2707566.4198 | 1227294.0063 | 2707559.8947 | 1227276.0745
26 | 2707532.7254 | 1227207.8611 | 2707551.5041 | 1227254.964
27 | 2707559.6278 | 1227275.341 | 2707551.5041 | 1227254.964
28 | 2707530.647 | 1227202.6478 | 2707532.7254 | 1227207.8611
29 | 2707559.6278 | 1227275.341 | 2707545.3567 | 1227277.4347
30 | 2707559.8947 | 1227276.0745 | 2707559.6278 | 1227275.341
31 | 2707504.1143 | 1227283.4772 | 2707540.3303 | 1227278.1721 | 2707545.3567 | 1227277.4347
32 | 2707504.1143 | 1227283.4772 | 2707453.4114 | 1227288.2843
33 | 2707504.1143 | 1227283.4772 | 2707510.7921 | 1227300.6617
34 | 2707504.1143 | 1227283.4772 | 2707492.3687 | 1227254.7545 | 2707491.8012 | 1227253.3091
35 | 2707444.0286 | 1227289.1739 | 2707453.4114 | 1227288.2843
36 | 2707479.282 | 1227221.4183 | 2707491.8012 | 1227253.3091
37 | 2707444.0286 | 1227289.1739 | 2707429.0604 | 1227258.2093
38 | 2707468.0188 | 1227192.7273 | 2707479.282 | 1227221.4183
39 | 2707429.0604 | 1227258.2093 | 2707412.3694 | 1227223.6808
40 | 2707649.0165 | 1227215.235 | 2707650.1957 | 1227221.9886
41 | 2707644.5681 | 1227189.7574 | 2707649.0165 | 1227215.235
42 | 2707644.5681 | 1227189.7574 | 2707662.5326 | 1227183.0172

## bus_geodata
| x | y | coords
0 | 2707480.7209 | 1227084.5649
1 | 2707490.3595 | 1227105.8622
2 | 2707504.6476 | 1227137.4329
3 | 2707533.1324 | 1227107.0717
4 | 2707539.3561 | 1227126.5153
5 | 2707442.0508 | 1227143.139
6 | 2707448.3087 | 1227142.519
7 | 2707455.3466 | 1227160.447
8 | 2707457.9385 | 1227167.0494
9 | 2707516.0609 | 1227166.0611
10 | 2707394.8293 | 1227168.936
11 | 2707395.9089 | 1227173.0709
12 | 2707466.3988 | 1227188.6007
13 | 2707516.6775 | 1227167.6077
14 | 2707402.8585 | 1227197.1576
15 | 2707558.2657 | 1227169.0958
16 | 2707580.6488 | 1227208.867
17 | 2707619.3268 | 1227266.6776
18 | 2707651.4012 | 1227308.4812
19 | 2707673.5366 | 1227293.3593
20 | 2707593.933 | 1227365.996
21 | 2707654.937 | 1227249.1437
22 | 2707573.9906 | 1227314.8118
23 | 2707652.9028 | 1227237.4928
24 | 2707566.4198 | 1227294.0063
25 | 2707551.5041 | 1227254.964
26 | 2707532.7254 | 1227207.8611
27 | 2707559.6278 | 1227275.341
28 | 2707530.647 | 1227202.6478
29 | 2707545.3567 | 1227277.4347
30 | 2707559.8947 | 1227276.0745
31 | 2707504.1143 | 1227283.4772
32 | 2707453.4114 | 1227288.2843
33 | 2707510.7921 | 1227300.6617
34 | 2707491.8012 | 1227253.3091
35 | 2707444.0286 | 1227289.1739
36 | 2707479.282 | 1227221.4183
37 | 2707429.0604 | 1227258.2093
38 | 2707468.0188 | 1227192.7273
39 | 2707412.3694 | 1227223.6808
40 | 2707650.1957 | 1227221.9886
41 | 2707649.0165 | 1227215.235
42 | 2707644.5681 | 1227189.7574
43 | 2707662.5326 | 1227183.0172
44 | 2707504.6476 | 1227137.4329

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9983 | -0.032687 | 0.0043681 | 0.0010947
1 | 0.99839 | -0.030901 | 0.0055199 | 0.0013834
2 | 0.9987 | -0.02491 | 0 | 0
3 | 0.97011 | -0.57676 | 0.0063365 | 0.0015881
4 | 0.97023 | -0.57436 | 0.018999 | 0.0047616
5 | 0.9781 | -0.42124 | 0.040709 | 0.010203
6 | 0.97834 | -0.41657 | 0 | 0
7 | 0.97907 | -0.40231 | 0.0025066 | 0.00062822
8 | 0.97935 | -0.39673 | 0.0019007 | 0.00047637
9 | 0.99898 | -0.019585 | 0.0069661 | 0.0017459
10 | 0.98109 | -0.36304 | 0.01759 | 0.0044086
11 | 0.98115 | -0.36168 | 0.0020237 | 0.00050718
12 | 0.98032 | -0.37777 | 0.0029647 | 0.00074303
13 | 0.99901 | -0.019095 | 0.012157 | 0.0030467
14 | 0.98161 | -0.35278 | 0.0017933 | 0.00044944
15 | 0.97133 | -0.55252 | 0.0037303 | 0.00093489
16 | 0.97257 | -0.52803 | 0.016333 | 0.0040935
17 | 0.97553 | -0.46988 | 0.01736 | 0.0043509
18 | 0.97861 | -0.40949 | 0 | 0
19 | 0.97798 | -0.4219 | 0 | 0
20 | 0.98529 | -0.27992 | 0 | 0
21 | 0.97682 | -0.44476 | 0.0029311 | 0.00073461
22 | 0.98981 | -0.19328 | 0.0055602 | 0.0013935
23 | 0.97657 | -0.44961 | 0.0083065 | 0.0020818
24 | 0.99078 | -0.17484 | 0.0041939 | 0.0010511
25 | 0.99391 | -0.11529 | 0.015215 | 0.0038133
26 | 0.99938 | -0.011602 | 0.0039963 | 0.0010016
27 | 0.99169 | -0.15755 | 0 | 0
28 | 1 | 0 | -0.27216 | -0.069517
29 | 0.99017 | -0.1867 | 0.0036141 | 0.00090578
30 | 0.99165 | -0.15827 | 0.0060765 | 0.0015229
31 | 0.98592 | -0.26874 | 0 | 0
32 | 0.98427 | -0.30079 | 0.0052439 | 0.0013143
33 | 0.98584 | -0.2702 | 0.0044211 | 0.001108
34 | 0.98378 | -0.31018 | 0.01267 | 0.0031753
35 | 0.98401 | -0.30585 | 0 | 0
36 | 0.98194 | -0.3461 | 0.0082758 | 0.0020741
37 | 0.98307 | -0.32431 | 0.0044689 | 0.00112
38 | 0.98052 | -0.37391 | 0.001747 | 0.00043785
39 | 0.98217 | -0.34184 | 0.0039145 | 0.00098108
40 | 0.97636 | -0.45368 | 0.0035507 | 0.00088988
41 | 0.9763 | -0.45501 | 0.004102 | 0.0010281
42 | 0.97614 | -0.45809 | 0 | 0
43 | 0.97602 | -0.46037 | 0.0064985 | 0.0016287
44 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0043681 | -0.0010947 | 0.0043684 | 0.0010947 | 3.716e-07 | -6.7848e-08 | 0.0065108 | 0.0065107 | 0.0065108 | 0.9983 | -0.032687 | 0.99839 | -0.030901 | 1.7887
1 | -0.0098884 | -0.0024781 | 0.0098912 | 0.0024794 | 2.8225e-06 | 1.3531e-06 | 0.014738 | 0.014738 | 0.014738 | 0.99839 | -0.030901 | 0.9987 | -0.02491 | 4.0488
2 | -0.0098912 | -0.0024794 | 0.0098937 | 0.0024807 | 2.5102e-06 | 1.2031e-06 | 0.014738 | 0.014737 | 0.014738 | 0.9987 | -0.02491 | 0.99898 | -0.019585 | 4.0488
3 | -0.0063365 | -0.0015881 | 0.0063372 | 0.0015883 | 7.2585e-07 | 2.1152e-07 | 0.0097193 | 0.0097192 | 0.0097193 | 0.97011 | -0.57676 | 0.97023 | -0.57436 | 2.6701
4 | -0.025336 | -0.0063499 | 0.025363 | 0.0063662 | 2.638e-05 | 1.6307e-05 | 0.038857 | 0.038857 | 0.038857 | 0.97023 | -0.57436 | 0.97133 | -0.55252 | 10.6751
5 | -0.040709 | -0.010203 | 0.040718 | 0.010208 | 9.0448e-06 | 5.7097e-06 | 0.061931 | 0.061931 | 0.061931 | 0.9781 | -0.42124 | 0.97834 | -0.41657 | 17.0141
6 | -0.040718 | -0.010208 | 0.040746 | 0.010226 | 2.7702e-05 | 1.7487e-05 | 0.061931 | 0.061931 | 0.061931 | 0.97834 | -0.41657 | 0.97907 | -0.40231 | 17.0141
7 | -0.043252 | -0.010854 | 0.043264 | 0.010861 | 1.1496e-05 | 7.2679e-06 | 0.065741 | 0.065741 | 0.065741 | 0.97907 | -0.40231 | 0.97935 | -0.39673 | 18.0607
8 | -0.045164 | -0.011338 | 0.045205 | 0.011364 | 4.0892e-05 | 2.5879e-05 | 0.068629 | 0.068629 | 0.068629 | 0.97935 | -0.39673 | 0.98032 | -0.37777 | 18.8541
9 | -0.01686 | -0.0042265 | 0.01686 | 0.0042268 | 3.9378e-07 | 2.3022e-07 | 0.025114 | 0.025114 | 0.025114 | 0.99898 | -0.019585 | 0.99901 | -0.019095 | 6.8994
10 | -0.01759 | -0.0044086 | 0.017592 | 0.0044093 | 1.1407e-06 | 6.7608e-07 | 0.02668 | 0.02668 | 0.02668 | 0.98109 | -0.36304 | 0.98115 | -0.36168 | 7.3296
11 | -0.019615 | -0.0049164 | 0.019624 | 0.0049215 | 8.3208e-06 | 5.0085e-06 | 0.029749 | 0.029749 | 0.029749 | 0.98115 | -0.36168 | 0.98161 | -0.35278 | 8.1727
12 | -0.04817 | -0.012107 | 0.048179 | 0.012112 | 8.8905e-06 | 5.634e-06 | 0.073129 | 0.073129 | 0.073129 | 0.98032 | -0.37777 | 0.98052 | -0.37391 | 20.0904
13 | -0.029017 | -0.0072735 | 0.029043 | 0.0072899 | 2.6425e-05 | 1.6418e-05 | 0.043221 | 0.043221 | 0.043221 | 0.99901 | -0.019095 | 1 | 0 | 11.8739
14 | -0.021417 | -0.0053709 | 0.021428 | 0.0053777 | 1.1169e-05 | 6.7908e-06 | 0.032467 | 0.032467 | 0.032467 | 0.98161 | -0.35278 | 0.98217 | -0.34184 | 8.9195
15 | -0.029093 | -0.0073011 | 0.029127 | 0.0073223 | 3.4019e-05 | 2.1206e-05 | 0.044572 | 0.044572 | 0.044572 | 0.97133 | -0.55252 | 0.97257 | -0.52803 | 12.245
16 | -0.04546 | -0.011416 | 0.045586 | 0.011496 | 0.00012651 | 8.0101e-05 | 0.069561 | 0.06956 | 0.069561 | 0.97257 | -0.52803 | 0.97553 | -0.46988 | 19.1101
17 | -0.062947 | -0.015847 | 0.063129 | 0.015963 | 0.00018227 | 0.00011599 | 0.096041 | 0.09604 | 0.096041 | 0.97553 | -0.46988 | 0.97861 | -0.40949 | 26.3848
18 | 0.025442 | 0.006395 | -0.025427 | -0.0063857 | 1.5059e-05 | 9.3012e-06 | 0.038692 | 0.038692 | 0.038692 | 0.97861 | -0.40949 | 0.97798 | -0.4219 | 10.6297
19 | -0.088571 | -0.022358 | 0.089124 | 0.022711 | 0.0005535 | 0.00035321 | 0.13473 | 0.13473 | 0.13473 | 0.97861 | -0.40949 | 0.98529 | -0.27992 | 37.0144
20 | 0.025427 | 0.0063857 | -0.025399 | -0.0063686 | 2.77e-05 | 1.711e-05 | 0.038692 | 0.038692 | 0.038692 | 0.97798 | -0.4219 | 0.97682 | -0.44476 | 10.6298
21 | -0.089124 | -0.022711 | 0.089499 | 0.02295 | 0.00037429 | 0.00023884 | 0.13473 | 0.13473 | 0.13473 | 0.98529 | -0.27992 | 0.98981 | -0.19328 | 37.0143
22 | 0.022468 | 0.005634 | -0.022463 | -0.0056308 | 5.1959e-06 | 3.1773e-06 | 0.034227 | 0.034227 | 0.034227 | 0.97682 | -0.44476 | 0.97657 | -0.44961 | 9.4031
23 | -0.095059 | -0.024343 | 0.095144 | 0.024397 | 8.4997e-05 | 5.3828e-05 | 0.14309 | 0.14309 | 0.14309 | 0.98981 | -0.19328 | 0.99078 | -0.17484 | 19.6553
24 | 0.014156 | 0.003549 | -0.014154 | -0.0035475 | 2.7462e-06 | 1.5607e-06 | 0.021571 | 0.021571 | 0.021571 | 0.97657 | -0.44961 | 0.97636 | -0.45368 | 5.926
25 | -0.099338 | -0.025448 | 0.099417 | 0.025499 | 7.9848e-05 | 5.0611e-05 | 0.14939 | 0.14939 | 0.14939 | 0.99078 | -0.17484 | 0.99165 | -0.15827 | 20.5204
26 | -0.23614 | -0.060378 | 0.23733 | 0.061139 | 0.0011912 | 0.00076106 | 0.35396 | 0.35396 | 0.35396 | 0.99391 | -0.11529 | 0.99938 | -0.011602 | 48.6212
27 | 0.22093 | 0.056564 | -0.22047 | -0.056276 | 0.00045114 | 0.00028816 | 0.33118 | 0.33118 | 0.33118 | 0.99391 | -0.11529 | 0.99169 | -0.15755 | 45.4923
28 | -0.24133 | -0.06214 | 0.24146 | 0.062227 | 0.00013631 | 8.7094e-05 | 0.35991 | 0.35991 | 0.35991 | 0.99938 | -0.011602 | 1 | 0 | 49.4385
29 | 0.11498 | 0.029252 | -0.11482 | -0.029149 | 0.00016128 | 0.00010303 | 0.17268 | 0.17268 | 0.17268 | 0.99169 | -0.15755 | 0.99017 | -0.1867 | 47.4388
30 | 0.1055 | 0.027024 | -0.10549 | -0.027022 | 3.6768e-06 | 2.333e-06 | 0.15851 | 0.15851 | 0.15851 | 0.99169 | -0.15755 | 0.99165 | -0.15827 | 21.7729
31 | 0.1112 | 0.028243 | -0.11076 | -0.027964 | 0.00043722 | 0.00027929 | 0.16725 | 0.16725 | 0.16725 | 0.99017 | -0.1867 | 0.98592 | -0.26874 | 45.9468
32 | 0.035164 | 0.0088608 | -0.03511 | -0.008827 | 5.3829e-05 | 3.3802e-05 | 0.053089 | 0.053089 | 0.053089 | 0.98592 | -0.26874 | 0.98427 | -0.30079 | 14.5849
33 | 0.0044214 | 0.001108 | -0.0044211 | -0.001108 | 3.0786e-07 | -3.8059e-08 | 0.006673 | 0.0066731 | 0.0066731 | 0.98592 | -0.26874 | 0.98584 | -0.2702 | 1.8333
34 | 0.071179 | 0.017995 | -0.071038 | -0.017905 | 0.00014117 | 8.9932e-05 | 0.10748 | 0.10748 | 0.10748 | 0.98592 | -0.26874 | 0.98378 | -0.31018 | 29.5287
35 | 0.029866 | 0.0075127 | -0.029859 | -0.0075082 | 7.2085e-06 | 4.4937e-06 | 0.045161 | 0.045161 | 0.045161 | 0.98427 | -0.30079 | 0.98401 | -0.30585 | 12.407
36 | 0.058368 | 0.01473 | -0.058268 | -0.014666 | 0.00010022 | 6.3706e-05 | 0.088321 | 0.088321 | 0.088321 | 0.98378 | -0.31018 | 0.98194 | -0.3461 | 24.264
37 | 0.029859 | 0.0075082 | -0.029833 | -0.0074918 | 2.6305e-05 | 1.6399e-05 | 0.045161 | 0.045162 | 0.045162 | 0.98401 | -0.30585 | 0.98307 | -0.32431 | 12.407
38 | 0.049992 | 0.012592 | -0.049926 | -0.01255 | 6.6376e-05 | 4.2091e-05 | 0.07578 | 0.07578 | 0.07578 | 0.98194 | -0.3461 | 0.98052 | -0.37391 | 20.8188
39 | 0.025364 | 0.0063718 | -0.025343 | -0.0063588 | 2.1204e-05 | 1.3085e-05 | 0.038397 | 0.038397 | 0.038397 | 0.98307 | -0.32431 | 0.98217 | -0.34184 | 10.5488
40 | 0.010603 | 0.0026576 | -0.010602 | -0.0026573 | 6.7133e-07 | 3.4392e-07 | 0.016159 | 0.016159 | 0.016159 | 0.97636 | -0.45368 | 0.9763 | -0.45501 | 4.4394
41 | 0.0065002 | 0.0016292 | -0.0064993 | -0.0016289 | 9.5197e-07 | 2.859e-07 | 0.0099073 | 0.0099074 | 0.0099074 | 0.9763 | -0.45501 | 0.97614 | -0.45809 | 2.7218
42 | 0.0064993 | 0.0016289 | -0.0064985 | -0.0016287 | 7.0626e-07 | 2.1218e-07 | 0.0099074 | 0.0099075 | 0.0099075 | 0.97614 | -0.45809 | 0.97602 | -0.46037 | 2.7218

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28828 | 0.073558

## res_load
| p_mw | q_mvar
0 | 0.0043681 | 0.0010947
1 | 0.0055199 | 0.0013834
2 | 0.0063365 | 0.0015881
3 | 0.018999 | 0.0047616
4 | 0.040709 | 0.010203
5 | 0.0025066 | 0.00062822
6 | 0.0019007 | 0.00047637
7 | 0.0069661 | 0.0017459
8 | 0.01759 | 0.0044086
9 | 0.0020237 | 0.00050718
10 | 0.0029647 | 0.00074303
11 | 0.012157 | 0.0030467
12 | 0.0017933 | 0.00044944
13 | 0.0037303 | 0.00093489
14 | 0.016333 | 0.0040935
15 | 0.01736 | 0.0043509
16 | 0.0029311 | 0.00073461
17 | 0.0055602 | 0.0013935
18 | 0.0083065 | 0.0020818
19 | 0.0041939 | 0.0010511
20 | 0.015215 | 0.0038133
21 | 0.0039963 | 0.0010016
22 | 0.016122 | 0.0040405
23 | 0.0036141 | 0.00090578
24 | 0.0060765 | 0.0015229
25 | 0.0052439 | 0.0013143
26 | 0.0044211 | 0.001108
27 | 0.01267 | 0.0031753
28 | 0.0082758 | 0.0020741
29 | 0.0044689 | 0.00112
30 | 0.001747 | 0.00043785
31 | 0.0039145 | 0.00098108
32 | 0.0035507 | 0.00088988
33 | 0.004102 | 0.0010281
34 | 0.0064985 | 0.0016287

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1