## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1346-10_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1346-10_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1346-10_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1346-10_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1346-10_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1346-10_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1346-10_0_4_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_1346-10_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1346-10_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1346-10_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1346-10_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1346-10_0_4_node_31 | 0.4 | n |  | TRUE
12 | bus_LV_1346-10_0_4_node_85 | 0.4 | n |  | TRUE
13 | bus_LV_1346-10_0_4_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_1346-10_0_4_node_32 | 0.4 | n |  | TRUE
15 | bus_LV_1346-10_0_4_node_86 | 0.4 | n |  | TRUE
16 | bus_LV_1346-10_0_4_node_36 | 0.4 | n |  | TRUE
17 | bus_LV_1346-10_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1346-10_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1346-10_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1346-10_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1346-10_0_4_node_103 | 0.4 | n |  | TRUE
22 | bus_LV_1346-10_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1346-10_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1346-10_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1346-10_0_4_node_94 | 0.4 | n |  | TRUE
26 | bus_LV_1346-10_0_4_node_95 | 0.4 | n |  | TRUE
27 | bus_LV_1346-10_0_4_node_96 | 0.4 | n |  | TRUE
28 | bus_LV_1346-10_0_4_node_97 | 0.4 | n |  | TRUE
29 | bus_LV_1346-10_0_4_node_99 | 0.4 | n |  | TRUE
30 | bus_LV_1346-10_0_4_node_98 | 0.4 | n |  | TRUE
31 | bus_LV_1346-10_0_4_node_102 | 0.4 | n |  | TRUE
32 | bus_LV_1346-10_0_4_node_104 | 0.4 | n |  | TRUE
33 | bus_LV_1346-10_0_4_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_1346-10_0_4_node_100 | 0.4 | n |  | TRUE
35 | bus_LV_1346-10_0_4_node_105 | 0.4 | n |  | TRUE
36 | bus_LV_1346-10_0_4_node_101 | 0.4 | n |  | TRUE
37 | bus_LV_1346-10_0_4_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_1346-10_0_4_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_1346-10_0_4_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_1346-10_0_4_node_21 | 0.4 | n |  | TRUE
41 | bus_LV_1346-10_0_4_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_1346-10_0_4_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_1346-10_0_4_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_1346-10_0_4_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_1346-10_0_4_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_1346-10_0_4_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_1346-10_0_4_node_87 | 0.4 | n |  | TRUE
48 | bus_LV_1346-10_0_4_node_88 | 0.4 | n |  | TRUE
49 | bus_LV_1346-10_0_4_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_1346-10_0_4_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_1346-10_0_4_node_58 | 0.4 | n |  | TRUE
52 | bus_LV_1346-10_0_4_node_30 | 0.4 | n |  | TRUE
53 | bus_LV_1346-10_0_4_node_59 | 0.4 | n |  | TRUE
54 | bus_LV_1346-10_0_4_node_60 | 0.4 | n |  | TRUE
55 | bus_LV_1346-10_0_4_node_61 | 0.4 | n |  | TRUE
56 | bus_LV_1346-10_0_4_node_62 | 0.4 | n |  | TRUE
57 | bus_LV_1346-10_0_4_node_34 | 0.4 | n |  | TRUE
58 | bus_LV_1346-10_0_4_node_73 | 0.4 | n |  | TRUE
59 | bus_LV_1346-10_0_4_node_74 | 0.4 | n |  | TRUE
60 | bus_LV_1346-10_0_4_node_37 | 0.4 | n |  | TRUE
61 | bus_LV_1346-10_0_4_node_38 | 0.4 | n |  | TRUE
62 | bus_LV_1346-10_0_4_node_57 | 0.4 | n |  | TRUE
63 | bus_LV_1346-10_0_4_node_78 | 0.4 | n |  | TRUE
64 | bus_LV_1346-10_0_4_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_1346-10_0_4_node_76 | 0.4 | n |  | TRUE
66 | bus_LV_1346-10_0_4_node_39 | 0.4 | n |  | TRUE
67 | bus_LV_1346-10_0_4_node_40 | 0.4 | n |  | TRUE
68 | bus_LV_1346-10_0_4_node_50 | 0.4 | n |  | TRUE
69 | bus_LV_1346-10_0_4_node_41 | 0.4 | n |  | TRUE
70 | bus_LV_1346-10_0_4_node_46 | 0.4 | n |  | TRUE
71 | bus_LV_1346-10_0_4_node_70 | 0.4 | n |  | TRUE
72 | bus_LV_1346-10_0_4_node_71 | 0.4 | n |  | TRUE
73 | bus_LV_1346-10_0_4_node_90 | 0.4 | n |  | TRUE
74 | bus_LV_1346-10_0_4_node_92 | 0.4 | n |  | TRUE
75 | bus_LV_1346-10_0_4_node_89 | 0.4 | n |  | TRUE
76 | bus_LV_1346-10_0_4_node_42 | 0.4 | n |  | TRUE
77 | bus_LV_1346-10_0_4_node_43 | 0.4 | n |  | TRUE
78 | bus_LV_1346-10_0_4_node_44 | 0.4 | n |  | TRUE
79 | bus_LV_1346-10_0_4_node_45 | 0.4 | n |  | TRUE
80 | bus_LV_1346-10_0_4_node_47 | 0.4 | n |  | TRUE
81 | bus_LV_1346-10_0_4_node_48 | 0.4 | n |  | TRUE
82 | bus_LV_1346-10_0_4_node_49 | 0.4 | n |  | TRUE
83 | bus_LV_1346-10_0_4_node_51 | 0.4 | n |  | TRUE
84 | bus_LV_1346-10_0_4_node_52 | 0.4 | n |  | TRUE
85 | bus_LV_1346-10_0_4_node_64 | 0.4 | n |  | TRUE
86 | bus_LV_1346-10_0_4_node_53 | 0.4 | n |  | TRUE
87 | bus_LV_1346-10_0_4_node_63 | 0.4 | n |  | TRUE
88 | bus_LV_1346-10_0_4_node_65 | 0.4 | n |  | TRUE
89 | bus_LV_1346-10_0_4_node_54 | 0.4 | n |  | TRUE
90 | bus_LV_1346-10_0_4_node_56 | 0.4 | n |  | TRUE
91 | bus_LV_1346-10_0_4_node_67 | 0.4 | n |  | TRUE
92 | bus_LV_1346-10_0_4_node_68 | 0.4 | n |  | TRUE
93 | bus_LV_1346-10_0_4_node_66 | 0.4 | n |  | TRUE
94 | bus_LV_1346-10_0_4_node_69 | 0.4 | n |  | TRUE
95 | bus_LV_1346-10_0_4_node_72 | 0.4 | n |  | TRUE
96 | bus_LV_1346-10_0_4_node_91 | 0.4 | n |  | TRUE
97 | bus_LV_1346-10_0_4_node_75 | 0.4 | n |  | TRUE
98 | bus_LV_1346-10_0_4_node_84 | 0.4 | n |  | TRUE
99 | bus_LV_1346-10_0_4_node_83 | 0.4 | n |  | TRUE
100 | bus_LV_1346-10_0_4_node_77 | 0.4 | n |  | TRUE
101 | bus_LV_1346-10_0_4_node_79 | 0.4 | n |  | TRUE
102 | bus_LV_1346-10_0_4_node_80 | 0.4 | n |  | TRUE
103 | bus_LV_1346-10_0_4_node_81 | 0.4 | n |  | TRUE
104 | bus_LV_1346-10_0_4_node_82 | 0.4 | n |  | TRUE
105 | bus_LV_1346-10_0_4_node_93 | 0.4 | n |  | TRUE
106 | bus_LV_1346-10_0_4_node_120 | 0.4 | n |  | TRUE
107 | bus_LV_1346-10_0_4_node_121 | 0.4 | n |  | TRUE
108 | bus_LV_1346-10_0_4_node_106 | 0.4 | n |  | TRUE
109 | bus_LV_1346-10_0_4_node_107 | 0.4 | n |  | TRUE
110 | bus_LV_1346-10_0_4_node_108 | 0.4 | n |  | TRUE
111 | bus_LV_1346-10_0_4_node_109 | 0.4 | n |  | TRUE
112 | bus_LV_1346-10_0_4_node_110 | 0.4 | n |  | TRUE
113 | bus_LV_1346-10_0_4_node_111 | 0.4 | n |  | TRUE
114 | bus_LV_1346-10_0_4_node_112 | 0.4 | n |  | TRUE
115 | bus_LV_1346-10_0_4_node_113 | 0.4 | n |  | TRUE
116 | bus_LV_1346-10_0_4_node_114 | 0.4 | n |  | TRUE
117 | bus_LV_1346-10_0_4_node_116 | 0.4 | n |  | TRUE
118 | bus_LV_1346-10_0_4_node_119 | 0.4 | n |  | TRUE
119 | bus_LV_1346-10_0_4_node_115 | 0.4 | n |  | TRUE
120 | bus_LV_1346-10_0_4_node_117 | 0.4 | n |  | TRUE
121 | bus_LV_1346-10_0_4_node_118 | 0.4 | n |  | TRUE
122 | bus_LV_1346-10_0_4_node_125 | 0.4 | n |  | TRUE
123 | bus_LV_1346-10_0_4_node_126 | 0.4 | n |  | TRUE
124 | bus_LV_1346-10_0_4_node_122 | 0.4 | n |  | TRUE
125 | bus_LV_1346-10_0_4_node_124 | 0.4 | n |  | TRUE
126 | bus_LV_1346-10_0_4_node_123 | 0.4 | n |  | TRUE
127 | bus_LV_1346-10_0_4_node_132 | 0.4 | n |  | TRUE
128 | bus_LV_1346-10_0_4_node_129 | 0.4 | n |  | TRUE
129 | bus_LV_1346-10_0_4_node_133 | 0.4 | n |  | TRUE
130 | bus_LV_1346-10_0_4_node_130 | 0.4 | n |  | TRUE
131 | bus_LV_1346-10_0_4_node_128 | 0.4 | n |  | TRUE
132 | bus_LV_1346-10_0_4_node_131 | 0.4 | n |  | TRUE
133 | bus_LV_1346-10_0_4_node_127 | 0.4 | n |  | TRUE
134 | bus_LV_1346-10_0_4_node_134 | 0.4 | n |  | TRUE
135 | bus_LV_1346-10_0_4_node_135 | 0.4 | n |  | TRUE
136 | bus_LV_1346-10_0_4_node_142 | 0.4 | n |  | TRUE
137 | bus_LV_1346-10_0_4_node_136 | 0.4 | n |  | TRUE
138 | bus_LV_1346-10_0_4_node_138 | 0.4 | n |  | TRUE
139 | bus_LV_1346-10_0_4_node_140 | 0.4 | n |  | TRUE
140 | bus_LV_1346-10_0_4_node_139 | 0.4 | n |  | TRUE
141 | bus_LV_1346-10_0_4_node_141 | 0.4 | n |  | TRUE
142 | bus_LV_1346-10_0_4_node_143 | 0.4 | n |  | TRUE
143 | bus_MV_19_0_node_126 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1346-10_0_4_load_0 | 0 | 0.0015117 | 0.00037888 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1346-10_0_4_load_4 | 3 | 0.0034297 | 0.00085955 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1346-10_0_4_load_5 | 4 | 0.0039711 | 0.00099525 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1346-10_0_4_load_6 | 5 | 0.005097 | 0.0012774 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1346-10_0_4_load_3 | 6 | 0.0028344 | 0.00071037 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1346-10_0_4_load_8 | 8 | 0.0027106 | 0.00067935 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1346-10_0_4_load_9 | 9 | 0.002259 | 0.00056616 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1346-10_0_4_load_31 | 11 | 0.0024806 | 0.00062169 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1346-10_0_4_load_85 | 12 | 0.0015064 | 0.00037753 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1346-10_0_4_load_35 | 13 | 0.003343 | 0.00083783 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1346-10_0_4_load_86 | 15 | 0.0034154 | 0.00085598 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1346-10_0_4_load_36 | 16 | 0.0029484 | 0.00073893 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1346-10_0_4_load_11 | 17 | 0.0070335 | 0.0017628 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1346-10_0_4_load_12 | 18 | 0.0074632 | 0.0018705 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1346-10_0_4_load_14 | 20 | 0.0014112 | 0.00035369 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1346-10_0_4_load_103 | 21 | 0.0016251 | 0.00040728 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1346-10_0_4_load_16 | 22 | 0.0014105 | 0.00035349 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1346-10_0_4_load_15 | 23 | 0.0048855 | 0.0012244 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1346-10_0_4_load_94 | 25 | 0.00096406 | 0.00024162 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1346-10_0_4_load_95 | 26 | 0.0014031 | 0.00035164 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1346-10_0_4_load_96 | 27 | 0.00098859 | 0.00024776 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1346-10_0_4_load_97 | 28 | 0.00024504 | 6.1413e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1346-10_0_4_load_98 | 30 | 0.0018035 | 0.00045199 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1346-10_0_4_load_102 | 31 | 0.00099859 | 0.00025027 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1346-10_0_4_load_104 | 32 | 0.00041687 | 0.00010448 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1346-10_0_4_load_18 | 33 | 0.0014111 | 0.00035365 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1346-10_0_4_load_105 | 35 | 0.0027819 | 0.00069722 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1346-10_0_4_load_101 | 36 | 0.00031243 | 7.8302e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1346-10_0_4_load_19 | 37 | 0.0014108 | 0.00035358 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1346-10_0_4_load_33 | 38 | 0.0015066 | 0.0003776 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1346-10_0_4_load_20 | 39 | 0.0014105 | 0.00035349 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1346-10_0_4_load_21 | 40 | 0.001412 | 0.00035388 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1346-10_0_4_load_22 | 41 | 0.001412 | 0.00035389 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1346-10_0_4_load_23 | 42 | 0.0014102 | 0.00035342 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1346-10_0_4_load_24 | 43 | 0.014626 | 0.0036655 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1346-10_0_4_load_25 | 44 | 0.0024312 | 0.0006093 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1346-10_0_4_load_26 | 45 | 0.0028801 | 0.00072181 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1346-10_0_4_load_27 | 46 | 0.0023054 | 0.00057778 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1346-10_0_4_load_87 | 47 | 0.0036054 | 0.0009036 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1346-10_0_4_load_88 | 48 | 0.0036582 | 0.00091684 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1346-10_0_4_load_28 | 49 | 0.0015575 | 0.00039033 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1346-10_0_4_load_58 | 51 | 0.0011097 | 0.00027812 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1346-10_0_4_load_30 | 52 | 0.0084091 | 0.0021075 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1346-10_0_4_load_59 | 53 | 0.0010391 | 0.00026042 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1346-10_0_4_load_60 | 54 | 0.0042775 | 0.001072 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1346-10_0_4_load_61 | 55 | 0.0010831 | 0.00027144 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1346-10_0_4_load_62 | 56 | 0.0025662 | 0.00064315 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1346-10_0_4_load_34 | 57 | 0.001279 | 0.00032054 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1346-10_0_4_load_73 | 58 | 0.0015066 | 0.0003776 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1346-10_0_4_load_74 | 59 | 0.0012784 | 0.0003204 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1346-10_0_4_load_37 | 60 | 0.016158 | 0.0040496 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1346-10_0_4_load_57 | 62 | 0.001559 | 0.00039073 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1346-10_0_4_load_78 | 63 | 0.0020909 | 0.00052404 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1346-10_0_4_load_55 | 64 | 0.0027063 | 0.00067826 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1346-10_0_4_load_76 | 65 | 0.0007453 | 0.00018679 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1346-10_0_4_load_39 | 66 | 0.0027291 | 0.00068398 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1346-10_0_4_load_40 | 67 | 0.0011475 | 0.00028759 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1346-10_0_4_load_50 | 68 | 0.0035001 | 0.00087721 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1346-10_0_4_load_46 | 70 | 0.006128 | 0.0015358 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1346-10_0_4_load_70 | 71 | 0.00202 | 0.00050627 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1346-10_0_4_load_71 | 72 | 0.0017379 | 0.00043556 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1346-10_0_4_load_90 | 73 | 0.0020687 | 0.00051847 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1346-10_0_4_load_92 | 74 | 0.00048588 | 0.00012177 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1346-10_0_4_load_89 | 75 | 0.0065128 | 0.0016323 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1346-10_0_4_load_42 | 76 | 0.0023647 | 0.00059264 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1346-10_0_4_load_45 | 79 | 0.0029632 | 0.00074265 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1346-10_0_4_load_48 | 81 | 0.0045022 | 0.0011283 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1346-10_0_4_load_49 | 82 | 0.0022001 | 0.00055139 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1346-10_0_4_load_51 | 83 | 0.0017259 | 0.00043254 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1346-10_0_4_load_52 | 84 | 0.0030749 | 0.00077064 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1346-10_0_4_load_64 | 85 | 0.0028117 | 0.00070467 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1346-10_0_4_load_63 | 87 | 0.0037597 | 0.00094227 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1346-10_0_4_load_65 | 88 | 0.0010464 | 0.00026225 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1346-10_0_4_load_54 | 89 | 0.0037899 | 0.00094985 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1346-10_0_4_load_56 | 90 | 0.0017266 | 0.00043272 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1346-10_0_4_load_67 | 91 | 0.0046257 | 0.0011593 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1346-10_0_4_load_68 | 92 | 0.0046241 | 0.0011589 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1346-10_0_4_load_66 | 93 | 0.0025183 | 0.00063114 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1346-10_0_4_load_69 | 94 | 0.0073123 | 0.0018326 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1346-10_0_4_load_72 | 95 | 0.0068018 | 0.0017047 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1346-10_0_4_load_91 | 96 | 0.00045964 | 0.0001152 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1346-10_0_4_load_75 | 97 | 0.0015066 | 0.0003776 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1346-10_0_4_load_84 | 98 | 0.0012784 | 0.0003204 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1346-10_0_4_load_83 | 99 | 0.0015066 | 0.0003776 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1346-10_0_4_load_77 | 100 | 0.00099564 | 0.00024953 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1346-10_0_4_load_79 | 101 | 0.0015066 | 0.0003776 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1346-10_0_4_load_80 | 102 | 0.0015066 | 0.0003776 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1346-10_0_4_load_81 | 103 | 0.001279 | 0.00032054 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1346-10_0_4_load_82 | 104 | 0.001507 | 0.00037769 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1346-10_0_4_load_93 | 105 | 0.0013966 | 0.00035002 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1346-10_0_4_load_120 | 106 | 0.00057546 | 0.00014422 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1346-10_0_4_load_121 | 107 | 0.00016887 | 4.2323e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1346-10_0_4_load_106 | 108 | 0.0004437 | 0.0001112 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1346-10_0_4_load_107 | 109 | 0.00090222 | 0.00022612 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1346-10_0_4_load_108 | 110 | 0.00023592 | 5.9126e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1346-10_0_4_load_109 | 111 | 0.00058008 | 0.00014538 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1346-10_0_4_load_110 | 112 | 0.0005273 | 0.00013216 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1346-10_0_4_load_111 | 113 | 0.00013301 | 3.3335e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1346-10_0_4_load_113 | 115 | 0.00026506 | 6.6429e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1346-10_0_4_load_114 | 116 | 0.00036311 | 9.1005e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1346-10_0_4_load_116 | 117 | 0.00032573 | 8.1636e-05 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1346-10_0_4_load_119 | 118 | 0.00012312 | 3.0857e-05 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1346-10_0_4_load_115 | 119 | 0.00025544 | 6.402e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1346-10_0_4_load_117 | 120 | 0.0001757 | 4.4035e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1346-10_0_4_load_118 | 121 | 0.0004388 | 0.00010997 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1346-10_0_4_load_125 | 122 | 0.002248 | 0.00056341 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1346-10_0_4_load_124 | 125 | 0.00033961 | 8.5114e-05 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1346-10_0_4_load_132 | 127 | 0.00017546 | 4.3973e-05 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1346-10_0_4_load_133 | 129 | 0.00027145 | 6.8032e-05 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1346-10_0_4_load_130 | 130 | 0.00050942 | 0.00012767 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1346-10_0_4_load_128 | 131 | 0.00013438 | 3.3679e-05 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1346-10_0_4_load_127 | 133 | 0.00047424 | 0.00011886 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1346-10_0_4_load_134 | 134 | 0.00034134 | 8.5547e-05 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1346-10_0_4_load_135 | 135 | 0.00043391 | 0.00010875 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_1346-10_0_4_load_142 | 136 | 0.00048426 | 0.00012137 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_1346-10_0_4_load_138 | 138 | 0.00030405 | 7.6202e-05 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_1346-10_0_4_load_140 | 139 | 0.00032637 | 8.1797e-05 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_1346-10_0_4_load_139 | 140 | 0.00063114 | 0.00015818 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_1346-10_0_4_load_141 | 141 | 0.0014126 | 0.00035403 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_1346-10_0_4_load_143 | 142 | 0.00037794 | 9.4721e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1346-10_0_4_line_0 |  | 0 | 1 | 0.0035925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_1346-10_0_4_line_1 |  | 0 | 2 | 0.014932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_1346-10_0_4_line_2 |  | 1 | 3 | 0.016186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_1346-10_0_4_line_3 |  | 2 | 4 | 0.041801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_1346-10_0_4_line_4 |  | 2 | 5 | 0.011499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1346-10_0_4_line_5 |  | 3 | 8 | 0.0034436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_1346-10_0_4_line_6 |  | 4 | 9 | 0.031069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_1346-10_0_4_line_7 |  | 5 | 10 | 0.0037817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1346-10_0_4_line_8 |  | 6 | 7 | 0.015597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1346-10_0_4_line_9 |  | 7 | 10 | 0.022279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1346-10_0_4_line_10 |  | 7 | 11 | 0.0017002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1346-10_0_4_line_11 |  | 8 | 12 | 0.022531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_1346-10_0_4_line_12 |  | 9 | 13 | 0.018143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_1346-10_0_4_line_13 |  | 11 | 14 | 0.029559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1346-10_0_4_line_14 |  | 12 | 15 | 0.019684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_1346-10_0_4_line_15 |  | 13 | 16 | 0.010798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_1346-10_0_4_line_16 |  | 14 | 38 | 0.06854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1346-10_0_4_line_17 |  | 14 | 24 | 0.004116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1346-10_0_4_line_18 |  | 16 | 60 | 0.030545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_1346-10_0_4_line_19 |  | 17 | 18 | 0.0035164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_1346-10_0_4_line_20 |  | 17 | 19 | 0.042154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_1346-10_0_4_line_21 |  | 18 | 20 | 0.037939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_1346-10_0_4_line_22 |  | 19 | 21 | 0.36394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1346-10_0_4_line_23 |  | 20 | 22 | 0.0015468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_1346-10_0_4_line_24 |  | 21 | 32 | 0.24131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1346-10_0_4_line_25 |  | 21 | 31 | 0.013733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1346-10_0_4_line_26 |  | 22 | 33 | 0.0013768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_1346-10_0_4_line_27 |  | 23 | 24 | 0.02652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1346-10_0_4_line_28 |  | 25 | 26 | 0.031678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_1346-10_0_4_line_29 |  | 25 | 27 | 0.051688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_1346-10_0_4_line_30 |  | 26 | 28 | 0.032426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1346-10_0_4_line_31 |  | 27 | 29 | 0.19767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_1346-10_0_4_line_32 |  | 28 | 30 | 0.0202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1346-10_0_4_line_33 |  | 29 | 34 | 0.017057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_1346-10_0_4_line_34 |  | 32 | 35 | 0.0090316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_1346-10_0_4_line_35 |  | 33 | 37 | 0.02323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_1346-10_0_4_line_36 |  | 34 | 36 | 0.022275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_1346-10_0_4_line_37 |  | 35 | 36 | 0.015343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_1346-10_0_4_line_38 |  | 37 | 39 | 0.0022788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_1346-10_0_4_line_39 |  | 38 | 57 | 0.004316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1346-10_0_4_line_40 |  | 39 | 40 | 0.0021086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_1346-10_0_4_line_41 |  | 40 | 41 | 0.025033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_1346-10_0_4_line_42 |  | 41 | 42 | 0.0021093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_1346-10_0_4_line_43 |  | 42 | 43 | 0.0057044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_1346-10_0_4_line_44 |  | 43 | 44 | 0.041796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_1346-10_0_4_line_45 |  | 44 | 45 | 0.0044169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_1346-10_0_4_line_46 |  | 45 | 46 | 0.0041503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_1346-10_0_4_line_47 |  | 46 | 47 | 0.020065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_1346-10_0_4_line_48 |  | 47 | 48 | 0.0089133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_1346-10_0_4_line_49 |  | 48 | 75 | 0.016405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_1346-10_0_4_line_50 |  | 49 | 50 | 0.021384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1346-10_0_4_line_51 |  | 49 | 51 | 0.063753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1346-10_0_4_line_52 |  | 50 | 52 | 0.029522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1346-10_0_4_line_53 |  | 51 | 53 | 0.032468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1346-10_0_4_line_54 |  | 51 | 54 | 0.0015209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1346-10_0_4_line_55 |  | 54 | 55 | 0.027479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1346-10_0_4_line_56 |  | 55 | 56 | 0.00038974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1346-10_0_4_line_57 |  | 56 | 93 | 0.02043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1346-10_0_4_line_58 |  | 57 | 58 | 0.00045229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1346-10_0_4_line_59 |  | 58 | 59 | 0.004658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1346-10_0_4_line_60 |  | 59 | 97 | 0.011964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1346-10_0_4_line_61 |  | 60 | 61 | 0.044166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_1346-10_0_4_line_62 |  | 61 | 62 | 0.051865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_1346-10_0_4_line_63 |  | 61 | 63 | 0.021489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1346-10_0_4_line_64 |  | 62 | 64 | 0.0046798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_1346-10_0_4_line_65 |  | 63 | 65 | 0.03433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1346-10_0_4_line_66 |  | 64 | 86 | 0.00087868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_1346-10_0_4_line_67 |  | 65 | 100 | 0.021758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1346-10_0_4_line_68 |  | 66 | 67 | 0.019013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_1346-10_0_4_line_69 |  | 66 | 68 | 0.040832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_1346-10_0_4_line_70 |  | 67 | 69 | 0.055649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_1346-10_0_4_line_71 |  | 68 | 70 | 0.040136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_1346-10_0_4_line_72 |  | 69 | 71 | 0.024394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_1346-10_0_4_line_73 |  | 70 | 77 | 0.0089011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_1346-10_0_4_line_74 |  | 71 | 72 | 0.0018955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_1346-10_0_4_line_75 |  | 72 | 96 | 0.022377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_1346-10_0_4_line_76 |  | 73 | 74 | 0.060197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_1346-10_0_4_line_77 |  | 73 | 75 | 0.033502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_1346-10_0_4_line_78 |  | 74 | 105 | 0.001773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_1346-10_0_4_line_79 |  | 74 | 96 | 0.021712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_1346-10_0_4_line_80 |  | 76 | 77 | 0.025731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_1346-10_0_4_line_81 |  | 76 | 78 | 0.01352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_1346-10_0_4_line_82 |  | 77 | 79 | 0.023431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1346-10_0_4_line_83 |  | 78 | 80 | 0.022468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_1346-10_0_4_line_84 |  | 78 | 81 | 0.038956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1346-10_0_4_line_85 |  | 79 | 82 | 0.0040369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1346-10_0_4_line_86 |  | 80 | 83 | 0.0076604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_1346-10_0_4_line_87 |  | 81 | 84 | 0.02445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1346-10_0_4_line_88 |  | 82 | 85 | 0.0053269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1346-10_0_4_line_89 |  | 83 | 86 | 0.015817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_1346-10_0_4_line_90 |  | 84 | 87 | 0.04604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1346-10_0_4_line_91 |  | 85 | 88 | 0.018444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1346-10_0_4_line_92 |  | 86 | 89 | 0.017965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1346-10_0_4_line_93 |  | 88 | 93 | 0.0014809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1346-10_0_4_line_94 |  | 89 | 90 | 0.0083048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1346-10_0_4_line_95 |  | 90 | 91 | 0.02626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1346-10_0_4_line_96 |  | 91 | 92 | 0.019023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1346-10_0_4_line_97 |  | 92 | 94 | 9.3315e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1346-10_0_4_line_98 |  | 94 | 95 | 0.027973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1346-10_0_4_line_99 |  | 97 | 98 | 0.0022148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1346-10_0_4_line_100 |  | 98 | 99 | 0.0025557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1346-10_0_4_line_101 |  | 99 | 103 | 0.0025546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1346-10_0_4_line_102 |  | 101 | 102 | 0.0047705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1346-10_0_4_line_103 |  | 101 | 103 | 0.0011269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1346-10_0_4_line_104 |  | 102 | 104 | 0.0052392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1346-10_0_4_line_105 |  | 105 | 106 | 0.11468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_1346-10_0_4_line_106 |  | 106 | 107 | 0.13453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_1346-10_0_4_line_107 |  | 107 | 124 | 0.047377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1346-10_0_4_line_108 |  | 108 | 109 | 0.098555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1346-10_0_4_line_109 |  | 109 | 110 | 0.029471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1346-10_0_4_line_110 |  | 110 | 111 | 0.010592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1346-10_0_4_line_111 |  | 111 | 112 | 0.0044264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1346-10_0_4_line_112 |  | 112 | 113 | 0.0035049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1346-10_0_4_line_113 |  | 113 | 114 | 0.03003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1346-10_0_4_line_114 |  | 114 | 115 | 0.074725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1346-10_0_4_line_115 |  | 115 | 116 | 0.099392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1346-10_0_4_line_116 |  | 115 | 117 | 0.11651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1346-10_0_4_line_117 |  | 116 | 119 | 0.009816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1346-10_0_4_line_118 |  | 117 | 120 | 0.02098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1346-10_0_4_line_119 |  | 118 | 119 | 0.099387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1346-10_0_4_line_120 |  | 120 | 121 | 0.038996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1346-10_0_4_line_121 |  | 121 | 122 | 0.036696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1346-10_0_4_line_122 |  | 122 | 123 | 0.075062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1346-10_0_4_line_123 |  | 123 | 133 | 0.12451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1346-10_0_4_line_124 |  | 124 | 125 | 0.02842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1346-10_0_4_line_125 |  | 125 | 129 | 0.0029908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1346-10_0_4_line_126 |  | 126 | 127 | 0.0251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1346-10_0_4_line_127 |  | 126 | 128 | 0.030125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1346-10_0_4_line_128 |  | 128 | 130 | 0.0071757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1346-10_0_4_line_129 |  | 128 | 131 | 0.076491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1346-10_0_4_line_130 |  | 129 | 132 | 0.029972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1346-10_0_4_line_131 |  | 130 | 132 | 0.0047366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1346-10_0_4_line_132 |  | 131 | 133 | 0.070634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1346-10_0_4_line_133 |  | 132 | 134 | 0.012228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1346-10_0_4_line_134 |  | 134 | 135 | 0.064904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1346-10_0_4_line_135 |  | 135 | 136 | 0.12653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1346-10_0_4_line_136 |  | 136 | 142 | 0.0084495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1346-10_0_4_line_137 |  | 136 | 140 | 0.035977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1346-10_0_4_line_138 |  | 137 | 138 | 0.056084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1346-10_0_4_line_139 |  | 137 | 139 | 0.11914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1346-10_0_4_line_140 |  | 138 | 140 | 0.018262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1346-10_0_4_line_141 |  | 139 | 141 | 0.015219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1346-10_0_4_trafo_86 | 0.63 MVA 20/0.4 kV | 143 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2712287.8502 | 1226031.7005 | 2712287.9192 | 1226035.2923
1 | 2712288.2056 | 1226050.2213 | 2712287.9192 | 1226035.2923
2 | 2712287.8502 | 1226031.7005 | 2712287.743 | 1226026.1387 | 2712287.4526 | 1226015.5195
3 | 2712288.2056 | 1226050.2213 | 2712329.9204 | 1226047.5312
4 | 2712288.2056 | 1226050.2213 | 2712276.7249 | 1226050.8748
5 | 2712287.3585 | 1226012.0772 | 2712287.4526 | 1226015.5195
6 | 2712360.9251 | 1226045.5318 | 2712329.9204 | 1226047.5312
7 | 2712272.9493 | 1226051.0897 | 2712276.7249 | 1226050.8748
8 | 2712250.6416 | 1226052.3587 | 2712250.1051 | 1226036.7708
9 | 2712272.9493 | 1226051.0897 | 2712250.6416 | 1226052.3587
10 | 2712250.6416 | 1226052.3587 | 2712248.944 | 1226052.4537
11 | 2712286.7426 | 1225989.5543 | 2712287.3585 | 1226012.0772
12 | 2712379.0308 | 1226044.3642 | 2712360.9251 | 1226045.5318
13 | 2712219.4312 | 1226054.1048 | 2712236.9643 | 1226053.1236 | 2712248.944 | 1226052.4537
14 | 2712286.2046 | 1225969.8779 | 2712286.7426 | 1225989.5543
15 | 2712379.0308 | 1226044.3642 | 2712389.8063 | 1226043.6693
16 | 2712219.4312 | 1226054.1048 | 2712219.2073 | 1226049.8973 | 2712216.5535 | 1225999.6757 | 2712218.3476 | 1225994.2054 | 2712223.2246 | 1225992.5072 | 2712226.3337 | 1225992.3338
17 | 2712215.3097 | 1226054.3383 | 2712219.4312 | 1226054.1048
18 | 2712389.8063 | 1226043.6693 | 2712420.2878 | 1226041.7036
19 | 2712110.8612 | 1226018.1241 | 2712110.6593 | 1226014.6135
20 | 2712113.2809 | 1226060.2087 | 2712110.8612 | 1226018.1241
21 | 2712121.71 | 1225983.6929 | 2712117.2122 | 1225984.4028 | 2712111.2893 | 1225988.8947 | 2712109.5866 | 1225995.9568 | 2712110.6593 | 1226014.6135
22 | 2712113.2809 | 1226060.2087 | 2711985.3392 | 1226400.9148
23 | 2712123.2379 | 1225983.4518 | 2712121.71 | 1225983.6929
24 | 2712209.4081 | 1226490.4898 | 2711985.3392 | 1226400.9148
25 | 2711971.642 | 1226401.9065 | 2711985.3392 | 1226400.9148
26 | 2712124.5979 | 1225983.2371 | 2712123.2379 | 1225983.4518
27 | 2712215.3097 | 1226054.3383 | 2712188.8335 | 1226055.8617
28 | 2712031.4621 | 1226675.5367 | 2712001.8278 | 1226686.7315
29 | 2712031.4621 | 1226675.5367 | 2712031.4621 | 1226675.5367 | 2712069.7588 | 1226640.8242
30 | 2711971.4931 | 1226698.189 | 2711992.4289 | 1226690.2799 | 2712000.9578 | 1226687.0602 | 2712001.8278 | 1226686.7315
31 | 2712227.1065 | 1226521.1834 | 2712069.7588 | 1226640.8242
32 | 2711952.5965 | 1226705.3277 | 2711971.4931 | 1226698.189
33 | 2712227.1065 | 1226521.1834 | 2712243.7888 | 1226517.4063
34 | 2712217.7945 | 1226493.8424 | 2712209.4081 | 1226490.4898
35 | 2712124.5979 | 1225983.2371 | 2712125.2048 | 1225983.1413 | 2712147.7919 | 1225982.016
36 | 2712243.7888 | 1226517.4063 | 2712240.9889 | 1226507.4903 | 2712232.0412 | 1226499.5377
37 | 2712217.7945 | 1226493.8424 | 2712232.0412 | 1226499.5377 | 2712232.0412 | 1226499.5377
38 | 2712150.0679 | 1225981.9026 | 2712147.7919 | 1225982.016
39 | 2712230.643 | 1225992.0934 | 2712226.3337 | 1225992.3338
40 | 2712152.1739 | 1225981.7977 | 2712150.0679 | 1225981.9026
41 | 2712152.1739 | 1225981.7977 | 2712177.176 | 1225980.552
42 | 2712179.2827 | 1225980.447 | 2712177.176 | 1225980.552
43 | 2712184.98 | 1225980.1632 | 2712179.2827 | 1225980.447
44 | 2712184.98 | 1225980.1632 | 2712199.3522 | 1225979.4471 | 2712202.8978 | 1225952.271 | 2712202.8978 | 1225952.271
45 | 2712202.8978 | 1225952.271 | 2712204.3914 | 1225948.1143
46 | 2712205.7947 | 1225944.2084 | 2712204.3914 | 1225948.1143
47 | 2712205.7947 | 1225944.2084 | 2712205.7947 | 1225944.2084 | 2712211.3772 | 1225940.8889 | 2712223.4962 | 1225934.7825
48 | 2712223.4962 | 1225934.7825 | 2712231.4561 | 1225930.7717
49 | 2712246.1065 | 1225923.3899 | 2712231.4561 | 1225930.7717
50 | 2712576.8298 | 1225823.29 | 2712574.2676 | 1225844.5201
51 | 2712554.3806 | 1225905.0915 | 2712574.2676 | 1225844.5201
52 | 2712576.8298 | 1225823.29 | 2712565.5534 | 1225827.3687 | 2712548.8711 | 1225821.9807
53 | 2712554.3806 | 1225905.0915 | 2712586.2343 | 1225911.3759
54 | 2712554.3806 | 1225905.0915 | 2712552.8885 | 1225904.7971
55 | 2712552.8885 | 1225904.7971 | 2712544.6095 | 1225903.1637 | 2712526.3108 | 1225897.9016
56 | 2712526.3108 | 1225897.9016 | 2712525.9363 | 1225897.7939
57 | 2712506.453 | 1225891.6815 | 2712513.6074 | 1225894.2485 | 2712525.9363 | 1225897.7939
58 | 2712230.643 | 1225992.0934 | 2712231.0946 | 1225992.0682
59 | 2712235.7453 | 1225991.8088 | 2712231.0946 | 1225992.0682
60 | 2712235.7453 | 1225991.8088 | 2712247.691 | 1225991.1426
61 | 2712464.3627 | 1226038.8613 | 2712420.2878 | 1226041.7036
62 | 2712464.3627 | 1226038.8613 | 2712463.2752 | 1225987.0076
63 | 2712464.3627 | 1226038.8613 | 2712485.8277 | 1226037.8366
64 | 2712463.1771 | 1225982.3288 | 2712463.2752 | 1225987.0076
65 | 2712520.1184 | 1226036.1995 | 2712485.8277 | 1226037.8366
66 | 2712463.1771 | 1225982.3288 | 2712463.1587 | 1225981.4503
67 | 2712520.1184 | 1226036.1995 | 2712541.8513 | 1226035.162
68 | 2712407.8473 | 1225830.4255 | 2712398.4026 | 1225832.0464 | 2712389.0995 | 1225833.5899
69 | 2712437.7521 | 1225858.2272 | 2712407.8473 | 1225830.4255
70 | 2712334.3251 | 1225843.234 | 2712348.4224 | 1225839.9309 | 2712370.9062 | 1225836.6084 | 2712389.0995 | 1225833.5899
71 | 2712437.7521 | 1225858.2272 | 2712443.2439 | 1225859.759 | 2712450.7893 | 1225863.7157 | 2712455.8424 | 1225869.9604 | 2712458.2455 | 1225877.6005 | 2712458.4813 | 1225882.3753 | 2712458.7134 | 1225887.4617
72 | 2712334.3251 | 1225843.234 | 2712309.9749 | 1225844.6887
73 | 2712459.1192 | 1225896.3536 | 2712458.7134 | 1225887.4617
74 | 2712309.9749 | 1225844.6887 | 2712308.0828 | 1225844.8017
75 | 2712308.0828 | 1225844.8017 | 2712285.7453 | 1225846.1361
76 | 2712274.8146 | 1225906.2442 | 2712264.0526 | 1225847.0167
77 | 2712246.1065 | 1225923.3899 | 2712258.8767 | 1225916.9554 | 2712274.8146 | 1225906.2442
78 | 2712264.0526 | 1225847.0167 | 2712262.2805 | 1225847.0739
79 | 2712285.7453 | 1225846.1361 | 2712279.1696 | 1225846.529 | 2712264.0526 | 1225847.0167
80 | 2712459.1192 | 1225896.3536 | 2712460.3082 | 1225922.0571
81 | 2712460.933 | 1225935.5622 | 2712460.3082 | 1225922.0571
82 | 2712459.1192 | 1225896.3536 | 2712465.1913 | 1225890.0079 | 2712471.6993 | 1225885.8722 | 2712478.4617 | 1225884.326
83 | 2712460.933 | 1225935.5622 | 2712462.0251 | 1225957.9999
84 | 2712460.933 | 1225935.5622 | 2712484.2283 | 1225939.0273 | 2712499.6071 | 1225939.921
85 | 2712482.4427 | 1225884.2044 | 2712480.0989 | 1225883.9517 | 2712478.4617 | 1225884.326
86 | 2712462.0251 | 1225957.9999 | 2712462.3949 | 1225965.6514
87 | 2712499.6071 | 1225939.921 | 2712509.7599 | 1225940.5111 | 2712524.0398 | 1225940.5628
88 | 2712482.4427 | 1225884.2044 | 2712486.9772 | 1225884.6934 | 2712487.6984 | 1225884.9521
89 | 2712463.1587 | 1225981.4503 | 2712462.3949 | 1225965.6514
90 | 2712524.0398 | 1225940.5628 | 2712570.08 | 1225940.7297
91 | 2712487.6984 | 1225884.9521 | 2712505.0591 | 1225891.1813
92 | 2712463.1587 | 1225981.4503 | 2712481.0624 | 1225979.9658
93 | 2712506.453 | 1225891.6815 | 2712505.0591 | 1225891.1813
94 | 2712489.3388 | 1225979.2796 | 2712481.0624 | 1225979.9658
95 | 2712489.3388 | 1225979.2796 | 2712515.5091 | 1225977.1096
96 | 2712515.5091 | 1225977.1096 | 2712534.4673 | 1225975.5377
97 | 2712534.5603 | 1225975.53 | 2712534.4673 | 1225975.5377
98 | 2712534.5603 | 1225975.53 | 2712562.4379 | 1225973.2185
99 | 2712249.9024 | 1225991.0192 | 2712247.691 | 1225991.1426
100 | 2712249.9024 | 1225991.0192 | 2712252.4541 | 1225990.8769
101 | 2712255.0048 | 1225990.7346 | 2712252.4541 | 1225990.8769
102 | 2712256.1299 | 1225990.6719 | 2712260.893 | 1225990.4062
103 | 2712256.1299 | 1225990.6719 | 2712255.0048 | 1225990.7346
104 | 2712266.1241 | 1225990.1145 | 2712260.893 | 1225990.4062
105 | 2712262.2805 | 1225847.0739 | 2712259.1978 | 1225732.4356
106 | 2712225.213 | 1225602.2698 | 2712259.1978 | 1225732.4356
107 | 2712243.5502 | 1225560.7618 | 2712223.8975 | 1225591.2144 | 2712225.213 | 1225602.2698 | 2712225.213 | 1225602.2698
108 | 2712331.697 | 1225120.6126 | 2712427.1554 | 1225145.1246
109 | 2712302.3286 | 1225118.2579 | 2712330.5459 | 1225120.3793 | 2712331.697 | 1225120.6126
110 | 2712302.3286 | 1225118.2579 | 2712291.7664 | 1225117.4638
111 | 2712287.3525 | 1225117.132 | 2712291.7664 | 1225117.4638
112 | 2712287.3525 | 1225117.132 | 2712283.8574 | 1225116.8692
113 | 2712254.0759 | 1225113.5647 | 2712254.6118 | 1225113.6972 | 2712260.6288 | 1225115.1228 | 2712283.8574 | 1225116.8692
114 | 2712254.0759 | 1225113.5647 | 2712226.5906 | 1225123.7987 | 2712190.7056 | 1225151.6025
115 | 2712190.7056 | 1225151.6025 | 2712164.2953 | 1225055.7838
116 | 2712190.7056 | 1225151.6025 | 2712088.2097 | 1225207.0098
117 | 2712168.6623 | 1225046.9928 | 2712164.2953 | 1225055.7838
118 | 2712088.2097 | 1225207.0098 | 2712075.4154 | 1225217.3212 | 2712074.513 | 1225221.7786
119 | 2712168.6623 | 1225046.9928 | 2712182.9844 | 1224948.6436
120 | 2712074.513 | 1225221.7786 | 2712067.3551 | 1225257.133 | 2712066.6409 | 1225259.9687
121 | 2712066.6409 | 1225259.9687 | 2712057.6783 | 1225295.5539
122 | 2712024.0611 | 1225361.1191 | 2712050.012 | 1225325.9921 | 2712057.6783 | 1225295.5539
123 | 2712136.1499 | 1225415.3222 | 2712024.0611 | 1225361.1191
124 | 2712243.5502 | 1225560.7618 | 2712256.5497 | 1225539.324 | 2712258.8247 | 1225536.8662
125 | 2712260.8563 | 1225534.6713 | 2712258.8247 | 1225536.8662
126 | 2712234.3314 | 1225523.3039 | 2712218.3147 | 1225523.0016 | 2712212.9995 | 1225521.378 | 2712211.1466 | 1225518.3074
127 | 2712234.3314 | 1225523.3039 | 2712240.4984 | 1225520.3735 | 2712253.6392 | 1225501.0956
128 | 2712253.6392 | 1225501.0956 | 2712260.2556 | 1225503.8729
129 | 2712253.6392 | 1225501.0956 | 2712209.2107 | 1225480.253 | 2712187.7622 | 1225463.1766
130 | 2712264.623 | 1225505.7063 | 2712262.3316 | 1225516.2266 | 2712262.7809 | 1225532.592 | 2712260.8563 | 1225534.6713
131 | 2712264.623 | 1225505.7063 | 2712260.2556 | 1225503.8729
132 | 2712136.1499 | 1225415.3222 | 2712147.346 | 1225423.3771 | 2712175.5929 | 1225453.4879 | 2712187.7622 | 1225463.1766
133 | 2712264.623 | 1225505.7063 | 2712275.8964 | 1225510.443
134 | 2712275.8964 | 1225510.443 | 2712335.7331 | 1225535.5847
135 | 2712335.7331 | 1225535.5847 | 2712420.4739 | 1225629.5424
136 | 2712419.1711 | 1225637.8908 | 2712420.4739 | 1225629.5424
137 | 2712420.4739 | 1225629.5424 | 2712423.9723 | 1225626.1837 | 2712428.9655 | 1225624.3766 | 2712443.4659 | 1225624.6508 | 2712453.5482 | 1225629.7844
138 | 2712509.9219 | 1225604.1133 | 2712499.9575 | 1225624.1958 | 2712494.1123 | 1225630.5568 | 2712484.4689 | 1225636.0788 | 2712478.3378 | 1225637.1081 | 2712470.8638 | 1225635.2698
139 | 2712509.9219 | 1225604.1133 | 2712478.414 | 1225489.2164
140 | 2712453.5482 | 1225629.7844 | 2712458.2086 | 1225632.1573 | 2712470.8638 | 1225635.2698
141 | 2712470.277 | 1225476.3556 | 2712478.414 | 1225489.2164

## bus_geodata
| x | y | coords
0 | 2712287.9192 | 1226035.2923
1 | 2712287.8502 | 1226031.7005
2 | 2712288.2056 | 1226050.2213
3 | 2712287.4526 | 1226015.5195
4 | 2712329.9204 | 1226047.5312
5 | 2712276.7249 | 1226050.8748
6 | 2712250.1051 | 1226036.7708
7 | 2712250.6416 | 1226052.3587
8 | 2712287.3585 | 1226012.0772
9 | 2712360.9251 | 1226045.5318
10 | 2712272.9493 | 1226051.0897
11 | 2712248.944 | 1226052.4537
12 | 2712286.7426 | 1225989.5543
13 | 2712379.0308 | 1226044.3642
14 | 2712219.4312 | 1226054.1048
15 | 2712286.2046 | 1225969.8779
16 | 2712389.8063 | 1226043.6693
17 | 2712110.8612 | 1226018.1241
18 | 2712110.6593 | 1226014.6135
19 | 2712113.2809 | 1226060.2087
20 | 2712121.71 | 1225983.6929
21 | 2711985.3392 | 1226400.9148
22 | 2712123.2379 | 1225983.4518
23 | 2712188.8335 | 1226055.8617
24 | 2712215.3097 | 1226054.3383
25 | 2712031.4621 | 1226675.5367
26 | 2712001.8278 | 1226686.7315
27 | 2712069.7588 | 1226640.8242
28 | 2711971.4931 | 1226698.189
29 | 2712227.1065 | 1226521.1834
30 | 2711952.5965 | 1226705.3277
31 | 2711971.6419 | 1226401.9065
32 | 2712209.4081 | 1226490.4898
33 | 2712124.5979 | 1225983.2371
34 | 2712243.7888 | 1226517.4063
35 | 2712217.7945 | 1226493.8424
36 | 2712232.0412 | 1226499.5377
37 | 2712147.7919 | 1225982.016
38 | 2712226.3337 | 1225992.3338
39 | 2712150.0679 | 1225981.9026
40 | 2712152.1739 | 1225981.7977
41 | 2712177.176 | 1225980.552
42 | 2712179.2827 | 1225980.447
43 | 2712184.98 | 1225980.1632
44 | 2712202.8978 | 1225952.271
45 | 2712204.3914 | 1225948.1143
46 | 2712205.7947 | 1225944.2084
47 | 2712223.4962 | 1225934.7825
48 | 2712231.4561 | 1225930.7717
49 | 2712574.2676 | 1225844.5201
50 | 2712576.8298 | 1225823.29
51 | 2712554.3806 | 1225905.0915
52 | 2712548.8711 | 1225821.9807
53 | 2712586.2343 | 1225911.3759
54 | 2712552.8885 | 1225904.7971
55 | 2712526.3108 | 1225897.9016
56 | 2712525.9363 | 1225897.7939
57 | 2712230.643 | 1225992.0934
58 | 2712231.0946 | 1225992.0682
59 | 2712235.7453 | 1225991.8088
60 | 2712420.2878 | 1226041.7036
61 | 2712464.3627 | 1226038.8613
62 | 2712463.2752 | 1225987.0076
63 | 2712485.8277 | 1226037.8366
64 | 2712463.1771 | 1225982.3288
65 | 2712520.1184 | 1226036.1995
66 | 2712407.8473 | 1225830.4255
67 | 2712389.0995 | 1225833.5899
68 | 2712437.7521 | 1225858.2272
69 | 2712334.3251 | 1225843.234
70 | 2712458.7134 | 1225887.4617
71 | 2712309.9749 | 1225844.6887
72 | 2712308.0828 | 1225844.8017
73 | 2712274.8146 | 1225906.2442
74 | 2712264.0526 | 1225847.0167
75 | 2712246.1065 | 1225923.3899
76 | 2712460.3082 | 1225922.0571
77 | 2712459.1192 | 1225896.3536
78 | 2712460.933 | 1225935.5622
79 | 2712478.4617 | 1225884.326
80 | 2712462.0251 | 1225957.9999
81 | 2712499.6071 | 1225939.921
82 | 2712482.4427 | 1225884.2044
83 | 2712462.3949 | 1225965.6514
84 | 2712524.0398 | 1225940.5628
85 | 2712487.6984 | 1225884.9521
86 | 2712463.1587 | 1225981.4503
87 | 2712570.08 | 1225940.7297
88 | 2712505.0591 | 1225891.1813
89 | 2712481.0624 | 1225979.9658
90 | 2712489.3388 | 1225979.2796
91 | 2712515.5091 | 1225977.1096
92 | 2712534.4673 | 1225975.5377
93 | 2712506.453 | 1225891.6815
94 | 2712534.5603 | 1225975.53
95 | 2712562.4379 | 1225973.2185
96 | 2712285.7453 | 1225846.1361
97 | 2712247.691 | 1225991.1426
98 | 2712249.9024 | 1225991.0192
99 | 2712252.4541 | 1225990.8769
100 | 2712541.8513 | 1226035.162
101 | 2712256.1299 | 1225990.6719
102 | 2712260.893 | 1225990.4062
103 | 2712255.0048 | 1225990.7346
104 | 2712266.1241 | 1225990.1145
105 | 2712262.2805 | 1225847.0739
106 | 2712259.1978 | 1225732.4356
107 | 2712225.213 | 1225602.2698
108 | 2712427.1554 | 1225145.1246
109 | 2712331.697 | 1225120.6126
110 | 2712302.3286 | 1225118.2579
111 | 2712291.7664 | 1225117.4638
112 | 2712287.3525 | 1225117.132
113 | 2712283.8574 | 1225116.8692
114 | 2712254.0759 | 1225113.5647
115 | 2712190.7056 | 1225151.6025
116 | 2712164.2953 | 1225055.7838
117 | 2712088.2097 | 1225207.0098
118 | 2712182.9843 | 1224948.6436
119 | 2712168.6623 | 1225046.9928
120 | 2712074.513 | 1225221.7786
121 | 2712066.6409 | 1225259.9687
122 | 2712057.6783 | 1225295.5539
123 | 2712024.0611 | 1225361.1191
124 | 2712243.5502 | 1225560.7618
125 | 2712258.8247 | 1225536.8662
126 | 2712234.3314 | 1225523.3039
127 | 2712211.1466 | 1225518.3074
128 | 2712253.6392 | 1225501.0956
129 | 2712260.8563 | 1225534.6713
130 | 2712260.2556 | 1225503.8729
131 | 2712187.7622 | 1225463.1766
132 | 2712264.623 | 1225505.7063
133 | 2712136.1499 | 1225415.3222
134 | 2712275.8964 | 1225510.443
135 | 2712335.7331 | 1225535.5847
136 | 2712420.4739 | 1225629.5424
137 | 2712509.9219 | 1225604.1133
138 | 2712470.8638 | 1225635.2698
139 | 2712478.414 | 1225489.2164
140 | 2712453.5482 | 1225629.7844
141 | 2712470.277 | 1225476.3556
142 | 2712419.1711 | 1225637.8908
143 | 2712287.8502 | 1226031.7005

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99608 | -0.074162 | 0.0015117 | 0.00037888
1 | 0.99629 | -0.070148 | 0 | 0
2 | 0.99521 | -0.090765 | 0 | 0
3 | 0.99725 | -0.052083 | 0.0034297 | 0.00085955
4 | 0.99306 | -0.13168 | 0.0039711 | 0.00099525
5 | 0.99488 | -0.097033 | 0.005097 | 0.0012774
6 | 0.99423 | -0.10969 | 0.0028344 | 0.00071037
7 | 0.99427 | -0.10891 | 0 | 0
8 | 0.99745 | -0.048193 | 0.0027106 | 0.00067935
9 | 0.99149 | -0.16166 | 0.002259 | 0.00056616
10 | 0.99479 | -0.098756 | 0 | 0
11 | 0.99423 | -0.1096 | 0.0024806 | 0.00062169
12 | 0.99881 | -0.02251 | 0.0015064 | 0.00037753
13 | 0.99058 | -0.17902 | 0.003343 | 0.00083783
14 | 0.99368 | -0.12032 | 0 | 0
15 | 1 | 0 | -0.26805 | -0.068429
16 | 0.99005 | -0.18921 | 0.0029484 | 0.00073893
17 | 0.97216 | -0.53816 | 0.0070335 | 0.0017628
18 | 0.97218 | -0.53786 | 0.0074632 | 0.0018705
19 | 0.97205 | -0.54043 | 0 | 0
20 | 0.97241 | -0.53328 | 0.0014112 | 0.00035369
21 | 0.97107 | -0.55998 | 0.0016251 | 0.00040728
22 | 0.97242 | -0.53308 | 0.0014105 | 0.00035349
23 | 0.99354 | -0.12296 | 0.0048855 | 0.0012244
24 | 0.99366 | -0.12068 | 0 | 0
25 | 0.97018 | -0.57777 | 0.00096406 | 0.00024162
26 | 0.97013 | -0.57878 | 0.0014031 | 0.00035164
27 | 0.97023 | -0.57671 | 0.00098859 | 0.00024776
28 | 0.97007 | -0.58001 | 0.00024504 | 6.1413e-05
29 | 0.97048 | -0.57174 | 0 | 0
30 | 0.97003 | -0.58069 | 0.0018035 | 0.00045199
31 | 0.97106 | -0.56023 | 0.00099859 | 0.00025027
32 | 0.97057 | -0.56999 | 0.00041687 | 0.00010448
33 | 0.97243 | -0.5329 | 0.0014111 | 0.00035365
34 | 0.9705 | -0.57131 | 0 | 0
35 | 0.97055 | -0.57035 | 0.0027819 | 0.00069722
36 | 0.97053 | -0.57075 | 0.00031243 | 7.8302e-05
37 | 0.97259 | -0.52965 | 0.0014108 | 0.00035358
38 | 0.9927 | -0.13929 | 0.0015066 | 0.0003776
39 | 0.97261 | -0.52931 | 0.0014105 | 0.00035349
40 | 0.97263 | -0.52899 | 0.001412 | 0.00035388
41 | 0.97283 | -0.525 | 0.001412 | 0.00035389
42 | 0.97284 | -0.52465 | 0.0014102 | 0.00035342
43 | 0.97289 | -0.52366 | 0.014626 | 0.0036655
44 | 0.9734 | -0.51365 | 0.0024312 | 0.0006093
45 | 0.97346 | -0.51254 | 0.0028801 | 0.00072181
46 | 0.97351 | -0.51144 | 0.0023054 | 0.00057778
47 | 0.97379 | -0.50594 | 0.0036054 | 0.0009036
48 | 0.97392 | -0.50334 | 0.0036582 | 0.00091684
49 | 0.97836 | -0.41611 | 0.0015575 | 0.00039033
50 | 0.9782 | -0.41939 | 0 | 0
51 | 0.97895 | -0.40455 | 0.0011097 | 0.00027812
52 | 0.97797 | -0.42391 | 0.0084091 | 0.0021075
53 | 0.97892 | -0.40516 | 0.0010391 | 0.00026042
54 | 0.97897 | -0.40421 | 0.0042775 | 0.001072
55 | 0.97939 | -0.39602 | 0.0010831 | 0.00027144
56 | 0.97939 | -0.3959 | 0.0025662 | 0.00064315
57 | 0.99264 | -0.14037 | 0.001279 | 0.00032054
58 | 0.99264 | -0.14047 | 0.0015066 | 0.0003776
59 | 0.99259 | -0.14141 | 0.0012784 | 0.0003204
60 | 0.98857 | -0.2177 | 0.016158 | 0.0040496
61 | 0.98659 | -0.25584 | 0 | 0
62 | 0.98432 | -0.29993 | 0.001559 | 0.00039073
63 | 0.98652 | -0.25731 | 0.0020909 | 0.00052404
64 | 0.98411 | -0.30388 | 0.0027063 | 0.00067826
65 | 0.98646 | -0.25838 | 0.0007453 | 0.00018679
66 | 0.979 | -0.40353 | 0.0027291 | 0.00068398
67 | 0.97857 | -0.41191 | 0.0011475 | 0.00028759
68 | 0.97994 | -0.38506 | 0.0035001 | 0.00087721
69 | 0.97733 | -0.43619 | 0 | 0
70 | 0.9809 | -0.36629 | 0.006128 | 0.0015358
71 | 0.97679 | -0.44685 | 0.00202 | 0.00050627
72 | 0.97675 | -0.44766 | 0.0017379 | 0.00043556
73 | 0.97475 | -0.487 | 0.0020687 | 0.00051847
74 | 0.97581 | -0.46616 | 0.00048588 | 0.00012177
75 | 0.97418 | -0.4983 | 0.0065128 | 0.0016323
76 | 0.98197 | -0.34549 | 0.0023647 | 0.00059264
77 | 0.98113 | -0.36189 | 0 | 0
78 | 0.98242 | -0.33675 | 0 | 0
79 | 0.98044 | -0.3753 | 0.0029632 | 0.00074265
80 | 0.98323 | -0.32108 | 0 | 0
81 | 0.98201 | -0.34473 | 0.0045022 | 0.0011283
82 | 0.98034 | -0.37739 | 0.0022001 | 0.00055139
83 | 0.9835 | -0.31575 | 0.0017259 | 0.00043254
84 | 0.98186 | -0.34775 | 0.0030749 | 0.00077064
85 | 0.98021 | -0.37995 | 0.0028117 | 0.00070467
86 | 0.98407 | -0.30461 | 0 | 0
87 | 0.9817 | -0.35088 | 0.0037597 | 0.00094227
88 | 0.9798 | -0.38785 | 0.0010464 | 0.00026225
89 | 0.9836 | -0.31396 | 0.0037899 | 0.00094985
90 | 0.9834 | -0.31771 | 0.0017266 | 0.00043272
91 | 0.98284 | -0.32878 | 0.0046257 | 0.0011593
92 | 0.98251 | -0.33521 | 0.0046241 | 0.0011589
93 | 0.97977 | -0.38846 | 0.0025183 | 0.00063114
94 | 0.98251 | -0.33524 | 0.0073123 | 0.0018326
95 | 0.98233 | -0.33867 | 0.0068018 | 0.0017047
96 | 0.97627 | -0.45707 | 0.00045964 | 0.0001152
97 | 0.99248 | -0.14355 | 0.0015066 | 0.0003776
98 | 0.99246 | -0.14388 | 0.0012784 | 0.0003204
99 | 0.99244 | -0.14421 | 0.0015066 | 0.0003776
100 | 0.98644 | -0.25877 | 0.00099564 | 0.00024953
101 | 0.99242 | -0.14457 | 0.0015066 | 0.0003776
102 | 0.99241 | -0.14482 | 0.0015066 | 0.0003776
103 | 0.99243 | -0.14448 | 0.001279 | 0.00032054
104 | 0.9924 | -0.14496 | 0.001507 | 0.00037769
105 | 0.9758 | -0.46628 | 0.0013966 | 0.00035002
106 | 0.97543 | -0.47366 | 0.00057546 | 0.00014422
107 | 0.97501 | -0.48196 | 0.00016887 | 4.2323e-05
108 | 0.97004 | -0.58037 | 0.0004437 | 0.0001112
109 | 0.97008 | -0.57956 | 0.00090222 | 0.00022612
110 | 0.97012 | -0.57882 | 0.00023592 | 5.9126e-05
111 | 0.97014 | -0.57851 | 0.00058008 | 0.00014538
112 | 0.97014 | -0.57833 | 0.0005273 | 0.00013216
113 | 0.97015 | -0.57816 | 0.00013301 | 3.3335e-05
114 | 0.97023 | -0.57658 | 0 | 0
115 | 0.97043 | -0.57267 | 0.00026506 | 6.6429e-05
116 | 0.97036 | -0.57405 | 0.00036311 | 9.1005e-05
117 | 0.97085 | -0.56438 | 0.00032573 | 8.1636e-05
118 | 0.97035 | -0.57434 | 0.00012312 | 3.0857e-05
119 | 0.97036 | -0.57411 | 0.00025544 | 6.402e-05
120 | 0.97093 | -0.56276 | 0.0001757 | 4.4035e-05
121 | 0.97108 | -0.55963 | 0.0004388 | 0.00010997
122 | 0.97125 | -0.55638 | 0.002248 | 0.00056341
123 | 0.97174 | -0.54662 | 0 | 0
124 | 0.97442 | -0.49351 | 0 | 0
125 | 0.97407 | -0.50044 | 0.00033961 | 8.5114e-05
126 | 0.97359 | -0.50999 | 0 | 0
127 | 0.97358 | -0.51007 | 0.00017546 | 4.3973e-05
128 | 0.97359 | -0.50989 | 0 | 0
129 | 0.97404 | -0.50115 | 0.00027145 | 6.8032e-05
130 | 0.97365 | -0.50886 | 0.00050942 | 0.00012767
131 | 0.97305 | -0.52067 | 0.00013438 | 3.3679e-05
132 | 0.97368 | -0.50813 | 0 | 0
133 | 0.97256 | -0.53045 | 0.00047424 | 0.00011886
134 | 0.97363 | -0.5091 | 0.00034134 | 8.5547e-05
135 | 0.97339 | -0.51386 | 0.00043391 | 0.00010875
136 | 0.97298 | -0.52211 | 0.00048426 | 0.00012137
137 | 0.97276 | -0.52638 | 0 | 0
138 | 0.97285 | -0.52458 | 0.00030405 | 7.6202e-05
139 | 0.97257 | -0.5302 | 0.00032637 | 8.1797e-05
140 | 0.97289 | -0.52389 | 0.00063114 | 0.00015818
141 | 0.97255 | -0.5306 | 0.0014126 | 0.00035403
142 | 0.97297 | -0.52217 | 0.00037794 | 9.4721e-05
143 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.25781 | -0.065911 | 0.25786 | 0.065943 | 5.0076e-05 | 3.1862e-05 | 0.3856 | 0.3856 | 0.3856 | 0.99608 | -0.074162 | 0.99629 | -0.070148 | 26.4833
1 | 0.2563 | 0.065532 | -0.25609 | -0.065401 | 0.00020571 | 0.00013087 | 0.38334 | 0.38334 | 0.38334 | 0.99608 | -0.074162 | 0.99521 | -0.090765 | 26.3282
2 | -0.25786 | -0.065943 | 0.25809 | 0.066086 | 0.00022562 | 0.00014355 | 0.3856 | 0.3856 | 0.3856 | 0.99629 | -0.070148 | 0.99725 | -0.052083 | 26.4833
3 | 0.22508 | 0.057611 | -0.22464 | -0.057328 | 0.00044497 | 0.00028261 | 0.33696 | 0.33696 | 0.33696 | 0.99521 | -0.090765 | 0.99306 | -0.13168 | 23.1432
4 | 0.031012 | 0.00779 | -0.031003 | -0.0077842 | 9.274e-06 | 5.786e-06 | 0.046375 | 0.046375 | 0.046375 | 0.99521 | -0.090765 | 0.99488 | -0.097033 | 12.7403
5 | -0.26152 | -0.066946 | 0.26157 | 0.066977 | 4.9283e-05 | 3.1361e-05 | 0.39071 | 0.39071 | 0.39071 | 0.99725 | -0.052083 | 0.99745 | -0.048193 | 26.8347
6 | 0.22066 | 0.056333 | -0.22035 | -0.056131 | 0.00031915 | 0.00020265 | 0.33101 | 0.33102 | 0.33102 | 0.99306 | -0.13168 | 0.99149 | -0.16166 | 22.7346
7 | 0.025906 | 0.0065068 | -0.025904 | -0.0065055 | 2.1296e-06 | 1.3138e-06 | 0.038751 | 0.038751 | 0.038751 | 0.99488 | -0.097033 | 0.99479 | -0.098756 | 10.646
8 | -0.0028344 | -0.00071037 | 0.0028345 | 0.00071024 | 1.0525e-07 | -1.3491e-07 | 0.0042421 | 0.0042421 | 0.0042421 | 0.99423 | -0.10969 | 0.99427 | -0.10891 | 1.1654
9 | -0.025891 | -0.0064977 | 0.025904 | 0.0065055 | 1.2546e-05 | 7.7403e-06 | 0.038752 | 0.038751 | 0.038752 | 0.99427 | -0.10891 | 0.99479 | -0.098756 | 10.646
10 | 0.023057 | 0.0057875 | -0.023056 | -0.005787 | 7.5929e-07 | 4.639e-07 | 0.034509 | 0.034509 | 0.034509 | 0.99427 | -0.10891 | 0.99423 | -0.1096 | 9.4806
11 | -0.26428 | -0.067656 | 0.2646 | 0.067866 | 0.00032917 | 0.00020949 | 0.39476 | 0.39476 | 0.39476 | 0.99745 | -0.048193 | 0.99881 | -0.02251 | 27.1125
12 | 0.21809 | 0.055564 | -0.2179 | -0.055448 | 0.00018258 | 0.00011591 | 0.32762 | 0.32763 | 0.32763 | 0.99149 | -0.16166 | 0.99058 | -0.17902 | 22.5017
13 | 0.020575 | 0.0051654 | -0.020565 | -0.005159 | 1.0513e-05 | 6.3454e-06 | 0.030797 | 0.030797 | 0.030797 | 0.99423 | -0.1096 | 0.99368 | -0.12032 | 8.4607
14 | -0.26611 | -0.068244 | 0.2664 | 0.068429 | 0.00029084 | 0.00018511 | 0.397 | 0.397 | 0.397 | 0.99881 | -0.02251 | 1 | 0 | 27.2666
15 | 0.21456 | 0.054611 | -0.21446 | -0.054544 | 0.00010535 | 6.6871e-05 | 0.3226 | 0.3226 | 0.3226 | 0.99058 | -0.17902 | 0.99005 | -0.18921 | 22.1569
16 | 0.015679 | 0.0039346 | -0.015664 | -0.0039264 | 1.417e-05 | 8.1821e-06 | 0.02348 | 0.02348 | 0.02348 | 0.99368 | -0.12032 | 0.9927 | -0.13929 | 6.4507
17 | 0.0048861 | 0.0012244 | -0.0048861 | -0.0012244 | 8.2634e-08 | -4.3161e-10 | 0.0073169 | 0.0073169 | 0.0073169 | 0.99368 | -0.12032 | 0.99366 | -0.12068 | 2.0101
18 | 0.21151 | 0.053805 | -0.21122 | -0.053621 | 0.00028989 | 0.00018396 | 0.31817 | 0.31817 | 0.31817 | 0.99005 | -0.18921 | 0.98857 | -0.2177 | 21.8526
19 | -0.018591 | -0.0046174 | 0.018591 | 0.0046174 | 2.6665e-07 | -3.7418e-09 | 0.028441 | 0.028441 | 0.028441 | 0.97216 | -0.53816 | 0.97218 | -0.53786 | 1.9534
20 | 0.011558 | 0.0028547 | -0.011556 | -0.002856 | 1.2347e-06 | -1.3002e-06 | 0.017675 | 0.017676 | 0.017676 | 0.97216 | -0.53816 | 0.97205 | -0.54043 | 1.214
21 | -0.026055 | -0.0064879 | 0.02606 | 0.0064896 | 5.6521e-06 | 1.7352e-06 | 0.039864 | 0.039863 | 0.039864 | 0.97218 | -0.53786 | 0.97241 | -0.53328 | 2.7379
22 | 0.011556 | 0.002856 | -0.011546 | -0.0028672 | 1.0664e-05 | -1.1203e-05 | 0.017676 | 0.017682 | 0.017682 | 0.97205 | -0.54043 | 0.97107 | -0.55998 | 1.2145
23 | -0.027471 | -0.0068433 | 0.027472 | 0.0068434 | 2.5608e-07 | 8.7138e-08 | 0.042023 | 0.042023 | 0.042023 | 0.97241 | -0.53328 | 0.97242 | -0.53308 | 2.8862
24 | 0.008922 | 0.0022098 | -0.0089178 | -0.002219 | 4.224e-06 | -9.2317e-06 | 0.013662 | 0.013666 | 0.013666 | 0.97107 | -0.55998 | 0.97057 | -0.56999 | 0.93863
25 | 0.00099861 | 0.00025011 | -0.00099859 | -0.00025027 | 1.2058e-08 | -1.6218e-07 | 0.0015301 | 0.0015302 | 0.0015302 | 0.97107 | -0.55998 | 0.97106 | -0.56023 | 0.42039
26 | -0.028882 | -0.0071969 | 0.028882 | 0.007197 | 2.5195e-07 | 9.2928e-08 | 0.044181 | 0.044181 | 0.044181 | 0.97242 | -0.53308 | 0.97243 | -0.5329 | 3.0344
27 | -0.0048855 | -0.0012244 | 0.0048861 | 0.0012244 | 5.3243e-07 | -2.7273e-09 | 0.007317 | 0.0073169 | 0.007317 | 0.99354 | -0.12296 | 0.99366 | -0.12068 | 2.0102
28 | 0.0034519 | 0.00086384 | -0.0034518 | -0.00086451 | 1.6647e-07 | -6.7577e-07 | 0.0052939 | 0.0052942 | 0.0052942 | 0.97018 | -0.57777 | 0.97013 | -0.57878 | 0.72723
29 | -0.004416 | -0.0011055 | 0.0044162 | 0.001103 | 2.2223e-07 | -2.411e-06 | 0.0067726 | 0.0067717 | 0.0067726 | 0.97018 | -0.57777 | 0.97023 | -0.57671 | 0.46515
30 | 0.0020487 | 0.00051287 | -0.0020486 | -0.0005132 | 1.2006e-07 | -3.2351e-07 | 0.0031422 | 0.0031423 | 0.0031423 | 0.97013 | -0.57878 | 0.97007 | -0.58001 | 0.86327
31 | -0.0054048 | -0.0013508 | 0.0054061 | 0.0013419 | 1.2723e-06 | -8.9529e-06 | 0.0082878 | 0.0082843 | 0.0082878 | 0.97023 | -0.57671 | 0.97048 | -0.57174 | 0.56922
32 | 0.0018035 | 0.00045178 | -0.0018035 | -0.00045199 | 5.7974e-08 | -2.1227e-07 | 0.0027664 | 0.0027665 | 0.0027665 | 0.97007 | -0.58001 | 0.97003 | -0.58069 | 0.76003
33 | -0.0054061 | -0.0013419 | 0.0054062 | 0.0013411 | 1.0974e-07 | -7.7282e-07 | 0.0082843 | 0.008284 | 0.0082843 | 0.97048 | -0.57174 | 0.9705 | -0.57131 | 0.56898
34 | 0.0085009 | 0.0021145 | -0.0085008 | -0.0021149 | 1.437e-07 | -3.5449e-07 | 0.013027 | 0.013028 | 0.013028 | 0.97057 | -0.56999 | 0.97055 | -0.57035 | 0.89475
35 | -0.030294 | -0.0075506 | 0.030298 | 0.0075525 | 4.6766e-06 | 1.8401e-06 | 0.04634 | 0.04634 | 0.04634 | 0.97243 | -0.5329 | 0.97259 | -0.52965 | 3.1827
36 | -0.0054062 | -0.0013411 | 0.0054063 | 0.0013401 | 1.433e-07 | -1.0093e-06 | 0.008284 | 0.0082836 | 0.008284 | 0.9705 | -0.57131 | 0.97053 | -0.57075 | 0.56896
37 | 0.0057189 | 0.0014177 | -0.0057188 | -0.0014184 | 1.1044e-07 | -6.8773e-07 | 0.0087624 | 0.0087626 | 0.0087626 | 0.97055 | -0.57035 | 0.97053 | -0.57075 | 0.60183
38 | -0.031709 | -0.0079061 | 0.03171 | 0.0079063 | 5.0249e-07 | 2.0847e-07 | 0.048498 | 0.048498 | 0.048498 | 0.97259 | -0.52965 | 0.97261 | -0.52931 | 3.3309
39 | 0.014158 | 0.0035488 | -0.014157 | -0.0035484 | 7.2893e-07 | 4.1072e-07 | 0.021222 | 0.021222 | 0.021222 | 0.9927 | -0.13929 | 0.99264 | -0.14037 | 5.8302
40 | -0.03312 | -0.0082598 | 0.03312 | 0.00826 | 5.0726e-07 | 2.1997e-07 | 0.050656 | 0.050656 | 0.050656 | 0.97261 | -0.52931 | 0.97263 | -0.52899 | 3.4791
41 | -0.034532 | -0.0086139 | 0.034539 | 0.0086168 | 6.5467e-06 | 2.9469e-06 | 0.052816 | 0.052816 | 0.052816 | 0.97263 | -0.52899 | 0.97283 | -0.525 | 3.6275
42 | -0.035951 | -0.0089707 | 0.035952 | 0.008971 | 5.9766e-07 | 2.7774e-07 | 0.054976 | 0.054976 | 0.054976 | 0.97283 | -0.525 | 0.97284 | -0.52465 | 3.7758
43 | -0.037362 | -0.0093244 | 0.037364 | 0.0093252 | 1.7456e-06 | 8.3386e-07 | 0.057133 | 0.057133 | 0.057133 | 0.97284 | -0.52465 | 0.97289 | -0.52366 | 3.9239
44 | -0.051989 | -0.012991 | 0.052014 | 0.013005 | 2.4766e-05 | 1.3773e-05 | 0.079502 | 0.079501 | 0.079502 | 0.97289 | -0.52366 | 0.9734 | -0.51365 | 5.4603
45 | -0.054445 | -0.013614 | 0.054448 | 0.013615 | 2.8676e-06 | 1.6156e-06 | 0.083218 | 0.083217 | 0.083218 | 0.9734 | -0.51365 | 0.97346 | -0.51254 | 5.7155
46 | -0.057328 | -0.014337 | 0.057331 | 0.014339 | 2.9872e-06 | 1.7054e-06 | 0.08762 | 0.08762 | 0.08762 | 0.97346 | -0.51254 | 0.97351 | -0.51144 | 6.0179
47 | -0.059636 | -0.014917 | 0.059652 | 0.014926 | 1.5627e-05 | 9.0029e-06 | 0.091144 | 0.091143 | 0.091144 | 0.97351 | -0.51144 | 0.97379 | -0.50594 | 6.2599
48 | -0.063257 | -0.015829 | 0.063265 | 0.015834 | 7.8061e-06 | 4.5523e-06 | 0.096653 | 0.096652 | 0.096653 | 0.97379 | -0.50594 | 0.97392 | -0.50334 | 6.6382
49 | -0.066923 | -0.016751 | 0.066939 | 0.01676 | 1.6077e-05 | 9.4724e-06 | 0.10224 | 0.10224 | 0.10224 | 0.97392 | -0.50334 | 0.97418 | -0.4983 | 7.0221
50 | 0.0084123 | 0.0021089 | -0.0084109 | -0.0021083 | 1.3127e-06 | 5.7166e-07 | 0.012795 | 0.012795 | 0.012795 | 0.97836 | -0.41611 | 0.9782 | -0.41939 | 3.515
51 | -0.0099697 | -0.0024992 | 0.0099752 | 0.0025019 | 5.4968e-06 | 2.7169e-06 | 0.015163 | 0.015163 | 0.015163 | 0.97836 | -0.41611 | 0.97895 | -0.40455 | 4.1658
52 | 0.0084109 | 0.0021083 | -0.0084091 | -0.0021075 | 1.8124e-06 | 7.8939e-07 | 0.012795 | 0.012795 | 0.012795 | 0.9782 | -0.41939 | 0.97797 | -0.42391 | 3.5151
53 | 0.0010391 | 0.00026003 | -0.0010391 | -0.00026042 | 3.0372e-08 | -3.8876e-07 | 0.0015793 | 0.0015795 | 0.0015795 | 0.97895 | -0.40455 | 0.97892 | -0.40516 | 0.43392
54 | -0.012124 | -0.0030401 | 0.012124 | 0.0030402 | 1.937e-07 | 1.0485e-07 | 0.018429 | 0.018429 | 0.018429 | 0.97895 | -0.40455 | 0.97897 | -0.40421 | 5.063
55 | -0.016402 | -0.0041122 | 0.016408 | 0.004116 | 6.4048e-06 | 3.7534e-06 | 0.024931 | 0.024931 | 0.024931 | 0.97897 | -0.40421 | 0.97939 | -0.39602 | 6.8491
56 | -0.017491 | -0.0043874 | 0.017491 | 0.0043875 | 1.0323e-07 | 6.1161e-08 | 0.026576 | 0.026576 | 0.026576 | 0.97939 | -0.39602 | 0.97939 | -0.3959 | 7.3012
57 | -0.020057 | -0.0050306 | 0.020065 | 0.0050349 | 7.1151e-06 | 4.2965e-06 | 0.030475 | 0.030475 | 0.030475 | 0.97939 | -0.3959 | 0.97977 | -0.38846 | 8.3723
58 | 0.012878 | 0.0032278 | -0.012878 | -0.0032278 | 6.3209e-08 | 3.4607e-08 | 0.019305 | 0.019305 | 0.019305 | 0.99264 | -0.14037 | 0.99264 | -0.14047 | 5.3035
59 | 0.011371 | 0.0028502 | -0.011371 | -0.0028499 | 5.0756e-07 | 2.6463e-07 | 0.017046 | 0.017046 | 0.017046 | 0.99264 | -0.14047 | 0.99259 | -0.14141 | 4.6831
60 | 0.010092 | 0.0025295 | -0.010091 | -0.002529 | 1.027e-06 | 5.0268e-07 | 0.01513 | 0.01513 | 0.01513 | 0.99259 | -0.14141 | 0.99248 | -0.14355 | 4.1566
61 | 0.19506 | 0.049571 | -0.1947 | -0.049345 | 0.00035754 | 0.00022656 | 0.29385 | 0.29385 | 0.29385 | 0.98857 | -0.2177 | 0.98659 | -0.25584 | 20.1822
62 | 0.19087 | 0.048385 | -0.19047 | -0.04813 | 0.00040351 | 0.0002556 | 0.28807 | 0.28807 | 0.28807 | 0.98659 | -0.25584 | 0.98432 | -0.29993 | 19.7853
63 | 0.0038323 | 0.00095961 | -0.003832 | -0.00095971 | 2.6919e-07 | -1.0211e-07 | 0.0057796 | 0.0057797 | 0.0057797 | 0.98659 | -0.25584 | 0.98652 | -0.25731 | 1.5878
64 | 0.18891 | 0.047739 | -0.18887 | -0.047716 | 3.5816e-05 | 2.2684e-05 | 0.28572 | 0.28572 | 0.28572 | 0.98432 | -0.29993 | 0.98411 | -0.30388 | 19.6234
65 | 0.001741 | 0.00043567 | -0.001741 | -0.00043605 | 8.8772e-08 | -3.8148e-07 | 0.0026259 | 0.002626 | 0.002626 | 0.98652 | -0.25731 | 0.98646 | -0.25838 | 0.72144
66 | 0.18617 | 0.047038 | -0.18616 | -0.047034 | 6.5335e-06 | 4.1368e-06 | 0.28163 | 0.28163 | 0.28163 | 0.98411 | -0.30388 | 0.98407 | -0.30461 | 19.3424
67 | 0.00099566 | 0.00024926 | -0.00099564 | -0.00024953 | 1.8403e-08 | -2.6598e-07 | 0.0015018 | 0.0015019 | 0.0015019 | 0.98646 | -0.25838 | 0.98644 | -0.25877 | 0.41261
68 | 0.097195 | 0.024473 | -0.097156 | -0.024449 | 3.8923e-05 | 2.3955e-05 | 0.14777 | 0.14777 | 0.14777 | 0.979 | -0.40353 | 0.97857 | -0.41191 | 10.1492
69 | -0.099924 | -0.025157 | 0.10001 | 0.025211 | 8.8347e-05 | 5.4487e-05 | 0.15192 | 0.15192 | 0.15192 | 0.979 | -0.40353 | 0.97994 | -0.38506 | 10.434
70 | 0.096009 | 0.024161 | -0.095897 | -0.024093 | 0.00011125 | 6.8407e-05 | 0.14603 | 0.14603 | 0.14603 | 0.97857 | -0.41191 | 0.97733 | -0.43619 | 10.0294
71 | -0.10351 | -0.026088 | 0.10361 | 0.026146 | 9.3023e-05 | 5.751e-05 | 0.15723 | 0.15723 | 0.15723 | 0.97994 | -0.38506 | 0.9809 | -0.36629 | 10.799
72 | 0.095897 | 0.024093 | -0.095849 | -0.024063 | 4.8766e-05 | 2.9988e-05 | 0.14603 | 0.14603 | 0.14603 | 0.97733 | -0.43619 | 0.97679 | -0.44685 | 10.0294
73 | -0.10973 | -0.027682 | 0.10976 | 0.027696 | 2.3142e-05 | 1.4361e-05 | 0.16653 | 0.16653 | 0.16653 | 0.9809 | -0.36629 | 0.98113 | -0.36189 | 11.4374
74 | 0.093829 | 0.023557 | -0.093825 | -0.023554 | 3.6313e-06 | 2.2291e-06 | 0.14295 | 0.14295 | 0.14295 | 0.97679 | -0.44685 | 0.97675 | -0.44766 | 9.8181
75 | 0.092087 | 0.023119 | -0.092046 | -0.023094 | 4.1297e-05 | 2.531e-05 | 0.1403 | 0.1403 | 0.1403 | 0.97675 | -0.44766 | 0.97627 | -0.45707 | 9.6363
76 | -0.07556 | -0.018935 | 0.075636 | 0.01898 | 7.5085e-05 | 4.505e-05 | 0.11535 | 0.11535 | 0.11535 | 0.97475 | -0.487 | 0.97581 | -0.46616 | 7.9222
77 | 0.073492 | 0.018416 | -0.073452 | -0.018392 | 3.9532e-05 | 2.3631e-05 | 0.11219 | 0.11219 | 0.11219 | 0.97475 | -0.487 | 0.97418 | -0.4983 | 7.7053
78 | 0.015425 | 0.0038526 | -0.015425 | -0.0038527 | 9.1928e-08 | -2.9761e-08 | 0.023517 | 0.023517 | 0.023517 | 0.97581 | -0.46616 | 0.9758 | -0.46628 | 1.6152
79 | -0.091546 | -0.022954 | 0.091586 | 0.022978 | 3.9671e-05 | 2.4304e-05 | 0.1396 | 0.1396 | 0.1396 | 0.97581 | -0.46616 | 0.97627 | -0.45707 | 9.5882
80 | 0.14151 | 0.035715 | -0.1414 | -0.035646 | 0.00011101 | 6.9747e-05 | 0.21452 | 0.21452 | 0.21452 | 0.98197 | -0.34549 | 0.98113 | -0.36189 | 14.7337
81 | -0.14387 | -0.036308 | 0.14393 | 0.036346 | 6.0293e-05 | 3.7903e-05 | 0.21811 | 0.2181 | 0.21811 | 0.98197 | -0.34549 | 0.98242 | -0.33675 | 14.9797
82 | 0.03164 | 0.0079493 | -0.03162 | -0.0079367 | 2.0239e-05 | 1.2657e-05 | 0.047994 | 0.047994 | 0.047994 | 0.98113 | -0.36189 | 0.98044 | -0.3753 | 13.1851
83 | -0.15528 | -0.039189 | 0.15539 | 0.039263 | 0.00011661 | 7.3489e-05 | 0.23529 | 0.23528 | 0.23529 | 0.98242 | -0.33675 | 0.98323 | -0.32108 | 16.1597
84 | 0.011343 | 0.0028436 | -0.011338 | -0.0028414 | 4.312e-06 | 2.2666e-06 | 0.01718 | 0.01718 | 0.01718 | 0.98242 | -0.33675 | 0.98201 | -0.34473 | 4.7199
85 | 0.028657 | 0.007194 | -0.028654 | -0.0071923 | 2.8641e-06 | 1.7821e-06 | 0.043496 | 0.043496 | 0.043496 | 0.98044 | -0.3753 | 0.98034 | -0.37739 | 11.9496
86 | -0.15539 | -0.039263 | 0.15543 | 0.039288 | 3.9757e-05 | 2.5056e-05 | 0.23528 | 0.23528 | 0.23528 | 0.98323 | -0.32108 | 0.9835 | -0.31575 | 16.1597
87 | 0.0068361 | 0.001713 | -0.0068351 | -0.0017127 | 9.838e-07 | 3.2035e-07 | 0.010358 | 0.010359 | 0.010359 | 0.98201 | -0.34473 | 0.98186 | -0.34775 | 2.8458
88 | 0.026454 | 0.0066409 | -0.026451 | -0.0066389 | 3.2213e-06 | 1.9945e-06 | 0.040157 | 0.040157 | 0.040157 | 0.98034 | -0.37739 | 0.98021 | -0.37995 | 11.0322
89 | -0.15716 | -0.039721 | 0.15724 | 0.039773 | 8.3923e-05 | 5.2907e-05 | 0.2379 | 0.2379 | 0.2379 | 0.9835 | -0.31575 | 0.98407 | -0.30461 | 16.339
90 | 0.0037603 | 0.00094205 | -0.0037597 | -0.00094227 | 5.6069e-07 | -2.2337e-07 | 0.0056986 | 0.0056988 | 0.0056988 | 0.98186 | -0.34775 | 0.9817 | -0.35088 | 1.5656
91 | 0.023639 | 0.0059342 | -0.02363 | -0.0059287 | 8.9087e-06 | 5.4692e-06 | 0.035889 | 0.035889 | 0.035889 | 0.98021 | -0.37995 | 0.9798 | -0.38785 | 9.8596
92 | 0.028917 | 0.0072603 | -0.028904 | -0.0072523 | 1.2883e-05 | 8.0171e-06 | 0.04373 | 0.04373 | 0.04373 | 0.98407 | -0.30461 | 0.9836 | -0.31396 | 12.0138
93 | 0.022584 | 0.0056665 | -0.022583 | -0.0056661 | 6.5335e-07 | 3.995e-07 | 0.0343 | 0.0343 | 0.0343 | 0.9798 | -0.38785 | 0.97977 | -0.38846 | 9.423
94 | 0.025114 | 0.0063024 | -0.02511 | -0.0062996 | 4.4962e-06 | 2.7722e-06 | 0.037997 | 0.037997 | 0.037997 | 0.9836 | -0.31396 | 0.9834 | -0.31771 | 10.4386
95 | 0.023383 | 0.0058669 | -0.023371 | -0.0058594 | 1.2329e-05 | 7.5579e-06 | 0.035384 | 0.035384 | 0.035384 | 0.9834 | -0.31771 | 0.98284 | -0.32878 | 9.7209
96 | 0.018745 | 0.0047 | -0.018739 | -0.0046966 | 5.746e-06 | 3.4365e-06 | 0.028381 | 0.028381 | 0.028381 | 0.98284 | -0.32878 | 0.98251 | -0.33521 | 7.7969
97 | 0.014115 | 0.0035377 | -0.014115 | -0.0035377 | 1.5992e-08 | 9.0527e-09 | 0.021378 | 0.021378 | 0.021378 | 0.98251 | -0.33521 | 0.98251 | -0.33524 | 5.873
98 | 0.0068029 | 0.001705 | -0.0068018 | -0.0017047 | 1.1136e-06 | 3.5848e-07 | 0.010303 | 0.010303 | 0.010303 | 0.98251 | -0.33524 | 0.98233 | -0.33867 | 2.8306
99 | 0.0085847 | 0.0021514 | -0.0085846 | -0.0021514 | 1.3759e-07 | 5.9438e-08 | 0.012871 | 0.012871 | 0.012871 | 0.99248 | -0.14355 | 0.99246 | -0.14388 | 3.536
100 | 0.0073061 | 0.001831 | -0.007306 | -0.0018309 | 1.15e-07 | 4.0576e-08 | 0.010954 | 0.010954 | 0.010954 | 0.99246 | -0.14388 | 0.99244 | -0.14421 | 3.0094
101 | 0.0057994 | 0.0014533 | -0.0057993 | -0.0014533 | 7.243e-08 | 1.3346e-08 | 0.0086953 | 0.0086953 | 0.0086953 | 0.99244 | -0.14421 | 0.99243 | -0.14448 | 2.3888
102 | 0.0030137 | 0.0007552 | -0.0030137 | -0.00075524 | 3.6527e-08 | -3.8263e-08 | 0.0045186 | 0.0045187 | 0.0045187 | 0.99242 | -0.14457 | 0.99241 | -0.14482 | 1.2414
103 | -0.0045203 | -0.0011328 | 0.0045204 | 0.0011328 | 1.9412e-08 | -2.1372e-09 | 0.0067776 | 0.0067776 | 0.0067776 | 0.99242 | -0.14457 | 0.99243 | -0.14448 | 1.862
104 | 0.001507 | 0.00037763 | -0.001507 | -0.00037769 | 1.0032e-08 | -6.1275e-08 | 0.0022596 | 0.0022596 | 0.0022596 | 0.99241 | -0.14482 | 0.9924 | -0.14496 | 0.62078
105 | 0.014028 | 0.0035026 | -0.014023 | -0.0035052 | 4.9183e-06 | -2.5804e-06 | 0.021387 | 0.021389 | 0.021389 | 0.9758 | -0.46628 | 0.97543 | -0.47366 | 1.4691
106 | 0.013448 | 0.003361 | -0.013443 | -0.0033643 | 5.3068e-06 | -3.3177e-06 | 0.020512 | 0.020514 | 0.020514 | 0.97543 | -0.47366 | 0.97501 | -0.48196 | 1.4089
107 | 0.013274 | 0.003322 | -0.013267 | -0.0033179 | 7.2899e-06 | 4.075e-06 | 0.020256 | 0.020256 | 0.020256 | 0.97501 | -0.48196 | 0.97442 | -0.49351 | 5.565
108 | -0.0004437 | -0.0001112 | 0.00044372 | 0.00011 | 1.711e-08 | -1.2058e-06 | 0.00068063 | 0.00068019 | 0.00068063 | 0.97004 | -0.58037 | 0.97008 | -0.57956 | 0.18699
109 | -0.0013459 | -0.00033611 | 0.001346 | 0.00033578 | 4.7084e-08 | -3.3374e-07 | 0.0020641 | 0.002064 | 0.0020641 | 0.97008 | -0.57956 | 0.97012 | -0.57882 | 0.56706
110 | -0.0015819 | -0.00039491 | 0.0015819 | 0.00039479 | 2.3374e-08 | -1.1582e-07 | 0.0024258 | 0.0024258 | 0.0024258 | 0.97012 | -0.57882 | 0.97014 | -0.57851 | 0.66644
111 | -0.002162 | -0.00054017 | 0.002162 | 0.00054013 | 1.8247e-08 | -4.2977e-08 | 0.0033155 | 0.0033155 | 0.0033155 | 0.97014 | -0.57851 | 0.97014 | -0.57833 | 0.91086
112 | -0.0026893 | -0.00067228 | 0.0026894 | 0.00067226 | 2.2357e-08 | -2.897e-08 | 0.0041243 | 0.0041243 | 0.0041243 | 0.97014 | -0.57833 | 0.97015 | -0.57816 | 1.133
113 | -0.0028224 | -0.00070559 | 0.0028226 | 0.00070535 | 2.1096e-07 | -2.3582e-07 | 0.0043283 | 0.0043282 | 0.0043283 | 0.97015 | -0.57816 | 0.97023 | -0.57658 | 1.1891
114 | -0.0028226 | -0.00070535 | 0.0028231 | 0.00070477 | 5.2489e-07 | -5.871e-07 | 0.0043282 | 0.0043278 | 0.0043282 | 0.97023 | -0.57658 | 0.97043 | -0.57267 | 1.1891
115 | 0.00074173 | 0.00018334 | -0.00074168 | -0.00018453 | 4.8153e-08 | -1.1971e-06 | 0.0011364 | 0.0011369 | 0.0011369 | 0.97043 | -0.57267 | 0.97036 | -0.57405 | 0.31232
116 | -0.0038299 | -0.00095453 | 0.0038314 | 0.00095406 | 1.5057e-06 | -4.7647e-07 | 0.0058707 | 0.0058701 | 0.0058707 | 0.97043 | -0.57267 | 0.97085 | -0.56438 | 1.6128
117 | 0.00037857 | 9.353e-05 | -0.00037857 | -9.3651e-05 | 1.2386e-09 | -1.2046e-07 | 0.00058004 | 0.00058008 | 0.00058008 | 0.97036 | -0.57405 | 0.97036 | -0.57411 | 0.15936
118 | -0.0041571 | -0.0010357 | 0.0041574 | 0.0010356 | 3.1917e-07 | -5.5179e-08 | 0.0063694 | 0.0063693 | 0.0063694 | 0.97085 | -0.56438 | 0.97093 | -0.56276 | 1.7498
119 | -0.00012312 | -3.0857e-05 | 0.00012312 | 2.963e-05 | 1.3255e-09 | -1.2269e-06 | 0.00018881 | 0.00018837 | 0.00018881 | 0.97035 | -0.57434 | 0.97036 | -0.57411 | 0.05187
120 | -0.0043331 | -0.0010797 | 0.0043338 | 0.0010796 | 6.4445e-07 | -6.9915e-08 | 0.0066386 | 0.0066384 | 0.0066386 | 0.97093 | -0.56276 | 0.97108 | -0.55963 | 1.8238
121 | -0.0047726 | -0.0011896 | 0.0047733 | 0.0011896 | 7.3548e-07 | 1.664e-08 | 0.0073108 | 0.0073106 | 0.0073108 | 0.97108 | -0.55963 | 0.97125 | -0.55638 | 2.0085
122 | -0.0070214 | -0.001753 | 0.0070246 | 0.0017542 | 3.2557e-06 | 1.1542e-06 | 0.010755 | 0.010754 | 0.010755 | 0.97125 | -0.55638 | 0.97174 | -0.54662 | 2.9546
123 | -0.0070246 | -0.0017542 | 0.00703 | 0.0017561 | 5.3998e-06 | 1.9121e-06 | 0.010754 | 0.010754 | 0.010754 | 0.97174 | -0.54662 | 0.97256 | -0.53045 | 2.9545
124 | 0.013267 | 0.0033179 | -0.013262 | -0.0033155 | 4.3731e-06 | 2.4449e-06 | 0.020256 | 0.020257 | 0.020257 | 0.97442 | -0.49351 | 0.97407 | -0.50044 | 5.565
125 | 0.012923 | 0.0032304 | -0.012922 | -0.0032301 | 4.3694e-07 | 2.4241e-07 | 0.019738 | 0.019738 | 0.019738 | 0.97407 | -0.50044 | 0.97404 | -0.50115 | 5.4225
126 | 0.00017546 | 4.3662e-05 | -0.00017546 | -4.3973e-05 | 6.7659e-10 | -3.117e-07 | 0.00026805 | 0.00026816 | 0.00026816 | 0.97359 | -0.50999 | 0.97358 | -0.51007 | 0.073671
127 | -0.00017546 | -4.3662e-05 | 0.00017546 | 4.3287e-05 | 8.113e-10 | -3.741e-07 | 0.00026805 | 0.00026792 | 0.00026805 | 0.97359 | -0.50999 | 0.97359 | -0.50989 | 0.073641
128 | -0.0078215 | -0.0019548 | 0.0078219 | 0.001955 | 3.8441e-07 | 1.5678e-07 | 0.011952 | 0.011952 | 0.011952 | 0.97359 | -0.50989 | 0.97365 | -0.50886 | 3.2836
129 | 0.007646 | 0.0019115 | -0.0076421 | -0.00191 | 3.9161e-06 | 1.5557e-06 | 0.011684 | 0.011685 | 0.011685 | 0.97359 | -0.50989 | 0.97305 | -0.52067 | 3.2101
130 | 0.012651 | 0.0031621 | -0.012646 | -0.0031598 | 4.1966e-06 | 2.3129e-06 | 0.019323 | 0.019323 | 0.019323 | 0.97404 | -0.50115 | 0.97368 | -0.50813 | 5.3086
131 | -0.0083313 | -0.0020826 | 0.0083316 | 0.0020828 | 2.8787e-07 | 1.2533e-07 | 0.012731 | 0.012731 | 0.012731 | 0.97365 | -0.50886 | 0.97368 | -0.50813 | 3.4975
132 | 0.0075077 | 0.0018763 | -0.0075043 | -0.0018749 | 3.4904e-06 | 1.3569e-06 | 0.011479 | 0.011479 | 0.011479 | 0.97305 | -0.52067 | 0.97256 | -0.53045 | 3.1537
133 | 0.0043149 | 0.001077 | -0.0043147 | -0.001077 | 1.993e-07 | -2.4534e-08 | 0.0065925 | 0.0065926 | 0.0065926 | 0.97368 | -0.50813 | 0.97363 | -0.5091 | 1.8112
134 | 0.0039733 | 0.00099148 | -0.0039724 | -0.00099171 | 8.9708e-07 | -2.3285e-07 | 0.0060709 | 0.0060712 | 0.0060712 | 0.97363 | -0.5091 | 0.97339 | -0.51386 | 1.6679
135 | 0.0035385 | 0.00088297 | -0.0035371 | -0.00088365 | 1.3878e-06 | -6.8394e-07 | 0.0054079 | 0.0054085 | 0.0054085 | 0.97339 | -0.51386 | 0.97298 | -0.52211 | 1.4858
136 | 0.00037794 | 9.4616e-05 | -0.00037794 | -9.4721e-05 | 1.0585e-09 | -1.0426e-07 | 0.00057796 | 0.000578 | 0.000578 | 0.97298 | -0.52211 | 0.97297 | -0.52217 | 0.15879
137 | 0.0026749 | 0.00066767 | -0.0026747 | -0.00066797 | 2.2568e-07 | -3.0235e-07 | 0.0040899 | 0.0040901 | 0.0040901 | 0.97298 | -0.52211 | 0.97289 | -0.52389 | 1.1236
138 | -0.0017393 | -0.00043437 | 0.0017394 | 0.00043377 | 1.488e-07 | -6.0107e-07 | 0.00266 | 0.0026598 | 0.00266 | 0.97276 | -0.52638 | 0.97285 | -0.52458 | 0.73077
139 | 0.0017393 | 0.00043437 | -0.001739 | -0.00043565 | 3.1618e-07 | -1.2764e-06 | 0.00266 | 0.0026606 | 0.0026606 | 0.97276 | -0.52638 | 0.97257 | -0.5302 | 0.73092
140 | -0.0020435 | -0.00050998 | 0.0020436 | 0.00050979 | 6.6869e-08 | -1.8397e-07 | 0.0031248 | 0.0031247 | 0.0031248 | 0.97285 | -0.52458 | 0.97289 | -0.52389 | 0.85847
141 | 0.0014126 | 0.00035385 | -0.0014126 | -0.00035403 | 2.6657e-08 | -1.7179e-07 | 0.0021612 | 0.0021613 | 0.0021613 | 0.97257 | -0.5302 | 0.97255 | -0.5306 | 0.59376

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27147 | 0.069285

## res_load
| p_mw | q_mvar
0 | 0.0015117 | 0.00037888
1 | 0.0034297 | 0.00085955
2 | 0.0039711 | 0.00099525
3 | 0.005097 | 0.0012774
4 | 0.0028344 | 0.00071037
5 | 0.0027106 | 0.00067935
6 | 0.002259 | 0.00056616
7 | 0.0024806 | 0.00062169
8 | 0.0015064 | 0.00037753
9 | 0.003343 | 0.00083783
10 | 0.0034154 | 0.00085598
11 | 0.0029484 | 0.00073893
12 | 0.0070335 | 0.0017628
13 | 0.0074632 | 0.0018705
14 | 0.0014112 | 0.00035369
15 | 0.0016251 | 0.00040728
16 | 0.0014105 | 0.00035349
17 | 0.0048855 | 0.0012244
18 | 0.00096406 | 0.00024162
19 | 0.0014031 | 0.00035164
20 | 0.00098859 | 0.00024776
21 | 0.00024504 | 6.1413e-05
22 | 0.0018035 | 0.00045199
23 | 0.00099859 | 0.00025027
24 | 0.00041687 | 0.00010448
25 | 0.0014111 | 0.00035365
26 | 0.0027819 | 0.00069722
27 | 0.00031243 | 7.8302e-05
28 | 0.0014108 | 0.00035358
29 | 0.0015066 | 0.0003776
30 | 0.0014105 | 0.00035349
31 | 0.001412 | 0.00035388
32 | 0.001412 | 0.00035389
33 | 0.0014102 | 0.00035342
34 | 0.014626 | 0.0036655
35 | 0.0024312 | 0.0006093
36 | 0.0028801 | 0.00072181
37 | 0.0023054 | 0.00057778
38 | 0.0036054 | 0.0009036
39 | 0.0036582 | 0.00091684
40 | 0.0015575 | 0.00039033
41 | 0.0011097 | 0.00027812
42 | 0.0084091 | 0.0021075
43 | 0.0010391 | 0.00026042
44 | 0.0042775 | 0.001072
45 | 0.0010831 | 0.00027144
46 | 0.0025662 | 0.00064315
47 | 0.001279 | 0.00032054
48 | 0.0015066 | 0.0003776
49 | 0.0012784 | 0.0003204
50 | 0.016158 | 0.0040496
51 | 0.001559 | 0.00039073
52 | 0.0020909 | 0.00052404
53 | 0.0027063 | 0.00067826
54 | 0.0007453 | 0.00018679
55 | 0.0027291 | 0.00068398
56 | 0.0011475 | 0.00028759
57 | 0.0035001 | 0.00087721
58 | 0.006128 | 0.0015358
59 | 0.00202 | 0.00050627
60 | 0.0017379 | 0.00043556
61 | 0.0020687 | 0.00051847
62 | 0.00048588 | 0.00012177
63 | 0.0065128 | 0.0016323
64 | 0.0023647 | 0.00059264
65 | 0.0029632 | 0.00074265
66 | 0.0045022 | 0.0011283
67 | 0.0022001 | 0.00055139
68 | 0.0017259 | 0.00043254
69 | 0.0030749 | 0.00077064
70 | 0.0028117 | 0.00070467
71 | 0.0037597 | 0.00094227
72 | 0.0010464 | 0.00026225
73 | 0.0037899 | 0.00094985
74 | 0.0017266 | 0.00043272
75 | 0.0046257 | 0.0011593
76 | 0.0046241 | 0.0011589
77 | 0.0025183 | 0.00063114
78 | 0.0073123 | 0.0018326
79 | 0.0068018 | 0.0017047
80 | 0.00045964 | 0.0001152
81 | 0.0015066 | 0.0003776
82 | 0.0012784 | 0.0003204
83 | 0.0015066 | 0.0003776
84 | 0.00099564 | 0.00024953
85 | 0.0015066 | 0.0003776
86 | 0.0015066 | 0.0003776
87 | 0.001279 | 0.00032054
88 | 0.001507 | 0.00037769
89 | 0.0013966 | 0.00035002
90 | 0.00057546 | 0.00014422
91 | 0.00016887 | 4.2323e-05
92 | 0.0004437 | 0.0001112
93 | 0.00090222 | 0.00022612
94 | 0.00023592 | 5.9126e-05
95 | 0.00058008 | 0.00014538
96 | 0.0005273 | 0.00013216
97 | 0.00013301 | 3.3335e-05
98 | 0.00026506 | 6.6429e-05
99 | 0.00036311 | 9.1005e-05
100 | 0.00032573 | 8.1636e-05
101 | 0.00012312 | 3.0857e-05
102 | 0.00025544 | 6.402e-05
103 | 0.0001757 | 4.4035e-05
104 | 0.0004388 | 0.00010997
105 | 0.002248 | 0.00056341
106 | 0.00033961 | 8.5114e-05
107 | 0.00017546 | 4.3973e-05
108 | 0.00027145 | 6.8032e-05
109 | 0.00050942 | 0.00012767
110 | 0.00013438 | 3.3679e-05
111 | 0.00047424 | 0.00011886
112 | 0.00034134 | 8.5547e-05
113 | 0.00043391 | 0.00010875
114 | 0.00048426 | 0.00012137
115 | 0.00030405 | 7.6202e-05
116 | 0.00032637 | 8.1797e-05
117 | 0.00063114 | 0.00015818
118 | 0.0014126 | 0.00035403
119 | 0.00037794 | 9.4721e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1