## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1346-16_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1346-16_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1346-16_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1346-16_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1346-16_0_5_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_1346-16_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1346-16_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1346-16_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1346-16_0_5_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1346-16_0_5_node_98 | 0.4 | n |  | TRUE
10 | bus_LV_1346-16_0_5_node_68 | 0.4 | n |  | TRUE
11 | bus_LV_1346-16_0_5_node_52 | 0.4 | n |  | TRUE
12 | bus_LV_1346-16_0_5_node_97 | 0.4 | n |  | TRUE
13 | bus_LV_1346-16_0_5_node_53 | 0.4 | n |  | TRUE
14 | bus_LV_1346-16_0_5_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1346-16_0_5_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1346-16_0_5_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1346-16_0_5_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1346-16_0_5_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1346-16_0_5_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1346-16_0_5_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1346-16_0_5_node_41 | 0.4 | n |  | TRUE
22 | bus_LV_1346-16_0_5_node_63 | 0.4 | n |  | TRUE
23 | bus_LV_1346-16_0_5_node_42 | 0.4 | n |  | TRUE
24 | bus_LV_1346-16_0_5_node_65 | 0.4 | n |  | TRUE
25 | bus_LV_1346-16_0_5_node_61 | 0.4 | n |  | TRUE
26 | bus_LV_1346-16_0_5_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1346-16_0_5_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_1346-16_0_5_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_1346-16_0_5_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_1346-16_0_5_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_1346-16_0_5_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_1346-16_0_5_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_1346-16_0_5_node_91 | 0.4 | n |  | TRUE
34 | bus_LV_1346-16_0_5_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_1346-16_0_5_node_77 | 0.4 | n |  | TRUE
36 | bus_LV_1346-16_0_5_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_1346-16_0_5_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_1346-16_0_5_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_1346-16_0_5_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_1346-16_0_5_node_126 | 0.4 | n |  | TRUE
41 | bus_LV_1346-16_0_5_node_114 | 0.4 | n |  | TRUE
42 | bus_LV_1346-16_0_5_node_115 | 0.4 | n |  | TRUE
43 | bus_LV_1346-16_0_5_node_123 | 0.4 | n |  | TRUE
44 | bus_LV_1346-16_0_5_node_113 | 0.4 | n |  | TRUE
45 | bus_LV_1346-16_0_5_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_1346-16_0_5_node_121 | 0.4 | n |  | TRUE
47 | bus_LV_1346-16_0_5_node_119 | 0.4 | n |  | TRUE
48 | bus_LV_1346-16_0_5_node_118 | 0.4 | n |  | TRUE
49 | bus_LV_1346-16_0_5_node_120 | 0.4 | n |  | TRUE
50 | bus_LV_1346-16_0_5_node_124 | 0.4 | n |  | TRUE
51 | bus_LV_1346-16_0_5_node_28 | 0.4 | n |  | TRUE
52 | bus_LV_1346-16_0_5_node_31 | 0.4 | n |  | TRUE
53 | bus_LV_1346-16_0_5_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_1346-16_0_5_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_1346-16_0_5_node_83 | 0.4 | n |  | TRUE
56 | bus_LV_1346-16_0_5_node_82 | 0.4 | n |  | TRUE
57 | bus_LV_1346-16_0_5_node_111 | 0.4 | n |  | TRUE
58 | bus_LV_1346-16_0_5_node_122 | 0.4 | n |  | TRUE
59 | bus_LV_1346-16_0_5_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_1346-16_0_5_node_89 | 0.4 | n |  | TRUE
61 | bus_LV_1346-16_0_5_node_71 | 0.4 | n |  | TRUE
62 | bus_LV_1346-16_0_5_node_33 | 0.4 | n |  | TRUE
63 | bus_LV_1346-16_0_5_node_34 | 0.4 | n |  | TRUE
64 | bus_LV_1346-16_0_5_node_35 | 0.4 | n |  | TRUE
65 | bus_LV_1346-16_0_5_node_36 | 0.4 | n |  | TRUE
66 | bus_LV_1346-16_0_5_node_37 | 0.4 | n |  | TRUE
67 | bus_LV_1346-16_0_5_node_38 | 0.4 | n |  | TRUE
68 | bus_LV_1346-16_0_5_node_39 | 0.4 | n |  | TRUE
69 | bus_LV_1346-16_0_5_node_40 | 0.4 | n |  | TRUE
70 | bus_LV_1346-16_0_5_node_67 | 0.4 | n |  | TRUE
71 | bus_LV_1346-16_0_5_node_75 | 0.4 | n |  | TRUE
72 | bus_LV_1346-16_0_5_node_93 | 0.4 | n |  | TRUE
73 | bus_LV_1346-16_0_5_node_73 | 0.4 | n |  | TRUE
74 | bus_LV_1346-16_0_5_node_92 | 0.4 | n |  | TRUE
75 | bus_LV_1346-16_0_5_node_90 | 0.4 | n |  | TRUE
76 | bus_LV_1346-16_0_5_node_94 | 0.4 | n |  | TRUE
77 | bus_LV_1346-16_0_5_node_95 | 0.4 | n |  | TRUE
78 | bus_LV_1346-16_0_5_node_56 | 0.4 | n |  | TRUE
79 | bus_LV_1346-16_0_5_node_57 | 0.4 | n |  | TRUE
80 | bus_LV_1346-16_0_5_node_45 | 0.4 | n |  | TRUE
81 | bus_LV_1346-16_0_5_node_46 | 0.4 | n |  | TRUE
82 | bus_LV_1346-16_0_5_node_47 | 0.4 | n |  | TRUE
83 | bus_LV_1346-16_0_5_node_48 | 0.4 | n |  | TRUE
84 | bus_LV_1346-16_0_5_node_49 | 0.4 | n |  | TRUE
85 | bus_LV_1346-16_0_5_node_50 | 0.4 | n |  | TRUE
86 | bus_LV_1346-16_0_5_node_51 | 0.4 | n |  | TRUE
87 | bus_LV_1346-16_0_5_node_69 | 0.4 | n |  | TRUE
88 | bus_LV_1346-16_0_5_node_70 | 0.4 | n |  | TRUE
89 | bus_LV_1346-16_0_5_node_54 | 0.4 | n |  | TRUE
90 | bus_LV_1346-16_0_5_node_55 | 0.4 | n |  | TRUE
91 | bus_LV_1346-16_0_5_node_78 | 0.4 | n |  | TRUE
92 | bus_LV_1346-16_0_5_node_81 | 0.4 | n |  | TRUE
93 | bus_LV_1346-16_0_5_node_76 | 0.4 | n |  | TRUE
94 | bus_LV_1346-16_0_5_node_80 | 0.4 | n |  | TRUE
95 | bus_LV_1346-16_0_5_node_58 | 0.4 | n |  | TRUE
96 | bus_LV_1346-16_0_5_node_59 | 0.4 | n |  | TRUE
97 | bus_LV_1346-16_0_5_node_79 | 0.4 | n |  | TRUE
98 | bus_LV_1346-16_0_5_node_60 | 0.4 | n |  | TRUE
99 | bus_LV_1346-16_0_5_node_62 | 0.4 | n |  | TRUE
100 | bus_LV_1346-16_0_5_node_64 | 0.4 | n |  | TRUE
101 | bus_LV_1346-16_0_5_node_66 | 0.4 | n |  | TRUE
102 | bus_LV_1346-16_0_5_node_84 | 0.4 | n |  | TRUE
103 | bus_LV_1346-16_0_5_node_72 | 0.4 | n |  | TRUE
104 | bus_LV_1346-16_0_5_node_74 | 0.4 | n |  | TRUE
105 | bus_LV_1346-16_0_5_node_87 | 0.4 | n |  | TRUE
106 | bus_LV_1346-16_0_5_node_99 | 0.4 | n |  | TRUE
107 | bus_LV_1346-16_0_5_node_100 | 0.4 | n |  | TRUE
108 | bus_LV_1346-16_0_5_node_104 | 0.4 | n |  | TRUE
109 | bus_LV_1346-16_0_5_node_101 | 0.4 | n |  | TRUE
110 | bus_LV_1346-16_0_5_node_102 | 0.4 | n |  | TRUE
111 | bus_LV_1346-16_0_5_node_103 | 0.4 | n |  | TRUE
112 | bus_LV_1346-16_0_5_node_108 | 0.4 | n |  | TRUE
113 | bus_LV_1346-16_0_5_node_105 | 0.4 | n |  | TRUE
114 | bus_LV_1346-16_0_5_node_106 | 0.4 | n |  | TRUE
115 | bus_LV_1346-16_0_5_node_107 | 0.4 | n |  | TRUE
116 | bus_LV_1346-16_0_5_node_116 | 0.4 | n |  | TRUE
117 | bus_LV_1346-16_0_5_node_109 | 0.4 | n |  | TRUE
118 | bus_LV_1346-16_0_5_node_110 | 0.4 | n |  | TRUE
119 | bus_LV_1346-16_0_5_node_112 | 0.4 | n |  | TRUE
120 | bus_LV_1346-16_0_5_node_117 | 0.4 | n |  | TRUE
121 | bus_LV_1346-16_0_5_node_127 | 0.4 | n |  | TRUE
122 | bus_LV_1346-16_0_5_node_128 | 0.4 | n |  | TRUE
123 | bus_LV_1346-16_0_5_node_85 | 0.4 | n |  | TRUE
124 | bus_LV_1346-16_0_5_node_86 | 0.4 | n |  | TRUE
125 | bus_LV_1346-16_0_5_node_88 | 0.4 | n |  | TRUE
126 | bus_LV_1346-16_0_5_node_96 | 0.4 | n |  | TRUE
127 | bus_MV_19_0_node_40 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1346-16_0_5_load_0 | 0 | 0.0042699 | 0.0010701 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1346-16_0_5_load_3 | 2 | 0.0028887 | 0.00072397 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1346-16_0_5_load_6 | 6 | 0.0044212 | 0.001108 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1346-16_0_5_load_7 | 7 | 0.0032859 | 0.00082352 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1346-16_0_5_load_8 | 8 | 0.0031987 | 0.00080166 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1346-16_0_5_load_98 | 9 | 0.0010786 | 0.00027031 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1346-16_0_5_load_68 | 10 | 0.0015325 | 0.00038408 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1346-16_0_5_load_52 | 11 | 0.0026173 | 0.00065595 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1346-16_0_5_load_97 | 12 | 0.0021415 | 0.0005367 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1346-16_0_5_load_10 | 14 | 0.0029051 | 0.0007281 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1346-16_0_5_load_11 | 15 | 0.0045279 | 0.0011348 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1346-16_0_5_load_12 | 16 | 0.001354 | 0.00033935 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1346-16_0_5_load_13 | 17 | 0.0041504 | 0.0010402 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1346-16_0_5_load_14 | 18 | 0.0023602 | 0.00059152 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1346-16_0_5_load_15 | 19 | 0.0011544 | 0.00028931 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1346-16_0_5_load_16 | 20 | 0.002553 | 0.00063983 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1346-16_0_5_load_41 | 21 | 0.0035101 | 0.0008797 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1346-16_0_5_load_42 | 23 | 0.0029399 | 0.0007368 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1346-16_0_5_load_65 | 24 | 0.0021746 | 0.000545 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1346-16_0_5_load_61 | 25 | 0.0023949 | 0.00060023 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1346-16_0_5_load_17 | 26 | 0.0033502 | 0.00083963 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1346-16_0_5_load_18 | 27 | 0.0032083 | 0.00080407 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1346-16_0_5_load_19 | 28 | 0.0026155 | 0.0006555 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1346-16_0_5_load_20 | 29 | 0.0026256 | 0.00065803 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1346-16_0_5_load_21 | 30 | 0.0011956 | 0.00029964 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1346-16_0_5_load_22 | 31 | 0.0032664 | 0.00081864 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1346-16_0_5_load_23 | 32 | 0.0043193 | 0.0010825 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1346-16_0_5_load_91 | 33 | 0.0044107 | 0.0011054 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1346-16_0_5_load_29 | 34 | 0.0037822 | 0.0009479 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1346-16_0_5_load_77 | 35 | 0.0026311 | 0.00065942 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1346-16_0_5_load_24 | 37 | 0.0035024 | 0.00087777 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1346-16_0_5_load_25 | 38 | 0.00065315 | 0.00016369 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1346-16_0_5_load_27 | 39 | 0.00051303 | 0.00012858 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1346-16_0_5_load_126 | 40 | 0.0048746 | 0.0012217 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1346-16_0_5_load_114 | 41 | 0.00037148 | 9.3101e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1346-16_0_5_load_123 | 43 | 0.00082829 | 0.00020759 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1346-16_0_5_load_30 | 45 | 0.00043625 | 0.00010933 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1346-16_0_5_load_119 | 47 | 0.0003038 | 7.6138e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1346-16_0_5_load_118 | 48 | 0.00031843 | 7.9805e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1346-16_0_5_load_120 | 49 | 0.00044161 | 0.00011068 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1346-16_0_5_load_124 | 50 | 0.00028142 | 7.0529e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1346-16_0_5_load_31 | 52 | 0.0042062 | 0.0010542 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1346-16_0_5_load_32 | 53 | 0.002796 | 0.00070073 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1346-16_0_5_load_43 | 54 | 0.00073497 | 0.0001842 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1346-16_0_5_load_83 | 55 | 0.0029311 | 0.0007346 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1346-16_0_5_load_111 | 57 | 0.0002327 | 5.8321e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1346-16_0_5_load_122 | 58 | 0.00073998 | 0.00018546 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1346-16_0_5_load_44 | 59 | 0.0018782 | 0.00047073 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1346-16_0_5_load_89 | 60 | 0.0035856 | 0.00089863 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1346-16_0_5_load_71 | 61 | 0.0024034 | 0.00060235 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1346-16_0_5_load_33 | 62 | 0.0037034 | 0.00092815 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1346-16_0_5_load_34 | 63 | 0.0045225 | 0.0011335 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1346-16_0_5_load_35 | 64 | 0.0028684 | 0.00071888 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1346-16_0_5_load_37 | 66 | 0.0028695 | 0.00071916 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1346-16_0_5_load_39 | 68 | 0.0043426 | 0.0010884 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1346-16_0_5_load_67 | 70 | 0.0039032 | 0.00097823 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1346-16_0_5_load_75 | 71 | 0.0029869 | 0.00074859 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1346-16_0_5_load_93 | 72 | 0.0035142 | 0.00088074 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1346-16_0_5_load_73 | 73 | 0.0032012 | 0.00080229 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1346-16_0_5_load_92 | 74 | 0.0046321 | 0.0011609 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1346-16_0_5_load_90 | 75 | 0.0034924 | 0.00087528 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1346-16_0_5_load_94 | 76 | 0.0023269 | 0.00058317 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1346-16_0_5_load_95 | 77 | 0.0054378 | 0.0013628 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1346-16_0_5_load_56 | 78 | 0.0019944 | 0.00049985 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1346-16_0_5_load_57 | 79 | 0.0024747 | 0.00062022 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1346-16_0_5_load_45 | 80 | 0.0021764 | 0.00054545 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1346-16_0_5_load_46 | 81 | 0.0021802 | 0.00054641 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1346-16_0_5_load_47 | 82 | 0.0024662 | 0.0006181 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1346-16_0_5_load_48 | 83 | 0.0025937 | 0.00065005 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1346-16_0_5_load_49 | 84 | 0.0021456 | 0.00053774 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1346-16_0_5_load_50 | 85 | 0.001526 | 0.00038245 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1346-16_0_5_load_51 | 86 | 0.0036511 | 0.00091505 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1346-16_0_5_load_69 | 87 | 0.000688 | 0.00017243 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1346-16_0_5_load_70 | 88 | 0.0015322 | 0.000384 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1346-16_0_5_load_54 | 89 | 0.004122 | 0.0010331 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1346-16_0_5_load_55 | 90 | 0.0023053 | 0.00057775 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1346-16_0_5_load_78 | 91 | 0.0027604 | 0.00069181 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1346-16_0_5_load_81 | 92 | 0.0047016 | 0.0011783 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1346-16_0_5_load_80 | 94 | 0.001729 | 0.00043334 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1346-16_0_5_load_58 | 95 | 0.0016169 | 0.00040524 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1346-16_0_5_load_59 | 96 | 0.0020274 | 0.00050811 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1346-16_0_5_load_79 | 97 | 0.00081607 | 0.00020453 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1346-16_0_5_load_60 | 98 | 0.0028039 | 0.00070272 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1346-16_0_5_load_62 | 99 | 0.0024451 | 0.00061279 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1346-16_0_5_load_64 | 100 | 0.00088542 | 0.00022191 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1346-16_0_5_load_66 | 101 | 0.0024377 | 0.00061093 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1346-16_0_5_load_84 | 102 | 0.0035836 | 0.00089813 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1346-16_0_5_load_72 | 103 | 0.0045194 | 0.0011327 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1346-16_0_5_load_74 | 104 | 0.0025066 | 0.0006282 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1346-16_0_5_load_87 | 105 | 0.0026308 | 0.00065934 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1346-16_0_5_load_99 | 106 | 0.00027052 | 6.7798e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1346-16_0_5_load_100 | 107 | 0.00025547 | 6.4026e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1346-16_0_5_load_104 | 108 | 0.00067215 | 0.00016846 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1346-16_0_5_load_102 | 110 | 0.00016473 | 4.1286e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1346-16_0_5_load_103 | 111 | 8.3743e-05 | 2.0988e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1346-16_0_5_load_108 | 112 | 0.00031231 | 7.8273e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1346-16_0_5_load_105 | 113 | 0.00030224 | 7.5748e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1346-16_0_5_load_106 | 114 | 0.0007194 | 0.0001803 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1346-16_0_5_load_107 | 115 | 0.00022749 | 5.7015e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1346-16_0_5_load_116 | 116 | 0.0021204 | 0.00053143 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1346-16_0_5_load_110 | 118 | 0.00024862 | 6.231e-05 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1346-16_0_5_load_112 | 119 | 0.00028552 | 7.1558e-05 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1346-16_0_5_load_117 | 120 | 0.0039464 | 0.00098906 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1346-16_0_5_load_127 | 121 | 0.0017681 | 0.00044312 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1346-16_0_5_load_128 | 122 | 0.00091318 | 0.00022886 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1346-16_0_5_load_85 | 123 | 0.003171 | 0.00079472 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1346-16_0_5_load_86 | 124 | 0.0039908 | 0.0010002 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1346-16_0_5_load_88 | 125 | 0.0041253 | 0.0010339 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1346-16_0_5_load_96 | 126 | 0.0015595 | 0.00039086 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 125 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1346-16_0_5_line_0 |  | 0 | 1 | 0.027538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1346-16_0_5_line_1 |  | 1 | 2 | 0.01596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1346-16_0_5_line_2 |  | 1 | 3 | 0.048644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1346-16_0_5_line_3 |  | 2 | 7 | 0.017833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1346-16_0_5_line_4 |  | 3 | 8 | 0.024184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1346-16_0_5_line_5 |  | 4 | 5 | 0.017107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1346-16_0_5_line_6 |  | 4 | 6 | 0.0141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1346-16_0_5_line_7 |  | 5 | 9 | 0.010486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1346-16_0_5_line_8 |  | 6 | 10 | 0.011471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1346-16_0_5_line_9 |  | 8 | 11 | 0.0032858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1346-16_0_5_line_10 |  | 9 | 12 | 0.0088378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1346-16_0_5_line_11 |  | 11 | 13 | 0.016978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1346-16_0_5_line_12 |  | 12 | 126 | 0.016475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1346-16_0_5_line_13 |  | 13 | 89 | 0.032288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_1346-16_0_5_line_14 |  | 13 | 90 | 0.012258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_1346-16_0_5_line_15 |  | 14 | 15 | 0.00069611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1346-16_0_5_line_16 |  | 14 | 16 | 0.01431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1346-16_0_5_line_17 |  | 15 | 17 | 0.0042221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1346-16_0_5_line_18 |  | 16 | 18 | 0.0058131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1346-16_0_5_line_19 |  | 17 | 19 | 0.0052226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1346-16_0_5_line_20 |  | 18 | 20 | 0.0029993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1346-16_0_5_line_21 |  | 19 | 21 | 0.018652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1346-16_0_5_line_22 |  | 20 | 22 | 0.016632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1346-16_0_5_line_23 |  | 21 | 23 | 0.0028546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1346-16_0_5_line_24 |  | 22 | 24 | 0.011018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1346-16_0_5_line_25 |  | 22 | 25 | 0.021849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1346-16_0_5_line_26 |  | 23 | 76 | 0.017622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1346-16_0_5_line_27 |  | 24 | 68 | 0.025552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1346-16_0_5_line_28 |  | 25 | 98 | 0.019167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1346-16_0_5_line_29 |  | 26 | 27 | 0.0011989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1346-16_0_5_line_30 |  | 26 | 28 | 0.021591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1346-16_0_5_line_31 |  | 27 | 29 | 0.024665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1346-16_0_5_line_32 |  | 28 | 30 | 5.0619e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1346-16_0_5_line_33 |  | 29 | 31 | 0.0028033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1346-16_0_5_line_34 |  | 30 | 32 | 0.010504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1346-16_0_5_line_35 |  | 31 | 33 | 0.023243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1346-16_0_5_line_36 |  | 32 | 34 | 0.01856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1346-16_0_5_line_37 |  | 33 | 35 | 0.001592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1346-16_0_5_line_38 |  | 34 | 36 | 0.020849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1346-16_0_5_line_39 |  | 36 | 37 | 0.015802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1346-16_0_5_line_40 |  | 37 | 38 | 0.03322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1346-16_0_5_line_41 |  | 38 | 39 | 0.016636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_1346-16_0_5_line_42 |  | 38 | 40 | 0.13587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_1346-16_0_5_line_43 |  | 39 | 45 | 0.0040951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_1346-16_0_5_line_44 |  | 40 | 46 | 0.10893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_1346-16_0_5_line_45 |  | 40 | 50 | 0.11378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1346-16_0_5_line_46 |  | 41 | 42 | 0.036109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_1346-16_0_5_line_47 |  | 41 | 43 | 0.10133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1346-16_0_5_line_48 |  | 41 | 44 | 0.086923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_1346-16_0_5_line_49 |  | 42 | 46 | 0.062981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_1346-16_0_5_line_50 |  | 42 | 47 | 0.017991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1346-16_0_5_line_51 |  | 43 | 58 | 0.011892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1346-16_0_5_line_52 |  | 44 | 57 | 0.029161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1346-16_0_5_line_53 |  | 45 | 54 | 0.021406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_1346-16_0_5_line_54 |  | 47 | 48 | 0.018621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1346-16_0_5_line_55 |  | 48 | 49 | 0.021576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1346-16_0_5_line_56 |  | 51 | 52 | 0.017526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_1346-16_0_5_line_57 |  | 51 | 53 | 0.021023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_1346-16_0_5_line_58 |  | 52 | 55 | 0.027161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_1346-16_0_5_line_59 |  | 53 | 56 | 0.012245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_1346-16_0_5_line_60 |  | 54 | 59 | 0.00035977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_1346-16_0_5_line_61 |  | 55 | 60 | 0.0038783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_1346-16_0_5_line_62 |  | 56 | 61 | 0.0086702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_1346-16_0_5_line_63 |  | 57 | 118 | 0.048708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1346-16_0_5_line_64 |  | 59 | 78 | 0.024157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_1346-16_0_5_line_65 |  | 60 | 105 | 0.021749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_1346-16_0_5_line_66 |  | 61 | 88 | 0.034767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_1346-16_0_5_line_67 |  | 62 | 63 | 0.0090786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_1346-16_0_5_line_68 |  | 62 | 64 | 0.013555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_1346-16_0_5_line_69 |  | 63 | 65 | 0.01335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_1346-16_0_5_line_70 |  | 64 | 66 | 0.015652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_1346-16_0_5_line_71 |  | 65 | 67 | 0.007037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_1346-16_0_5_line_72 |  | 65 | 68 | 0.016286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1346-16_0_5_line_73 |  | 66 | 69 | 0.0024958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_1346-16_0_5_line_74 |  | 67 | 70 | 0.014759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_1346-16_0_5_line_75 |  | 69 | 71 | 0.014546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_1346-16_0_5_line_76 |  | 70 | 72 | 0.026078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_1346-16_0_5_line_77 |  | 71 | 73 | 0.0097516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_1346-16_0_5_line_78 |  | 72 | 86 | 0.003414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_1346-16_0_5_line_79 |  | 73 | 103 | 0.01179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_1346-16_0_5_line_80 |  | 74 | 75 | 0.003101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1346-16_0_5_line_81 |  | 75 | 125 | 0.024488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1346-16_0_5_line_82 |  | 76 | 77 | 0.004775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1346-16_0_5_line_83 |  | 77 | 126 | 0.0050344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1346-16_0_5_line_84 |  | 78 | 79 | 0.010201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_1346-16_0_5_line_85 |  | 79 | 95 | 0.01435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_1346-16_0_5_line_86 |  | 80 | 81 | 0.0051961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_1346-16_0_5_line_87 |  | 80 | 82 | 0.020103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_1346-16_0_5_line_88 |  | 81 | 83 | 0.023707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_1346-16_0_5_line_89 |  | 82 | 84 | 0.0046652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_1346-16_0_5_line_90 |  | 83 | 85 | 0.002634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_1346-16_0_5_line_91 |  | 84 | 86 | 0.021508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_1346-16_0_5_line_92 |  | 85 | 87 | 0.019947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_1346-16_0_5_line_93 |  | 87 | 88 | 0.00026331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_1346-16_0_5_line_94 |  | 88 | 102 | 0.10803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1346-16_0_5_line_95 |  | 89 | 91 | 0.0046865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_1346-16_0_5_line_96 |  | 90 | 92 | 0.028262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_1346-16_0_5_line_97 |  | 91 | 93 | 0.017667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_1346-16_0_5_line_98 |  | 92 | 94 | 0.0024638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_1346-16_0_5_line_99 |  | 93 | 104 | 0.003157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_1346-16_0_5_line_100 |  | 94 | 97 | 0.0068049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_1346-16_0_5_line_101 |  | 95 | 96 | 0.017467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_1346-16_0_5_line_102 |  | 96 | 97 | 0.014544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_1346-16_0_5_line_103 |  | 98 | 99 | 0.0041269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1346-16_0_5_line_104 |  | 99 | 100 | 0.0073669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1346-16_0_5_line_105 |  | 100 | 101 | 0.023193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1346-16_0_5_line_106 |  | 103 | 104 | 0.0152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_1346-16_0_5_line_107 |  | 105 | 123 | 0.0022995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_1346-16_0_5_line_108 |  | 106 | 107 | 0.0095289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1346-16_0_5_line_109 |  | 107 | 108 | 0.23301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1346-16_0_5_line_110 |  | 108 | 110 | 0.027654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1346-16_0_5_line_111 |  | 109 | 110 | 0.019167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1346-16_0_5_line_112 |  | 109 | 111 | 0.03294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1346-16_0_5_line_113 |  | 111 | 112 | 0.090662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1346-16_0_5_line_114 |  | 112 | 116 | 0.10076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1346-16_0_5_line_115 |  | 112 | 117 | 0.12237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1346-16_0_5_line_116 |  | 112 | 115 | 0.015268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1346-16_0_5_line_117 |  | 113 | 114 | 0.0060993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1346-16_0_5_line_118 |  | 114 | 115 | 0.12182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1346-16_0_5_line_119 |  | 116 | 120 | 0.026098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1346-16_0_5_line_120 |  | 117 | 118 | 0.015956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1346-16_0_5_line_121 |  | 118 | 119 | 0.07356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1346-16_0_5_line_122 |  | 120 | 121 | 0.04822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1346-16_0_5_line_123 |  | 121 | 122 | 0.065069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1346-16_0_5_line_124 |  | 123 | 124 | 0.021779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_1346-16_0_5_line_125 |  | 124 | 125 | 0.0029411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1346-16_0_5_trafo_88 | 0.63 MVA 20/0.4 kV | 127 | 125 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2711117.137 | 1225790.4322 | 2711101.0537 | 1225789.2755 | 2711091.3223 | 1225783.3124
1 | 2711117.137 | 1225790.4322 | 2711117.2763 | 1225806.3918
2 | 2711119.5604 | 1225741.8962 | 2711119.5794 | 1225760.7664 | 2711117.137 | 1225790.4322
3 | 2711117.2763 | 1225806.3918 | 2711117.3084 | 1225810.0725 | 2711116.6342 | 1225824.2087
4 | 2711119.5604 | 1225741.8962 | 2711136.4685 | 1225741.1224 | 2711143.7076 | 1225741.6536
5 | 2711187.2212 | 1225798.9253 | 2711170.1375 | 1225797.3383
6 | 2711170.1375 | 1225797.3383 | 2711171.2398 | 1225783.2818
7 | 2711187.2212 | 1225798.9253 | 2711191.9215 | 1225799.3691 | 2711197.6615 | 1225799.9027
8 | 2711171.2398 | 1225783.2818 | 2711171.8101 | 1225776.009 | 2711174.0446 | 1225772.4814
9 | 2711143.7076 | 1225741.6536 | 2711146.9847 | 1225741.8941
10 | 2711197.6615 | 1225799.9027 | 2711206.4614 | 1225800.7209
11 | 2711163.9171 | 1225743.1366 | 2711146.9847 | 1225741.8941
12 | 2711222.8618 | 1225802.2848 | 2711216.3246 | 1225801.6379 | 2711206.4614 | 1225800.7209
13 | 2711163.9171 | 1225743.1366 | 2711196.096 | 1225745.7883
14 | 2711163.9171 | 1225743.1366 | 2711164.5952 | 1225730.8977
15 | 2711280.9609 | 1225808.0344 | 2711281.6536 | 1225808.1029
16 | 2711295.8937 | 1225809.5122 | 2711281.6536 | 1225808.1029
17 | 2711280.9609 | 1225808.0344 | 2711276.7592 | 1225807.6186
18 | 2711295.8937 | 1225809.5122 | 2711301.6785 | 1225810.0846
19 | 2711271.562 | 1225807.1043 | 2711276.7592 | 1225807.6186
20 | 2711304.6633 | 1225810.38 | 2711301.6785 | 1225810.0846
21 | 2711271.562 | 1225807.1043 | 2711253.001 | 1225805.2674
22 | 2711321.214 | 1225812.0179 | 2711304.6633 | 1225810.38
23 | 2711253.001 | 1225805.2674 | 2711250.1602 | 1225804.9863
24 | 2711321.214 | 1225812.0179 | 2711322.2712 | 1225801.0508
25 | 2711321.214 | 1225812.0179 | 2711319.1152 | 1225833.7659
26 | 2711232.6235 | 1225803.2508 | 2711250.1602 | 1225804.9863
27 | 2711324.7231 | 1225775.6167 | 2711322.2712 | 1225801.0508
28 | 2711317.2741 | 1225852.8447 | 2711319.1152 | 1225833.7659
29 | 2711223.4662 | 1225652.8498 | 2711223.4019 | 1225654.047
30 | 2711223.4662 | 1225652.8498 | 2711224.6248 | 1225631.2903
31 | 2711222.0784 | 1225678.6764 | 2711223.4019 | 1225654.047
32 | 2711224.6275 | 1225631.2397 | 2711224.6248 | 1225631.2903
33 | 2711222.0784 | 1225678.6764 | 2711221.928 | 1225681.4757
34 | 2711224.6275 | 1225631.2397 | 2711225.1911 | 1225620.7504
35 | 2711221.928 | 1225681.4757 | 2711220.6809 | 1225704.6851
36 | 2711225.1911 | 1225620.7504 | 2711226.187 | 1225602.2175
37 | 2711220.5954 | 1225706.2748 | 2711220.6809 | 1225704.6851
38 | 2711227.3057 | 1225581.3984 | 2711226.187 | 1225602.2175
39 | 2711227.3057 | 1225581.3984 | 2711211.7188 | 1225578.8022
40 | 2711211.7188 | 1225578.8022 | 2711178.9502 | 1225573.3443
41 | 2711172.5669 | 1225587.008 | 2711173.0836 | 1225577.6825 | 2711178.9502 | 1225573.3443 | 2711178.9502 | 1225573.3443
42 | 2711178.9502 | 1225573.3443 | 2711146.5056 | 1225441.4051
43 | 2711172.3404 | 1225591.0968 | 2711172.5669 | 1225587.008
44 | 2711165.1559 | 1225334.0833 | 2711146.5056 | 1225441.4051
45 | 2711146.5056 | 1225441.4051 | 2711047.2856 | 1225385.722
46 | 2711223.0621 | 1225310.0024 | 2711257.5658 | 1225299.3542
47 | 2711257.5658 | 1225299.3542 | 2711306.9519 | 1225387.8296
48 | 2711257.5658 | 1225299.3542 | 2711338.7695 | 1225268.3454
49 | 2711165.1559 | 1225334.0833 | 2711186.461 | 1225322.8839 | 2711193.7057 | 1225319.0719 | 2711223.0621 | 1225310.0024
50 | 2711223.0621 | 1225310.0024 | 2711217.9335 | 1225300.8107 | 2711210.4815 | 1225300.3636
51 | 2711306.9519 | 1225387.8296 | 2711303.2877 | 1225396.0229 | 2711300.5209 | 1225396.9446
52 | 2711338.7695 | 1225268.3454 | 2711365.8235 | 1225257.4619
53 | 2711172.3404 | 1225591.0968 | 2711171.1563 | 1225612.47
54 | 2711197.9767 | 1225292.1443 | 2711199.626 | 1225299.7123 | 2711210.4815 | 1225300.3636
55 | 2711197.9767 | 1225292.1443 | 2711193.3825 | 1225271.0628
56 | 2711283.8901 | 1225589.3511 | 2711282.6802 | 1225606.8351
57 | 2711283.8901 | 1225589.3511 | 2711304.6422 | 1225592.7118
58 | 2711282.6802 | 1225606.8351 | 2711280.8052 | 1225633.931
59 | 2711316.7294 | 1225594.6692 | 2711304.6422 | 1225592.7118
60 | 2711171.1563 | 1225612.47 | 2711171.1364 | 1225612.8292
61 | 2711280.5375 | 1225637.8001 | 2711280.8052 | 1225633.931
62 | 2711316.7294 | 1225594.6692 | 2711325.2777 | 1225596.1183
63 | 2711411.5754 | 1225240.8351 | 2711388.5022 | 1225248.3385 | 2711365.8235 | 1225257.4619
64 | 2711169.8001 | 1225636.9495 | 2711171.1364 | 1225612.8292
65 | 2711280.5375 | 1225637.8001 | 2711279.0361 | 1225659.4968
66 | 2711325.2777 | 1225596.1183 | 2711338.778 | 1225598.4067 | 2711343.1532 | 1225604.8824 | 2711342.314 | 1225618.1152
67 | 2711304.0431 | 1225756.525 | 2711313.0465 | 1225757.6913
68 | 2711290.6006 | 1225754.7838 | 2711304.0431 | 1225756.525
69 | 2711326.2858 | 1225759.4062 | 2711313.0465 | 1225757.6913
70 | 2711275.0787 | 1225752.7732 | 2711290.6006 | 1225754.7838
71 | 2711333.3092 | 1225760.1048 | 2711326.2858 | 1225759.4062
72 | 2711326.2858 | 1225759.4062 | 2711324.7231 | 1225775.6167
73 | 2711272.6036 | 1225752.4526 | 2711275.0787 | 1225752.7732
74 | 2711333.3092 | 1225760.1048 | 2711334.2433 | 1225745.3749
75 | 2711272.6036 | 1225752.4526 | 2711258.1154 | 1225751.1626
76 | 2711334.2433 | 1225745.3749 | 2711335.8938 | 1225719.3496
77 | 2711248.4022 | 1225750.2977 | 2711258.1154 | 1225751.1626
78 | 2711336.1099 | 1225715.9425 | 2711335.8938 | 1225719.3496
79 | 2711236.6583 | 1225749.2521 | 2711248.4022 | 1225750.2977
80 | 2711275.4803 | 1225710.8811 | 2711275.2662 | 1225713.9747
81 | 2711275.4803 | 1225710.8811 | 2711277.1708 | 1225686.4519
82 | 2711232.6235 | 1225803.2508 | 2711227.8717 | 1225802.7806
83 | 2711222.8618 | 1225802.2848 | 2711227.8717 | 1225802.7806
84 | 2711169.8001 | 1225636.9495 | 2711169.2358 | 1225647.1353
85 | 2711168.442 | 1225661.4629 | 2711169.2358 | 1225647.1353
86 | 2711339.3677 | 1225664.5733 | 2711339.0388 | 1225669.759
87 | 2711337.7664 | 1225689.8218 | 2711339.0388 | 1225669.759
88 | 2711340.8681 | 1225640.9136 | 2711339.3677 | 1225664.5733
89 | 2711337.4712 | 1225694.4776 | 2711337.7664 | 1225689.8218
90 | 2711341.0348 | 1225638.2849 | 2711340.8681 | 1225640.9136
91 | 2711337.4712 | 1225694.4776 | 2711336.1099 | 1225715.9425
92 | 2711342.2973 | 1225618.378 | 2711341.0348 | 1225638.2849
93 | 2711342.314 | 1225618.1152 | 2711342.2973 | 1225618.378
94 | 2711342.314 | 1225618.1152 | 2711445.2195 | 1225585.2223
95 | 2711200.7666 | 1225746.1732 | 2711196.096 | 1225745.7883
96 | 2711164.5952 | 1225730.8977 | 2711166.1585 | 1225702.6794
97 | 2711218.3735 | 1225747.6241 | 2711200.7666 | 1225746.1732
98 | 2711166.1585 | 1225702.6794 | 2711166.2948 | 1225700.2194
99 | 2711218.3735 | 1225747.6241 | 2711221.5181 | 1225747.9041
100 | 2711166.6712 | 1225693.4249 | 2711166.2948 | 1225700.2194
101 | 2711167.4758 | 1225678.9029 | 2711168.442 | 1225661.4629
102 | 2711166.6712 | 1225693.4249 | 2711167.4758 | 1225678.9029
103 | 2711317.2741 | 1225852.8447 | 2711316.8776 | 1225856.9524
104 | 2711316.17 | 1225864.2853 | 2711316.8776 | 1225856.9524
105 | 2711316.17 | 1225864.2853 | 2711315.8144 | 1225867.9705 | 2711313.4317 | 1225887.3153
106 | 2711236.6583 | 1225749.2521 | 2711221.5181 | 1225747.9041
107 | 2711278.8773 | 1225661.7908 | 2711279.0361 | 1225659.4968
108 | 2711853.4794 | 1225073.4148 | 2711861.1536 | 1225079.0633
109 | 2711628.9432 | 1225135.6884 | 2711853.4794 | 1225073.4148
110 | 2711628.9432 | 1225135.6884 | 2711616.5007 | 1225149.824 | 2711613.1021 | 1225157.9649
111 | 2711605.718 | 1225175.6525 | 2711613.1021 | 1225157.9649
112 | 2711605.718 | 1225175.6525 | 2711572.7815 | 1225175.1846
113 | 2711572.7815 | 1225175.1846 | 2711546.3285 | 1225261.902
114 | 2711546.3285 | 1225261.902 | 2711510.6599 | 1225356.1405
115 | 2711546.3285 | 1225261.902 | 2711426.7491 | 1225235.9006
116 | 2711546.3285 | 1225261.902 | 2711561.2475 | 1225265.146
117 | 2711687.8611 | 1225283.3635 | 2711681.7972 | 1225282.7073
118 | 2711561.2475 | 1225265.146 | 2711681.7972 | 1225282.7073
119 | 2711517.3483 | 1225378.3929 | 2711518.587 | 1225362.5165 | 2711510.6599 | 1225356.1405
120 | 2711426.7491 | 1225235.9006 | 2711411.5754 | 1225240.8351
121 | 2711411.5754 | 1225240.8351 | 2711386.8388 | 1225171.5587
122 | 2711517.3483 | 1225378.3929 | 2711516.9799 | 1225383.1132 | 2711508.8603 | 1225389.8995 | 2711508.5531 | 1225396.1763 | 2711513.386 | 1225399.2692 | 2711524.9425 | 1225404.9233 | 2711532.7129 | 1225406.8895
123 | 2711532.7129 | 1225406.8895 | 2711551.7118 | 1225411.6968 | 2711572.9145 | 1225419.3222 | 2711595.7796 | 1225421.1581
124 | 2711278.8773 | 1225661.7908 | 2711277.3738 | 1225683.5179
125 | 2711277.3738 | 1225683.5179 | 2711277.1708 | 1225686.4519

## bus_geodata
| x | y | coords
0 | 2711091.3223 | 1225783.3124
1 | 2711117.137 | 1225790.4322
2 | 2711117.2763 | 1225806.3918
3 | 2711119.5604 | 1225741.8962
4 | 2711170.1375 | 1225797.3383
5 | 2711187.2212 | 1225798.9253
6 | 2711171.2398 | 1225783.2818
7 | 2711116.6342 | 1225824.2087
8 | 2711143.7076 | 1225741.6537
9 | 2711197.6615 | 1225799.9027
10 | 2711174.0446 | 1225772.4814
11 | 2711146.9847 | 1225741.8941
12 | 2711206.4614 | 1225800.7209
13 | 2711163.9171 | 1225743.1366
14 | 2711281.6536 | 1225808.1029
15 | 2711280.9609 | 1225808.0344
16 | 2711295.8937 | 1225809.5122
17 | 2711276.7592 | 1225807.6186
18 | 2711301.6785 | 1225810.0846
19 | 2711271.562 | 1225807.1043
20 | 2711304.6633 | 1225810.38
21 | 2711253.001 | 1225805.2674
22 | 2711321.214 | 1225812.0179
23 | 2711250.1602 | 1225804.9863
24 | 2711322.2712 | 1225801.0508
25 | 2711319.1152 | 1225833.7659
26 | 2711223.4662 | 1225652.8498
27 | 2711223.4019 | 1225654.047
28 | 2711224.6248 | 1225631.2903
29 | 2711222.0784 | 1225678.6764
30 | 2711224.6275 | 1225631.2397
31 | 2711221.928 | 1225681.4757
32 | 2711225.1911 | 1225620.7504
33 | 2711220.6809 | 1225704.6851
34 | 2711226.187 | 1225602.2175
35 | 2711220.5954 | 1225706.2748
36 | 2711227.3057 | 1225581.3984
37 | 2711211.7188 | 1225578.8022
38 | 2711178.9502 | 1225573.3443
39 | 2711172.5669 | 1225587.008
40 | 2711146.5056 | 1225441.4051
41 | 2711257.5658 | 1225299.3542
42 | 2711223.0621 | 1225310.0024
43 | 2711306.9519 | 1225387.8296
44 | 2711338.7695 | 1225268.3454
45 | 2711172.3404 | 1225591.0968
46 | 2711165.1559 | 1225334.0833
47 | 2711210.4815 | 1225300.3636
48 | 2711197.9767 | 1225292.1443
49 | 2711193.3825 | 1225271.0628
50 | 2711047.2856 | 1225385.722
51 | 2711283.8901 | 1225589.3511
52 | 2711282.6802 | 1225606.8351
53 | 2711304.6422 | 1225592.7118
54 | 2711171.1563 | 1225612.47
55 | 2711280.8052 | 1225633.931
56 | 2711316.7294 | 1225594.6692
57 | 2711365.8235 | 1225257.4619
58 | 2711300.5209 | 1225396.9446
59 | 2711171.1364 | 1225612.8292
60 | 2711280.5375 | 1225637.8001
61 | 2711325.2777 | 1225596.1183
62 | 2711304.0431 | 1225756.525
63 | 2711313.0465 | 1225757.6913
64 | 2711290.6006 | 1225754.7838
65 | 2711326.2858 | 1225759.4062
66 | 2711275.0787 | 1225752.7732
67 | 2711333.3092 | 1225760.1048
68 | 2711324.7231 | 1225775.6167
69 | 2711272.6036 | 1225752.4526
70 | 2711334.2433 | 1225745.3749
71 | 2711258.1154 | 1225751.1626
72 | 2711335.8938 | 1225719.3496
73 | 2711248.4022 | 1225750.2977
74 | 2711275.2662 | 1225713.9747
75 | 2711275.4803 | 1225710.8811
76 | 2711232.6235 | 1225803.2508
77 | 2711227.8717 | 1225802.7806
78 | 2711169.8001 | 1225636.9495
79 | 2711169.2358 | 1225647.1353
80 | 2711339.0388 | 1225669.759
81 | 2711339.3677 | 1225664.5733
82 | 2711337.7664 | 1225689.8218
83 | 2711340.8681 | 1225640.9136
84 | 2711337.4712 | 1225694.4776
85 | 2711341.0348 | 1225638.2849
86 | 2711336.1099 | 1225715.9425
87 | 2711342.2973 | 1225618.378
88 | 2711342.314 | 1225618.1152
89 | 2711196.096 | 1225745.7883
90 | 2711164.5952 | 1225730.8977
91 | 2711200.7666 | 1225746.1732
92 | 2711166.1585 | 1225702.6794
93 | 2711218.3735 | 1225747.6241
94 | 2711166.2948 | 1225700.2194
95 | 2711168.442 | 1225661.4629
96 | 2711167.4758 | 1225678.9029
97 | 2711166.6712 | 1225693.4249
98 | 2711317.2741 | 1225852.8447
99 | 2711316.8776 | 1225856.9524
100 | 2711316.17 | 1225864.2853
101 | 2711313.4317 | 1225887.3153
102 | 2711445.2195 | 1225585.2223
103 | 2711236.6583 | 1225749.2521
104 | 2711221.5181 | 1225747.9041
105 | 2711279.0361 | 1225659.4968
106 | 2711861.1536 | 1225079.0633
107 | 2711853.4794 | 1225073.4148
108 | 2711628.9432 | 1225135.6884
109 | 2711605.718 | 1225175.6525
110 | 2711613.1021 | 1225157.9649
111 | 2711572.7815 | 1225175.1846
112 | 2711546.3285 | 1225261.902
113 | 2711687.8611 | 1225283.3635
114 | 2711681.7972 | 1225282.7073
115 | 2711561.2475 | 1225265.146
116 | 2711510.66 | 1225356.1405
117 | 2711426.7491 | 1225235.9006
118 | 2711411.5754 | 1225240.8351
119 | 2711386.8388 | 1225171.5587
120 | 2711517.3483 | 1225378.3929
121 | 2711532.7129 | 1225406.8895
122 | 2711595.7796 | 1225421.1581
123 | 2711278.8773 | 1225661.7908
124 | 2711277.3738 | 1225683.5179
125 | 2711277.1708 | 1225686.4519
126 | 2711222.8618 | 1225802.2848
127 | 2711272.6036 | 1225752.4526

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97862 | -0.41114 | 0.0042699 | 0.0010701
1 | 0.97873 | -0.409 | 0 | 0
2 | 0.97864 | -0.41079 | 0.0028887 | 0.00072397
3 | 0.9792 | -0.39976 | 0 | 0
4 | 0.97797 | -0.42396 | 0 | 0
5 | 0.97807 | -0.4221 | 0 | 0
6 | 0.97789 | -0.42549 | 0.0044212 | 0.001108
7 | 0.97858 | -0.41186 | 0.0032859 | 0.00082352
8 | 0.97943 | -0.39517 | 0.0031987 | 0.00080166
9 | 0.97812 | -0.42097 | 0.0010786 | 0.00027031
10 | 0.97788 | -0.42581 | 0.0015325 | 0.00038408
11 | 0.97947 | -0.39435 | 0.0026173 | 0.00065595
12 | 0.97818 | -0.41983 | 0.0021415 | 0.0005367
13 | 0.97973 | -0.38934 | 0 | 0
14 | 0.9795 | -0.39394 | 0.0029051 | 0.0007281
15 | 0.97948 | -0.39438 | 0.0045279 | 0.0011348
16 | 0.98 | -0.38415 | 0.001354 | 0.00033935
17 | 0.97936 | -0.3967 | 0.0041504 | 0.0010402
18 | 0.98021 | -0.38003 | 0.0023602 | 0.00059152
19 | 0.97923 | -0.39918 | 0.0011544 | 0.00028931
20 | 0.98033 | -0.37778 | 0.002553 | 0.00063983
21 | 0.9788 | -0.40764 | 0.0035101 | 0.0008797
22 | 0.981 | -0.36453 | 0 | 0
23 | 0.97875 | -0.40876 | 0.0029399 | 0.0007368
24 | 0.98156 | -0.35357 | 0.0021746 | 0.000545
25 | 0.98078 | -0.36887 | 0.0023949 | 0.00060023
26 | 0.97386 | -0.50463 | 0.0033502 | 0.00083963
27 | 0.97384 | -0.50498 | 0.0032083 | 0.00080407
28 | 0.97425 | -0.4969 | 0.0026155 | 0.0006555
29 | 0.97355 | -0.51085 | 0.0026256 | 0.00065803
30 | 0.97425 | -0.49688 | 0.0011956 | 0.00029964
31 | 0.97352 | -0.51138 | 0.0032664 | 0.00081864
32 | 0.97448 | -0.49238 | 0.0043193 | 0.0010825
33 | 0.97337 | -0.51439 | 0.0044107 | 0.0011054
34 | 0.97496 | -0.48298 | 0.0037822 | 0.0009479
35 | 0.97336 | -0.51447 | 0.0026311 | 0.00065942
36 | 0.97557 | -0.47098 | 0 | 0
37 | 0.97603 | -0.46189 | 0.0035024 | 0.00087777
38 | 0.97711 | -0.4407 | 0.00065315 | 0.00016369
39 | 0.97733 | -0.43642 | 0.00051303 | 0.00012858
40 | 0.97646 | -0.45358 | 0.0048746 | 0.0012217
41 | 0.97571 | -0.46823 | 0.00037148 | 9.3101e-05
42 | 0.97583 | -0.46584 | 0 | 0
43 | 0.97557 | -0.47115 | 0.00082829 | 0.00020759
44 | 0.97521 | -0.47823 | 0 | 0
45 | 0.97738 | -0.43536 | 0.00043625 | 0.00010933
46 | 0.97606 | -0.46135 | 0 | 0
47 | 0.97582 | -0.46619 | 0.0003038 | 7.6138e-05
48 | 0.9758 | -0.46645 | 0.00031843 | 7.9805e-05
49 | 0.97579 | -0.46662 | 0.00044161 | 0.00011068
50 | 0.97643 | -0.45417 | 0.00028142 | 7.0529e-05
51 | 0.99475 | -0.099371 | 0 | 0
52 | 0.99566 | -0.082055 | 0.0042062 | 0.0010542
53 | 0.99366 | -0.12018 | 0.002796 | 0.00070073
54 | 0.97767 | -0.42976 | 0.00073497 | 0.0001842
55 | 0.9971 | -0.054781 | 0.0029311 | 0.0007346
56 | 0.99303 | -0.13218 | 0 | 0
57 | 0.97486 | -0.48495 | 0.0002327 | 5.8321e-05
58 | 0.97556 | -0.47131 | 0.00073998 | 0.00018546
59 | 0.97767 | -0.42967 | 0.0018782 | 0.00047073
60 | 0.99731 | -0.050843 | 0.0035856 | 0.00089863
61 | 0.99258 | -0.14068 | 0.0024034 | 0.00060235
62 | 0.98319 | -0.32192 | 0.0037034 | 0.00092815
63 | 0.98344 | -0.31687 | 0.0045225 | 0.0011335
64 | 0.98281 | -0.32924 | 0.0028684 | 0.00071888
65 | 0.98384 | -0.30918 | 0 | 0
66 | 0.98239 | -0.33749 | 0.0028695 | 0.00071916
67 | 0.98415 | -0.30318 | 0 | 0
68 | 0.98291 | -0.32721 | 0.0043426 | 0.0010884
69 | 0.98232 | -0.33877 | 0 | 0
70 | 0.9848 | -0.29061 | 0.0039032 | 0.00097823
71 | 0.98193 | -0.34626 | 0.0029869 | 0.00074859
72 | 0.98596 | -0.26799 | 0.0035142 | 0.00088074
73 | 0.98168 | -0.35115 | 0.0032012 | 0.00080229
74 | 0.99981 | -0.0037189 | 0.0046321 | 0.0011609
75 | 0.99982 | -0.0034684 | 0.0034924 | 0.00087528
76 | 0.97844 | -0.41469 | 0.0023269 | 0.00058317
77 | 0.97837 | -0.4161 | 0.0054378 | 0.0013628
78 | 0.97801 | -0.42307 | 0.0019944 | 0.00049985
79 | 0.97815 | -0.4202 | 0.0024747 | 0.00062022
80 | 0.98829 | -0.22305 | 0.0021764 | 0.00054545
81 | 0.98854 | -0.21824 | 0.0021802 | 0.00054641
82 | 0.98734 | -0.24146 | 0.0024662 | 0.0006181
83 | 0.98969 | -0.19613 | 0.0025937 | 0.00065005
84 | 0.98712 | -0.24568 | 0.0021456 | 0.00053774
85 | 0.98982 | -0.19364 | 0.001526 | 0.00038245
86 | 0.98612 | -0.26498 | 0.0036511 | 0.00091505
87 | 0.99081 | -0.17472 | 0.000688 | 0.00017243
88 | 0.99082 | -0.17447 | 0.0015322 | 0.000384
89 | 0.98043 | -0.37559 | 0.004122 | 0.0010331
90 | 0.97951 | -0.39365 | 0.0023053 | 0.00057775
91 | 0.98054 | -0.37351 | 0.0027604 | 0.00069181
92 | 0.97901 | -0.40332 | 0.0047016 | 0.0011783
93 | 0.98095 | -0.36544 | 0 | 0
94 | 0.97897 | -0.40411 | 0.001729 | 0.00043334
95 | 0.97837 | -0.41599 | 0.0016169 | 0.00040524
96 | 0.97864 | -0.41074 | 0.0020274 | 0.00050811
97 | 0.97887 | -0.40624 | 0.00081607 | 0.00020453
98 | 0.98063 | -0.37185 | 0.0028039 | 0.00070272
99 | 0.98061 | -0.37228 | 0.0024451 | 0.00061279
100 | 0.98059 | -0.37272 | 0.00088542 | 0.00022191
101 | 0.98053 | -0.37375 | 0.0024377 | 0.00061093
102 | 0.99047 | -0.18135 | 0.0035836 | 0.00089813
103 | 0.98139 | -0.3569 | 0.0045194 | 0.0011327
104 | 0.98103 | -0.364 | 0.0025066 | 0.0006282
105 | 0.99849 | -0.02845 | 0.0026308 | 0.00065934
106 | 0.97246 | -0.53263 | 0.00027052 | 6.7798e-05
107 | 0.97246 | -0.53258 | 0.00025547 | 6.4026e-05
108 | 0.97257 | -0.5303 | 0.00067215 | 0.00016846
109 | 0.97263 | -0.5292 | 0 | 0
110 | 0.9726 | -0.52969 | 0.00016473 | 4.1286e-05
111 | 0.97267 | -0.52837 | 8.3743e-05 | 2.0988e-05
112 | 0.97279 | -0.52594 | 0.00031231 | 7.8273e-05
113 | 0.97266 | -0.52862 | 0.00030224 | 7.5748e-05
114 | 0.97266 | -0.52859 | 0.0007194 | 0.0001803
115 | 0.97277 | -0.52629 | 0.00022749 | 5.7015e-05
116 | 0.97197 | -0.5422 | 0.0021204 | 0.00053143
117 | 0.97413 | -0.49941 | 0 | 0
118 | 0.97431 | -0.49596 | 0.00024862 | 6.231e-05
119 | 0.97429 | -0.49635 | 0.00028552 | 7.1558e-05
120 | 0.97181 | -0.54539 | 0.0039464 | 0.00098906
121 | 0.97169 | -0.54778 | 0.0017681 | 0.00044312
122 | 0.97163 | -0.54888 | 0.00091318 | 0.00022886
123 | 0.99862 | -0.026059 | 0.003171 | 0.00079472
124 | 0.99983 | -0.0031416 | 0.0039908 | 0.0010002
125 | 1 | 0 | -0.25895 | -0.066072
126 | 0.97832 | -0.41708 | 0.0015595 | 0.00039086
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0042699 | -0.0010701 | 0.0042703 | 0.0010701 | 4.3528e-07 | -6.7454e-08 | 0.0064924 | 0.0064923 | 0.0064924 | 0.97862 | -0.41114 | 0.97873 | -0.409 | 1.7836
1 | 0.0061752 | 0.0015475 | -0.0061747 | -0.0015474 | 5.2755e-07 | 1.3708e-07 | 0.0093885 | 0.0093886 | 0.0093886 | 0.97873 | -0.409 | 0.97864 | -0.41079 | 2.5793
2 | -0.010446 | -0.0026176 | 0.01045 | 0.0026199 | 4.6004e-06 | 2.3327e-06 | 0.015881 | 0.015881 | 0.015881 | 0.97873 | -0.409 | 0.9792 | -0.39976 | 4.3629
3 | 0.003286 | 0.0008234 | -0.0032859 | -0.00082352 | 1.6694e-07 | -1.1721e-07 | 0.0049964 | 0.0049964 | 0.0049964 | 0.97864 | -0.41079 | 0.97858 | -0.41186 | 1.3726
4 | -0.01045 | -0.0026199 | 0.010452 | 0.0026211 | 2.2872e-06 | 1.1595e-06 | 0.015881 | 0.01588 | 0.015881 | 0.9792 | -0.39976 | 0.97943 | -0.39517 | 4.3628
5 | -0.0059541 | -0.0014921 | 0.0059546 | 0.0014922 | 5.2649e-07 | 1.2228e-07 | 0.0090593 | 0.0090593 | 0.0090593 | 0.97797 | -0.42396 | 0.97807 | -0.4221 | 2.4888
6 | 0.0059541 | 0.0014921 | -0.0059537 | -0.001492 | 4.3395e-07 | 1.0082e-07 | 0.0090593 | 0.0090594 | 0.0090594 | 0.97797 | -0.42396 | 0.97789 | -0.42549 | 2.4888
7 | -0.0059546 | -0.0014922 | 0.005955 | 0.0014923 | 3.2272e-07 | 7.4931e-08 | 0.0090593 | 0.0090592 | 0.0090593 | 0.97807 | -0.4221 | 0.97812 | -0.42097 | 2.4888
8 | 0.0015325 | 0.00038395 | -0.0015325 | -0.00038408 | 2.3392e-08 | -1.2894e-07 | 0.0023319 | 0.002332 | 0.002332 | 0.97789 | -0.42549 | 0.97788 | -0.42581 | 0.64066
9 | -0.013651 | -0.0034227 | 0.013652 | 0.003423 | 5.3003e-07 | 2.9786e-07 | 0.02074 | 0.02074 | 0.02074 | 0.97943 | -0.39517 | 0.97947 | -0.39435 | 5.6978
10 | -0.0070335 | -0.0017626 | 0.0070339 | 0.0017627 | 3.7944e-07 | 1.3191e-07 | 0.0107 | 0.0107 | 0.0107 | 0.97812 | -0.42097 | 0.97818 | -0.41983 | 2.9396
11 | -0.016269 | -0.004079 | 0.016273 | 0.0040812 | 3.8894e-06 | 2.2755e-06 | 0.024716 | 0.024716 | 0.024716 | 0.97947 | -0.39435 | 0.97973 | -0.38934 | 6.7902
12 | -0.0091754 | -0.0022994 | 0.0091766 | 0.0023 | 1.2036e-06 | 5.6345e-07 | 0.013958 | 0.013958 | 0.013958 | 0.97818 | -0.41983 | 0.97832 | -0.41708 | 3.8345
13 | -0.094068 | -0.023658 | 0.09413 | 0.023696 | 6.1812e-05 | 3.7932e-05 | 0.1429 | 0.1429 | 0.1429 | 0.97973 | -0.38934 | 0.98043 | -0.37559 | 9.8146
14 | 0.077795 | 0.019576 | -0.077779 | -0.019567 | 1.6051e-05 | 9.6552e-06 | 0.11818 | 0.11818 | 0.11818 | 0.97973 | -0.38934 | 0.97951 | -0.39365 | 8.117
15 | 0.034809 | 0.0087331 | -0.034808 | -0.0087326 | 7.3003e-07 | 4.5845e-07 | 0.052883 | 0.052883 | 0.052883 | 0.9795 | -0.39394 | 0.97948 | -0.39438 | 14.5283
16 | -0.037714 | -0.0094611 | 0.037731 | 0.0094722 | 1.7616e-05 | 1.1094e-05 | 0.057296 | 0.057296 | 0.057296 | 0.9795 | -0.39394 | 0.98 | -0.38415 | 15.7407
17 | 0.03028 | 0.0075978 | -0.030277 | -0.0075957 | 3.3509e-06 | 2.0914e-06 | 0.046004 | 0.046004 | 0.046004 | 0.97948 | -0.39438 | 0.97936 | -0.3967 | 12.6385
18 | -0.039085 | -0.0098116 | 0.039093 | 0.0098164 | 7.6791e-06 | 4.8413e-06 | 0.059352 | 0.059352 | 0.059352 | 0.98 | -0.38415 | 0.98021 | -0.38003 | 16.3055
19 | 0.026126 | 0.0065555 | -0.026123 | -0.0065536 | 3.0865e-06 | 1.9096e-06 | 0.039698 | 0.039698 | 0.039698 | 0.97936 | -0.3967 | 0.97923 | -0.39918 | 10.9061
20 | -0.041453 | -0.010408 | 0.041458 | 0.010411 | 4.4549e-06 | 2.8133e-06 | 0.062935 | 0.062935 | 0.062935 | 0.98021 | -0.38003 | 0.98033 | -0.37778 | 17.2898
21 | 0.024969 | 0.0062643 | -0.024959 | -0.0062581 | 1.007e-05 | 6.2104e-06 | 0.037944 | 0.037944 | 0.037944 | 0.97923 | -0.39918 | 0.9788 | -0.40764 | 10.4242
22 | -0.044011 | -0.011051 | 0.044038 | 0.011068 | 2.7839e-05 | 1.7607e-05 | 0.06681 | 0.06681 | 0.06681 | 0.98033 | -0.37778 | 0.981 | -0.36453 | 18.3544
23 | 0.021449 | 0.0053784 | -0.021447 | -0.0053777 | 1.1382e-06 | 6.9258e-07 | 0.032608 | 0.032608 | 0.032608 | 0.9788 | -0.40764 | 0.97875 | -0.40876 | 8.9582
24 | -0.055009 | -0.013818 | 0.055038 | 0.013837 | 2.8774e-05 | 1.8276e-05 | 0.083451 | 0.083451 | 0.083451 | 0.981 | -0.36453 | 0.98156 | -0.35357 | 22.9261
25 | 0.010971 | 0.0027501 | -0.010968 | -0.0027489 | 2.2689e-06 | 1.1763e-06 | 0.016641 | 0.016641 | 0.016641 | 0.981 | -0.36453 | 0.98078 | -0.36887 | 4.5717
26 | 0.018508 | 0.0046409 | -0.018502 | -0.0046378 | 5.2324e-06 | 3.1273e-06 | 0.028138 | 0.028139 | 0.028139 | 0.97875 | -0.40876 | 0.97844 | -0.41469 | 7.7304
27 | -0.057213 | -0.014382 | 0.057285 | 0.014427 | 7.2106e-05 | 4.5824e-05 | 0.086748 | 0.086747 | 0.086748 | 0.98156 | -0.35357 | 0.98291 | -0.32721 | 23.8317
28 | 0.0085735 | 0.0021486 | -0.0085723 | -0.0021481 | 1.2161e-06 | 5.3648e-07 | 0.013008 | 0.013008 | 0.013008 | 0.98078 | -0.36887 | 0.98063 | -0.37185 | 3.5735
29 | 0.016147 | 0.0040482 | -0.016147 | -0.0040481 | 2.7368e-07 | 1.6024e-07 | 0.024673 | 0.024673 | 0.024673 | 0.97386 | -0.50463 | 0.97384 | -0.50498 | 6.7782
30 | -0.019497 | -0.0048879 | 0.019505 | 0.0048922 | 7.186e-06 | 4.3303e-06 | 0.029792 | 0.029792 | 0.029792 | 0.97386 | -0.50463 | 0.97425 | -0.4969 | 8.1845
31 | 0.012939 | 0.003244 | -0.012935 | -0.003242 | 3.6154e-06 | 2.007e-06 | 0.019771 | 0.019771 | 0.019771 | 0.97384 | -0.50498 | 0.97355 | -0.51085 | 5.4315
32 | -0.02212 | -0.0055477 | 0.02212 | 0.0055477 | 2.167e-08 | 1.3235e-08 | 0.033786 | 0.033786 | 0.033786 | 0.97425 | -0.4969 | 0.97425 | -0.49688 | 9.2819
33 | 0.01031 | 0.002584 | -0.010309 | -0.0025838 | 2.6103e-07 | 1.322e-07 | 0.015758 | 0.015758 | 0.015758 | 0.97355 | -0.51085 | 0.97352 | -0.51138 | 4.329
34 | -0.023316 | -0.0058473 | 0.023321 | 0.0058504 | 4.9958e-06 | 3.0665e-06 | 0.035612 | 0.035612 | 0.035612 | 0.97425 | -0.49688 | 0.97448 | -0.49238 | 9.7836
35 | 0.0070428 | 0.0017652 | -0.0070418 | -0.0017648 | 1.0101e-06 | 3.5749e-07 | 0.010765 | 0.010765 | 0.010765 | 0.97352 | -0.51138 | 0.97337 | -0.51439 | 2.9574
36 | -0.02764 | -0.0069329 | 0.027652 | 0.0069406 | 1.2399e-05 | 7.7039e-06 | 0.042208 | 0.042208 | 0.042208 | 0.97448 | -0.49238 | 0.97496 | -0.48298 | 11.5955
37 | 0.0026311 | 0.00065941 | -0.0026311 | -0.00065942 | 9.6589e-09 | -1.3607e-08 | 0.0040223 | 0.0040223 | 0.0040223 | 0.97337 | -0.51439 | 0.97336 | -0.51447 | 1.105
38 | -0.031434 | -0.0078885 | 0.031452 | 0.0078998 | 1.7999e-05 | 1.1259e-05 | 0.04798 | 0.04798 | 0.04798 | 0.97496 | -0.48298 | 0.97557 | -0.47098 | 13.1813
39 | -0.031452 | -0.0078998 | 0.031466 | 0.0079083 | 1.3641e-05 | 8.533e-06 | 0.04798 | 0.04798 | 0.04798 | 0.97557 | -0.47098 | 0.97603 | -0.46189 | 13.1813
40 | -0.034968 | -0.0087861 | 0.035004 | 0.0088083 | 3.5416e-05 | 2.2251e-05 | 0.053319 | 0.053319 | 0.053319 | 0.97603 | -0.46189 | 0.97711 | -0.4407 | 14.6482
41 | -0.056405 | -0.014161 | 0.056417 | 0.014168 | 1.151e-05 | 6.5328e-06 | 0.085907 | 0.085907 | 0.085907 | 0.97711 | -0.4407 | 0.97733 | -0.43642 | 5.9002
42 | 0.020748 | 0.0051891 | -0.020735 | -0.0051878 | 1.2715e-05 | 1.3346e-06 | 0.031593 | 0.031595 | 0.031595 | 0.97711 | -0.4407 | 0.97646 | -0.45358 | 2.17
43 | -0.05693 | -0.014296 | 0.056933 | 0.014298 | 2.885e-06 | 1.6411e-06 | 0.086688 | 0.086688 | 0.086688 | 0.97733 | -0.43642 | 0.97738 | -0.43536 | 5.9538
44 | 0.015579 | 0.003897 | -0.015574 | -0.0038987 | 5.7553e-06 | -1.7648e-06 | 0.023739 | 0.023741 | 0.023741 | 0.97646 | -0.45358 | 0.97606 | -0.46135 | 1.6305
45 | 0.00028142 | 6.9111e-05 | -0.00028142 | -7.0529e-05 | 7.838e-09 | -1.4182e-06 | 0.00042835 | 0.00042886 | 0.00042886 | 0.97646 | -0.45358 | 0.97643 | -0.45417 | 0.11782
46 | -0.014505 | -0.0036346 | 0.014506 | 0.0036338 | 1.6564e-06 | -7.4412e-07 | 0.02212 | 0.02212 | 0.02212 | 0.97571 | -0.46823 | 0.97583 | -0.46584 | 1.5193
47 | 0.0015685 | 0.00039177 | -0.0015683 | -0.0003929 | 2.1737e-07 | -1.1262e-06 | 0.0023916 | 0.002392 | 0.002392 | 0.97571 | -0.46823 | 0.97557 | -0.47115 | 0.65715
48 | 0.012565 | 0.0031497 | -0.012559 | -0.003148 | 5.9848e-06 | 1.6601e-06 | 0.019162 | 0.019163 | 0.019163 | 0.97571 | -0.46823 | 0.97521 | -0.47823 | 2.6323
49 | -0.01557 | -0.0038997 | 0.015574 | 0.0038987 | 3.328e-06 | -1.0181e-06 | 0.023742 | 0.023741 | 0.023742 | 0.97583 | -0.46584 | 0.97606 | -0.46135 | 1.6306
50 | 0.0010639 | 0.00026591 | -0.0010638 | -0.00026613 | 1.775e-08 | -2.134e-07 | 0.001622 | 0.0016221 | 0.0016221 | 0.97583 | -0.46584 | 0.97582 | -0.46619 | 0.44562
51 | 0.00073999 | 0.00018531 | -0.00073998 | -0.00018546 | 5.6807e-09 | -1.4484e-07 | 0.0011286 | 0.0011287 | 0.0011287 | 0.97557 | -0.47115 | 0.97556 | -0.47131 | 0.31008
52 | 0.012559 | 0.003148 | -0.012555 | -0.0031458 | 4.0158e-06 | 2.2064e-06 | 0.019163 | 0.019163 | 0.019163 | 0.97521 | -0.47823 | 0.97486 | -0.48495 | 5.2646
53 | -0.057369 | -0.014407 | 0.057384 | 0.014416 | 1.5313e-05 | 8.7267e-06 | 0.087352 | 0.087351 | 0.087352 | 0.97738 | -0.43536 | 0.97767 | -0.42976 | 5.9994
54 | 0.00076005 | 0.00018999 | -0.00076004 | -0.00019022 | 9.3774e-09 | -2.2661e-07 | 0.0011588 | 0.0011589 | 0.0011589 | 0.97582 | -0.46619 | 0.9758 | -0.46645 | 0.31838
55 | 0.00044161 | 0.00011041 | -0.00044161 | -0.00011068 | 3.6688e-09 | -2.6718e-07 | 0.00067332 | 0.00067342 | 0.00067342 | 0.9758 | -0.46645 | 0.97579 | -0.46662 | 0.18501
56 | -0.22752 | -0.058169 | 0.22771 | 0.05829 | 0.00019078 | 0.00012119 | 0.34075 | 0.34075 | 0.34075 | 0.99475 | -0.099371 | 0.99566 | -0.082055 | 23.4032
57 | 0.22752 | 0.058169 | -0.22729 | -0.058023 | 0.00022884 | 0.00014537 | 0.34075 | 0.34075 | 0.34075 | 0.99475 | -0.099371 | 0.99366 | -0.12018 | 23.4033
58 | -0.23192 | -0.059344 | 0.23223 | 0.059539 | 0.00030667 | 0.00019485 | 0.34704 | 0.34704 | 0.34704 | 0.99566 | -0.082055 | 0.9971 | -0.054781 | 23.835
59 | 0.2245 | 0.057322 | -0.22437 | -0.05724 | 0.00013003 | 8.2588e-05 | 0.33656 | 0.33656 | 0.33656 | 0.99366 | -0.12018 | 0.99303 | -0.13218 | 23.1157
60 | -0.058119 | -0.0146 | 0.058119 | 0.0146 | 2.6399e-07 | 1.5091e-07 | 0.08847 | 0.08847 | 0.08847 | 0.97767 | -0.42976 | 0.97767 | -0.42967 | 6.0762
61 | -0.23516 | -0.060273 | 0.2352 | 0.060302 | 4.49e-05 | 2.8534e-05 | 0.35141 | 0.35141 | 0.35141 | 0.9971 | -0.054781 | 0.99731 | -0.050843 | 24.1353
62 | 0.22437 | 0.05724 | -0.22428 | -0.057181 | 9.2075e-05 | 5.8479e-05 | 0.33656 | 0.33657 | 0.33657 | 0.99303 | -0.13218 | 0.99258 | -0.14068 | 23.1157
63 | 0.012322 | 0.0030875 | -0.012316 | -0.003084 | 6.4613e-06 | 3.5283e-06 | 0.018808 | 0.018808 | 0.018808 | 0.97486 | -0.48495 | 0.97431 | -0.49596 | 5.1671
64 | -0.059998 | -0.015071 | 0.060017 | 0.015082 | 1.889e-05 | 1.0877e-05 | 0.091329 | 0.091328 | 0.091329 | 0.97767 | -0.42967 | 0.97801 | -0.42307 | 6.2726
65 | -0.23879 | -0.061201 | 0.23905 | 0.061365 | 0.00025951 | 0.00016495 | 0.35676 | 0.35676 | 0.35676 | 0.99731 | -0.050843 | 0.99849 | -0.02845 | 24.5028
66 | 0.22187 | 0.056579 | -0.22151 | -0.05635 | 0.00036136 | 0.00022947 | 0.33296 | 0.33296 | 0.33296 | 0.99258 | -0.14068 | 0.99082 | -0.17447 | 22.8683
67 | -0.12395 | -0.031274 | 0.12398 | 0.031293 | 2.9976e-05 | 1.8724e-05 | 0.18767 | 0.18767 | 0.18767 | 0.98319 | -0.32192 | 0.98344 | -0.31687 | 12.8894
68 | 0.12025 | 0.030346 | -0.12021 | -0.03032 | 4.2123e-05 | 2.6271e-05 | 0.18206 | 0.18207 | 0.18207 | 0.98319 | -0.32192 | 0.98281 | -0.32924 | 12.5045
69 | -0.1285 | -0.032426 | 0.12855 | 0.032456 | 4.7353e-05 | 2.9628e-05 | 0.19451 | 0.19451 | 0.19451 | 0.98344 | -0.31687 | 0.98384 | -0.30918 | 13.3594
70 | 0.11734 | 0.029601 | -0.11729 | -0.029572 | 4.6346e-05 | 2.8868e-05 | 0.17772 | 0.17772 | 0.17772 | 0.98281 | -0.32924 | 0.98239 | -0.33749 | 12.2062
71 | -0.19023 | -0.048006 | 0.19029 | 0.04804 | 5.4657e-05 | 3.4623e-05 | 0.28783 | 0.28783 | 0.28783 | 0.98384 | -0.30918 | 0.98415 | -0.30318 | 19.7688
72 | 0.06168 | 0.01555 | -0.061627 | -0.015516 | 5.3186e-05 | 3.3833e-05 | 0.093322 | 0.093322 | 0.093322 | 0.98384 | -0.30918 | 0.98291 | -0.32721 | 25.6378
73 | 0.11442 | 0.028853 | -0.11441 | -0.028848 | 7.0335e-06 | 4.375e-06 | 0.17338 | 0.17338 | 0.17338 | 0.98239 | -0.33749 | 0.98232 | -0.33877 | 11.9077
74 | -0.19029 | -0.04804 | 0.1904 | 0.048113 | 0.00011464 | 7.2617e-05 | 0.28783 | 0.28783 | 0.28783 | 0.98415 | -0.30318 | 0.9848 | -0.29061 | 19.7688
75 | 0.11441 | 0.028848 | -0.11437 | -0.028823 | 4.099e-05 | 2.5498e-05 | 0.17338 | 0.17338 | 0.17338 | 0.98232 | -0.33877 | 0.98193 | -0.34626 | 11.9077
76 | -0.1943 | -0.049091 | 0.19451 | 0.049225 | 0.00021093 | 0.00013367 | 0.29373 | 0.29373 | 0.29373 | 0.9848 | -0.29061 | 0.98596 | -0.26799 | 20.1738
77 | 0.11139 | 0.028074 | -0.11136 | -0.028058 | 2.6065e-05 | 1.6188e-05 | 0.16885 | 0.16885 | 0.16885 | 0.98193 | -0.34626 | 0.98168 | -0.35115 | 11.5969
78 | -0.19803 | -0.050105 | 0.19806 | 0.050124 | 2.862e-05 | 1.8143e-05 | 0.29903 | 0.29903 | 0.29903 | 0.98596 | -0.26799 | 0.98612 | -0.26498 | 20.5381
79 | 0.10816 | 0.027256 | -0.10813 | -0.027237 | 2.9729e-05 | 1.843e-05 | 0.164 | 0.164 | 0.164 | 0.98168 | -0.35115 | 0.98139 | -0.3569 | 11.2636
80 | -0.0046321 | -0.0011609 | 0.0046321 | 0.0011609 | 5.5267e-08 | -5.297e-09 | 0.0068939 | 0.0068939 | 0.0068939 | 0.99981 | -0.0037189 | 0.99982 | -0.0034684 | 1.8939
81 | -0.0081245 | -0.0020362 | 0.0081259 | 0.0020367 | 1.3426e-06 | 5.3805e-07 | 0.012092 | 0.012091 | 0.012092 | 0.99982 | -0.0034684 | 1 | 0 | 3.3219
82 | 0.016175 | 0.0040546 | -0.016174 | -0.004054 | 1.0836e-06 | 6.3354e-07 | 0.0246 | 0.0246 | 0.0246 | 0.97844 | -0.41469 | 0.97837 | -0.4161 | 6.7582
83 | 0.010737 | 0.0026911 | -0.010736 | -0.0026909 | 5.0342e-07 | 2.5897e-07 | 0.01633 | 0.01633 | 0.01633 | 0.97837 | -0.4161 | 0.97832 | -0.41708 | 4.4861
84 | -0.062011 | -0.015582 | 0.062019 | 0.015587 | 8.516e-06 | 4.9381e-06 | 0.094363 | 0.094363 | 0.094363 | 0.97801 | -0.42307 | 0.97815 | -0.4202 | 6.481
85 | -0.064494 | -0.016207 | 0.064507 | 0.016214 | 1.2954e-05 | 7.5696e-06 | 0.098127 | 0.098127 | 0.098127 | 0.97815 | -0.4202 | 0.97837 | -0.41599 | 6.7395
86 | -0.20891 | -0.053001 | 0.20896 | 0.053031 | 4.8266e-05 | 3.0624e-05 | 0.31477 | 0.31477 | 0.31477 | 0.98829 | -0.22305 | 0.98854 | -0.21824 | 21.6189
87 | 0.20673 | 0.052455 | -0.20655 | -0.052339 | 0.00018287 | 0.00011601 | 0.31149 | 0.31149 | 0.31149 | 0.98829 | -0.22305 | 0.98734 | -0.24146 | 21.3938
88 | -0.21114 | -0.053578 | 0.21136 | 0.05372 | 0.00022483 | 0.00014267 | 0.31805 | 0.31805 | 0.31805 | 0.98854 | -0.21824 | 0.98969 | -0.19613 | 21.8443
89 | 0.20408 | 0.051721 | -0.20404 | -0.051695 | 4.143e-05 | 2.6277e-05 | 0.30778 | 0.30778 | 0.30778 | 0.98734 | -0.24146 | 0.98712 | -0.24568 | 21.1386
90 | -0.21395 | -0.05437 | 0.21398 | 0.054387 | 2.5596e-05 | 1.6246e-05 | 0.32195 | 0.32195 | 0.32195 | 0.98969 | -0.19613 | 0.98982 | -0.19364 | 22.1121
91 | 0.2019 | 0.051157 | -0.20171 | -0.051039 | 0.00018701 | 0.00011859 | 0.30454 | 0.30454 | 0.30454 | 0.98712 | -0.24568 | 0.98612 | -0.26498 | 20.9164
92 | -0.21551 | -0.054769 | 0.2157 | 0.054894 | 0.0001966 | 0.0001248 | 0.32425 | 0.32425 | 0.32425 | 0.98982 | -0.19364 | 0.99081 | -0.17472 | 22.2696
93 | -0.21639 | -0.055066 | 0.21639 | 0.055068 | 2.6119e-06 | 1.6581e-06 | 0.32528 | 0.32528 | 0.32528 | 0.99081 | -0.17472 | 0.99082 | -0.17447 | 22.3406
94 | 0.0035848 | 0.00089749 | -0.0035836 | -0.00089813 | 1.1742e-06 | -6.3947e-07 | 0.0053833 | 0.0053838 | 0.0053838 | 0.99082 | -0.17447 | 0.99047 | -0.18135 | 1.4791
95 | -0.098252 | -0.024729 | 0.098262 | 0.024735 | 9.7745e-06 | 6.0193e-06 | 0.14916 | 0.14916 | 0.14916 | 0.98043 | -0.37559 | 0.98054 | -0.37351 | 10.2442
96 | 0.075474 | 0.018989 | -0.075439 | -0.018968 | 3.4847e-05 | 2.088e-05 | 0.11468 | 0.11468 | 0.11468 | 0.97951 | -0.39365 | 0.97901 | -0.40332 | 7.8766
97 | -0.10102 | -0.025426 | 0.10106 | 0.025451 | 3.8946e-05 | 2.4034e-05 | 0.15334 | 0.15334 | 0.15334 | 0.98054 | -0.37351 | 0.98095 | -0.36544 | 10.5319
98 | 0.070737 | 0.01779 | -0.070735 | -0.017788 | 2.6711e-06 | 1.5856e-06 | 0.10754 | 0.10754 | 0.10754 | 0.97901 | -0.40332 | 0.97897 | -0.40411 | 7.3858
99 | -0.10106 | -0.025451 | 0.10107 | 0.025455 | 6.9595e-06 | 4.2946e-06 | 0.15334 | 0.15334 | 0.15334 | 0.98095 | -0.36544 | 0.98103 | -0.364 | 10.5319
100 | 0.069006 | 0.017355 | -0.068999 | -0.017351 | 7.0212e-06 | 4.1514e-06 | 0.10491 | 0.10491 | 0.10491 | 0.97897 | -0.40411 | 0.97887 | -0.40624 | 7.2053
101 | -0.066124 | -0.01662 | 0.066141 | 0.016629 | 1.6568e-05 | 9.7256e-06 | 0.10059 | 0.10059 | 0.10059 | 0.97837 | -0.41599 | 0.97864 | -0.41074 | 6.9084
102 | -0.068168 | -0.017138 | 0.068183 | 0.017146 | 1.4654e-05 | 8.6474e-06 | 0.10367 | 0.10367 | 0.10367 | 0.97864 | -0.41074 | 0.97887 | -0.40624 | 7.1201
103 | 0.0057684 | 0.0014454 | -0.0057683 | -0.0014454 | 1.1857e-07 | 2.3819e-08 | 0.008753 | 0.008753 | 0.008753 | 0.98063 | -0.37185 | 0.98061 | -0.37228 | 2.4047
104 | 0.0033233 | 0.00083258 | -0.0033232 | -0.00083262 | 7.0252e-08 | -4.7974e-08 | 0.0050427 | 0.0050428 | 0.0050428 | 0.98061 | -0.37228 | 0.98059 | -0.37272 | 1.3854
105 | 0.0024378 | 0.00061072 | -0.0024377 | -0.00061093 | 1.1902e-07 | -2.1639e-07 | 0.0036992 | 0.0036993 | 0.0036993 | 0.98059 | -0.37272 | 0.98053 | -0.37375 | 1.0163
106 | 0.10361 | 0.026105 | -0.10357 | -0.026083 | 3.5191e-05 | 2.1754e-05 | 0.15715 | 0.15715 | 0.15715 | 0.98139 | -0.3569 | 0.98103 | -0.364 | 10.793
107 | -0.24168 | -0.062025 | 0.24171 | 0.062043 | 2.8044e-05 | 1.7828e-05 | 0.36068 | 0.36068 | 0.36068 | 0.99849 | -0.02845 | 0.99862 | -0.026059 | 24.772
108 | -0.00027052 | -6.7798e-05 | 0.00027052 | 6.768e-05 | 6.122e-10 | -1.1783e-07 | 0.00041394 | 0.00041389 | 0.00041394 | 0.97246 | -0.53263 | 0.97246 | -0.53258 | 0.11372
109 | -0.00052598 | -0.00013171 | 0.00052604 | 0.00012885 | 5.6523e-08 | -2.855e-06 | 0.0008048 | 0.00080376 | 0.0008048 | 0.97246 | -0.53258 | 0.97257 | -0.5303 | 0.2211
110 | -0.0011982 | -0.00029731 | 0.0011982 | 0.00029699 | 3.4807e-08 | -3.209e-07 | 0.0018321 | 0.001832 | 0.0018321 | 0.97257 | -0.5303 | 0.9726 | -0.52969 | 0.50333
111 | 0.001363 | 0.00033806 | -0.001363 | -0.00033827 | 3.1216e-08 | -2.179e-07 | 0.002084 | 0.002084 | 0.002084 | 0.97263 | -0.5292 | 0.9726 | -0.52969 | 0.57254
112 | -0.001363 | -0.00033806 | 0.001363 | 0.00033768 | 5.3642e-08 | -3.745e-07 | 0.002084 | 0.0020838 | 0.002084 | 0.97263 | -0.5292 | 0.97267 | -0.52837 | 0.57252
113 | -0.0014468 | -0.00035867 | 0.001447 | 0.00035765 | 1.6631e-07 | -1.019e-06 | 0.0022119 | 0.0022115 | 0.0022119 | 0.97267 | -0.52837 | 0.97279 | -0.52594 | 0.60767
114 | 0.0087562 | 0.0021947 | -0.0087494 | -0.0021916 | 6.7789e-06 | 3.0886e-06 | 0.013394 | 0.013394 | 0.013394 | 0.97279 | -0.52594 | 0.97197 | -0.5422 | 3.6798
115 | -0.011765 | -0.002942 | 0.01178 | 0.00295 | 1.4857e-05 | 7.9872e-06 | 0.017993 | 0.017993 | 0.017993 | 0.97279 | -0.52594 | 0.97413 | -0.49941 | 4.9432
116 | 0.0012493 | 0.00031137 | -0.0012492 | -0.00031155 | 2.0894e-08 | -1.7617e-07 | 0.0019103 | 0.0019104 | 0.0019104 | 0.97279 | -0.52594 | 0.97277 | -0.52629 | 0.52483
117 | -0.00030224 | -7.5748e-05 | 0.00030224 | 7.5673e-05 | 4.89e-10 | -7.5389e-08 | 0.00046238 | 0.00046235 | 0.00046238 | 0.97266 | -0.52862 | 0.97266 | -0.52859 | 0.12703
118 | -0.0010216 | -0.00025597 | 0.0010217 | 0.00025453 | 1.1155e-07 | -1.4408e-06 | 0.0015629 | 0.0015624 | 0.0015629 | 0.97266 | -0.52859 | 0.97277 | -0.52629 | 0.42937
119 | 0.006629 | 0.0016602 | -0.006628 | -0.0016599 | 1.0079e-06 | 3.2164e-07 | 0.010148 | 0.010148 | 0.010148 | 0.97197 | -0.5422 | 0.97181 | -0.54539 | 2.788
120 | -0.01178 | -0.00295 | 0.011782 | 0.002951 | 1.9371e-06 | 1.0411e-06 | 0.017993 | 0.017993 | 0.017993 | 0.97413 | -0.49941 | 0.97431 | -0.49596 | 4.9431
121 | 0.00028553 | 7.0645e-05 | -0.00028552 | -7.1558e-05 | 5.2416e-09 | -9.1273e-07 | 0.00043574 | 0.00043607 | 0.00043607 | 0.97431 | -0.49596 | 0.97429 | -0.49635 | 0.1198
122 | 0.0026816 | 0.0006708 | -0.0026813 | -0.00067121 | 3.0481e-07 | -4.0229e-07 | 0.0041056 | 0.0041058 | 0.0041058 | 0.97181 | -0.54539 | 0.97169 | -0.54778 | 1.128
123 | 0.00091323 | 0.00022809 | -0.00091318 | -0.00022886 | 4.7713e-08 | -7.7542e-07 | 0.0013982 | 0.0013985 | 0.0013985 | 0.97169 | -0.54778 | 0.97163 | -0.54888 | 0.3842
124 | -0.24488 | -0.062837 | 0.24515 | 0.063011 | 0.00027262 | 0.00017334 | 0.36541 | 0.3654 | 0.36541 | 0.99862 | -0.026059 | 0.99983 | -0.0031416 | 25.0965
125 | -0.24914 | -0.064011 | 0.24918 | 0.064035 | 3.8022e-05 | 2.418e-05 | 0.37134 | 0.37134 | 0.37134 | 0.99983 | -0.0031416 | 1 | 0 | 25.5044

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.26308 | 0.067106

## res_load
| p_mw | q_mvar
0 | 0.0042699 | 0.0010701
1 | 0.0028887 | 0.00072397
2 | 0.0044212 | 0.001108
3 | 0.0032859 | 0.00082352
4 | 0.0031987 | 0.00080166
5 | 0.0010786 | 0.00027031
6 | 0.0015325 | 0.00038408
7 | 0.0026173 | 0.00065595
8 | 0.0021415 | 0.0005367
9 | 0.0029051 | 0.0007281
10 | 0.0045279 | 0.0011348
11 | 0.001354 | 0.00033935
12 | 0.0041504 | 0.0010402
13 | 0.0023602 | 0.00059152
14 | 0.0011544 | 0.00028931
15 | 0.002553 | 0.00063983
16 | 0.0035101 | 0.0008797
17 | 0.0029399 | 0.0007368
18 | 0.0021746 | 0.000545
19 | 0.0023949 | 0.00060023
20 | 0.0033502 | 0.00083963
21 | 0.0032083 | 0.00080407
22 | 0.0026155 | 0.0006555
23 | 0.0026256 | 0.00065803
24 | 0.0011956 | 0.00029964
25 | 0.0032664 | 0.00081864
26 | 0.0043193 | 0.0010825
27 | 0.0044107 | 0.0011054
28 | 0.0037822 | 0.0009479
29 | 0.0026311 | 0.00065942
30 | 0.0035024 | 0.00087777
31 | 0.00065315 | 0.00016369
32 | 0.00051303 | 0.00012858
33 | 0.0048746 | 0.0012217
34 | 0.00037148 | 9.3101e-05
35 | 0.00082829 | 0.00020759
36 | 0.00043625 | 0.00010933
37 | 0.0003038 | 7.6138e-05
38 | 0.00031843 | 7.9805e-05
39 | 0.00044161 | 0.00011068
40 | 0.00028142 | 7.0529e-05
41 | 0.0042062 | 0.0010542
42 | 0.002796 | 0.00070073
43 | 0.00073497 | 0.0001842
44 | 0.0029311 | 0.0007346
45 | 0.0002327 | 5.8321e-05
46 | 0.00073998 | 0.00018546
47 | 0.0018782 | 0.00047073
48 | 0.0035856 | 0.00089863
49 | 0.0024034 | 0.00060235
50 | 0.0037034 | 0.00092815
51 | 0.0045225 | 0.0011335
52 | 0.0028684 | 0.00071888
53 | 0.0028695 | 0.00071916
54 | 0.0043426 | 0.0010884
55 | 0.0039032 | 0.00097823
56 | 0.0029869 | 0.00074859
57 | 0.0035142 | 0.00088074
58 | 0.0032012 | 0.00080229
59 | 0.0046321 | 0.0011609
60 | 0.0034924 | 0.00087528
61 | 0.0023269 | 0.00058317
62 | 0.0054378 | 0.0013628
63 | 0.0019944 | 0.00049985
64 | 0.0024747 | 0.00062022
65 | 0.0021764 | 0.00054545
66 | 0.0021802 | 0.00054641
67 | 0.0024662 | 0.0006181
68 | 0.0025937 | 0.00065005
69 | 0.0021456 | 0.00053774
70 | 0.001526 | 0.00038245
71 | 0.0036511 | 0.00091505
72 | 0.000688 | 0.00017243
73 | 0.0015322 | 0.000384
74 | 0.004122 | 0.0010331
75 | 0.0023053 | 0.00057775
76 | 0.0027604 | 0.00069181
77 | 0.0047016 | 0.0011783
78 | 0.001729 | 0.00043334
79 | 0.0016169 | 0.00040524
80 | 0.0020274 | 0.00050811
81 | 0.00081607 | 0.00020453
82 | 0.0028039 | 0.00070272
83 | 0.0024451 | 0.00061279
84 | 0.00088542 | 0.00022191
85 | 0.0024377 | 0.00061093
86 | 0.0035836 | 0.00089813
87 | 0.0045194 | 0.0011327
88 | 0.0025066 | 0.0006282
89 | 0.0026308 | 0.00065934
90 | 0.00027052 | 6.7798e-05
91 | 0.00025547 | 6.4026e-05
92 | 0.00067215 | 0.00016846
93 | 0.00016473 | 4.1286e-05
94 | 8.3743e-05 | 2.0988e-05
95 | 0.00031231 | 7.8273e-05
96 | 0.00030224 | 7.5748e-05
97 | 0.0007194 | 0.0001803
98 | 0.00022749 | 5.7015e-05
99 | 0.0021204 | 0.00053143
100 | 0.00024862 | 6.231e-05
101 | 0.00028552 | 7.1558e-05
102 | 0.0039464 | 0.00098906
103 | 0.0017681 | 0.00044312
104 | 0.00091318 | 0.00022886
105 | 0.003171 | 0.00079472
106 | 0.0039908 | 0.0010002
107 | 0.0041253 | 0.0010339
108 | 0.0015595 | 0.00039086

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1