## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1349-11_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1349-11_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1349-11_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1349-11_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1349-11_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1349-11_0_4_node_112 | 0.4 | n |  | TRUE
6 | bus_LV_1349-11_0_4_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_1349-11_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1349-11_0_4_node_110 | 0.4 | n |  | TRUE
9 | bus_LV_1349-11_0_4_node_111 | 0.4 | n |  | TRUE
10 | bus_LV_1349-11_0_4_node_109 | 0.4 | n |  | TRUE
11 | bus_LV_1349-11_0_4_node_118 | 0.4 | n |  | TRUE
12 | bus_LV_1349-11_0_4_node_116 | 0.4 | n |  | TRUE
13 | bus_LV_1349-11_0_4_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1349-11_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1349-11_0_4_node_90 | 0.4 | n |  | TRUE
16 | bus_LV_1349-11_0_4_node_77 | 0.4 | n |  | TRUE
17 | bus_LV_1349-11_0_4_node_127 | 0.4 | n |  | TRUE
18 | bus_LV_1349-11_0_4_node_117 | 0.4 | n |  | TRUE
19 | bus_LV_1349-11_0_4_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_1349-11_0_4_node_70 | 0.4 | n |  | TRUE
21 | bus_LV_1349-11_0_4_node_68 | 0.4 | n |  | TRUE
22 | bus_LV_1349-11_0_4_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_1349-11_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1349-11_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1349-11_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_1349-11_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1349-11_0_4_node_41 | 0.4 | n |  | TRUE
28 | bus_LV_1349-11_0_4_node_107 | 0.4 | n |  | TRUE
29 | bus_LV_1349-11_0_4_node_73 | 0.4 | n |  | TRUE
30 | bus_LV_1349-11_0_4_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_1349-11_0_4_node_106 | 0.4 | n |  | TRUE
32 | bus_LV_1349-11_0_4_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_1349-11_0_4_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_1349-11_0_4_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_1349-11_0_4_node_108 | 0.4 | n |  | TRUE
36 | bus_LV_1349-11_0_4_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_1349-11_0_4_node_42 | 0.4 | n |  | TRUE
38 | bus_LV_1349-11_0_4_node_17 | 0.4 | n |  | TRUE
39 | bus_LV_1349-11_0_4_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_1349-11_0_4_node_19 | 0.4 | n |  | TRUE
41 | bus_LV_1349-11_0_4_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_1349-11_0_4_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_1349-11_0_4_node_22 | 0.4 | n |  | TRUE
44 | bus_LV_1349-11_0_4_node_28 | 0.4 | n |  | TRUE
45 | bus_LV_1349-11_0_4_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_1349-11_0_4_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_1349-11_0_4_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_1349-11_0_4_node_105 | 0.4 | n |  | TRUE
49 | bus_LV_1349-11_0_4_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_1349-11_0_4_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_1349-11_0_4_node_33 | 0.4 | n |  | TRUE
52 | bus_LV_1349-11_0_4_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_1349-11_0_4_node_35 | 0.4 | n |  | TRUE
54 | bus_LV_1349-11_0_4_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_1349-11_0_4_node_40 | 0.4 | n |  | TRUE
56 | bus_LV_1349-11_0_4_node_37 | 0.4 | n |  | TRUE
57 | bus_LV_1349-11_0_4_node_36 | 0.4 | n |  | TRUE
58 | bus_LV_1349-11_0_4_node_79 | 0.4 | n |  | TRUE
59 | bus_LV_1349-11_0_4_node_80 | 0.4 | n |  | TRUE
60 | bus_LV_1349-11_0_4_node_44 | 0.4 | n |  | TRUE
61 | bus_LV_1349-11_0_4_node_45 | 0.4 | n |  | TRUE
62 | bus_LV_1349-11_0_4_node_67 | 0.4 | n |  | TRUE
63 | bus_LV_1349-11_0_4_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_1349-11_0_4_node_65 | 0.4 | n |  | TRUE
65 | bus_LV_1349-11_0_4_node_66 | 0.4 | n |  | TRUE
66 | bus_LV_1349-11_0_4_node_47 | 0.4 | n |  | TRUE
67 | bus_LV_1349-11_0_4_node_113 | 0.4 | n |  | TRUE
68 | bus_LV_1349-11_0_4_node_48 | 0.4 | n |  | TRUE
69 | bus_LV_1349-11_0_4_node_60 | 0.4 | n |  | TRUE
70 | bus_LV_1349-11_0_4_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_1349-11_0_4_node_49 | 0.4 | n |  | TRUE
72 | bus_LV_1349-11_0_4_node_50 | 0.4 | n |  | TRUE
73 | bus_LV_1349-11_0_4_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_1349-11_0_4_node_129 | 0.4 | n |  | TRUE
75 | bus_LV_1349-11_0_4_node_54 | 0.4 | n |  | TRUE
76 | bus_LV_1349-11_0_4_node_130 | 0.4 | n |  | TRUE
77 | bus_LV_1349-11_0_4_node_114 | 0.4 | n |  | TRUE
78 | bus_LV_1349-11_0_4_node_57 | 0.4 | n |  | TRUE
79 | bus_LV_1349-11_0_4_node_52 | 0.4 | n |  | TRUE
80 | bus_LV_1349-11_0_4_node_53 | 0.4 | n |  | TRUE
81 | bus_LV_1349-11_0_4_node_55 | 0.4 | n |  | TRUE
82 | bus_LV_1349-11_0_4_node_56 | 0.4 | n |  | TRUE
83 | bus_LV_1349-11_0_4_node_62 | 0.4 | n |  | TRUE
84 | bus_LV_1349-11_0_4_node_61 | 0.4 | n |  | TRUE
85 | bus_LV_1349-11_0_4_node_59 | 0.4 | n |  | TRUE
86 | bus_LV_1349-11_0_4_node_63 | 0.4 | n |  | TRUE
87 | bus_LV_1349-11_0_4_node_64 | 0.4 | n |  | TRUE
88 | bus_LV_1349-11_0_4_node_69 | 0.4 | n |  | TRUE
89 | bus_LV_1349-11_0_4_node_71 | 0.4 | n |  | TRUE
90 | bus_LV_1349-11_0_4_node_72 | 0.4 | n |  | TRUE
91 | bus_LV_1349-11_0_4_node_120 | 0.4 | n |  | TRUE
92 | bus_LV_1349-11_0_4_node_119 | 0.4 | n |  | TRUE
93 | bus_LV_1349-11_0_4_node_115 | 0.4 | n |  | TRUE
94 | bus_LV_1349-11_0_4_node_100 | 0.4 | n |  | TRUE
95 | bus_LV_1349-11_0_4_node_121 | 0.4 | n |  | TRUE
96 | bus_LV_1349-11_0_4_node_74 | 0.4 | n |  | TRUE
97 | bus_LV_1349-11_0_4_node_75 | 0.4 | n |  | TRUE
98 | bus_LV_1349-11_0_4_node_76 | 0.4 | n |  | TRUE
99 | bus_LV_1349-11_0_4_node_78 | 0.4 | n |  | TRUE
100 | bus_LV_1349-11_0_4_node_87 | 0.4 | n |  | TRUE
101 | bus_LV_1349-11_0_4_node_88 | 0.4 | n |  | TRUE
102 | bus_LV_1349-11_0_4_node_81 | 0.4 | n |  | TRUE
103 | bus_LV_1349-11_0_4_node_82 | 0.4 | n |  | TRUE
104 | bus_LV_1349-11_0_4_node_83 | 0.4 | n |  | TRUE
105 | bus_LV_1349-11_0_4_node_84 | 0.4 | n |  | TRUE
106 | bus_LV_1349-11_0_4_node_85 | 0.4 | n |  | TRUE
107 | bus_LV_1349-11_0_4_node_104 | 0.4 | n |  | TRUE
108 | bus_LV_1349-11_0_4_node_86 | 0.4 | n |  | TRUE
109 | bus_LV_1349-11_0_4_node_96 | 0.4 | n |  | TRUE
110 | bus_LV_1349-11_0_4_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_1349-11_0_4_node_97 | 0.4 | n |  | TRUE
112 | bus_LV_1349-11_0_4_node_98 | 0.4 | n |  | TRUE
113 | bus_LV_1349-11_0_4_node_94 | 0.4 | n |  | TRUE
114 | bus_LV_1349-11_0_4_node_91 | 0.4 | n |  | TRUE
115 | bus_LV_1349-11_0_4_node_92 | 0.4 | n |  | TRUE
116 | bus_LV_1349-11_0_4_node_93 | 0.4 | n |  | TRUE
117 | bus_LV_1349-11_0_4_node_95 | 0.4 | n |  | TRUE
118 | bus_LV_1349-11_0_4_node_102 | 0.4 | n |  | TRUE
119 | bus_LV_1349-11_0_4_node_103 | 0.4 | n |  | TRUE
120 | bus_LV_1349-11_0_4_node_99 | 0.4 | n |  | TRUE
121 | bus_LV_1349-11_0_4_node_101 | 0.4 | n |  | TRUE
122 | bus_LV_1349-11_0_4_node_128 | 0.4 | n |  | TRUE
123 | bus_LV_1349-11_0_4_node_122 | 0.4 | n |  | TRUE
124 | bus_LV_1349-11_0_4_node_123 | 0.4 | n |  | TRUE
125 | bus_LV_1349-11_0_4_node_124 | 0.4 | n |  | TRUE
126 | bus_LV_1349-11_0_4_node_125 | 0.4 | n |  | TRUE
127 | bus_MV_18_0_node_96 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1349-11_0_4_load_0 | 0 | 0.0068095 | 0.0017066 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1349-11_0_4_load_1 | 1 | 0.092365 | 0.023149 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1349-11_0_4_load_3 | 3 | 0.015711 | 0.0039374 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1349-11_0_4_load_112 | 5 | 0.0040437 | 0.0010135 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1349-11_0_4_load_5 | 7 | 0.0077015 | 0.0019302 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1349-11_0_4_load_111 | 9 | 0.0018425 | 0.00046178 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1349-11_0_4_load_109 | 10 | 0.0036824 | 0.0009229 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1349-11_0_4_load_116 | 12 | 0.015604 | 0.0039107 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1349-11_0_4_load_6 | 13 | 0.0013998 | 0.00035081 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1349-11_0_4_load_7 | 14 | 0.0012955 | 0.00032469 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1349-11_0_4_load_90 | 15 | 0.0015177 | 0.00038037 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1349-11_0_4_load_117 | 18 | 0.0053876 | 0.0013503 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1349-11_0_4_load_9 | 19 | 0.0046101 | 0.0011554 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1349-11_0_4_load_70 | 20 | 0.0028093 | 0.00070408 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1349-11_0_4_load_68 | 21 | 0.0018377 | 0.00046058 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1349-11_0_4_load_11 | 22 | 0.00024805 | 6.2167e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1349-11_0_4_load_15 | 24 | 0.00033848 | 8.483e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1349-11_0_4_load_16 | 25 | 0.0010061 | 0.00025214 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1349-11_0_4_load_14 | 26 | 0.0018716 | 0.00046907 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1349-11_0_4_load_106 | 31 | 0.0059112 | 0.0014815 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1349-11_0_4_load_24 | 32 | 0.00035522 | 8.9027e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1349-11_0_4_load_26 | 33 | 0.0009651 | 0.00024188 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1349-11_0_4_load_23 | 34 | 0.00029104 | 7.2942e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1349-11_0_4_load_108 | 35 | 0.0026697 | 0.0006691 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1349-11_0_4_load_34 | 36 | 0.0023288 | 0.00058365 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1349-11_0_4_load_42 | 37 | 0.00038006 | 9.5253e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1349-11_0_4_load_17 | 38 | 0.00024163 | 6.0558e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1349-11_0_4_load_18 | 39 | 0.00027801 | 6.9677e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1349-11_0_4_load_19 | 40 | 0.00073327 | 0.00018378 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1349-11_0_4_load_22 | 43 | 0.0002652 | 6.6464e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1349-11_0_4_load_28 | 44 | 0.00023269 | 5.8318e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1349-11_0_4_load_27 | 45 | 0.0013204 | 0.00033092 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1349-11_0_4_load_29 | 46 | 0.00037031 | 9.2808e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1349-11_0_4_load_30 | 47 | 0.00069319 | 0.00017373 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1349-11_0_4_load_105 | 48 | 0.0047245 | 0.0011841 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1349-11_0_4_load_31 | 49 | 0.001071 | 0.00026843 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1349-11_0_4_load_32 | 50 | 0.0034644 | 0.00086826 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1349-11_0_4_load_33 | 51 | 0.00039577 | 9.919e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1349-11_0_4_load_43 | 52 | 0.011061 | 0.0027721 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1349-11_0_4_load_35 | 53 | 0.00032465 | 8.1365e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1349-11_0_4_load_40 | 55 | 0.00085534 | 0.00021437 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1349-11_0_4_load_37 | 56 | 0.00075321 | 0.00018877 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1349-11_0_4_load_36 | 57 | 0.00052693 | 0.00013206 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1349-11_0_4_load_79 | 58 | 0.00025667 | 6.4327e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1349-11_0_4_load_80 | 59 | 0.00075468 | 0.00018914 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1349-11_0_4_load_44 | 60 | 0.003264 | 0.00081805 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1349-11_0_4_load_46 | 63 | 0.0030489 | 0.00076413 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1349-11_0_4_load_65 | 64 | 0.00065797 | 0.0001649 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1349-11_0_4_load_66 | 65 | 0.0022494 | 0.00056375 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1349-11_0_4_load_47 | 66 | 0.0012146 | 0.0003044 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1349-11_0_4_load_113 | 67 | 0.0043349 | 0.0010864 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1349-11_0_4_load_48 | 68 | 0.00084205 | 0.00021104 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1349-11_0_4_load_60 | 69 | 0.0011432 | 0.0002865 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1349-11_0_4_load_49 | 71 | 0.0017484 | 0.00043819 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1349-11_0_4_load_51 | 73 | 0.0011372 | 0.00028502 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1349-11_0_4_load_130 | 76 | 0.0014551 | 0.00036468 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1349-11_0_4_load_114 | 77 | 0.0021561 | 0.00054038 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1349-11_0_4_load_57 | 78 | 0.002244 | 0.00056241 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1349-11_0_4_load_52 | 79 | 0.0026124 | 0.00065472 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1349-11_0_4_load_55 | 81 | 0.0014734 | 0.00036927 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1349-11_0_4_load_62 | 83 | 0.0022203 | 0.00055645 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1349-11_0_4_load_61 | 84 | 0.0019521 | 0.00048923 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1349-11_0_4_load_59 | 85 | 0.0026753 | 0.0006705 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1349-11_0_4_load_64 | 87 | 0.0028721 | 0.00071982 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1349-11_0_4_load_72 | 90 | 0.0014591 | 0.00036567 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1349-11_0_4_load_120 | 91 | 0.0027342 | 0.00068526 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1349-11_0_4_load_119 | 92 | 0.0017895 | 0.00044848 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1349-11_0_4_load_121 | 95 | 0.0026913 | 0.0006745 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1349-11_0_4_load_74 | 96 | 0.047662 | 0.011945 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1349-11_0_4_load_75 | 97 | 0.0085782 | 0.0021499 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1349-11_0_4_load_76 | 98 | 0.029922 | 0.0074993 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1349-11_0_4_load_78 | 99 | 0.0085583 | 0.0021449 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1349-11_0_4_load_87 | 100 | 0.0014292 | 0.00035819 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1349-11_0_4_load_81 | 102 | 0.00039761 | 9.9649e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1349-11_0_4_load_83 | 104 | 0.00046083 | 0.00011549 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1349-11_0_4_load_84 | 105 | 0.003232 | 0.00081001 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1349-11_0_4_load_85 | 106 | 0.00040677 | 0.00010195 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1349-11_0_4_load_104 | 107 | 0.003443 | 0.00086288 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1349-11_0_4_load_86 | 108 | 0.0033575 | 0.00084147 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1349-11_0_4_load_96 | 109 | 0.0032801 | 0.00082208 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1349-11_0_4_load_89 | 110 | 0.0023062 | 0.00057798 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1349-11_0_4_load_98 | 112 | 0.0023056 | 0.00057783 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1349-11_0_4_load_94 | 113 | 0.0023069 | 0.00057818 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1349-11_0_4_load_91 | 114 | 0.002307 | 0.00057818 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1349-11_0_4_load_92 | 115 | 0.0021019 | 0.0005268 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1349-11_0_4_load_95 | 117 | 0.0041665 | 0.0010442 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1349-11_0_4_load_102 | 118 | 0.0023064 | 0.00057804 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1349-11_0_4_load_103 | 119 | 0.0036012 | 0.00090255 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1349-11_0_4_load_101 | 121 | 0.0017351 | 0.00043485 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1349-11_0_4_load_128 | 122 | 0.081174 | 0.020344 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1349-11_0_4_load_122 | 123 | 0.0011832 | 0.00029653 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1349-11_0_4_load_123 | 124 | 0.0016086 | 0.00040315 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1349-11_0_4_load_124 | 125 | 0.0011664 | 0.00029234 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1349-11_0_4_load_125 | 126 | 0.0011787 | 0.00029541 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1349-11_0_4_line_0 |  | 0 | 1 | 0.0019295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1349-11_0_4_line_1 |  | 0 | 2 | 0.021425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1349-11_0_4_line_2 |  | 1 | 3 | 0.026313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1349-11_0_4_line_3 |  | 2 | 4 | 0.037597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1349-11_0_4_line_4 |  | 2 | 5 | 0.13806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1349-11_0_4_line_5 |  | 4 | 6 | 0.049449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1349-11_0_4_line_6 |  | 4 | 7 | 0.050892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1349-11_0_4_line_7 |  | 5 | 8 | 0.026759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1349-11_0_4_line_8 |  | 6 | 11 | 0.039503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1349-11_0_4_line_9 |  | 6 | 12 | 0.048762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1349-11_0_4_line_10 |  | 7 | 13 | 0.0046143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1349-11_0_4_line_11 |  | 8 | 9 | 0.053453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1349-11_0_4_line_12 |  | 8 | 10 | 0.044923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1349-11_0_4_line_13 |  | 9 | 67 | 0.021927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1349-11_0_4_line_14 |  | 11 | 17 | 0.021427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1349-11_0_4_line_15 |  | 12 | 18 | 0.012419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1349-11_0_4_line_16 |  | 13 | 14 | 0.00066579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_1349-11_0_4_line_17 |  | 14 | 15 | 0.030728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_1349-11_0_4_line_18 |  | 15 | 16 | 0.014658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1349-11_0_4_line_19 |  | 16 | 100 | 0.010796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1349-11_0_4_line_20 |  | 16 | 97 | 0.031915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1349-11_0_4_line_21 |  | 17 | 122 | 0.006942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1349-11_0_4_line_22 |  | 19 | 20 | 0.1673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1349-11_0_4_line_23 |  | 20 | 21 | 0.034578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1349-11_0_4_line_24 |  | 21 | 88 | 0.010389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1349-11_0_4_line_25 |  | 22 | 23 | 0.013443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1349-11_0_4_line_26 |  | 23 | 24 | 0.017377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1349-11_0_4_line_27 |  | 23 | 25 | 0.083744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1349-11_0_4_line_28 |  | 24 | 32 | 0.17915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1349-11_0_4_line_29 |  | 26 | 27 | 0.039864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1349-11_0_4_line_30 |  | 27 | 37 | 0.018653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1349-11_0_4_line_31 |  | 28 | 29 | 0.035682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1349-11_0_4_line_32 |  | 28 | 30 | 0.12479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1349-11_0_4_line_33 |  | 28 | 31 | 0.029751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1349-11_0_4_line_34 |  | 29 | 35 | 0.005382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1349-11_0_4_line_35 |  | 29 | 36 | 0.032505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1349-11_0_4_line_36 |  | 30 | 41 | 0.038658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1349-11_0_4_line_37 |  | 30 | 39 | 0.023682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1349-11_0_4_line_38 |  | 31 | 48 | 0.033176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1349-11_0_4_line_39 |  | 32 | 33 | 0.013193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1349-11_0_4_line_40 |  | 32 | 34 | 0.0099751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1349-11_0_4_line_41 |  | 33 | 45 | 0.0080925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1349-11_0_4_line_42 |  | 34 | 43 | 0.040166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1349-11_0_4_line_43 |  | 37 | 52 | 0.054305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1349-11_0_4_line_44 |  | 38 | 39 | 0.030219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1349-11_0_4_line_45 |  | 38 | 40 | 0.0086571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1349-11_0_4_line_46 |  | 41 | 42 | 0.018664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1349-11_0_4_line_47 |  | 41 | 43 | 0.039887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1349-11_0_4_line_48 |  | 42 | 44 | 0.014178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1349-11_0_4_line_49 |  | 44 | 46 | 0.076626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1349-11_0_4_line_50 |  | 46 | 47 | 0.0062374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1349-11_0_4_line_51 |  | 48 | 121 | 0.017313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1349-11_0_4_line_52 |  | 49 | 50 | 0.018638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1349-11_0_4_line_53 |  | 49 | 51 | 0.0039296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1349-11_0_4_line_54 |  | 50 | 52 | 0.19551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1349-11_0_4_line_55 |  | 51 | 53 | 0.02819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1349-11_0_4_line_56 |  | 53 | 54 | 0.019596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1349-11_0_4_line_57 |  | 54 | 55 | 0.016544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1349-11_0_4_line_58 |  | 54 | 56 | 0.0327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1349-11_0_4_line_59 |  | 55 | 58 | 0.018584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1349-11_0_4_line_60 |  | 56 | 57 | 0.028267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1349-11_0_4_line_61 |  | 58 | 59 | 0.014142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1349-11_0_4_line_62 |  | 59 | 102 | 0.0027609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1349-11_0_4_line_63 |  | 60 | 61 | 0.050329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1349-11_0_4_line_64 |  | 60 | 62 | 0.18302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1349-11_0_4_line_65 |  | 61 | 63 | 0.0029289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1349-11_0_4_line_66 |  | 62 | 64 | 0.059577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1349-11_0_4_line_67 |  | 63 | 66 | 0.084635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1349-11_0_4_line_68 |  | 64 | 65 | 0.022526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1349-11_0_4_line_69 |  | 66 | 68 | 0.0044786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1349-11_0_4_line_70 |  | 67 | 77 | 0.0030961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1349-11_0_4_line_71 |  | 68 | 69 | 0.012998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1349-11_0_4_line_72 |  | 69 | 70 | 0.0026993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1349-11_0_4_line_73 |  | 70 | 85 | 0.004276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1349-11_0_4_line_74 |  | 70 | 81 | 0.03358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1349-11_0_4_line_75 |  | 71 | 72 | 0.059604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1349-11_0_4_line_76 |  | 72 | 73 | 0.036398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1349-11_0_4_line_77 |  | 72 | 74 | 0.12403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1349-11_0_4_line_78 |  | 73 | 75 | 0.011876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1349-11_0_4_line_79 |  | 74 | 76 | 0.033134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1349-11_0_4_line_80 |  | 74 | 77 | 0.17372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1349-11_0_4_line_81 |  | 75 | 78 | 0.013454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1349-11_0_4_line_82 |  | 75 | 79 | 0.01216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1349-11_0_4_line_83 |  | 78 | 84 | 0.022882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1349-11_0_4_line_84 |  | 79 | 80 | 0.018784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1349-11_0_4_line_85 |  | 80 | 81 | 0.048046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1349-11_0_4_line_86 |  | 80 | 82 | 0.041341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1349-11_0_4_line_87 |  | 82 | 83 | 0.019246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1349-11_0_4_line_88 |  | 83 | 86 | 0.039822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1349-11_0_4_line_89 |  | 86 | 87 | 0.018072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1349-11_0_4_line_90 |  | 88 | 89 | 0.015606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1349-11_0_4_line_91 |  | 88 | 90 | 0.03802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1349-11_0_4_line_92 |  | 89 | 91 | 0.060341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1349-11_0_4_line_93 |  | 90 | 92 | 0.0059258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1349-11_0_4_line_94 |  | 91 | 95 | 0.019886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1349-11_0_4_line_95 |  | 92 | 93 | 0.054575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1349-11_0_4_line_96 |  | 93 | 94 | 0.005299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1349-11_0_4_line_97 |  | 94 | 99 | 0.066466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1349-11_0_4_line_98 |  | 95 | 123 | 0.023884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1349-11_0_4_line_99 |  | 96 | 97 | 0.010049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1349-11_0_4_line_100 |  | 96 | 98 | 0.035758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1349-11_0_4_line_101 |  | 98 | 99 | 0.055803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1349-11_0_4_line_102 |  | 100 | 101 | 0.014737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1349-11_0_4_line_103 |  | 101 | 108 | 0.018311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1349-11_0_4_line_104 |  | 102 | 103 | 0.015543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1349-11_0_4_line_105 |  | 103 | 104 | 0.0030778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1349-11_0_4_line_106 |  | 103 | 105 | 0.027302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1349-11_0_4_line_107 |  | 104 | 106 | 0.023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1349-11_0_4_line_108 |  | 105 | 107 | 0.013251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1349-11_0_4_line_109 |  | 106 | 108 | 0.022495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1349-11_0_4_line_110 |  | 107 | 109 | 0.0056576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1349-11_0_4_line_111 |  | 109 | 116 | 0.030171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1349-11_0_4_line_112 |  | 110 | 111 | 0.013476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1349-11_0_4_line_113 |  | 111 | 112 | 0.0439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1349-11_0_4_line_114 |  | 111 | 113 | 0.019974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1349-11_0_4_line_115 |  | 112 | 120 | 0.025629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1349-11_0_4_line_116 |  | 113 | 115 | 0.013811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1349-11_0_4_line_117 |  | 114 | 115 | 0.0087639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1349-11_0_4_line_118 |  | 114 | 116 | 0.0093088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1349-11_0_4_line_119 |  | 116 | 117 | 0.014154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1349-11_0_4_line_120 |  | 117 | 118 | 0.0015387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1349-11_0_4_line_121 |  | 118 | 119 | 0.014992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1349-11_0_4_line_122 |  | 120 | 121 | 0.020446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1349-11_0_4_line_123 |  | 123 | 124 | 0.0015727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1349-11_0_4_line_124 |  | 124 | 125 | 0.021506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1349-11_0_4_line_125 |  | 125 | 126 | 0.0011378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1349-11_0_4_trafo_5 | 0.63 MVA 20/0.4 kV | 127 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2709178.8151 | 1227963.7231 | 2709178.9812 | 1227961.8008
1 | 2709176.9708 | 1227985.0683 | 2709178.8151 | 1227963.7231
2 | 2709177.9854 | 1227936.0164 | 2709180.59 | 1227943.1808 | 2709178.9812 | 1227961.8008
3 | 2709214.4153 | 1227989.5033 | 2709176.9708 | 1227985.0683
4 | 2709176.9708 | 1227985.0683 | 2709041.1854 | 1228010.0488
5 | 2709209.8196 | 1228038.734 | 2709210.5268 | 1228032.42 | 2709213.5803 | 1227996.5823 | 2709214.4153 | 1227989.5033
6 | 2709214.4153 | 1227989.5033 | 2709218.3202 | 1227972.918 | 2709231.1241 | 1227957.5415 | 2709243.8262 | 1227952.036
7 | 2709038.8809 | 1228036.7081 | 2709041.1854 | 1228010.0488
8 | 2709205.7175 | 1228078.0218 | 2709206.5661 | 1228071.021 | 2709209.8196 | 1228038.734
9 | 2709209.8196 | 1228038.734 | 2709258.4147 | 1228042.7667
10 | 2709243.8262 | 1227952.036 | 2709248.0598 | 1227950.201
11 | 2709038.8809 | 1228036.7081 | 2709029.574 | 1228035.848 | 2708986.8088 | 1228046.6435
12 | 2709038.8809 | 1228036.7081 | 2709034.5478 | 1228081.4218
13 | 2708965.5492 | 1228052.0101 | 2708986.8088 | 1228046.6435
14 | 2709205.7175 | 1228078.0218 | 2709203.4994 | 1228099.3306
15 | 2709258.4147 | 1228042.7667 | 2709270.7907 | 1228043.7938
16 | 2709248.6707 | 1227949.9363 | 2709248.0598 | 1227950.201
17 | 2709276.8648 | 1227937.7161 | 2709248.6707 | 1227949.9363
18 | 2709290.3141 | 1227931.8869 | 2709276.8648 | 1227937.7161
19 | 2709290.3141 | 1227931.8869 | 2709300.0185 | 1227927.1569
20 | 2709290.3141 | 1227931.8869 | 2709303.6748 | 1227960.871
21 | 2709210.3178 | 1228100.7346 | 2709203.4994 | 1228099.3306
22 | 2709492.1667 | 1228042.4822 | 2709630.112 | 1228137.1445
23 | 2709492.1667 | 1228042.4822 | 2709459.7803 | 1228030.3682
24 | 2709450.05 | 1228026.7286 | 2709459.7803 | 1228030.3682
25 | 2709545.6486 | 1227477.2053 | 2709537.8462 | 1227474.0481 | 2709533.3229 | 1227471.8573
26 | 2709545.6486 | 1227477.2053 | 2709561.7594 | 1227483.7183
27 | 2709555.8866 | 1227400.8471 | 2709539.7228 | 1227419.9195 | 2709536.4757 | 1227435.2936 | 2709537.8599 | 1227449.4409 | 2709542.48 | 1227466.928 | 2709545.6486 | 1227477.2053
28 | 2709593.5576 | 1227660.0206 | 2709561.7594 | 1227483.7183
29 | 2709356.8112 | 1227582.3665 | 2709349.7517 | 1227543.1328
30 | 2709356.8112 | 1227582.3665 | 2709338.6555 | 1227586.6438
31 | 2709394.2136 | 1227778.2913 | 2709429.4731 | 1227772.1906
32 | 2709429.4731 | 1227772.1906 | 2709552.6695 | 1227752.2984
33 | 2709429.4731 | 1227772.1906 | 2709429.3165 | 1227786.0538 | 2709427.7337 | 1227801.8615
34 | 2709395.0329 | 1227783.6104 | 2709394.2136 | 1227778.2913
35 | 2709394.2136 | 1227778.2913 | 2709374.8714 | 1227781.1044 | 2709362.139 | 1227783.5198
36 | 2709590.7572 | 1227745.3501 | 2709580.438 | 1227746.3386 | 2709552.6695 | 1227752.2984
37 | 2709552.6695 | 1227752.2984 | 2709547.3901 | 1227729.2125
38 | 2709425.5065 | 1227834.9383 | 2709425.6578 | 1227828.3408 | 2709425.8246 | 1227820.9271 | 2709427.7337 | 1227801.8615
39 | 2709606.6734 | 1227658.591 | 2709593.5576 | 1227660.0206
40 | 2709587.7902 | 1227665.7553 | 2709588.9782 | 1227660.5198 | 2709593.5576 | 1227660.0206
41 | 2709614.7182 | 1227657.7141 | 2709606.6734 | 1227658.591
42 | 2709586.1651 | 1227705.8071 | 2709586.8249 | 1227670.0095 | 2709587.7902 | 1227665.7553
43 | 2709285.7975 | 1227599.0965 | 2709338.6555 | 1227586.6438
44 | 2709548.3681 | 1227699.2694 | 2709545.9917 | 1227723.0978 | 2709547.3901 | 1227729.2125
45 | 2709549.2273 | 1227690.655 | 2709548.3681 | 1227699.2694
46 | 2709609.3908 | 1227743.5698 | 2709590.7572 | 1227745.3501
47 | 2709590.7572 | 1227745.3501 | 2709586.0324 | 1227713.0053 | 2709586.1651 | 1227705.8071
48 | 2709609.3908 | 1227743.5698 | 2709608.5581 | 1227757.7235
49 | 2709608.5581 | 1227757.7235 | 2709608.1323 | 1227764.9629 | 2709595.1619 | 1227771.6178 | 2709586.0864 | 1227781.6249 | 2709569.0821 | 1227819.2468
50 | 2709566.5132 | 1227824.9306 | 2709569.0821 | 1227819.2468
51 | 2709426.3296 | 1227852.2266 | 2709425.4661 | 1227836.6991 | 2709425.5065 | 1227834.9383
52 | 2709299.3367 | 1227795.4896 | 2709317.6442 | 1227791.996
53 | 2709299.3367 | 1227795.4896 | 2709295.4767 | 1227796.2262
54 | 2709317.6442 | 1227791.996 | 2709285.7975 | 1227599.0965
55 | 2709267.7936 | 1227801.55 | 2709290.2278 | 1227797.2278 | 2709295.4767 | 1227796.2262
56 | 2709248.551 | 1227805.2573 | 2709267.7936 | 1227801.55
57 | 2709248.551 | 1227805.2573 | 2709256.2499 | 1227819.9011
58 | 2709248.551 | 1227805.2573 | 2709217.4987 | 1227815.5067
59 | 2709256.2499 | 1227819.9011 | 2709258.7456 | 1227824.6481 | 2709268.0861 | 1227834.0045
60 | 2709191.0979 | 1227825.5989 | 2709214.852 | 1227816.3803 | 2709217.4987 | 1227815.5067
61 | 2709271.5318 | 1227847.7205 | 2709268.0861 | 1227834.0045 | 2709268.0861 | 1227834.0045
62 | 2709272.2045 | 1227850.3982 | 2709271.5318 | 1227847.7205
63 | 2708982.0135 | 1227855.1621 | 2708984.9492 | 1227835.6011 | 2708993.7854 | 1227814.1913 | 2708997.4417 | 1227807.772
64 | 2708997.4417 | 1227807.772 | 2708886.5892 | 1227662.1469
65 | 2708982.0135 | 1227855.1621 | 2708979.0852 | 1227855.2177
66 | 2708886.5892 | 1227662.1469 | 2708898.0336 | 1227658.0755 | 2708922.3955 | 1227648.1361 | 2708934.0952 | 1227643.369 | 2708931.8822 | 1227635.1777
67 | 2708979.0852 | 1227855.2177 | 2708937.0052 | 1227856.0163 | 2708904.5893 | 1227853.8322 | 2708894.624 | 1227852.4697
68 | 2708931.8822 | 1227635.1777 | 2708930.9222 | 1227631.6242 | 2708925.6684 | 1227619.2631 | 2708926.2327 | 1227613.8783
69 | 2708894.624 | 1227852.4697 | 2708890.1867 | 1227851.863
70 | 2708965.5492 | 1228052.0101 | 2708962.5473 | 1228052.7679
71 | 2708890.1867 | 1227851.863 | 2708877.3083 | 1227850.1021
72 | 2708874.6339 | 1227849.7364 | 2708877.3083 | 1227850.1021
73 | 2708874.6339 | 1227849.7364 | 2708875.0983 | 1227845.4862
74 | 2708874.6339 | 1227849.7364 | 2708841.6179 | 1227843.6084
75 | 2708766.7788 | 1227907.1626 | 2708814.3285 | 1227913.6147 | 2708818.2773 | 1227902.6876
76 | 2708766.7788 | 1227907.1626 | 2708771.0557 | 1227892.5519 | 2708780.897 | 1227873.804
77 | 2708766.7788 | 1227907.1626 | 2708790.4728 | 1228028.91
78 | 2708786.4169 | 1227863.2885 | 2708780.897 | 1227873.804
79 | 2708790.4728 | 1228028.91 | 2708782.4661 | 1228031.5545 | 2708757.934 | 1228035.1531
80 | 2708790.4728 | 1228028.91 | 2708962.5473 | 1228052.7679
81 | 2708786.4169 | 1227863.2885 | 2708773.2836 | 1227860.3693
82 | 2708786.4169 | 1227863.2885 | 2708789.6545 | 1227851.5675
83 | 2708773.2836 | 1227860.3693 | 2708750.9472 | 1227855.4046
84 | 2708794.656 | 1227833.4611 | 2708789.6545 | 1227851.5675
85 | 2708794.656 | 1227833.4611 | 2708840.271 | 1227843.3584 | 2708841.6179 | 1227843.6084
86 | 2708754.6274 | 1227823.1325 | 2708785.2587 | 1227830.8984 | 2708794.656 | 1227833.4611
87 | 2708754.6274 | 1227823.1325 | 2708736.0091 | 1227818.2586
88 | 2708697.4525 | 1227808.2987 | 2708729.1906 | 1227816.4737 | 2708736.0091 | 1227818.2586
89 | 2708697.4525 | 1227808.2987 | 2708690.1578 | 1227824.8329
90 | 2709450.05 | 1228026.7286 | 2709434.4994 | 1228024.9523
91 | 2709450.05 | 1228026.7286 | 2709460.1085 | 1227990.0637
92 | 2709434.4994 | 1228024.9523 | 2709433.0628 | 1228045.7639 | 2709430.9274 | 1228062.1259 | 2709425.8651 | 1228084.5409
93 | 2709460.4308 | 1227984.1466 | 2709460.1085 | 1227990.0637 | 2709460.1085 | 1227990.0637
94 | 2709425.8651 | 1228084.5409 | 2709425.8606 | 1228084.5608 | 2709421.2821 | 1228103.8913
95 | 2709431.361 | 1227954.5746 | 2709451.5701 | 1227953.6345 | 2709455.9768 | 1227955.1167 | 2709457.7517 | 1227959.575 | 2709460.2723 | 1227969.6401 | 2709460.658 | 1227979.9773 | 2709460.4308 | 1227984.1466
96 | 2709430.8137 | 1227949.305 | 2709431.361 | 1227954.5746
97 | 2709430.8137 | 1227949.305 | 2709384.7492 | 1227969.2841 | 2709382.3896 | 1227975.5899 | 2709373.7104 | 1227979.5086
98 | 2709421.2821 | 1228103.8913 | 2709415.7775 | 1228127.132
99 | 2709307.8817 | 1227969.9974 | 2709303.6748 | 1227960.871
100 | 2709307.8817 | 1227969.9974 | 2709322.8511 | 1228002.4715
101 | 2709373.7104 | 1227979.5086 | 2709322.8511 | 1228002.4715 | 2709322.8511 | 1228002.4715
102 | 2709313.266 | 1227920.7001 | 2709300.0185 | 1227927.1569
103 | 2709313.266 | 1227920.7001 | 2709305.6812 | 1227904.0336
104 | 2709277.3722 | 1227864.8762 | 2709274.8523 | 1227860.938 | 2709272.2045 | 1227850.3982
105 | 2709277.3722 | 1227864.8762 | 2709279.3554 | 1227867.2298
106 | 2709277.3722 | 1227864.8762 | 2709303.9412 | 1227858.592
107 | 2709279.3554 | 1227867.2298 | 2709294.1761 | 1227884.818
108 | 2709303.9412 | 1227858.592 | 2709316.8366 | 1227855.542
109 | 2709294.1761 | 1227884.818 | 2709296.6732 | 1227887.7814 | 2709302.6004 | 1227897.2642 | 2709305.6812 | 1227904.0336
110 | 2709322.3423 | 1227854.2398 | 2709316.8366 | 1227855.542
111 | 2709351.703 | 1227847.2953 | 2709322.3423 | 1227854.2398
112 | 2709362.9522 | 1227897.9182 | 2709350.7027 | 1227903.5348
113 | 2709362.9522 | 1227897.9182 | 2709403.22 | 1227880.4322
114 | 2709362.9522 | 1227897.9182 | 2709358.6194 | 1227878.4201
115 | 2709427.465 | 1227872.6409 | 2709416.5055 | 1227874.6631 | 2709403.22 | 1227880.4322
116 | 2709358.6194 | 1227878.4201 | 2709355.6234 | 1227864.9377
117 | 2709353.7223 | 1227856.3825 | 2709355.6234 | 1227864.9377
118 | 2709351.703 | 1227847.2953 | 2709353.7223 | 1227856.3825
119 | 2709351.703 | 1227847.2953 | 2709350.3468 | 1227833.2062
120 | 2709350.1994 | 1227831.6745 | 2709350.3468 | 1227833.2062
121 | 2709348.763 | 1227816.7515 | 2709350.1994 | 1227831.6745
122 | 2709427.465 | 1227872.6409 | 2709426.3296 | 1227852.2266
123 | 2709415.7775 | 1228127.132 | 2709415.415 | 1228128.6623
124 | 2709415.415 | 1228128.6623 | 2709413.1557 | 1228138.2011 | 2709411.563 | 1228149.7953
125 | 2709411.4081 | 1228150.9226 | 2709411.563 | 1228149.7953

## bus_geodata
| x | y | coords
0 | 2709178.8151 | 1227963.7231
1 | 2709178.9812 | 1227961.8008
2 | 2709176.9708 | 1227985.0683
3 | 2709177.9854 | 1227936.0164
4 | 2709214.4153 | 1227989.5033
5 | 2709041.1854 | 1228010.0488
6 | 2709209.8196 | 1228038.734
7 | 2709243.8262 | 1227952.036
8 | 2709038.8809 | 1228036.7081
9 | 2708986.8088 | 1228046.6435
10 | 2709034.5478 | 1228081.4218
11 | 2709205.7175 | 1228078.0218
12 | 2709258.4147 | 1228042.7667
13 | 2709248.0598 | 1227950.201
14 | 2709248.6707 | 1227949.9363
15 | 2709276.8648 | 1227937.7161
16 | 2709290.3141 | 1227931.8869
17 | 2709203.4994 | 1228099.3306
18 | 2709270.7907 | 1228043.7938
19 | 2709630.112 | 1228137.1445
20 | 2709492.1667 | 1228042.4822
21 | 2709459.7803 | 1228030.3682
22 | 2709533.3229 | 1227471.8573
23 | 2709545.6486 | 1227477.2053
24 | 2709561.7594 | 1227483.7183
25 | 2709555.8866 | 1227400.8471
26 | 2709349.7517 | 1227543.1328
27 | 2709356.8112 | 1227582.3665
28 | 2709429.4731 | 1227772.1906
29 | 2709394.2136 | 1227778.2913
30 | 2709552.6695 | 1227752.2984
31 | 2709427.7337 | 1227801.8615
32 | 2709593.5576 | 1227660.0206
33 | 2709606.6734 | 1227658.591
34 | 2709587.7902 | 1227665.7553
35 | 2709395.0329 | 1227783.6104
36 | 2709362.139 | 1227783.5198
37 | 2709338.6555 | 1227586.6438
38 | 2709548.3681 | 1227699.2694
39 | 2709547.3901 | 1227729.2125
40 | 2709549.2273 | 1227690.655
41 | 2709590.7572 | 1227745.3501
42 | 2709609.3908 | 1227743.5698
43 | 2709586.1651 | 1227705.8071
44 | 2709608.5581 | 1227757.7235
45 | 2709614.7182 | 1227657.7141
46 | 2709569.0821 | 1227819.2468
47 | 2709566.5132 | 1227824.9306
48 | 2709425.5065 | 1227834.9383
49 | 2709299.3367 | 1227795.4896
50 | 2709317.6442 | 1227791.996
51 | 2709295.4767 | 1227796.2262
52 | 2709285.7975 | 1227599.0965
53 | 2709267.7936 | 1227801.55
54 | 2709248.551 | 1227805.2573
55 | 2709256.2499 | 1227819.9011
56 | 2709217.4987 | 1227815.5067
57 | 2709191.0979 | 1227825.5989
58 | 2709268.0861 | 1227834.0045
59 | 2709271.5318 | 1227847.7205
60 | 2708997.4417 | 1227807.772
61 | 2708982.0135 | 1227855.1621
62 | 2708886.5892 | 1227662.1469
63 | 2708979.0852 | 1227855.2177
64 | 2708931.8822 | 1227635.1777
65 | 2708926.2327 | 1227613.8783
66 | 2708894.624 | 1227852.4697
67 | 2708965.5492 | 1228052.0101
68 | 2708890.1867 | 1227851.863
69 | 2708877.3083 | 1227850.1021
70 | 2708874.6339 | 1227849.7364
71 | 2708818.2773 | 1227902.6877
72 | 2708766.7788 | 1227907.1626
73 | 2708780.897 | 1227873.804
74 | 2708790.4728 | 1228028.91
75 | 2708786.4169 | 1227863.2885
76 | 2708757.934 | 1228035.1531
77 | 2708962.5473 | 1228052.7679
78 | 2708773.2836 | 1227860.3693
79 | 2708789.6545 | 1227851.5675
80 | 2708794.656 | 1227833.4611
81 | 2708841.6179 | 1227843.6084
82 | 2708754.6274 | 1227823.1325
83 | 2708736.0091 | 1227818.2586
84 | 2708750.9472 | 1227855.4046
85 | 2708875.0983 | 1227845.4862
86 | 2708697.4525 | 1227808.2987
87 | 2708690.1578 | 1227824.8329
88 | 2709450.05 | 1228026.7286
89 | 2709434.4994 | 1228024.9523
90 | 2709460.1085 | 1227990.0637
91 | 2709425.8651 | 1228084.5409
92 | 2709460.4308 | 1227984.1466
93 | 2709431.361 | 1227954.5746
94 | 2709430.8137 | 1227949.305
95 | 2709421.2821 | 1228103.8913
96 | 2709307.8817 | 1227969.9974
97 | 2709303.6748 | 1227960.871
98 | 2709322.8511 | 1228002.4715
99 | 2709373.7104 | 1227979.5086
100 | 2709300.0185 | 1227927.1569
101 | 2709313.266 | 1227920.7001
102 | 2709272.2045 | 1227850.3982
103 | 2709277.3722 | 1227864.8762
104 | 2709279.3554 | 1227867.2298
105 | 2709303.9412 | 1227858.592
106 | 2709294.1761 | 1227884.818
107 | 2709316.8366 | 1227855.542
108 | 2709305.6812 | 1227904.0336
109 | 2709322.3423 | 1227854.2398
110 | 2709350.7027 | 1227903.5348
111 | 2709362.9522 | 1227897.9182
112 | 2709403.22 | 1227880.4322
113 | 2709358.6194 | 1227878.4201
114 | 2709353.7223 | 1227856.3825
115 | 2709355.6234 | 1227864.9377
116 | 2709351.703 | 1227847.2953
117 | 2709350.3468 | 1227833.2062
118 | 2709350.1994 | 1227831.6745
119 | 2709348.763 | 1227816.7515
120 | 2709427.465 | 1227872.6409
121 | 2709426.3296 | 1227852.2266
122 | 2709210.3178 | 1228100.7346
123 | 2709415.7775 | 1228127.132
124 | 2709415.415 | 1228128.6623
125 | 2709411.563 | 1228149.7953
126 | 2709411.4081 | 1228150.9226
127 | 2709290.3141 | 1227931.8869

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98867 | -0.217 | 0.0068095 | 0.0017066
1 | 0.98848 | -0.22072 | 0.092365 | 0.023149
2 | 0.99093 | -0.17321 | 0 | 0
3 | 0.9881 | -0.2281 | 0.015711 | 0.0039374
4 | 0.99376 | -0.11871 | 0 | 0
5 | 0.98779 | -0.23334 | 0.0040437 | 0.0010135
6 | 0.98911 | -0.20829 | 0 | 0
7 | 1 | 0 | -0.47963 | -0.12216
8 | 0.98724 | -0.24407 | 0 | 0
9 | 0.98519 | -0.28351 | 0.0018425 | 0.00046178
10 | 0.98709 | -0.24703 | 0.0036824 | 0.0009229
11 | 0.98615 | -0.26559 | 0 | 0
12 | 0.98817 | -0.22655 | 0.015604 | 0.0039107
13 | 0.99956 | -0.0082839 | 0.0013998 | 0.00035081
14 | 0.9995 | -0.0094716 | 0.0012955 | 0.00032469
15 | 0.99663 | -0.064103 | 0.0015177 | 0.00038037
16 | 0.99527 | -0.090078 | 0 | 0
17 | 0.98455 | -0.29682 | 0 | 0
18 | 0.98811 | -0.22774 | 0.0053876 | 0.0013503
19 | 0.98263 | -0.33506 | 0.0046101 | 0.0011554
20 | 0.98334 | -0.32114 | 0.0028093 | 0.00070408
21 | 0.98358 | -0.31651 | 0.0018377 | 0.00046058
22 | 0.9781 | -0.42313 | 0.00024805 | 6.2167e-05
23 | 0.97811 | -0.42307 | 0 | 0
24 | 0.97813 | -0.42267 | 0.00033848 | 8.483e-05
25 | 0.97803 | -0.42461 | 0.0010061 | 0.00025214
26 | 0.98332 | -0.32112 | 0.0018716 | 0.00046907
27 | 0.98338 | -0.31977 | 0 | 0
28 | 0.97984 | -0.3889 | 0 | 0
29 | 0.97968 | -0.39214 | 0 | 0
30 | 0.97899 | -0.40559 | 0 | 0
31 | 0.98018 | -0.38222 | 0.0059112 | 0.0014815
32 | 0.97839 | -0.41745 | 0.00035522 | 8.9027e-05
33 | 0.97836 | -0.418 | 0.0009651 | 0.00024188
34 | 0.97843 | -0.41668 | 0.00029104 | 7.2942e-05
35 | 0.97966 | -0.3924 | 0.0026697 | 0.0006691
36 | 0.97961 | -0.39351 | 0.0023288 | 0.00058365
37 | 0.98342 | -0.31914 | 0.00038006 | 9.5253e-05
38 | 0.97894 | -0.40666 | 0.00024163 | 6.0558e-05
39 | 0.97897 | -0.40613 | 0.00027801 | 6.9677e-05
40 | 0.97893 | -0.40678 | 0.00073327 | 0.00018378
41 | 0.97878 | -0.40988 | 0 | 0
42 | 0.97875 | -0.41032 | 0 | 0
43 | 0.9786 | -0.41337 | 0.0002652 | 6.6464e-05
44 | 0.97874 | -0.41066 | 0.00023269 | 5.8318e-05
45 | 0.97835 | -0.4182 | 0.0013204 | 0.00033092
46 | 0.97866 | -0.41214 | 0.00037031 | 9.2808e-05
47 | 0.97866 | -0.41222 | 0.00069319 | 0.00017373
48 | 0.98074 | -0.37123 | 0.0047245 | 0.0011841
49 | 0.98622 | -0.26452 | 0.001071 | 0.00026843
50 | 0.98593 | -0.27013 | 0.0034644 | 0.00086826
51 | 0.98628 | -0.26327 | 0.00039577 | 9.919e-05
52 | 0.98353 | -0.31694 | 0.011061 | 0.0027721
53 | 0.98676 | -0.25405 | 0.00032465 | 8.1365e-05
54 | 0.98709 | -0.24753 | 0 | 0
55 | 0.98739 | -0.24166 | 0.00085534 | 0.00021437
56 | 0.98705 | -0.24828 | 0.00075321 | 0.00018877
57 | 0.98704 | -0.24855 | 0.00052693 | 0.00013206
58 | 0.98775 | -0.23478 | 0.00025667 | 6.4327e-05
59 | 0.98802 | -0.22948 | 0.00075468 | 0.00018914
60 | 0.97091 | -0.56286 | 0.003264 | 0.00081805
61 | 0.9712 | -0.55711 | 0 | 0
62 | 0.97041 | -0.57272 | 0 | 0
63 | 0.97121 | -0.55677 | 0.0030489 | 0.00076413
64 | 0.97025 | -0.57593 | 0.00065797 | 0.0001649
65 | 0.9702 | -0.57687 | 0.0022494 | 0.00056375
66 | 0.97194 | -0.54235 | 0.0012146 | 0.0003044
67 | 0.98439 | -0.29902 | 0.0043349 | 0.0010864
68 | 0.97199 | -0.54148 | 0.00084205 | 0.00021104
69 | 0.97212 | -0.53878 | 0.0011432 | 0.0002865
70 | 0.97215 | -0.53816 | 0 | 0
71 | 0.97525 | -0.47713 | 0.0017484 | 0.00043819
72 | 0.97534 | -0.47522 | 0 | 0
73 | 0.97434 | -0.495 | 0.0011372 | 0.00028502
74 | 0.97897 | -0.40417 | 0 | 0
75 | 0.97402 | -0.50122 | 0 | 0
76 | 0.97893 | -0.40505 | 0.0014551 | 0.00036468
77 | 0.98429 | -0.30097 | 0.0021561 | 0.00054038
78 | 0.97397 | -0.50225 | 0.002244 | 0.00056241
79 | 0.97375 | -0.50665 | 0.0026124 | 0.00065472
80 | 0.97337 | -0.51413 | 0 | 0
81 | 0.97263 | -0.5288 | 0.0014734 | 0.00036927
82 | 0.97317 | -0.51801 | 0 | 0
83 | 0.97308 | -0.51982 | 0.0022203 | 0.00055645
84 | 0.97393 | -0.50307 | 0.0019521 | 0.00048923
85 | 0.97214 | -0.53837 | 0.0026753 | 0.0006705
86 | 0.97298 | -0.52192 | 0 | 0
87 | 0.97293 | -0.52288 | 0.0028721 | 0.00071982
88 | 0.98367 | -0.31478 | 0 | 0
89 | 0.98351 | -0.31775 | 0 | 0
90 | 0.98436 | -0.30121 | 0.0014591 | 0.00036567
91 | 0.98293 | -0.32924 | 0.0027342 | 0.00068526
92 | 0.98448 | -0.29894 | 0.0017895 | 0.00044848
93 | 0.98564 | -0.27631 | 0 | 0
94 | 0.98575 | -0.27411 | 0 | 0
95 | 0.98278 | -0.33205 | 0.0026913 | 0.0006745
96 | 0.99081 | -0.17593 | 0.047662 | 0.011945
97 | 0.99182 | -0.15647 | 0.0085782 | 0.0021499
98 | 0.98879 | -0.2151 | 0.029922 | 0.0074993
99 | 0.98716 | -0.24663 | 0.0085583 | 0.0021449
100 | 0.99444 | -0.10603 | 0.0014292 | 0.00035819
101 | 0.99331 | -0.12747 | 0 | 0
102 | 0.98808 | -0.22841 | 0.00039761 | 9.9649e-05
103 | 0.98839 | -0.22227 | 0 | 0
104 | 0.98861 | -0.21797 | 0.00046083 | 0.00011549
105 | 0.98698 | -0.24964 | 0.003232 | 0.00081001
106 | 0.99028 | -0.18575 | 0.00040677 | 0.00010195
107 | 0.98633 | -0.26218 | 0.003443 | 0.00086288
108 | 0.99192 | -0.15418 | 0.0033575 | 0.00084147
109 | 0.98607 | -0.26719 | 0.0032801 | 0.00082208
110 | 0.98323 | -0.32253 | 0.0023062 | 0.00057798
111 | 0.98326 | -0.32197 | 0 | 0
112 | 0.98216 | -0.3434 | 0.0023056 | 0.00057783
113 | 0.9838 | -0.31141 | 0.0023069 | 0.00057818
114 | 0.98448 | -0.29822 | 0.002307 | 0.00057818
115 | 0.98421 | -0.30354 | 0.0021019 | 0.0005268
116 | 0.98479 | -0.29218 | 0 | 0
117 | 0.98466 | -0.29474 | 0.0041665 | 0.0010442
118 | 0.98465 | -0.29491 | 0.0023064 | 0.00057804
119 | 0.9846 | -0.29588 | 0.0036012 | 0.00090255
120 | 0.98158 | -0.35486 | 0 | 0
121 | 0.98111 | -0.36402 | 0.0017351 | 0.00043485
122 | 0.98403 | -0.30695 | 0.081174 | 0.020344
123 | 0.98267 | -0.33427 | 0.0011832 | 0.00029653
124 | 0.98266 | -0.33438 | 0.0016086 | 0.00040315
125 | 0.98262 | -0.33529 | 0.0011664 | 0.00029234
126 | 0.98262 | -0.33531 | 0.0011787 | 0.00029541
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.1081 | 0.027102 | -0.10808 | -0.027089 | 1.9154e-05 | 1.2234e-05 | 0.1627 | 0.1627 | 0.1627 | 0.98867 | -0.217 | 0.98848 | -0.22072 | 44.6982
1 | -0.11491 | -0.028808 | 0.11515 | 0.028962 | 0.00024032 | 0.00015353 | 0.17295 | 0.17295 | 0.17295 | 0.98867 | -0.217 | 0.99093 | -0.17321 | 47.5138
2 | 0.015716 | 0.0039406 | -0.015711 | -0.0039374 | 5.5232e-06 | 3.1977e-06 | 0.023659 | 0.023659 | 0.023659 | 0.98848 | -0.22072 | 0.9881 | -0.2281 | 6.4997
3 | -0.16465 | -0.041596 | 0.16509 | 0.041871 | 0.00043136 | 0.0002751 | 0.24737 | 0.24737 | 0.24737 | 0.99093 | -0.17321 | 0.99376 | -0.11871 | 33.9791
4 | 0.049504 | 0.012634 | -0.049361 | -0.012545 | 0.00014337 | 8.8208e-05 | 0.074418 | 0.074419 | 0.074419 | 0.99093 | -0.17321 | 0.98779 | -0.23334 | 10.2224
5 | 0.10301 | 0.026143 | -0.10257 | -0.025861 | 0.00044182 | 0.00028213 | 0.15436 | 0.15436 | 0.15436 | 0.99376 | -0.11871 | 0.98911 | -0.20829 | 42.4062
6 | -0.2681 | -0.068014 | 0.26964 | 0.068998 | 0.00154 | 0.00098425 | 0.40173 | 0.40173 | 0.40173 | 0.99376 | -0.11871 | 1 | 0 | 55.1821
7 | 0.045317 | 0.011532 | -0.045293 | -0.011518 | 2.3424e-05 | 1.4307e-05 | 0.068328 | 0.068328 | 0.068328 | 0.98779 | -0.23334 | 0.98724 | -0.24407 | 9.3857
8 | 0.081558 | 0.020589 | -0.081335 | -0.020446 | 0.0002232 | 0.00014234 | 0.12275 | 0.12275 | 0.12275 | 0.98911 | -0.20829 | 0.98615 | -0.26559 | 33.7221
9 | 0.02101 | 0.0052721 | -0.020992 | -0.0052611 | 1.8271e-05 | 1.1068e-05 | 0.03161 | 0.03161 | 0.03161 | 0.98911 | -0.20829 | 0.98817 | -0.22655 | 8.6842
10 | 0.20835 | 0.053164 | -0.20826 | -0.053111 | 8.3336e-05 | 5.3214e-05 | 0.31036 | 0.31036 | 0.31036 | 1 | 0 | 0.99956 | -0.0082839 | 42.6319
11 | 0.04161 | 0.010595 | -0.041531 | -0.010545 | 7.8997e-05 | 4.9876e-05 | 0.062777 | 0.062777 | 0.062777 | 0.98724 | -0.24407 | 0.98519 | -0.28351 | 17.2465
12 | 0.003683 | 0.00092266 | -0.0036824 | -0.0009229 | 5.1911e-07 | -2.4209e-07 | 0.005551 | 0.0055512 | 0.0055512 | 0.98724 | -0.24407 | 0.98709 | -0.24703 | 1.5251
13 | 0.039689 | 0.010083 | -0.039659 | -0.010065 | 2.9595e-05 | 1.8662e-05 | 0.059994 | 0.059994 | 0.059994 | 0.98519 | -0.28351 | 0.98439 | -0.29902 | 16.482
14 | 0.081335 | 0.020446 | -0.081214 | -0.020369 | 0.00012107 | 7.721e-05 | 0.12275 | 0.12275 | 0.12275 | 0.98615 | -0.26559 | 0.98455 | -0.29682 | 33.7221
15 | 0.005388 | 0.0013503 | -0.0053876 | -0.0013503 | 3.0655e-07 | 3.7112e-08 | 0.0081133 | 0.0081134 | 0.0081134 | 0.98817 | -0.22655 | 0.98811 | -0.22774 | 2.2289
16 | 0.20686 | 0.05276 | -0.20685 | -0.052752 | 1.1864e-05 | 7.5753e-06 | 0.30828 | 0.30828 | 0.30828 | 0.99956 | -0.0082839 | 0.9995 | -0.0094716 | 42.3457
17 | 0.20556 | 0.052428 | -0.20502 | -0.052082 | 0.00054072 | 0.00034526 | 0.30635 | 0.30635 | 0.30635 | 0.9995 | -0.0094716 | 0.99663 | -0.064103 | 42.0808
18 | 0.2035 | 0.051702 | -0.20324 | -0.05154 | 0.00025413 | 0.00016226 | 0.30408 | 0.30408 | 0.30408 | 0.99663 | -0.064103 | 0.99527 | -0.090078 | 41.7695
19 | 0.084727 | 0.021561 | -0.084662 | -0.02152 | 6.5081e-05 | 4.1512e-05 | 0.12679 | 0.12679 | 0.12679 | 0.99527 | -0.090078 | 0.99444 | -0.10603 | 34.8326
20 | 0.11852 | 0.029979 | -0.11814 | -0.029738 | 0.00037619 | 0.00024035 | 0.17729 | 0.17729 | 0.17729 | 0.99527 | -0.090078 | 0.99182 | -0.15647 | 48.7066
21 | 0.081214 | 0.020369 | -0.081174 | -0.020344 | 3.9224e-05 | 2.5015e-05 | 0.12275 | 0.12275 | 0.12275 | 0.98455 | -0.29682 | 0.98403 | -0.30695 | 33.7221
22 | -0.0046101 | -0.0011554 | 0.0046132 | 0.0011552 | 3.0573e-06 | -1.6413e-07 | 0.0069812 | 0.0069804 | 0.0069812 | 0.98263 | -0.33506 | 0.98334 | -0.32114 | 1.9179
23 | -0.0074225 | -0.0018593 | 0.0074241 | 0.0018599 | 1.6357e-06 | 6.0809e-07 | 0.011232 | 0.011231 | 0.011232 | 0.98334 | -0.32114 | 0.98358 | -0.31651 | 3.0856
24 | -0.0092618 | -0.0023205 | 0.0092626 | 0.0023209 | 7.6483e-07 | 3.5763e-07 | 0.014012 | 0.014012 | 0.014012 | 0.98358 | -0.31651 | 0.98367 | -0.31478 | 3.8493
25 | -0.00024805 | -6.2167e-05 | 0.00024805 | 6.1999e-05 | 7.1775e-10 | -1.6826e-07 | 0.00037736 | 0.0003773 | 0.00037736 | 0.9781 | -0.42313 | 0.97811 | -0.42307 | 0.10367
26 | -0.0012542 | -0.00031314 | 0.0012542 | 0.00031294 | 2.3712e-08 | -2.0294e-07 | 0.0019076 | 0.0019075 | 0.0019076 | 0.97811 | -0.42307 | 0.97813 | -0.42267 | 0.52407
27 | 0.0010061 | 0.00025114 | -0.0010061 | -0.00025214 | 7.3561e-08 | -1.0039e-06 | 0.0015303 | 0.0015307 | 0.0015307 | 0.97811 | -0.42307 | 0.97803 | -0.42461 | 0.42052
28 | -0.0015927 | -0.00039777 | 0.0015931 | 0.00039577 | 3.941e-07 | -1.997e-06 | 0.0024224 | 0.0024216 | 0.0024224 | 0.97813 | -0.42267 | 0.97839 | -0.41745 | 0.66551
29 | -0.0018716 | -0.00046907 | 0.0018717 | 0.00046864 | 1.1991e-07 | -4.2897e-07 | 0.0028322 | 0.0028321 | 0.0028322 | 0.98332 | -0.32112 | 0.98338 | -0.31977 | 0.77809
30 | -0.0018717 | -0.00046864 | 0.0018718 | 0.00046844 | 5.61e-08 | -2.0075e-07 | 0.0028321 | 0.002832 | 0.0028321 | 0.98338 | -0.31977 | 0.98342 | -0.31914 | 0.77804
31 | 0.0049995 | 0.0012524 | -0.0049987 | -0.0012524 | 7.7129e-07 | 4.426e-08 | 0.0075921 | 0.0075923 | 0.0075923 | 0.97984 | -0.3889 | 0.97968 | -0.39214 | 2.0858
32 | 0.0073481 | 0.0018359 | -0.0073423 | -0.0018338 | 5.8256e-06 | 2.1579e-06 | 0.011157 | 0.011158 | 0.011158 | 0.97984 | -0.3889 | 0.97899 | -0.40559 | 3.0653
33 | -0.012348 | -0.0030884 | 0.012352 | 0.0030905 | 3.9218e-06 | 2.1351e-06 | 0.018749 | 0.018749 | 0.018749 | 0.97984 | -0.3889 | 0.98018 | -0.38222 | 5.1509
34 | 0.0026698 | 0.00066905 | -0.0026697 | -0.0006691 | 3.3187e-08 | -4.6527e-08 | 0.004055 | 0.0040551 | 0.0040551 | 0.97968 | -0.39214 | 0.97966 | -0.3924 | 1.114
35 | 0.0023289 | 0.00058333 | -0.0023288 | -0.00058365 | 1.5252e-07 | -3.1164e-07 | 0.0035372 | 0.0035374 | 0.0035374 | 0.97968 | -0.39214 | 0.97961 | -0.39351 | 0.97181
36 | 0.0060893 | 0.0015205 | -0.0060881 | -0.0015202 | 1.2413e-06 | 3.0847e-07 | 0.0092534 | 0.0092536 | 0.0092536 | 0.97899 | -0.40559 | 0.97878 | -0.40988 | 2.5422
37 | 0.001253 | 0.00031326 | -0.0012529 | -0.00031354 | 3.2202e-08 | -2.7716e-07 | 0.0019042 | 0.0019043 | 0.0019043 | 0.97899 | -0.40559 | 0.97897 | -0.40613 | 0.52316
38 | -0.018263 | -0.004572 | 0.018272 | 0.0045777 | 9.5615e-06 | 5.7009e-06 | 0.027723 | 0.027723 | 0.027723 | 0.98018 | -0.38222 | 0.98074 | -0.37123 | 7.6162
39 | 0.0022856 | 0.00057257 | -0.0022855 | -0.0005727 | 5.9779e-08 | -1.2743e-07 | 0.003476 | 0.003476 | 0.003476 | 0.97839 | -0.41745 | 0.97836 | -0.418 | 0.95495
40 | -0.0042339 | -0.0010574 | 0.004234 | 0.0010573 | 1.5504e-07 | -2.6055e-08 | 0.0064379 | 0.0064378 | 0.0064379 | 0.97839 | -0.41745 | 0.97843 | -0.41668 | 1.7686
41 | 0.0013204 | 0.00033083 | -0.0013204 | -0.00033092 | 1.2239e-08 | -9.3789e-08 | 0.0020082 | 0.0020082 | 0.0020082 | 0.97836 | -0.418 | 0.97835 | -0.4182 | 0.55171
42 | -0.0045251 | -0.0011303 | 0.0045258 | 0.0011302 | 7.1303e-07 | -4.8207e-08 | 0.0068804 | 0.0068803 | 0.0068804 | 0.97843 | -0.41668 | 0.9786 | -0.41337 | 1.8902
43 | -0.0022518 | -0.00056369 | 0.0022521 | 0.00056315 | 2.3637e-07 | -5.3781e-07 | 0.003407 | 0.0034068 | 0.003407 | 0.98342 | -0.31914 | 0.98353 | -0.31694 | 0.936
44 | -0.00097491 | -0.00024423 | 0.00097493 | 0.00024386 | 2.4882e-08 | -3.6402e-07 | 0.0014818 | 0.0014817 | 0.0014818 | 0.97894 | -0.40666 | 0.97897 | -0.40613 | 0.4071
45 | 0.00073328 | 0.00018367 | -0.00073327 | -0.00018378 | 4.0331e-09 | -1.0626e-07 | 0.0011146 | 0.0011146 | 0.0011146 | 0.97894 | -0.40666 | 0.97893 | -0.40678 | 0.30621
46 | 0.0012963 | 0.00032348 | -0.0012963 | -0.0003237 | 2.7171e-08 | -2.1718e-07 | 0.0019703 | 0.0019703 | 0.0019703 | 0.97878 | -0.40988 | 0.97875 | -0.41032 | 0.5413
47 | 0.0047918 | 0.0011967 | -0.004791 | -0.0011967 | 7.9348e-07 | 6.6015e-09 | 0.0072833 | 0.0072835 | 0.0072835 | 0.97878 | -0.40988 | 0.9786 | -0.41337 | 2.001
48 | 0.0012963 | 0.0003237 | -0.0012963 | -0.00032386 | 2.0642e-08 | -1.6497e-07 | 0.0019703 | 0.0019704 | 0.0019704 | 0.97875 | -0.41032 | 0.97874 | -0.41066 | 0.54132
49 | 0.0010636 | 0.00026555 | -0.0010635 | -0.00026646 | 7.5115e-08 | -9.1483e-07 | 0.0016166 | 0.001617 | 0.001617 | 0.97874 | -0.41066 | 0.97866 | -0.41214 | 0.44423
50 | 0.00069319 | 0.00017365 | -0.00069319 | -0.00017373 | 2.5983e-09 | -7.6712e-08 | 0.0010539 | 0.001054 | 0.001054 | 0.97866 | -0.41214 | 0.97866 | -0.41222 | 0.28955
51 | -0.022997 | -0.0057618 | 0.023005 | 0.0057666 | 7.9035e-06 | 4.8397e-06 | 0.034891 | 0.034891 | 0.034891 | 0.98074 | -0.37123 | 0.98111 | -0.36402 | 9.5854
52 | 0.016811 | 0.0042227 | -0.016807 | -0.00422 | 4.4981e-06 | 2.641e-06 | 0.025369 | 0.025369 | 0.025369 | 0.98622 | -0.26452 | 0.98593 | -0.27013 | 6.9694
53 | -0.017883 | -0.0044911 | 0.017884 | 0.0044918 | 1.073e-06 | 6.366e-07 | 0.026985 | 0.026985 | 0.026985 | 0.98622 | -0.26452 | 0.98628 | -0.26327 | 7.4134
54 | 0.013343 | 0.0033518 | -0.013313 | -0.0033352 | 2.974e-05 | 1.6547e-05 | 0.02014 | 0.020141 | 0.020141 | 0.98593 | -0.27013 | 0.98353 | -0.31694 | 5.5332
55 | -0.018279 | -0.0045909 | 0.018287 | 0.0045957 | 8.0422e-06 | 4.7871e-06 | 0.027582 | 0.027582 | 0.027582 | 0.98628 | -0.26327 | 0.98676 | -0.25405 | 7.5774
56 | -0.018612 | -0.0046771 | 0.018618 | 0.0046805 | 5.7907e-06 | 3.4556e-06 | 0.028071 | 0.028071 | 0.028071 | 0.98676 | -0.25405 | 0.98709 | -0.24753 | 7.7119
57 | -0.019898 | -0.0050006 | 0.019904 | 0.005004 | 5.5839e-06 | 3.3622e-06 | 0.030001 | 0.030001 | 0.030001 | 0.98709 | -0.24753 | 0.98739 | -0.24166 | 8.242
58 | 0.0012802 | 0.00032009 | -0.0012801 | -0.00032048 | 4.5661e-08 | -3.8876e-07 | 0.0019296 | 0.0019297 | 0.0019297 | 0.98709 | -0.24753 | 0.98705 | -0.24828 | 0.53015
59 | -0.020759 | -0.0052184 | 0.020766 | 0.0052225 | 6.8228e-06 | 4.1288e-06 | 0.03129 | 0.03129 | 0.03129 | 0.98739 | -0.24166 | 0.98775 | -0.23478 | 8.5961
60 | 0.00052694 | 0.0001317 | -0.00052693 | -0.00013206 | 6.6881e-09 | -3.5702e-07 | 0.00079425 | 0.00079438 | 0.00079438 | 0.98705 | -0.24828 | 0.98704 | -0.24855 | 0.21824
61 | -0.021022 | -0.0052868 | 0.021028 | 0.00529 | 5.3213e-06 | 3.2245e-06 | 0.031676 | 0.031676 | 0.031676 | 0.98775 | -0.23478 | 0.98802 | -0.22948 | 8.7023
62 | -0.021782 | -0.0054792 | 0.021784 | 0.0054799 | 1.1147e-06 | 6.7805e-07 | 0.032813 | 0.032813 | 0.032813 | 0.98802 | -0.22948 | 0.98808 | -0.22841 | 9.0145
63 | -0.0061733 | -0.0015446 | 0.006175 | 0.0015451 | 1.6891e-06 | 4.5842e-07 | 0.0094604 | 0.0094601 | 0.0094604 | 0.97091 | -0.56286 | 0.9712 | -0.55711 | 2.599
64 | 0.0029093 | 0.0007266 | -0.0029079 | -0.00072799 | 1.3641e-06 | -1.3892e-06 | 0.0044579 | 0.0044587 | 0.0044587 | 0.97091 | -0.56286 | 0.97041 | -0.57272 | 1.2249
65 | -0.006175 | -0.0015451 | 0.0061751 | 0.0015451 | 9.8294e-08 | 2.6664e-08 | 0.0094601 | 0.0094601 | 0.0094601 | 0.9712 | -0.55711 | 0.97121 | -0.55677 | 2.5989
66 | 0.0029079 | 0.00072799 | -0.0029075 | -0.00072844 | 4.4417e-07 | -4.5165e-07 | 0.0044587 | 0.0044589 | 0.0044589 | 0.97041 | -0.57272 | 0.97025 | -0.57593 | 1.225
67 | -0.009224 | -0.0023093 | 0.0092304 | 0.0023123 | 6.3378e-06 | 3.0081e-06 | 0.014131 | 0.014131 | 0.014131 | 0.97121 | -0.55677 | 0.97194 | -0.54235 | 3.8823
68 | 0.0022495 | 0.00056354 | -0.0022494 | -0.00056375 | 1.0054e-07 | -2.1385e-07 | 0.0034498 | 0.0034499 | 0.0034499 | 0.97025 | -0.57593 | 0.9702 | -0.57687 | 0.94779
69 | -0.010445 | -0.0026167 | 0.010445 | 0.0026169 | 4.2944e-07 | 2.1933e-07 | 0.01599 | 0.01599 | 0.01599 | 0.97194 | -0.54235 | 0.97199 | -0.54148 | 4.393
70 | 0.035324 | 0.0089783 | -0.035321 | -0.0089762 | 3.316e-06 | 2.0829e-06 | 0.053442 | 0.053442 | 0.053442 | 0.98439 | -0.29902 | 0.98429 | -0.30097 | 14.6818
71 | -0.011287 | -0.0028279 | 0.011289 | 0.0028287 | 1.4554e-06 | 7.7032e-07 | 0.01728 | 0.01728 | 0.01728 | 0.97199 | -0.54148 | 0.97212 | -0.53878 | 4.7471
72 | -0.012432 | -0.0031152 | 0.012432 | 0.0031154 | 3.6655e-07 | 2.0112e-07 | 0.019029 | 0.019029 | 0.019029 | 0.97212 | -0.53878 | 0.97215 | -0.53816 | 5.2278
73 | 0.0026754 | 0.00067047 | -0.0026753 | -0.0006705 | 2.6889e-08 | -3.5808e-08 | 0.004095 | 0.004095 | 0.004095 | 0.97215 | -0.53816 | 0.97214 | -0.53837 | 1.125
74 | -0.015108 | -0.0037859 | 0.015114 | 0.0037898 | 6.7336e-06 | 3.8929e-06 | 0.023124 | 0.023124 | 0.023124 | 0.97215 | -0.53816 | 0.97263 | -0.5288 | 6.3528
75 | -0.0017484 | -0.00043819 | 0.0017485 | 0.00043755 | 1.5905e-07 | -6.4202e-07 | 0.0026677 | 0.0026674 | 0.0026677 | 0.97525 | -0.47713 | 0.97534 | -0.47522 | 0.73287
76 | 0.02969 | 0.0074643 | -0.029662 | -0.0074468 | 2.8015e-05 | 1.7476e-05 | 0.045305 | 0.045305 | 0.045305 | 0.97534 | -0.47522 | 0.97434 | -0.495 | 12.4464
77 | -0.031439 | -0.0079018 | 0.031546 | 0.0079688 | 0.00010704 | 6.695e-05 | 0.047972 | 0.047971 | 0.047972 | 0.97534 | -0.47522 | 0.97897 | -0.40417 | 13.1791
78 | 0.028525 | 0.0071618 | -0.028516 | -0.0071565 | 8.4537e-06 | 5.2625e-06 | 0.043568 | 0.043568 | 0.043568 | 0.97434 | -0.495 | 0.97402 | -0.50122 | 11.9692
79 | 0.0014552 | 0.0003643 | -0.0014551 | -0.00036468 | 6.0782e-08 | -3.7769e-07 | 0.0022117 | 0.0022118 | 0.0022118 | 0.97897 | -0.40417 | 0.97893 | -0.40505 | 0.60764
80 | -0.033001 | -0.0083331 | 0.033165 | 0.0084359 | 0.00016406 | 0.0001028 | 0.050183 | 0.050182 | 0.050183 | 0.97897 | -0.40417 | 0.98429 | -0.30097 | 13.7866
81 | 0.0041964 | 0.0010514 | -0.0041962 | -0.0010514 | 2.0734e-07 | -3.4746e-08 | 0.0064107 | 0.0064107 | 0.0064107 | 0.97402 | -0.50122 | 0.97397 | -0.50225 | 1.7612
82 | 0.02432 | 0.0061051 | -0.024314 | -0.0061013 | 6.2958e-06 | 3.878e-06 | 0.037157 | 0.037157 | 0.037157 | 0.97402 | -0.50122 | 0.97375 | -0.50665 | 10.2081
83 | 0.0019521 | 0.000489 | -0.0019521 | -0.00048923 | 7.6321e-08 | -2.3591e-07 | 0.0029823 | 0.0029824 | 0.0029824 | 0.97397 | -0.50225 | 0.97393 | -0.50307 | 0.81935
84 | 0.021701 | 0.0054465 | -0.021694 | -0.0054418 | 7.7482e-06 | 4.7253e-06 | 0.033165 | 0.033165 | 0.033165 | 0.97375 | -0.50665 | 0.97337 | -0.51413 | 9.1114
85 | 0.016599 | 0.0041659 | -0.016588 | -0.004159 | 1.1604e-05 | 6.8299e-06 | 0.025378 | 0.025378 | 0.025378 | 0.97337 | -0.51413 | 0.97263 | -0.5288 | 6.9721
86 | 0.0050942 | 0.0012759 | -0.0050932 | -0.0012759 | 9.4015e-07 | 8.7939e-08 | 0.0077873 | 0.0077875 | 0.0077875 | 0.97337 | -0.51413 | 0.97317 | -0.51801 | 2.1394
87 | 0.0050932 | 0.0012759 | -0.0050928 | -0.0012758 | 4.3769e-07 | 4.1019e-08 | 0.0077875 | 0.0077876 | 0.0077876 | 0.97317 | -0.51801 | 0.97308 | -0.51982 | 2.1394
88 | 0.0028725 | 0.00071937 | -0.0028722 | -0.00071968 | 2.8813e-07 | -3.1024e-07 | 0.0043924 | 0.0043926 | 0.0043926 | 0.97308 | -0.51982 | 0.97298 | -0.52192 | 1.2068
89 | 0.0028722 | 0.00071968 | -0.0028721 | -0.00071982 | 1.3076e-07 | -1.4075e-07 | 0.0043926 | 0.0043927 | 0.0043927 | 0.97298 | -0.52192 | 0.97293 | -0.52288 | 1.2068
90 | 0.010571 | 0.0026511 | -0.01057 | -0.0026504 | 1.4967e-06 | 7.5983e-07 | 0.015992 | 0.015992 | 0.015992 | 0.98367 | -0.31478 | 0.98351 | -0.31775 | 4.3935
91 | -0.019834 | -0.004972 | 0.019847 | 0.0049797 | 1.2835e-05 | 7.7313e-06 | 0.030004 | 0.030004 | 0.030004 | 0.98367 | -0.31478 | 0.98436 | -0.30121 | 8.2428
92 | 0.01057 | 0.0026504 | -0.010564 | -0.0026474 | 5.7873e-06 | 2.9386e-06 | 0.015992 | 0.015993 | 0.015993 | 0.98351 | -0.31775 | 0.98293 | -0.32924 | 4.3936
93 | -0.021306 | -0.0053454 | 0.021308 | 0.0053468 | 2.3054e-06 | 1.4001e-06 | 0.032209 | 0.032209 | 0.032209 | 0.98436 | -0.30121 | 0.98448 | -0.29894 | 8.8487
94 | 0.0078299 | 0.0019622 | -0.0078289 | -0.0019618 | 1.0478e-06 | 4.1855e-07 | 0.011853 | 0.011853 | 0.011853 | 0.98293 | -0.32924 | 0.98278 | -0.33205 | 3.2564
95 | -0.023098 | -0.0057953 | 0.023123 | 0.0058105 | 2.4947e-05 | 1.5271e-05 | 0.034914 | 0.034914 | 0.034914 | 0.98448 | -0.29894 | 0.98564 | -0.27631 | 9.5917
96 | -0.023123 | -0.0058105 | 0.023125 | 0.005812 | 2.4222e-06 | 1.4827e-06 | 0.034914 | 0.034914 | 0.034914 | 0.98564 | -0.27631 | 0.98575 | -0.27411 | 9.5917
97 | -0.023125 | -0.005812 | 0.023155 | 0.0058306 | 3.0382e-05 | 1.8596e-05 | 0.034914 | 0.034913 | 0.034914 | 0.98575 | -0.27411 | 0.98716 | -0.24663 | 9.5917
98 | 0.0051376 | 0.0012872 | -0.005137 | -0.0012872 | 5.4193e-07 | 4.4229e-08 | 0.0077786 | 0.0077787 | 0.0077787 | 0.98278 | -0.33205 | 0.98267 | -0.33427 | 2.137
99 | -0.10946 | -0.027523 | 0.10956 | 0.027588 | 0.00010188 | 6.5074e-05 | 0.16442 | 0.16442 | 0.16442 | 0.99081 | -0.17593 | 0.99182 | -0.15647 | 45.1709
100 | 0.0618 | 0.015578 | -0.061684 | -0.015505 | 0.00011559 | 7.3516e-05 | 0.092843 | 0.092843 | 0.092843 | 0.99081 | -0.17593 | 0.98879 | -0.2151 | 25.5064
101 | 0.031762 | 0.0080054 | -0.031714 | -0.0079755 | 4.784e-05 | 2.9903e-05 | 0.047814 | 0.047814 | 0.047814 | 0.98879 | -0.2151 | 0.98716 | -0.24663 | 13.1357
102 | 0.083233 | 0.021161 | -0.083147 | -0.021107 | 8.5871e-05 | 5.4767e-05 | 0.12465 | 0.12465 | 0.12465 | 0.99444 | -0.10603 | 0.99331 | -0.12747 | 34.2451
103 | 0.083147 | 0.021107 | -0.08304 | -0.021039 | 0.0001067 | 6.8049e-05 | 0.12465 | 0.12465 | 0.12465 | 0.99331 | -0.12747 | 0.99192 | -0.15418 | 34.2451
104 | -0.022181 | -0.0055795 | 0.022188 | 0.0055835 | 6.5065e-06 | 3.965e-06 | 0.033412 | 0.033411 | 0.033412 | 0.98808 | -0.22841 | 0.98839 | -0.22227 | 9.179
105 | -0.078556 | -0.019814 | 0.078572 | 0.019825 | 1.6156e-05 | 1.03e-05 | 0.11831 | 0.11831 | 0.11831 | 0.98839 | -0.22227 | 0.98861 | -0.21797 | 32.503
106 | 0.056369 | 0.014231 | -0.056295 | -0.014184 | 7.3797e-05 | 4.6881e-05 | 0.084899 | 0.0849 | 0.0849 | 0.98839 | -0.22227 | 0.98698 | -0.24964 | 23.324
107 | -0.079033 | -0.01994 | 0.079155 | 0.020018 | 0.00012215 | 7.7879e-05 | 0.119 | 0.119 | 0.119 | 0.98861 | -0.21797 | 0.99028 | -0.18575 | 32.6935
108 | 0.053063 | 0.013374 | -0.053031 | -0.013354 | 3.1824e-05 | 2.0198e-05 | 0.080027 | 0.080027 | 0.080027 | 0.98698 | -0.24964 | 0.98633 | -0.26218 | 21.9854
109 | -0.079562 | -0.02012 | 0.079683 | 0.020197 | 0.0001207 | 7.6957e-05 | 0.11962 | 0.11962 | 0.11962 | 0.99028 | -0.18575 | 0.99192 | -0.15418 | 32.8614
110 | 0.049588 | 0.012491 | -0.049576 | -0.012483 | 1.1881e-05 | 7.5315e-06 | 0.074833 | 0.074833 | 0.074833 | 0.98633 | -0.26218 | 0.98607 | -0.26719 | 20.5585
111 | 0.046296 | 0.011661 | -0.046241 | -0.011626 | 5.5254e-05 | 3.4978e-05 | 0.069883 | 0.069883 | 0.069883 | 0.98607 | -0.26719 | 0.98479 | -0.29218 | 19.1987
112 | -0.0023062 | -0.00057798 | 0.0023062 | 0.00057785 | 6.1555e-08 | -1.3152e-07 | 0.0034902 | 0.0034901 | 0.0034902 | 0.98323 | -0.32253 | 0.98326 | -0.32197 | 0.95883
113 | 0.027097 | 0.0068114 | -0.02707 | -0.0067943 | 2.7694e-05 | 1.7168e-05 | 0.041015 | 0.041015 | 0.041015 | 0.98326 | -0.32197 | 0.98216 | -0.3434 | 11.2679
114 | -0.029404 | -0.0073893 | 0.029418 | 0.0073985 | 1.4836e-05 | 9.2414e-06 | 0.044505 | 0.044505 | 0.044505 | 0.98326 | -0.32197 | 0.9838 | -0.31141 | 12.2267
115 | 0.024764 | 0.0062164 | -0.024751 | -0.0062081 | 1.3531e-05 | 8.3357e-06 | 0.037522 | 0.037522 | 0.037522 | 0.98216 | -0.3434 | 0.98158 | -0.35486 | 10.3083
116 | -0.031725 | -0.0079767 | 0.031737 | 0.0079842 | 1.193e-05 | 7.4598e-06 | 0.047994 | 0.047994 | 0.047994 | 0.9838 | -0.31141 | 0.98421 | -0.30354 | 13.1852
117 | 0.033848 | 0.0085163 | -0.033839 | -0.008511 | 8.6058e-06 | 5.3963e-06 | 0.051172 | 0.051172 | 0.051172 | 0.98448 | -0.29822 | 0.98421 | -0.30354 | 14.0583
118 | -0.036155 | -0.0090945 | 0.036165 | 0.0091011 | 1.0429e-05 | 6.5563e-06 | 0.054659 | 0.054659 | 0.054659 | 0.98448 | -0.29822 | 0.98479 | -0.29218 | 15.0162
119 | 0.010076 | 0.0025253 | -0.010074 | -0.0025247 | 1.2302e-06 | 6.0728e-07 | 0.015224 | 0.015224 | 0.015224 | 0.98479 | -0.29218 | 0.98466 | -0.29474 | 4.1825
120 | 0.0059078 | 0.0014805 | -0.0059078 | -0.0014805 | 4.5993e-08 | 9.8632e-09 | 0.0089279 | 0.0089279 | 0.0089279 | 0.98466 | -0.29474 | 0.98465 | -0.29491 | 2.4527
121 | 0.0036014 | 0.00090247 | -0.0036012 | -0.00090255 | 1.6653e-07 | -8.4107e-08 | 0.0054424 | 0.0054425 | 0.0054425 | 0.98465 | -0.29491 | 0.9846 | -0.29588 | 1.4952
122 | 0.024751 | 0.0062081 | -0.02474 | -0.0062014 | 1.0795e-05 | 6.6504e-06 | 0.037522 | 0.037522 | 0.037522 | 0.98158 | -0.35486 | 0.98111 | -0.36402 | 10.3083
123 | 0.0039539 | 0.00099067 | -0.0039538 | -0.00099068 | 2.114e-08 | -6.3939e-09 | 0.0059871 | 0.0059871 | 0.0059871 | 0.98267 | -0.33427 | 0.98266 | -0.33438 | 1.6448
124 | 0.0023452 | 0.00058753 | -0.0023451 | -0.00058773 | 1.0171e-07 | -2.0734e-07 | 0.0035512 | 0.0035513 | 0.0035513 | 0.98266 | -0.33438 | 0.98262 | -0.33529 | 0.97564
125 | 0.0011787 | 0.00029539 | -0.0011787 | -0.00029541 | 1.3594e-09 | -1.3543e-08 | 0.0017849 | 0.0017849 | 0.0017849 | 0.98262 | -0.33529 | 0.98262 | -0.33531 | 0.49037

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48733 | 0.12409

## res_load
| p_mw | q_mvar
0 | 0.0068095 | 0.0017066
1 | 0.092365 | 0.023149
2 | 0.015711 | 0.0039374
3 | 0.0040437 | 0.0010135
4 | 0.0077015 | 0.0019302
5 | 0.0018425 | 0.00046178
6 | 0.0036824 | 0.0009229
7 | 0.015604 | 0.0039107
8 | 0.0013998 | 0.00035081
9 | 0.0012955 | 0.00032469
10 | 0.0015177 | 0.00038037
11 | 0.0053876 | 0.0013503
12 | 0.0046101 | 0.0011554
13 | 0.0028093 | 0.00070408
14 | 0.0018377 | 0.00046058
15 | 0.00024805 | 6.2167e-05
16 | 0.00033848 | 8.483e-05
17 | 0.0010061 | 0.00025214
18 | 0.0018716 | 0.00046907
19 | 0.0059112 | 0.0014815
20 | 0.00035522 | 8.9027e-05
21 | 0.0009651 | 0.00024188
22 | 0.00029104 | 7.2942e-05
23 | 0.0026697 | 0.0006691
24 | 0.0023288 | 0.00058365
25 | 0.00038006 | 9.5253e-05
26 | 0.00024163 | 6.0558e-05
27 | 0.00027801 | 6.9677e-05
28 | 0.00073327 | 0.00018378
29 | 0.0002652 | 6.6464e-05
30 | 0.00023269 | 5.8318e-05
31 | 0.0013204 | 0.00033092
32 | 0.00037031 | 9.2808e-05
33 | 0.00069319 | 0.00017373
34 | 0.0047245 | 0.0011841
35 | 0.001071 | 0.00026843
36 | 0.0034644 | 0.00086826
37 | 0.00039577 | 9.919e-05
38 | 0.011061 | 0.0027721
39 | 0.00032465 | 8.1365e-05
40 | 0.00085534 | 0.00021437
41 | 0.00075321 | 0.00018877
42 | 0.00052693 | 0.00013206
43 | 0.00025667 | 6.4327e-05
44 | 0.00075468 | 0.00018914
45 | 0.003264 | 0.00081805
46 | 0.0030489 | 0.00076413
47 | 0.00065797 | 0.0001649
48 | 0.0022494 | 0.00056375
49 | 0.0012146 | 0.0003044
50 | 0.0043349 | 0.0010864
51 | 0.00084205 | 0.00021104
52 | 0.0011432 | 0.0002865
53 | 0.0017484 | 0.00043819
54 | 0.0011372 | 0.00028502
55 | 0.0014551 | 0.00036468
56 | 0.0021561 | 0.00054038
57 | 0.002244 | 0.00056241
58 | 0.0026124 | 0.00065472
59 | 0.0014734 | 0.00036927
60 | 0.0022203 | 0.00055645
61 | 0.0019521 | 0.00048923
62 | 0.0026753 | 0.0006705
63 | 0.0028721 | 0.00071982
64 | 0.0014591 | 0.00036567
65 | 0.0027342 | 0.00068526
66 | 0.0017895 | 0.00044848
67 | 0.0026913 | 0.0006745
68 | 0.047662 | 0.011945
69 | 0.0085782 | 0.0021499
70 | 0.029922 | 0.0074993
71 | 0.0085583 | 0.0021449
72 | 0.0014292 | 0.00035819
73 | 0.00039761 | 9.9649e-05
74 | 0.00046083 | 0.00011549
75 | 0.003232 | 0.00081001
76 | 0.00040677 | 0.00010195
77 | 0.003443 | 0.00086288
78 | 0.0033575 | 0.00084147
79 | 0.0032801 | 0.00082208
80 | 0.0023062 | 0.00057798
81 | 0.0023056 | 0.00057783
82 | 0.0023069 | 0.00057818
83 | 0.002307 | 0.00057818
84 | 0.0021019 | 0.0005268
85 | 0.0041665 | 0.0010442
86 | 0.0023064 | 0.00057804
87 | 0.0036012 | 0.00090255
88 | 0.0017351 | 0.00043485
89 | 0.081174 | 0.020344
90 | 0.0011832 | 0.00029653
91 | 0.0016086 | 0.00040315
92 | 0.0011664 | 0.00029234
93 | 0.0011787 | 0.00029541

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1