## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1349-6_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1349-6_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1349-6_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1349-6_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1349-6_0_3_node_93 | 0.4 | n |  | TRUE
5 | bus_LV_1349-6_0_3_node_125 | 0.4 | n |  | TRUE
6 | bus_LV_1349-6_0_3_node_68 | 0.4 | n |  | TRUE
7 | bus_LV_1349-6_0_3_node_94 | 0.4 | n |  | TRUE
8 | bus_LV_1349-6_0_3_node_126 | 0.4 | n |  | TRUE
9 | bus_LV_1349-6_0_3_node_69 | 0.4 | n |  | TRUE
10 | bus_LV_1349-6_0_3_node_66 | 0.4 | n |  | TRUE
11 | bus_LV_1349-6_0_3_node_4 | 0.4 | n |  | TRUE
12 | bus_LV_1349-6_0_3_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_1349-6_0_3_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_1349-6_0_3_node_98 | 0.4 | n |  | TRUE
15 | bus_LV_1349-6_0_3_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_1349-6_0_3_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1349-6_0_3_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_1349-6_0_3_node_37 | 0.4 | n |  | TRUE
19 | bus_LV_1349-6_0_3_node_63 | 0.4 | n |  | TRUE
20 | bus_LV_1349-6_0_3_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_1349-6_0_3_node_64 | 0.4 | n |  | TRUE
22 | bus_LV_1349-6_0_3_node_62 | 0.4 | n |  | TRUE
23 | bus_LV_1349-6_0_3_node_9 | 0.4 | n |  | TRUE
24 | bus_LV_1349-6_0_3_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_1349-6_0_3_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_1349-6_0_3_node_87 | 0.4 | n |  | TRUE
27 | bus_LV_1349-6_0_3_node_70 | 0.4 | n |  | TRUE
28 | bus_LV_1349-6_0_3_node_122 | 0.4 | n |  | TRUE
29 | bus_LV_1349-6_0_3_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_1349-6_0_3_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_1349-6_0_3_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_1349-6_0_3_node_39 | 0.4 | n |  | TRUE
33 | bus_LV_1349-6_0_3_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_1349-6_0_3_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_1349-6_0_3_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_1349-6_0_3_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_1349-6_0_3_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_1349-6_0_3_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_1349-6_0_3_node_42 | 0.4 | n |  | TRUE
40 | bus_LV_1349-6_0_3_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_1349-6_0_3_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_1349-6_0_3_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_1349-6_0_3_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_1349-6_0_3_node_116 | 0.4 | n |  | TRUE
45 | bus_LV_1349-6_0_3_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_1349-6_0_3_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_1349-6_0_3_node_117 | 0.4 | n |  | TRUE
48 | bus_LV_1349-6_0_3_node_24 | 0.4 | n |  | TRUE
49 | bus_LV_1349-6_0_3_node_25 | 0.4 | n |  | TRUE
50 | bus_LV_1349-6_0_3_node_26 | 0.4 | n |  | TRUE
51 | bus_LV_1349-6_0_3_node_27 | 0.4 | n |  | TRUE
52 | bus_LV_1349-6_0_3_node_28 | 0.4 | n |  | TRUE
53 | bus_LV_1349-6_0_3_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_1349-6_0_3_node_45 | 0.4 | n |  | TRUE
55 | bus_LV_1349-6_0_3_node_29 | 0.4 | n |  | TRUE
56 | bus_LV_1349-6_0_3_node_30 | 0.4 | n |  | TRUE
57 | bus_LV_1349-6_0_3_node_31 | 0.4 | n |  | TRUE
58 | bus_LV_1349-6_0_3_node_32 | 0.4 | n |  | TRUE
59 | bus_LV_1349-6_0_3_node_33 | 0.4 | n |  | TRUE
60 | bus_LV_1349-6_0_3_node_35 | 0.4 | n |  | TRUE
61 | bus_LV_1349-6_0_3_node_51 | 0.4 | n |  | TRUE
62 | bus_LV_1349-6_0_3_node_52 | 0.4 | n |  | TRUE
63 | bus_LV_1349-6_0_3_node_44 | 0.4 | n |  | TRUE
64 | bus_LV_1349-6_0_3_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_1349-6_0_3_node_50 | 0.4 | n |  | TRUE
66 | bus_LV_1349-6_0_3_node_47 | 0.4 | n |  | TRUE
67 | bus_LV_1349-6_0_3_node_48 | 0.4 | n |  | TRUE
68 | bus_LV_1349-6_0_3_node_55 | 0.4 | n |  | TRUE
69 | bus_LV_1349-6_0_3_node_118 | 0.4 | n |  | TRUE
70 | bus_LV_1349-6_0_3_node_56 | 0.4 | n |  | TRUE
71 | bus_LV_1349-6_0_3_node_57 | 0.4 | n |  | TRUE
72 | bus_LV_1349-6_0_3_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_1349-6_0_3_node_54 | 0.4 | n |  | TRUE
74 | bus_LV_1349-6_0_3_node_58 | 0.4 | n |  | TRUE
75 | bus_LV_1349-6_0_3_node_59 | 0.4 | n |  | TRUE
76 | bus_LV_1349-6_0_3_node_73 | 0.4 | n |  | TRUE
77 | bus_LV_1349-6_0_3_node_72 | 0.4 | n |  | TRUE
78 | bus_LV_1349-6_0_3_node_71 | 0.4 | n |  | TRUE
79 | bus_LV_1349-6_0_3_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_1349-6_0_3_node_61 | 0.4 | n |  | TRUE
81 | bus_LV_1349-6_0_3_node_107 | 0.4 | n |  | TRUE
82 | bus_LV_1349-6_0_3_node_123 | 0.4 | n |  | TRUE
83 | bus_LV_1349-6_0_3_node_106 | 0.4 | n |  | TRUE
84 | bus_LV_1349-6_0_3_node_124 | 0.4 | n |  | TRUE
85 | bus_LV_1349-6_0_3_node_105 | 0.4 | n |  | TRUE
86 | bus_LV_1349-6_0_3_node_109 | 0.4 | n |  | TRUE
87 | bus_LV_1349-6_0_3_node_81 | 0.4 | n |  | TRUE
88 | bus_LV_1349-6_0_3_node_82 | 0.4 | n |  | TRUE
89 | bus_LV_1349-6_0_3_node_83 | 0.4 | n |  | TRUE
90 | bus_LV_1349-6_0_3_node_65 | 0.4 | n |  | TRUE
91 | bus_LV_1349-6_0_3_node_67 | 0.4 | n |  | TRUE
92 | bus_LV_1349-6_0_3_node_119 | 0.4 | n |  | TRUE
93 | bus_LV_1349-6_0_3_node_90 | 0.4 | n |  | TRUE
94 | bus_LV_1349-6_0_3_node_120 | 0.4 | n |  | TRUE
95 | bus_LV_1349-6_0_3_node_89 | 0.4 | n |  | TRUE
96 | bus_LV_1349-6_0_3_node_74 | 0.4 | n |  | TRUE
97 | bus_LV_1349-6_0_3_node_75 | 0.4 | n |  | TRUE
98 | bus_LV_1349-6_0_3_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_1349-6_0_3_node_77 | 0.4 | n |  | TRUE
100 | bus_LV_1349-6_0_3_node_76 | 0.4 | n |  | TRUE
101 | bus_LV_1349-6_0_3_node_78 | 0.4 | n |  | TRUE
102 | bus_LV_1349-6_0_3_node_80 | 0.4 | n |  | TRUE
103 | bus_LV_1349-6_0_3_node_108 | 0.4 | n |  | TRUE
104 | bus_LV_1349-6_0_3_node_86 | 0.4 | n |  | TRUE
105 | bus_LV_1349-6_0_3_node_84 | 0.4 | n |  | TRUE
106 | bus_LV_1349-6_0_3_node_92 | 0.4 | n |  | TRUE
107 | bus_LV_1349-6_0_3_node_91 | 0.4 | n |  | TRUE
108 | bus_LV_1349-6_0_3_node_85 | 0.4 | n |  | TRUE
109 | bus_LV_1349-6_0_3_node_88 | 0.4 | n |  | TRUE
110 | bus_LV_1349-6_0_3_node_121 | 0.4 | n |  | TRUE
111 | bus_LV_1349-6_0_3_node_95 | 0.4 | n |  | TRUE
112 | bus_LV_1349-6_0_3_node_96 | 0.4 | n |  | TRUE
113 | bus_LV_1349-6_0_3_node_97 | 0.4 | n |  | TRUE
114 | bus_LV_1349-6_0_3_node_100 | 0.4 | n |  | TRUE
115 | bus_LV_1349-6_0_3_node_99 | 0.4 | n |  | TRUE
116 | bus_LV_1349-6_0_3_node_102 | 0.4 | n |  | TRUE
117 | bus_LV_1349-6_0_3_node_101 | 0.4 | n |  | TRUE
118 | bus_LV_1349-6_0_3_node_103 | 0.4 | n |  | TRUE
119 | bus_LV_1349-6_0_3_node_112 | 0.4 | n |  | TRUE
120 | bus_LV_1349-6_0_3_node_110 | 0.4 | n |  | TRUE
121 | bus_LV_1349-6_0_3_node_111 | 0.4 | n |  | TRUE
122 | bus_LV_1349-6_0_3_node_113 | 0.4 | n |  | TRUE
123 | bus_LV_1349-6_0_3_node_114 | 0.4 | n |  | TRUE
124 | bus_LV_1349-6_0_3_node_115 | 0.4 | n |  | TRUE
125 | bus_LV_1349-6_0_3_node_128 | 0.4 | n |  | TRUE
126 | bus_LV_1349-6_0_3_node_127 | 0.4 | n |  | TRUE
127 | bus_MV_19_0_node_100 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1349-6_0_3_load_0 | 0 | 0.0026583 | 0.00066622 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1349-6_0_3_load_93 | 4 | 0.00069512 | 0.00017421 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1349-6_0_3_load_125 | 5 | 0.002369 | 0.00059373 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1349-6_0_3_load_126 | 8 | 0.0025292 | 0.00063387 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1349-6_0_3_load_66 | 10 | 0.00042676 | 0.00010696 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1349-6_0_3_load_4 | 11 | 0.00036332 | 9.1058e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1349-6_0_3_load_5 | 12 | 0.00037975 | 9.5173e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1349-6_0_3_load_8 | 17 | 0.0068226 | 0.0017099 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1349-6_0_3_load_37 | 18 | 0.0018256 | 0.00045755 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1349-6_0_3_load_64 | 21 | 0.0053025 | 0.0013289 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1349-6_0_3_load_62 | 22 | 0.0082379 | 0.0020646 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1349-6_0_3_load_9 | 23 | 0.0017077 | 0.000428 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1349-6_0_3_load_11 | 25 | 0.0031391 | 0.00078674 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1349-6_0_3_load_122 | 28 | 0.0065694 | 0.0016464 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1349-6_0_3_load_13 | 29 | 0.001197 | 0.0003 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1349-6_0_3_load_14 | 30 | 0.0028201 | 0.00070679 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1349-6_0_3_load_16 | 31 | 0.0014812 | 0.00037123 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1349-6_0_3_load_20 | 33 | 0.0015718 | 0.00039394 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1349-6_0_3_load_38 | 34 | 0.0022112 | 0.00055417 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1349-6_0_3_load_18 | 36 | 0.0017674 | 0.00044296 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1349-6_0_3_load_19 | 37 | 0.00098863 | 0.00024777 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1349-6_0_3_load_42 | 39 | 0.0013679 | 0.00034283 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1349-6_0_3_load_22 | 40 | 0.0011769 | 0.00029495 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1349-6_0_3_load_23 | 41 | 0.00099893 | 0.00025036 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1349-6_0_3_load_43 | 42 | 0.0012942 | 0.00032435 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1349-6_0_3_load_116 | 44 | 0.00093707 | 0.00023485 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1349-6_0_3_load_41 | 45 | 0.0017601 | 0.00044113 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1349-6_0_3_load_36 | 46 | 0.0028247 | 0.00070793 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1349-6_0_3_load_117 | 47 | 0.0014542 | 0.00036446 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1349-6_0_3_load_24 | 48 | 0.0056092 | 0.0014058 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1349-6_0_3_load_25 | 49 | 0.0011696 | 0.00029312 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1349-6_0_3_load_26 | 50 | 0.0014933 | 0.00037425 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1349-6_0_3_load_27 | 51 | 0.00098797 | 0.00024761 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1349-6_0_3_load_28 | 52 | 0.00094923 | 0.0002379 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1349-6_0_3_load_46 | 53 | 0.0048935 | 0.0012264 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1349-6_0_3_load_45 | 54 | 0.0011704 | 0.00029332 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1349-6_0_3_load_29 | 55 | 0.0043057 | 0.0010791 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1349-6_0_3_load_30 | 56 | 0.0015097 | 0.00037838 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1349-6_0_3_load_31 | 57 | 0.0014214 | 0.00035624 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1349-6_0_3_load_32 | 58 | 0.0014028 | 0.00035159 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1349-6_0_3_load_33 | 59 | 0.0043692 | 0.001095 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1349-6_0_3_load_35 | 60 | 0.0012333 | 0.00030909 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1349-6_0_3_load_51 | 61 | 0.0061489 | 0.0015411 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1349-6_0_3_load_52 | 62 | 0.0033901 | 0.00084965 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1349-6_0_3_load_44 | 63 | 0.00036302 | 9.098e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1349-6_0_3_load_49 | 64 | 0.00066664 | 0.00016708 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1349-6_0_3_load_50 | 65 | 0.00037973 | 9.517e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1349-6_0_3_load_47 | 66 | 0.0024946 | 0.0006252 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1349-6_0_3_load_48 | 67 | 0.0029258 | 0.00073328 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1349-6_0_3_load_55 | 68 | 0.0020971 | 0.00052557 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1349-6_0_3_load_118 | 69 | 0.0094 | 0.0023559 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1349-6_0_3_load_56 | 70 | 0.00071929 | 0.00018027 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1349-6_0_3_load_57 | 71 | 0.00085143 | 0.00021339 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1349-6_0_3_load_53 | 72 | 0.0063676 | 0.0015959 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1349-6_0_3_load_54 | 73 | 0.0036339 | 0.00091075 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1349-6_0_3_load_59 | 75 | 0.00075076 | 0.00018816 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1349-6_0_3_load_73 | 76 | 0.0010852 | 0.00027198 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1349-6_0_3_load_72 | 77 | 0.00042037 | 0.00010535 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1349-6_0_3_load_71 | 78 | 0.0010831 | 0.00027145 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1349-6_0_3_load_60 | 79 | 0.00050254 | 0.00012595 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1349-6_0_3_load_107 | 81 | 0.00094963 | 0.000238 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1349-6_0_3_load_123 | 82 | 0.0021096 | 0.00052872 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1349-6_0_3_load_106 | 83 | 0.00049585 | 0.00012427 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1349-6_0_3_load_124 | 84 | 0.00044866 | 0.00011244 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1349-6_0_3_load_105 | 85 | 0.0023776 | 0.00059587 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1349-6_0_3_load_109 | 86 | 0.0063076 | 0.0015808 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1349-6_0_3_load_83 | 89 | 0.0066189 | 0.0016589 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1349-6_0_3_load_65 | 90 | 0.001899 | 0.00047594 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1349-6_0_3_load_119 | 92 | 0.0059955 | 0.0015026 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1349-6_0_3_load_90 | 93 | 0.002929 | 0.00073408 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1349-6_0_3_load_89 | 95 | 0.0024469 | 0.00061326 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1349-6_0_3_load_74 | 96 | 0.0014465 | 0.00036253 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1349-6_0_3_load_75 | 97 | 0.00097868 | 0.00024528 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1349-6_0_3_load_79 | 98 | 0.0005735 | 0.00014373 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1349-6_0_3_load_77 | 99 | 0.0018072 | 0.00045293 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1349-6_0_3_load_76 | 100 | 0.0012701 | 0.00031831 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1349-6_0_3_load_80 | 102 | 0.00034871 | 8.7395e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1349-6_0_3_load_108 | 103 | 0.001004 | 0.00025162 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1349-6_0_3_load_84 | 105 | 0.0032226 | 0.00080765 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1349-6_0_3_load_92 | 106 | 0.005843 | 0.0014644 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1349-6_0_3_load_91 | 107 | 0.0040725 | 0.0010207 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1349-6_0_3_load_85 | 108 | 0.013431 | 0.0033661 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1349-6_0_3_load_95 | 111 | 0.0022748 | 0.00057013 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1349-6_0_3_load_96 | 112 | 0.00066042 | 0.00016552 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1349-6_0_3_load_97 | 113 | 0.0037493 | 0.00093967 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1349-6_0_3_load_99 | 115 | 0.00041741 | 0.00010461 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1349-6_0_3_load_102 | 116 | 0.00092821 | 0.00023263 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1349-6_0_3_load_101 | 117 | 0.00041507 | 0.00010403 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1349-6_0_3_load_112 | 119 | 0.0011944 | 0.00029934 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1349-6_0_3_load_110 | 120 | 0.00096243 | 0.00024121 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1349-6_0_3_load_113 | 122 | 0.0012589 | 0.00031552 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1349-6_0_3_load_114 | 123 | 0.001808 | 0.00045312 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1349-6_0_3_load_115 | 124 | 0.015473 | 0.003878 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1349-6_0_3_load_128 | 125 | 0.0089849 | 0.0022518 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1349-6_0_3_load_127 | 126 | 0.0023553 | 0.00059029 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1349-6_0_3_line_0 |  | 0 | 1 | 0.048132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1349-6_0_3_line_1 |  | 1 | 2 | 0.006946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1349-6_0_3_line_2 |  | 1 | 3 | 0.02155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1349-6_0_3_line_3 |  | 2 | 4 | 0.030991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1349-6_0_3_line_4 |  | 3 | 5 | 0.035558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1349-6_0_3_line_5 |  | 4 | 6 | 0.0016418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1349-6_0_3_line_6 |  | 6 | 10 | 0.016109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1349-6_0_3_line_7 |  | 7 | 8 | 0.045691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1349-6_0_3_line_8 |  | 7 | 9 | 0.017622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1349-6_0_3_line_9 |  | 9 | 92 | 0.016884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1349-6_0_3_line_10 |  | 9 | 91 | 0.028848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1349-6_0_3_line_11 |  | 10 | 90 | 0.014611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1349-6_0_3_line_12 |  | 11 | 12 | 0.0070489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1349-6_0_3_line_13 |  | 12 | 13 | 0.04332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1349-6_0_3_line_14 |  | 13 | 14 | 0.017699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1349-6_0_3_line_15 |  | 14 | 28 | 0.022206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1349-6_0_3_line_16 |  | 15 | 16 | 0.00232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1349-6_0_3_line_17 |  | 15 | 17 | 0.022092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_1349-6_0_3_line_18 |  | 16 | 18 | 0.016161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1349-6_0_3_line_19 |  | 16 | 19 | 0.038984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1349-6_0_3_line_20 |  | 18 | 20 | 0.016667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_1349-6_0_3_line_21 |  | 19 | 21 | 0.019605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1349-6_0_3_line_22 |  | 19 | 22 | 0.023408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1349-6_0_3_line_23 |  | 20 | 46 | 0.037224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_1349-6_0_3_line_24 |  | 20 | 58 | 0.013814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1349-6_0_3_line_25 |  | 21 | 87 | 0.032216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1349-6_0_3_line_26 |  | 23 | 24 | 0.00076942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1349-6_0_3_line_27 |  | 24 | 25 | 0.034696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1349-6_0_3_line_28 |  | 25 | 26 | 0.01267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1349-6_0_3_line_29 |  | 26 | 27 | 0.012805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1349-6_0_3_line_30 |  | 27 | 93 | 0.013358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1349-6_0_3_line_31 |  | 27 | 91 | 0.025165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1349-6_0_3_line_32 |  | 28 | 109 | 0.01954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1349-6_0_3_line_33 |  | 29 | 30 | 0.017801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1349-6_0_3_line_34 |  | 30 | 31 | 0.088276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1349-6_0_3_line_35 |  | 31 | 32 | 0.039415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1349-6_0_3_line_36 |  | 32 | 33 | 0.043538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1349-6_0_3_line_37 |  | 32 | 34 | 0.0075846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1349-6_0_3_line_38 |  | 33 | 35 | 0.027261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1349-6_0_3_line_39 |  | 34 | 57 | 0.0089626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1349-6_0_3_line_40 |  | 35 | 36 | 0.012831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_1349-6_0_3_line_41 |  | 35 | 37 | 0.030411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_1349-6_0_3_line_42 |  | 36 | 38 | 0.033754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_1349-6_0_3_line_43 |  | 37 | 39 | 0.00094754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_1349-6_0_3_line_44 |  | 38 | 40 | 0.017094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_1349-6_0_3_line_45 |  | 38 | 41 | 0.013111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1349-6_0_3_line_46 |  | 39 | 42 | 0.012482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_1349-6_0_3_line_47 |  | 40 | 43 | 0.022793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_1349-6_0_3_line_48 |  | 41 | 44 | 0.015982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1349-6_0_3_line_49 |  | 42 | 63 | 0.0057771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_1349-6_0_3_line_50 |  | 43 | 45 | 0.014228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1349-6_0_3_line_51 |  | 43 | 46 | 0.01689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_1349-6_0_3_line_52 |  | 44 | 47 | 0.0029411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1349-6_0_3_line_53 |  | 45 | 51 | 0.016827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1349-6_0_3_line_54 |  | 48 | 49 | 0.019709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1349-6_0_3_line_55 |  | 48 | 50 | 0.0013269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1349-6_0_3_line_56 |  | 49 | 51 | 0.0049127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1349-6_0_3_line_57 |  | 50 | 52 | 0.025969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1349-6_0_3_line_58 |  | 52 | 53 | 0.010876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1349-6_0_3_line_59 |  | 53 | 54 | 0.016538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1349-6_0_3_line_60 |  | 54 | 66 | 0.0031887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1349-6_0_3_line_61 |  | 55 | 56 | 0.0021343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1349-6_0_3_line_62 |  | 56 | 57 | 0.019931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1349-6_0_3_line_63 |  | 58 | 59 | 0.017634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1349-6_0_3_line_64 |  | 59 | 60 | 0.0015984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1349-6_0_3_line_65 |  | 60 | 61 | 0.021843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1349-6_0_3_line_66 |  | 61 | 62 | 0.018959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1349-6_0_3_line_67 |  | 62 | 72 | 0.004726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1349-6_0_3_line_68 |  | 63 | 64 | 0.024269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_1349-6_0_3_line_69 |  | 64 | 65 | 0.025765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_1349-6_0_3_line_70 |  | 65 | 70 | 0.015404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_1349-6_0_3_line_71 |  | 66 | 67 | 8.782e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1349-6_0_3_line_72 |  | 67 | 68 | 8.3453e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1349-6_0_3_line_73 |  | 68 | 69 | 0.02141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1349-6_0_3_line_74 |  | 70 | 71 | 0.015644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_1349-6_0_3_line_75 |  | 71 | 74 | 0.022825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_1349-6_0_3_line_76 |  | 72 | 73 | 0.0012696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1349-6_0_3_line_77 |  | 74 | 75 | 0.021987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_1349-6_0_3_line_78 |  | 75 | 76 | 0.084397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_1349-6_0_3_line_79 |  | 76 | 77 | 0.036964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_1349-6_0_3_line_80 |  | 77 | 78 | 0.054945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_1349-6_0_3_line_81 |  | 78 | 96 | 0.10897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_1349-6_0_3_line_82 |  | 79 | 80 | 0.019192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_1349-6_0_3_line_83 |  | 79 | 81 | 0.11326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_1349-6_0_3_line_84 |  | 80 | 82 | 0.085802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_1349-6_0_3_line_85 |  | 81 | 83 | 0.044381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_1349-6_0_3_line_86 |  | 82 | 86 | 0.1416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_1349-6_0_3_line_87 |  | 83 | 85 | 0.019469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_1349-6_0_3_line_88 |  | 84 | 85 | 0.039071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1349-6_0_3_line_89 |  | 85 | 117 | 0.078028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_1349-6_0_3_line_90 |  | 86 | 101 | 0.40552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_1349-6_0_3_line_91 |  | 86 | 103 | 0.00083337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1349-6_0_3_line_92 |  | 87 | 88 | 0.029013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1349-6_0_3_line_93 |  | 87 | 89 | 0.021939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1349-6_0_3_line_94 |  | 88 | 104 | 0.00894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1349-6_0_3_line_95 |  | 88 | 105 | 0.016244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1349-6_0_3_line_96 |  | 89 | 95 | 0.042002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1349-6_0_3_line_97 |  | 90 | 91 | 0.0030824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1349-6_0_3_line_98 |  | 92 | 94 | 0.010606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1349-6_0_3_line_99 |  | 93 | 95 | 0.0025222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1349-6_0_3_line_100 |  | 94 | 110 | 0.025091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1349-6_0_3_line_101 |  | 94 | 109 | 0.006651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1349-6_0_3_line_102 |  | 96 | 97 | 0.058101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_1349-6_0_3_line_103 |  | 97 | 98 | 0.0023226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_1349-6_0_3_line_104 |  | 98 | 99 | 0.024512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_1349-6_0_3_line_105 |  | 99 | 100 | 0.024483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_1349-6_0_3_line_106 |  | 100 | 101 | 0.036059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_1349-6_0_3_line_107 |  | 101 | 102 | 0.030239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1349-6_0_3_line_108 |  | 104 | 106 | 0.0095027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1349-6_0_3_line_109 |  | 104 | 107 | 0.017143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1349-6_0_3_line_110 |  | 105 | 108 | 0.0028836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1349-6_0_3_line_111 |  | 110 | 125 | 0.029972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1349-6_0_3_line_112 |  | 110 | 126 | 0.024212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1349-6_0_3_line_113 |  | 111 | 112 | 0.036068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1349-6_0_3_line_114 |  | 112 | 113 | 0.019784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_1349-6_0_3_line_115 |  | 112 | 114 | 0.033746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
116 | LV_1349-6_0_3_line_116 |  | 113 | 116 | 0.022701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_1349-6_0_3_line_117 |  | 114 | 117 | 0.022315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_1349-6_0_3_line_118 |  | 114 | 115 | 0.0123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1349-6_0_3_line_119 |  | 116 | 118 | 0.033201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
120 | LV_1349-6_0_3_line_120 |  | 118 | 119 | 0.089594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_1349-6_0_3_line_121 |  | 119 | 122 | 0.024876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
122 | LV_1349-6_0_3_line_122 |  | 119 | 121 | 0.015941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1349-6_0_3_line_123 |  | 120 | 121 | 0.025682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1349-6_0_3_line_124 |  | 122 | 123 | 0.017266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
125 | LV_1349-6_0_3_line_125 |  | 123 | 124 | 0.0026166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1349-6_0_3_trafo_8 | 0.63 MVA 20/0.4 kV | 127 | 17 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2710264.6474 | 1226826.9271 | 2710286.8521 | 1226819.9778 | 2710310.695 | 1226812.9227
1 | 2710257.9698 | 1226828.9049 | 2710264.6474 | 1226826.9271
2 | 2710262.9979 | 1226848.0125 | 2710265.1667 | 1226843.0712 | 2710264.9097 | 1226836.0834 | 2710264.6474 | 1226826.9271
3 | 2710257.9698 | 1226828.9049 | 2710228.4086 | 1226838.2094
4 | 2710262.9979 | 1226848.0125 | 2710274.3563 | 1226859.3427 | 2710277.8596 | 1226860.5197 | 2710288.5466 | 1226848.7866
5 | 2710226.8425 | 1226838.7023 | 2710228.4086 | 1226838.2094
6 | 2710226.8425 | 1226838.7023 | 2710211.4642 | 1226843.4991
7 | 2710252.1422 | 1226875.7991 | 2710253.3147 | 1226876.7549 | 2710232.9193 | 1226885.895 | 2710219.6729 | 1226868.4476
8 | 2710203.7187 | 1226876.0245 | 2710209.8161 | 1226873.0351 | 2710219.6729 | 1226868.4476
9 | 2710203.7187 | 1226876.0245 | 2710196.7721 | 1226881.0663 | 2710188.7909 | 1226883.3472
10 | 2710194.5733 | 1226848.7678 | 2710199.7839 | 1226867.8565 | 2710203.7187 | 1226876.0245
11 | 2710197.5159 | 1226847.8499 | 2710211.4642 | 1226843.4991
12 | 2710102.0741 | 1226959.5171 | 2710095.0263 | 1226959.3866
13 | 2710125.7837 | 1226923.2618 | 2710102.0741 | 1226959.5171
14 | 2710125.7837 | 1226923.2618 | 2710129.8965 | 1226922.6374 | 2710132.5306 | 1226921.2184 | 2710133.2757 | 1226919.4642 | 2710134.3858 | 1226915.6041 | 2710135.4487 | 1226914.2894 | 2710137.1993 | 1226913.499 | 2710138.1461 | 1226913.1385
15 | 2710138.1461 | 1226913.1385 | 2710157.7555 | 1226902.7191
16 | 2710076.3374 | 1226808.8158 | 2710075.3911 | 1226806.6966
17 | 2710076.3374 | 1226808.8158 | 2710089.4044 | 1226826.6294
18 | 2710075.3911 | 1226806.6966 | 2710074.2135 | 1226803.15 | 2710070.3038 | 1226791.3576
19 | 2710075.3911 | 1226806.6966 | 2710112.7008 | 1226795.0448
20 | 2710065.0588 | 1226775.5375 | 2710070.3038 | 1226791.3576
21 | 2710112.7008 | 1226795.0448 | 2710131.5817 | 1226789.7658
22 | 2710112.7008 | 1226795.0448 | 2710119.6246 | 1226817.4054
23 | 2710065.0588 | 1226775.5375 | 2710053.1071 | 1226740.2847
24 | 2710065.0588 | 1226775.5375 | 2710078.2846 | 1226771.548
25 | 2710162.6074 | 1226781.0913 | 2710131.5817 | 1226789.7658
26 | 2710112.5451 | 1226872.634 | 2710112.3373 | 1226871.8932
27 | 2710112.5451 | 1226872.634 | 2710124.5262 | 1226868.775 | 2710145.7941 | 1226862.7366
28 | 2710157.9824 | 1226859.276 | 2710145.7941 | 1226862.7366
29 | 2710157.9824 | 1226859.276 | 2710170.3644 | 1226855.8804
30 | 2710170.3644 | 1226855.8804 | 2710167.1303 | 1226842.9199
31 | 2710194.5733 | 1226848.7678 | 2710170.3644 | 1226855.8804
32 | 2710175.0109 | 1226893.5506 | 2710157.7555 | 1226902.7191
33 | 2710105.5839 | 1226572.6448 | 2710091.6405 | 1226583.711
34 | 2710012.003 | 1226545.6246 | 2710091.6405 | 1226583.711
35 | 2709990.0445 | 1226577.9899 | 2709996.0083 | 1226565.0237 | 2710012.003 | 1226545.6246
36 | 2709990.0445 | 1226577.9899 | 2709996.2306 | 1226595.6287 | 2710005.838 | 1226618.5415
37 | 2709990.0445 | 1226577.9899 | 2709984.9697 | 1226572.3532
38 | 2710016.3795 | 1226643.682 | 2710005.838 | 1226618.5415
39 | 2709984.9697 | 1226572.3532 | 2709978.9729 | 1226565.6924
40 | 2710016.3795 | 1226643.682 | 2710021.0339 | 1226655.6387
41 | 2710016.3795 | 1226643.682 | 2710006.7244 | 1226648.4182 | 2709991.9736 | 1226661.4109
42 | 2710033.2783 | 1226687.0939 | 2710021.0339 | 1226655.6387
43 | 2709991.9736 | 1226661.4109 | 2709991.4406 | 1226662.1942
44 | 2710033.2783 | 1226687.0939 | 2710039.4736 | 1226703.026
45 | 2710033.2783 | 1226687.0939 | 2710021.2766 | 1226692.3722
46 | 2709991.4406 | 1226662.1942 | 2709984.4185 | 1226672.5142
47 | 2710047.684 | 1226724.2885 | 2710041.3834 | 1226707.9374 | 2710039.4736 | 1226703.026
48 | 2710012.6743 | 1226705.5611 | 2710020.0553 | 1226692.9094 | 2710021.2766 | 1226692.3722
49 | 2709981.1686 | 1226677.2905 | 2709984.4185 | 1226672.5142
50 | 2710047.684 | 1226724.2885 | 2710061.1343 | 1226719.6503
51 | 2710047.684 | 1226724.2885 | 2710053.1071 | 1226740.2847
52 | 2710011.1923 | 1226708.1015 | 2710012.6743 | 1226705.5611
53 | 2710061.1343 | 1226719.6503 | 2710077.0424 | 1226714.1647
54 | 2710081.6867 | 1226712.5632 | 2710100.3188 | 1226706.1382
55 | 2710101.5732 | 1226705.7056 | 2710100.3188 | 1226706.1382
56 | 2710081.6867 | 1226712.5632 | 2710077.0424 | 1226714.1647
57 | 2710126.4601 | 1226699.3878 | 2710120.2743 | 1226699.2569 | 2710101.5732 | 1226705.7056
58 | 2710137.3338 | 1226699.618 | 2710126.4601 | 1226699.3878
59 | 2710153.2902 | 1226695.9285 | 2710141.3113 | 1226699.7021 | 2710137.3338 | 1226699.618
60 | 2710153.2902 | 1226695.9285 | 2710156.3316 | 1226694.9704
61 | 2709965.6374 | 1226550.8806 | 2709964.2093 | 1226549.2944
62 | 2709965.6374 | 1226550.8806 | 2709978.9729 | 1226565.6924
63 | 2710078.2846 | 1226771.548 | 2710095.1676 | 1226766.4553
64 | 2710096.6979 | 1226765.9937 | 2710095.1676 | 1226766.4553
65 | 2710096.6979 | 1226765.9937 | 2710117.6102 | 1226759.6856
66 | 2710135.761 | 1226754.2104 | 2710117.6102 | 1226759.6856
67 | 2710135.761 | 1226754.2104 | 2710140.2856 | 1226752.8456
68 | 2709981.1686 | 1226677.2905 | 2709976.9175 | 1226683.5382 | 2709970.1699 | 1226698.8279
69 | 2709970.1699 | 1226698.8279 | 2709959.7673 | 1226722.4
70 | 2709953.5478 | 1226736.493 | 2709959.7673 | 1226722.4
71 | 2710156.4154 | 1226694.9441 | 2710156.3316 | 1226694.9704
72 | 2710156.495 | 1226694.919 | 2710156.4154 | 1226694.9441
73 | 2710176.9155 | 1226688.4861 | 2710156.495 | 1226694.919
74 | 2709953.5478 | 1226736.493 | 2709947.2317 | 1226750.805
75 | 2709930.5242 | 1226765.365 | 2709938.2956 | 1226762.0394 | 2709947.0312 | 1226751.2594 | 2709947.2317 | 1226750.805
76 | 2710141.5011 | 1226752.4789 | 2710140.2856 | 1226752.8456
77 | 2709930.5242 | 1226765.365 | 2709930.8839 | 1226787.3491
78 | 2709930.8839 | 1226787.3491 | 2709847.5953 | 1226800.9803
79 | 2709811.0158 | 1226805.8063 | 2709824.4664 | 1226805.1145 | 2709847.5953 | 1226800.9803
80 | 2709756.4224 | 1226811.1121 | 2709758.6579 | 1226810.7489 | 2709776.7442 | 1226807.569 | 2709811.0158 | 1226805.8063
81 | 2709649.9504 | 1226834.295 | 2709756.4224 | 1226811.1121
82 | 2709886.372 | 1227198.1103 | 2709879.0164 | 1227180.3841
83 | 2709985.395 | 1227141.5035 | 2709879.0164 | 1227180.3841
84 | 2709886.372 | 1227198.1103 | 2709817.572 | 1227249.3789
85 | 2710019.3681 | 1227115.6366 | 2710011.3664 | 1227118.6599 | 2710004.8883 | 1227130.3601 | 2709985.395 | 1227141.5035
86 | 2709817.572 | 1227249.3789 | 2709701.6674 | 1227330.7135
87 | 2710019.3681 | 1227115.6366 | 2710027.9474 | 1227112.3951 | 2710036.4549 | 1227106.5935
88 | 2710074.3232 | 1227116.2113 | 2710036.4549 | 1227106.5935
89 | 2710100.9203 | 1227062.6324 | 2710036.4549 | 1227106.5935
90 | 2709564.6137 | 1226949.0551 | 2709701.6674 | 1227330.7135
91 | 2709701.6674 | 1227330.7135 | 2709701.4269 | 1227331.5114
92 | 2710190.3566 | 1226772.3652 | 2710162.6074 | 1226781.0913
93 | 2710162.6074 | 1226781.0913 | 2710168.7767 | 1226802.1447
94 | 2710190.3566 | 1226772.3652 | 2710187.9004 | 1226763.7687
95 | 2710190.3566 | 1226772.3652 | 2710195.5772 | 1226773.7407 | 2710199.1302 | 1226783.9871
96 | 2710168.7767 | 1226802.1447 | 2710172.39 | 1226814.4755 | 2710170.7652 | 1226817.8813 | 2710168.3488 | 1226821.0501 | 2710166.1986 | 1226823.3565 | 2710163.4344 | 1226828.1089 | 2710166.5197 | 1226840.4728
97 | 2710194.5733 | 1226848.7678 | 2710197.5159 | 1226847.8499
98 | 2710180.6193 | 1226889.9517 | 2710187.7104 | 1226883.656 | 2710188.7909 | 1226883.3472
99 | 2710167.1303 | 1226842.9199 | 2710166.5197 | 1226840.4728
100 | 2710193.9233 | 1226911.2475 | 2710180.6193 | 1226889.9517
101 | 2710175.0109 | 1226893.5506 | 2710180.6193 | 1226889.9517
102 | 2709649.9504 | 1226834.295 | 2709643.0348 | 1226836.1254 | 2709634.8198 | 1226843.3795 | 2709630.4924 | 1226854.8195 | 2709622.6759 | 1226869.6534 | 2709616.1473 | 1226878.4935
103 | 2709614.7675 | 1226880.3619 | 2709616.1473 | 1226878.4935
104 | 2709600.2055 | 1226900.08 | 2709614.7675 | 1226880.3619
105 | 2709585.7668 | 1226919.8525 | 2709594.134 | 1226908.3012 | 2709600.2055 | 1226900.08
106 | 2709564.6137 | 1226949.0551 | 2709585.7668 | 1226919.8525
107 | 2709564.6137 | 1226949.0551 | 2709562.2938 | 1226918.9056
108 | 2710187.9004 | 1226763.7687 | 2710185.0545 | 1226754.7022
109 | 2710187.9004 | 1226763.7687 | 2710204.243 | 1226758.5922
110 | 2710200.0749 | 1226786.7116 | 2710199.1302 | 1226783.9871
111 | 2710171.2821 | 1226922.1365 | 2710173.1218 | 1226925.9512 | 2710188.5343 | 1226917.3301 | 2710193.9233 | 1226911.2475
112 | 2710209.1827 | 1226898.2091 | 2710211.5355 | 1226901.7443 | 2710193.9233 | 1226911.2475
113 | 2710148.1853 | 1227018.3966 | 2710151.3787 | 1227031.9957 | 2710152.8667 | 1227054.0442
114 | 2710152.8667 | 1227054.0442 | 2710154.1988 | 1227073.7829
115 | 2710152.8667 | 1227054.0442 | 2710119.3567 | 1227050.0611
116 | 2710155.7274 | 1227096.4327 | 2710154.1988 | 1227073.7829
117 | 2710119.3567 | 1227050.0611 | 2710110.9574 | 1227055.7878 | 2710100.9203 | 1227062.6324
118 | 2710119.3567 | 1227050.0611 | 2710116.6559 | 1227038.061
119 | 2710157.963 | 1227129.5582 | 2710155.7274 | 1227096.4327
120 | 2710157.963 | 1227129.5582 | 2710197.7011 | 1227209.8574
121 | 2710197.7011 | 1227209.8574 | 2710220.7582 | 1227200.5189
122 | 2710182.9264 | 1227215.8414 | 2710197.7011 | 1227209.8574
123 | 2710182.9264 | 1227215.8414 | 2710193.5201 | 1227239.2365
124 | 2710220.7582 | 1227200.5189 | 2710236.7615 | 1227194.0373
125 | 2710239.1868 | 1227193.0551 | 2710236.7615 | 1227194.0373

## bus_geodata
| x | y | coords
0 | 2710310.695 | 1226812.9227
1 | 2710264.6474 | 1226826.9271
2 | 2710257.9698 | 1226828.9049
3 | 2710262.9979 | 1226848.0125
4 | 2710228.4086 | 1226838.2094
5 | 2710288.5466 | 1226848.7866
6 | 2710226.8425 | 1226838.7023
7 | 2710219.6729 | 1226868.4476
8 | 2710252.1422 | 1226875.7991
9 | 2710203.7187 | 1226876.0245
10 | 2710211.4642 | 1226843.4991
11 | 2710095.0263 | 1226959.3866
12 | 2710102.0741 | 1226959.5171
13 | 2710125.7837 | 1226923.2618
14 | 2710138.1461 | 1226913.1385
15 | 2710076.3374 | 1226808.8158
16 | 2710075.3911 | 1226806.6966
17 | 2710089.4044 | 1226826.6294
18 | 2710070.3038 | 1226791.3576
19 | 2710112.7008 | 1226795.0448
20 | 2710065.0588 | 1226775.5375
21 | 2710131.5817 | 1226789.7658
22 | 2710119.6246 | 1226817.4054
23 | 2710112.3373 | 1226871.8932
24 | 2710112.5451 | 1226872.634
25 | 2710145.7941 | 1226862.7366
26 | 2710157.9824 | 1226859.276
27 | 2710170.3644 | 1226855.8804
28 | 2710157.7555 | 1226902.7191
29 | 2710105.5839 | 1226572.6448
30 | 2710091.6405 | 1226583.711
31 | 2710012.003 | 1226545.6246
32 | 2709990.0445 | 1226577.9899
33 | 2710005.838 | 1226618.5415
34 | 2709984.9697 | 1226572.3532
35 | 2710016.3795 | 1226643.682
36 | 2710021.0339 | 1226655.6387
37 | 2709991.9736 | 1226661.4109
38 | 2710033.2783 | 1226687.0939
39 | 2709991.4406 | 1226662.1942
40 | 2710039.4736 | 1226703.026
41 | 2710021.2766 | 1226692.3722
42 | 2709984.4185 | 1226672.5142
43 | 2710047.684 | 1226724.2885
44 | 2710012.6743 | 1226705.5611
45 | 2710061.1343 | 1226719.6503
46 | 2710053.1071 | 1226740.2847
47 | 2710011.1923 | 1226708.1015
48 | 2710100.3188 | 1226706.1382
49 | 2710081.6867 | 1226712.5632
50 | 2710101.5732 | 1226705.7056
51 | 2710077.0424 | 1226714.1647
52 | 2710126.4601 | 1226699.3878
53 | 2710137.3338 | 1226699.618
54 | 2710153.2902 | 1226695.9285
55 | 2709964.2093 | 1226549.2944
56 | 2709965.6374 | 1226550.8806
57 | 2709978.9729 | 1226565.6924
58 | 2710078.2846 | 1226771.548
59 | 2710095.1676 | 1226766.4553
60 | 2710096.6979 | 1226765.9937
61 | 2710117.6102 | 1226759.6856
62 | 2710135.761 | 1226754.2104
63 | 2709981.1686 | 1226677.2905
64 | 2709970.1699 | 1226698.8279
65 | 2709959.7673 | 1226722.4
66 | 2710156.3316 | 1226694.9704
67 | 2710156.4154 | 1226694.9441
68 | 2710156.495 | 1226694.919
69 | 2710176.9155 | 1226688.4861
70 | 2709953.5478 | 1226736.493
71 | 2709947.2317 | 1226750.805
72 | 2710140.2856 | 1226752.8456
73 | 2710141.5011 | 1226752.4789
74 | 2709930.5242 | 1226765.365
75 | 2709930.8839 | 1226787.3491
76 | 2709847.5953 | 1226800.9803
77 | 2709811.0158 | 1226805.8063
78 | 2709756.4224 | 1226811.1121
79 | 2709879.0164 | 1227180.3841
80 | 2709886.372 | 1227198.1103
81 | 2709985.395 | 1227141.5035
82 | 2709817.572 | 1227249.3789
83 | 2710019.3681 | 1227115.6366
84 | 2710074.3232 | 1227116.2113
85 | 2710036.4549 | 1227106.5935
86 | 2709701.6674 | 1227330.7135
87 | 2710162.6074 | 1226781.0913
88 | 2710190.3566 | 1226772.3652
89 | 2710168.7767 | 1226802.1447
90 | 2710197.5159 | 1226847.8499
91 | 2710194.5733 | 1226848.7678
92 | 2710188.7909 | 1226883.3472
93 | 2710167.1303 | 1226842.9199
94 | 2710180.6193 | 1226889.9517
95 | 2710166.5197 | 1226840.4728
96 | 2709649.9504 | 1226834.295
97 | 2709616.1473 | 1226878.4935
98 | 2709614.7675 | 1226880.3619
99 | 2709600.2055 | 1226900.08
100 | 2709585.7668 | 1226919.8525
101 | 2709564.6137 | 1226949.0551
102 | 2709562.2938 | 1226918.9056
103 | 2709701.4269 | 1227331.5114
104 | 2710187.9004 | 1226763.7687
105 | 2710199.1302 | 1226783.9871
106 | 2710185.0545 | 1226754.7022
107 | 2710204.243 | 1226758.5922
108 | 2710200.0749 | 1226786.7116
109 | 2710175.0109 | 1226893.5506
110 | 2710193.9233 | 1226911.2475
111 | 2710148.1853 | 1227018.3966
112 | 2710152.8667 | 1227054.0442
113 | 2710154.1988 | 1227073.7829
114 | 2710119.3567 | 1227050.0611
115 | 2710116.6559 | 1227038.061
116 | 2710155.7274 | 1227096.4327
117 | 2710100.9203 | 1227062.6324
118 | 2710157.963 | 1227129.5582
119 | 2710197.7011 | 1227209.8574
120 | 2710193.5201 | 1227239.2365
121 | 2710182.9264 | 1227215.8414
122 | 2710220.7582 | 1227200.5189
123 | 2710236.7615 | 1227194.0373
124 | 2710239.1868 | 1227193.0551
125 | 2710171.2821 | 1226922.1365
126 | 2710209.1827 | 1226898.2091
127 | 2710076.3374 | 1226808.8158

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98636 | -0.26251 | 0.0026583 | 0.00066622
1 | 0.98648 | -0.26021 | 0 | 0
2 | 0.98651 | -0.25959 | 0 | 0
3 | 0.98643 | -0.26113 | 0 | 0
4 | 0.98665 | -0.2568 | 0.00069512 | 0.00017421
5 | 0.98635 | -0.26264 | 0.002369 | 0.00059373
6 | 0.98666 | -0.25663 | 0 | 0
7 | 0.98609 | -0.26777 | 0 | 0
8 | 0.98598 | -0.26984 | 0.0025292 | 0.00063387
9 | 0.98613 | -0.26697 | 0 | 0
10 | 0.98675 | -0.25498 | 0.00042676 | 0.00010696
11 | 0.98533 | -0.28258 | 0.00036332 | 9.1058e-05
12 | 0.98533 | -0.28253 | 0.00037975 | 9.5173e-05
13 | 0.98536 | -0.28196 | 0 | 0
14 | 0.98537 | -0.28172 | 0 | 0
15 | 0.99837 | -0.031003 | 0 | 0
16 | 0.9982 | -0.034264 | 0 | 0
17 | 1 | 0 | -0.24537 | -0.06208
18 | 0.99746 | -0.048309 | 0.0018256 | 0.00045755
19 | 0.9949 | -0.097349 | 0 | 0
20 | 0.99671 | -0.062638 | 0 | 0
21 | 0.99339 | -0.12638 | 0.0053025 | 0.0013289
22 | 0.99473 | -0.10074 | 0.0082379 | 0.0020646
23 | 0.9875 | -0.24035 | 0.0017077 | 0.000428
24 | 0.9875 | -0.24033 | 0 | 0
25 | 0.98755 | -0.23927 | 0.0031391 | 0.00078674
26 | 0.98761 | -0.23817 | 0 | 0
27 | 0.98767 | -0.23706 | 0 | 0
28 | 0.98539 | -0.28142 | 0.0065694 | 0.0016464
29 | 0.99105 | -0.17123 | 0.001197 | 0.0003
30 | 0.99107 | -0.17085 | 0.0028201 | 0.00070679
31 | 0.99139 | -0.16456 | 0.0014812 | 0.00037123
32 | 0.99159 | -0.16071 | 0 | 0
33 | 0.99219 | -0.14918 | 0.0015718 | 0.00039394
34 | 0.99153 | -0.16198 | 0.0022112 | 0.00055417
35 | 0.9926 | -0.1412 | 0 | 0
36 | 0.9929 | -0.13542 | 0.0017674 | 0.00044296
37 | 0.99204 | -0.15195 | 0.00098863 | 0.00024777
38 | 0.99371 | -0.11988 | 0 | 0
39 | 0.99202 | -0.15228 | 0.0013679 | 0.00034283
40 | 0.99414 | -0.11167 | 0.0011769 | 0.00029495
41 | 0.99367 | -0.12066 | 0.00099893 | 0.00025036
42 | 0.9918 | -0.15652 | 0.0012942 | 0.00032435
43 | 0.99472 | -0.10059 | 0 | 0
44 | 0.99364 | -0.12134 | 0.00093707 | 0.00023485
45 | 0.99427 | -0.10935 | 0.0017601 | 0.00044113
46 | 0.99533 | -0.08892 | 0.0028247 | 0.00070793
47 | 0.99363 | -0.12141 | 0.0014542 | 0.00036446
48 | 0.99306 | -0.1328 | 0.0056092 | 0.0014058
49 | 0.99361 | -0.122 | 0.0011696 | 0.00029312
50 | 0.99303 | -0.1334 | 0.0014933 | 0.00037425
51 | 0.99376 | -0.11921 | 0.00098797 | 0.00024761
52 | 0.99246 | -0.14439 | 0.00094923 | 0.0002379
53 | 0.99223 | -0.14882 | 0.0048935 | 0.0012264
54 | 0.99196 | -0.15411 | 0.0011704 | 0.00029332
55 | 0.99135 | -0.16535 | 0.0043057 | 0.0010791
56 | 0.99136 | -0.16519 | 0.0015097 | 0.00037838
57 | 0.99147 | -0.16313 | 0.0014214 | 0.00035624
58 | 0.99638 | -0.069075 | 0.0014028 | 0.00035159
59 | 0.99597 | -0.076863 | 0.0043692 | 0.001095
60 | 0.99594 | -0.077446 | 0.0012333 | 0.00030909
61 | 0.99555 | -0.08495 | 0.0061489 | 0.0015411
62 | 0.99532 | -0.089415 | 0.0033901 | 0.00084965
63 | 0.9917 | -0.15844 | 0.00036302 | 9.098e-05
64 | 0.99128 | -0.16646 | 0.00066664 | 0.00016708
65 | 0.99084 | -0.17488 | 0.00037973 | 9.517e-05
66 | 0.99191 | -0.15507 | 0.0024946 | 0.0006252
67 | 0.9919 | -0.15509 | 0.0029258 | 0.00073328
68 | 0.9919 | -0.15511 | 0.0020971 | 0.00052557
69 | 0.99172 | -0.15868 | 0.0094 | 0.0023559
70 | 0.99058 | -0.17988 | 0.00071929 | 0.00018027
71 | 0.99031 | -0.18489 | 0.00085143 | 0.00021339
72 | 0.99528 | -0.090247 | 0.0063676 | 0.0015959
73 | 0.99528 | -0.090328 | 0.0036339 | 0.00091075
74 | 0.98994 | -0.1921 | 0 | 0
75 | 0.98958 | -0.19904 | 0.00075076 | 0.00018816
76 | 0.9882 | -0.22537 | 0.0010852 | 0.00027198
77 | 0.98762 | -0.23668 | 0.00042037 | 0.00010535
78 | 0.98675 | -0.25338 | 0.0010831 | 0.00027145
79 | 0.97481 | -0.48584 | 0.00050254 | 0.00012595
80 | 0.97501 | -0.48186 | 0 | 0
81 | 0.97363 | -0.50904 | 0.00094963 | 0.000238
82 | 0.97592 | -0.46406 | 0.0021096 | 0.00052872
83 | 0.97319 | -0.51789 | 0.00049585 | 0.00012427
84 | 0.97298 | -0.52203 | 0.00044866 | 0.00011244
85 | 0.97299 | -0.52171 | 0.0023776 | 0.00059587
86 | 0.97751 | -0.43293 | 0.0063076 | 0.0015808
87 | 0.99106 | -0.17124 | 0 | 0
88 | 0.99036 | -0.18493 | 0 | 0
89 | 0.99001 | -0.19154 | 0.0066189 | 0.0016589
90 | 0.98683 | -0.25337 | 0.001899 | 0.00047594
91 | 0.98685 | -0.25292 | 0 | 0
92 | 0.98575 | -0.27443 | 0.0059955 | 0.0015026
93 | 0.98816 | -0.2275 | 0.002929 | 0.00073408
94 | 0.98557 | -0.27798 | 0 | 0
95 | 0.98826 | -0.22556 | 0.0024469 | 0.00061326
96 | 0.98507 | -0.28588 | 0.0014465 | 0.00036253
97 | 0.98419 | -0.30275 | 0.00097868 | 0.00024528
98 | 0.98416 | -0.30341 | 0.0005735 | 0.00014373
99 | 0.9838 | -0.31031 | 0.0018072 | 0.00045293
100 | 0.98346 | -0.31694 | 0.0012701 | 0.00031831
101 | 0.98297 | -0.32643 | 0 | 0
102 | 0.98296 | -0.32662 | 0.00034871 | 8.7395e-05
103 | 0.97751 | -0.43294 | 0.001004 | 0.00025162
104 | 0.99028 | -0.18651 | 0 | 0
105 | 0.99011 | -0.18974 | 0.0032226 | 0.00080765
106 | 0.99023 | -0.18749 | 0.005843 | 0.0014644
107 | 0.99021 | -0.18775 | 0.0040725 | 0.0010207
108 | 0.99008 | -0.19043 | 0.013431 | 0.0033661
109 | 0.98552 | -0.27886 | 0 | 0
110 | 0.9853 | -0.28309 | 0 | 0
111 | 0.97171 | -0.54703 | 0.0022748 | 0.00057013
112 | 0.97179 | -0.54551 | 0.00066042 | 0.00016552
113 | 0.97163 | -0.5486 | 0.0037493 | 0.00093967
114 | 0.97209 | -0.53963 | 0 | 0
115 | 0.97208 | -0.53973 | 0.00041741 | 0.00010461
116 | 0.97148 | -0.55163 | 0.00092821 | 0.00023263
117 | 0.97228 | -0.53569 | 0.00041507 | 0.00010403
118 | 0.97126 | -0.55586 | 0 | 0
119 | 0.97069 | -0.56729 | 0.0011944 | 0.00029934
120 | 0.97065 | -0.56804 | 0.00096243 | 0.00024121
121 | 0.97067 | -0.56758 | 0 | 0
122 | 0.97054 | -0.57014 | 0.0012589 | 0.00031552
123 | 0.9704 | -0.5729 | 0.001808 | 0.00045312
124 | 0.97037 | -0.57365 | 0.015473 | 0.003878
125 | 0.98506 | -0.28793 | 0.0089849 | 0.0022518
126 | 0.98525 | -0.28412 | 0.0023553 | 0.00059029
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0026583 | -0.00066622 | 0.0026586 | 0.00066579 | 2.9025e-07 | -4.2865e-07 | 0.0040102 | 0.00401 | 0.0040102 | 0.98636 | -0.26251 | 0.98648 | -0.26021 | 1.1017
1 | -0.0050278 | -0.001259 | 0.005028 | 0.001259 | 1.498e-07 | 7.1928e-09 | 0.0075837 | 0.0075836 | 0.0075837 | 0.98648 | -0.26021 | 0.98651 | -0.25959 | 2.0834
2 | 0.0023693 | 0.00059318 | -0.0023692 | -0.00059339 | 1.0321e-07 | -2.0906e-07 | 0.0035737 | 0.0035738 | 0.0035738 | 0.98648 | -0.26021 | 0.98643 | -0.26113 | 0.9818
3 | -0.005028 | -0.001259 | 0.0050287 | 0.001259 | 6.6836e-07 | 3.2012e-08 | 0.0075836 | 0.0075835 | 0.0075836 | 0.98651 | -0.25959 | 0.98665 | -0.2568 | 2.0834
4 | 0.0023692 | 0.00059339 | -0.002369 | -0.00059373 | 1.7031e-07 | -3.4489e-07 | 0.0035738 | 0.0035739 | 0.0035739 | 0.98643 | -0.26113 | 0.98635 | -0.26264 | 0.98184
5 | -0.0057238 | -0.0014332 | 0.0057238 | 0.0014332 | 4.5872e-08 | 8.3903e-09 | 0.0086318 | 0.0086318 | 0.0086318 | 0.98665 | -0.2568 | 0.98666 | -0.25663 | 2.3714
6 | -0.0057238 | -0.0014332 | 0.0057243 | 0.0014333 | 4.5009e-07 | 8.2304e-08 | 0.0086318 | 0.0086318 | 0.0086318 | 0.98666 | -0.25663 | 0.98675 | -0.25498 | 2.3714
7 | 0.0025294 | 0.00063345 | -0.0025292 | -0.00063387 | 2.4962e-07 | -4.2305e-07 | 0.0038168 | 0.003817 | 0.003817 | 0.98609 | -0.26777 | 0.98598 | -0.26984 | 1.0486
8 | -0.0025294 | -0.00063345 | 0.0025295 | 0.00063329 | 9.6264e-08 | -1.632e-07 | 0.0038168 | 0.0038167 | 0.0038168 | 0.98609 | -0.26777 | 0.98613 | -0.26697 | 1.0486
9 | 0.024666 | 0.0061862 | -0.024658 | -0.0061808 | 8.772e-06 | 5.3988e-06 | 0.037222 | 0.037222 | 0.037222 | 0.98613 | -0.26697 | 0.98575 | -0.27443 | 10.2257
10 | -0.027196 | -0.0068195 | 0.027214 | 0.0068307 | 1.8219e-05 | 1.1292e-05 | 0.041038 | 0.041038 | 0.041038 | 0.98613 | -0.26697 | 0.98685 | -0.25292 | 11.2742
11 | -0.006151 | -0.0015403 | 0.0061515 | 0.0015404 | 4.7138e-07 | 1.1503e-07 | 0.0092753 | 0.0092752 | 0.0092753 | 0.98675 | -0.25498 | 0.98683 | -0.25337 | 2.5482
12 | -0.00036332 | -9.1058e-05 | 0.00036333 | 9.0968e-05 | 7.9575e-10 | -8.9275e-08 | 0.00054868 | 0.00054865 | 0.00054868 | 0.98533 | -0.28258 | 0.98533 | -0.28253 | 0.15074
13 | -0.00074307 | -0.00018614 | 0.00074309 | 0.0001856 | 2.0452e-08 | -5.387e-07 | 0.0011221 | 0.0011219 | 0.0011221 | 0.98533 | -0.28253 | 0.98536 | -0.28196 | 0.30828
14 | -0.00074309 | -0.0001856 | 0.0007431 | 0.00018538 | 8.3537e-09 | -2.201e-07 | 0.0011219 | 0.0011219 | 0.0011219 | 0.98536 | -0.28196 | 0.98537 | -0.28172 | 0.30822
15 | -0.0007431 | -0.00018538 | 0.00074311 | 0.00018511 | 1.0479e-08 | -2.7616e-07 | 0.0011219 | 0.0011218 | 0.0011219 | 0.98537 | -0.28172 | 0.98539 | -0.28142 | 0.3082
16 | 0.24335 | 0.061848 | -0.24331 | -0.061824 | 3.8215e-05 | 2.4366e-05 | 0.36301 | 0.36301 | 0.36301 | 0.99837 | -0.031003 | 0.9982 | -0.034264 | 33.2424
17 | -0.24335 | -0.061848 | 0.24372 | 0.06208 | 0.0003639 | 0.00023203 | 0.36301 | 0.36301 | 0.36301 | 0.99837 | -0.031003 | 1 | 0 | 33.2424
18 | 0.15033 | 0.038217 | -0.15023 | -0.038153 | 0.00010162 | 6.4406e-05 | 0.22429 | 0.22429 | 0.22429 | 0.9982 | -0.034264 | 0.99746 | -0.048309 | 20.5395
19 | 0.092982 | 0.023606 | -0.092701 | -0.023427 | 0.0002813 | 0.00017953 | 0.13872 | 0.13872 | 0.13872 | 0.9982 | -0.034264 | 0.9949 | -0.097349 | 38.1089
20 | 0.1484 | 0.037695 | -0.1483 | -0.03763 | 0.00010228 | 6.4805e-05 | 0.22157 | 0.22157 | 0.22157 | 0.99746 | -0.048309 | 0.99671 | -0.062638 | 20.2901
21 | 0.084462 | 0.021362 | -0.084344 | -0.021287 | 0.00011745 | 7.4913e-05 | 0.12639 | 0.12639 | 0.12639 | 0.9949 | -0.097349 | 0.99339 | -0.12638 | 34.7235
22 | 0.0082392 | 0.0020652 | -0.0082379 | -0.0020646 | 1.333e-06 | 5.492e-07 | 0.012323 | 0.012323 | 0.012323 | 0.9949 | -0.097349 | 0.99473 | -0.10074 | 3.3855
23 | 0.12173 | 0.03096 | -0.12157 | -0.030863 | 0.00015394 | 9.7069e-05 | 0.18189 | 0.18189 | 0.18189 | 0.99671 | -0.062638 | 0.99533 | -0.08892 | 16.6568
24 | 0.026574 | 0.0066701 | -0.026566 | -0.0066651 | 8.1552e-06 | 5.0394e-06 | 0.039677 | 0.039677 | 0.039677 | 0.99671 | -0.062638 | 0.99638 | -0.069075 | 10.9002
25 | 0.079042 | 0.019958 | -0.078872 | -0.01985 | 0.0001695 | 0.00010806 | 0.11845 | 0.11845 | 0.11845 | 0.99339 | -0.12638 | 0.99106 | -0.17124 | 32.5415
26 | -0.0017077 | -0.000428 | 0.0017077 | 0.00042799 | 1.9107e-09 | -8.6207e-09 | 0.0025733 | 0.0025733 | 0.0025733 | 0.9875 | -0.24035 | 0.9875 | -0.24033 | 0.70696
27 | -0.0017077 | -0.00042799 | 0.0017078 | 0.0004276 | 8.6152e-08 | -3.8876e-07 | 0.0025733 | 0.0025732 | 0.0025733 | 0.9875 | -0.24033 | 0.98755 | -0.23927 | 0.70695
28 | -0.004847 | -0.0012143 | 0.0048472 | 0.0012143 | 2.5341e-07 | 6.1466e-11 | 0.0073031 | 0.007303 | 0.0073031 | 0.98755 | -0.23927 | 0.98761 | -0.23817 | 2.0063
29 | -0.0048472 | -0.0012143 | 0.0048475 | 0.0012143 | 2.561e-07 | 4.07e-11 | 0.007303 | 0.007303 | 0.007303 | 0.98761 | -0.23817 | 0.98767 | -0.23706 | 2.0063
30 | -0.040139 | -0.010078 | 0.040157 | 0.01009 | 1.8323e-05 | 1.1555e-05 | 0.06048 | 0.06048 | 0.06048 | 0.98767 | -0.23706 | 0.98816 | -0.2275 | 16.6153
31 | 0.035291 | 0.0088639 | -0.035265 | -0.0088471 | 2.6685e-05 | 1.6757e-05 | 0.053177 | 0.053177 | 0.053177 | 0.98767 | -0.23706 | 0.98685 | -0.25292 | 14.609
32 | -0.0073125 | -0.0018316 | 0.0073134 | 0.0018319 | 8.9342e-07 | 3.2284e-07 | 0.011042 | 0.011042 | 0.011042 | 0.98539 | -0.28142 | 0.98552 | -0.27886 | 3.0335
33 | -0.001197 | -0.0003 | 0.001197 | 0.00029979 | 2.1562e-08 | -2.1558e-07 | 0.0017973 | 0.0017972 | 0.0017973 | 0.99105 | -0.17123 | 0.99107 | -0.17085 | 0.49375
34 | -0.0040172 | -0.0010066 | 0.0040184 | 0.0010062 | 1.2042e-06 | -3.6724e-07 | 0.0060314 | 0.006031 | 0.0060314 | 0.99107 | -0.17085 | 0.99139 | -0.16456 | 1.657
35 | -0.0054996 | -0.0013774 | 0.0055006 | 0.0013776 | 1.007e-06 | 1.3615e-07 | 0.0082542 | 0.008254 | 0.0082542 | 0.99139 | -0.16456 | 0.99159 | -0.16071 | 2.2676
36 | -0.01495 | -0.003746 | 0.014958 | 0.0037507 | 8.2172e-06 | 4.697e-06 | 0.022434 | 0.022434 | 0.022434 | 0.99159 | -0.16071 | 0.99219 | -0.14918 | 6.1633
37 | 0.0094496 | 0.0023684 | -0.009449 | -0.0023681 | 5.7193e-07 | 2.682e-07 | 0.01418 | 0.01418 | 0.01418 | 0.99159 | -0.16071 | 0.99153 | -0.16198 | 3.8957
38 | -0.01653 | -0.0041446 | 0.016537 | 0.0041483 | 6.2832e-06 | 3.669e-06 | 0.024792 | 0.024791 | 0.024792 | 0.99219 | -0.14918 | 0.9926 | -0.1412 | 6.8109
39 | 0.0072379 | 0.001814 | -0.0072375 | -0.0018138 | 3.9655e-07 | 1.382e-07 | 0.010862 | 0.010862 | 0.010862 | 0.99153 | -0.16198 | 0.99147 | -0.16313 | 2.9841
40 | -0.077164 | -0.019622 | 0.077185 | 0.019635 | 2.1499e-05 | 1.3261e-05 | 0.11578 | 0.11578 | 0.11578 | 0.9926 | -0.1412 | 0.9929 | -0.13542 | 10.6023
41 | 0.060627 | 0.015474 | -0.060596 | -0.015455 | 3.147e-05 | 1.8962e-05 | 0.090986 | 0.090987 | 0.090987 | 0.9926 | -0.1412 | 0.99204 | -0.15195 | 8.3321
42 | -0.078953 | -0.020078 | 0.079012 | 0.020115 | 5.9174e-05 | 3.6561e-05 | 0.11843 | 0.11843 | 0.11843 | 0.9929 | -0.13542 | 0.99371 | -0.11988 | 10.8449
43 | 0.059607 | 0.015207 | -0.059606 | -0.015207 | 9.4883e-07 | 5.7055e-07 | 0.089504 | 0.089504 | 0.089504 | 0.99204 | -0.15195 | 0.99202 | -0.15228 | 8.1963
44 | -0.082402 | -0.020964 | 0.082435 | 0.020984 | 3.2592e-05 | 2.0194e-05 | 0.1235 | 0.1235 | 0.1235 | 0.99371 | -0.11988 | 0.99414 | -0.11167 | 11.3097
45 | 0.0033904 | 0.00084938 | -0.0033903 | -0.00084947 | 1.2672e-07 | -8.8743e-08 | 0.0050768 | 0.0050768 | 0.0050768 | 0.99371 | -0.11988 | 0.99367 | -0.12066 | 1.3947
46 | 0.058238 | 0.014864 | -0.058226 | -0.014857 | 1.1933e-05 | 7.1538e-06 | 0.087452 | 0.087452 | 0.087452 | 0.99202 | -0.15228 | 0.9918 | -0.15652 | 8.0084
47 | -0.083612 | -0.021279 | 0.083656 | 0.021307 | 4.4705e-05 | 2.7724e-05 | 0.12526 | 0.12526 | 0.12526 | 0.99414 | -0.11167 | 0.99472 | -0.10059 | 11.471
48 | 0.0023914 | 0.00059912 | -0.0023913 | -0.00059928 | 7.6852e-08 | -1.5783e-07 | 0.003581 | 0.003581 | 0.003581 | 0.99367 | -0.12066 | 0.99364 | -0.12134 | 0.9838
49 | 0.056932 | 0.014532 | -0.056927 | -0.014529 | 5.2803e-06 | 3.1558e-06 | 0.08551 | 0.085511 | 0.085511 | 0.9918 | -0.15652 | 0.9917 | -0.15844 | 7.8306
50 | 0.035026 | 0.0088062 | -0.035012 | -0.008797 | 1.4653e-05 | 9.1934e-06 | 0.052406 | 0.052406 | 0.052406 | 0.99472 | -0.10059 | 0.99427 | -0.10935 | 14.3973
51 | -0.11868 | -0.030113 | 0.11875 | 0.030155 | 6.6646e-05 | 4.1996e-05 | 0.17767 | 0.17767 | 0.17767 | 0.99472 | -0.10059 | 0.99533 | -0.08892 | 16.2701
52 | 0.0014542 | 0.00036442 | -0.0014542 | -0.00036446 | 5.2305e-09 | -3.4748e-08 | 0.0021777 | 0.0021777 | 0.0021777 | 0.99364 | -0.12134 | 0.99363 | -0.12141 | 0.59828
53 | 0.033252 | 0.0083559 | -0.033236 | -0.0083461 | 1.5632e-05 | 9.7864e-06 | 0.049772 | 0.049772 | 0.049772 | 0.99427 | -0.10935 | 0.99376 | -0.11921 | 13.6737
54 | -0.031058 | -0.0077927 | 0.031074 | 0.0078027 | 1.6009e-05 | 9.9907e-06 | 0.046541 | 0.046541 | 0.046541 | 0.99306 | -0.1328 | 0.99361 | -0.122 | 12.7861
55 | 0.025449 | 0.0063869 | -0.025448 | -0.0063864 | 7.2369e-07 | 4.4599e-07 | 0.038136 | 0.038136 | 0.038136 | 0.99306 | -0.1328 | 0.99303 | -0.1334 | 10.477
56 | -0.032244 | -0.0080958 | 0.032248 | 0.0080985 | 4.2965e-06 | 2.6861e-06 | 0.048293 | 0.048293 | 0.048293 | 0.99361 | -0.122 | 0.99376 | -0.11921 | 13.2673
57 | 0.023955 | 0.0060122 | -0.023942 | -0.0060045 | 1.255e-05 | 7.6963e-06 | 0.035899 | 0.035899 | 0.035899 | 0.99303 | -0.1334 | 0.99246 | -0.14439 | 9.8623
58 | 0.022993 | 0.0057666 | -0.022988 | -0.0057636 | 4.8476e-06 | 2.962e-06 | 0.034476 | 0.034476 | 0.034476 | 0.99246 | -0.14439 | 0.99223 | -0.14882 | 9.4713
59 | 0.018095 | 0.0045372 | -0.01809 | -0.0045344 | 4.567e-06 | 2.7093e-06 | 0.027137 | 0.027137 | 0.027137 | 0.99223 | -0.14882 | 0.99196 | -0.15411 | 7.4552
60 | 0.01692 | 0.0042411 | -0.016919 | -0.0042407 | 7.7034e-07 | 4.5185e-07 | 0.025381 | 0.025381 | 0.025381 | 0.99196 | -0.15411 | 0.99191 | -0.15507 | 6.9729
61 | -0.0043057 | -0.0010791 | 0.0043057 | 0.0010791 | 3.3429e-08 | -6.1238e-09 | 0.0064628 | 0.0064628 | 0.0064628 | 0.99135 | -0.16535 | 0.99136 | -0.16519 | 1.7755
62 | -0.0058155 | -0.0014575 | 0.005816 | 0.0014576 | 5.6946e-07 | 1.0745e-07 | 0.0087289 | 0.0087288 | 0.0087289 | 0.99136 | -0.16519 | 0.99147 | -0.16313 | 2.398
63 | 0.025163 | 0.0063135 | -0.025154 | -0.0063077 | 9.34e-06 | 5.748e-06 | 0.037582 | 0.037582 | 0.037582 | 0.99638 | -0.069075 | 0.99597 | -0.076863 | 10.3247
64 | 0.020785 | 0.0052127 | -0.020784 | -0.0052124 | 5.7803e-07 | 3.4914e-07 | 0.031054 | 0.031054 | 0.031054 | 0.99597 | -0.076863 | 0.99594 | -0.077446 | 8.5314
65 | 0.019551 | 0.0049033 | -0.019544 | -0.0048991 | 6.9897e-06 | 4.1893e-06 | 0.029212 | 0.029212 | 0.029212 | 0.99594 | -0.077446 | 0.99555 | -0.08495 | 8.0252
66 | 0.013395 | 0.003358 | -0.013392 | -0.0033564 | 2.8498e-06 | 1.5774e-06 | 0.020021 | 0.020021 | 0.020021 | 0.99555 | -0.08495 | 0.99532 | -0.089415 | 5.5003
67 | 0.010002 | 0.0025068 | -0.010002 | -0.0025066 | 3.9626e-07 | 1.9219e-07 | 0.014953 | 0.014953 | 0.014953 | 0.99532 | -0.089415 | 0.99528 | -0.090247 | 4.108
68 | 0.056564 | 0.014438 | -0.056542 | -0.014425 | 2.1901e-05 | 1.3077e-05 | 0.084966 | 0.084966 | 0.084966 | 0.9917 | -0.15844 | 0.99128 | -0.16646 | 7.7808
69 | 0.055875 | 0.014258 | -0.055852 | -0.014244 | 2.2707e-05 | 1.3536e-05 | 0.083966 | 0.083966 | 0.083966 | 0.99128 | -0.16646 | 0.99084 | -0.17488 | 7.6892
70 | 0.055473 | 0.014149 | -0.055459 | -0.014141 | 1.3392e-05 | 7.9757e-06 | 0.083396 | 0.083396 | 0.083396 | 0.99084 | -0.17488 | 0.99058 | -0.17988 | 7.637
71 | 0.014424 | 0.0036155 | -0.014424 | -0.0036155 | 1.5421e-08 | 8.7371e-09 | 0.021639 | 0.021639 | 0.021639 | 0.99191 | -0.15507 | 0.9919 | -0.15509 | 5.9448
72 | 0.011499 | 0.0028822 | -0.011499 | -0.0028822 | 9.311e-09 | 4.8826e-09 | 0.01725 | 0.01725 | 0.01725 | 0.9919 | -0.15509 | 0.9919 | -0.15511 | 4.739
73 | 0.0094016 | 0.0023566 | -0.0094 | -0.0023559 | 1.5971e-06 | 7.4585e-07 | 0.014104 | 0.014104 | 0.014104 | 0.9919 | -0.15511 | 0.99172 | -0.15868 | 3.8748
74 | 0.05474 | 0.013961 | -0.054727 | -0.013953 | 1.325e-05 | 7.8759e-06 | 0.082315 | 0.082316 | 0.082316 | 0.99058 | -0.17988 | 0.99031 | -0.18489 | 7.5381
75 | 0.053875 | 0.01374 | -0.053857 | -0.013729 | 1.8736e-05 | 1.111e-05 | 0.081036 | 0.081037 | 0.081037 | 0.99031 | -0.18489 | 0.98994 | -0.1921 | 7.4209
76 | 0.0036339 | 0.00091074 | -0.0036339 | -0.00091075 | 1.4054e-08 | -7.5052e-09 | 0.005433 | 0.005433 | 0.005433 | 0.99528 | -0.090247 | 0.99528 | -0.090328 | 1.4926
77 | 0.053857 | 0.013729 | -0.053839 | -0.013718 | 1.8048e-05 | 1.0703e-05 | 0.081037 | 0.081037 | 0.081037 | 0.98994 | -0.1921 | 0.98958 | -0.19904 | 7.421
78 | 0.053088 | 0.01353 | -0.05302 | -0.01349 | 6.7363e-05 | 3.9864e-05 | 0.079908 | 0.079909 | 0.079909 | 0.98958 | -0.19904 | 0.9882 | -0.22537 | 7.3177
79 | 0.051935 | 0.013218 | -0.051907 | -0.013201 | 2.831e-05 | 1.6698e-05 | 0.078275 | 0.078276 | 0.078276 | 0.9882 | -0.22537 | 0.98762 | -0.23668 | 7.1681
80 | 0.051487 | 0.013096 | -0.051445 | -0.013071 | 4.1404e-05 | 2.4391e-05 | 0.077642 | 0.077643 | 0.077643 | 0.98762 | -0.23668 | 0.98675 | -0.25338 | 7.1102
81 | 0.050362 | 0.0128 | -0.050283 | -0.012754 | 7.8695e-05 | 4.6196e-05 | 0.07601 | 0.076011 | 0.076011 | 0.98675 | -0.25338 | 0.98507 | -0.28588 | 6.9607
82 | -0.034034 | -0.0085547 | 0.03404 | 0.0085581 | 6.477e-06 | 3.4273e-06 | 0.051961 | 0.05196 | 0.051961 | 0.97481 | -0.48584 | 0.97501 | -0.48186 | 4.7583
83 | 0.033531 | 0.0084287 | -0.033494 | -0.0084092 | 3.7105e-05 | 1.9516e-05 | 0.051194 | 0.051195 | 0.051195 | 0.97481 | -0.48584 | 0.97363 | -0.50904 | 4.6882
84 | -0.03404 | -0.0085581 | 0.034069 | 0.0085734 | 2.8956e-05 | 1.5319e-05 | 0.05196 | 0.051959 | 0.05196 | 0.97501 | -0.48186 | 0.97592 | -0.46406 | 4.7583
85 | 0.032545 | 0.0081712 | -0.032531 | -0.0081641 | 1.3728e-05 | 7.1305e-06 | 0.049744 | 0.049744 | 0.049744 | 0.97363 | -0.50904 | 0.97319 | -0.51789 | 4.5553
86 | -0.036179 | -0.0091022 | 0.036233 | 0.0091313 | 5.3882e-05 | 2.9168e-05 | 0.055176 | 0.055174 | 0.055176 | 0.97592 | -0.46406 | 0.97751 | -0.43293 | 5.0527
87 | 0.032035 | 0.0080398 | -0.032029 | -0.0080368 | 5.8398e-06 | 3.0119e-06 | 0.048986 | 0.048986 | 0.048986 | 0.97319 | -0.51789 | 0.97299 | -0.52171 | 4.4859
88 | -0.00044866 | -0.00011244 | 0.00044866 | 0.00011196 | 6.8961e-09 | -4.8084e-07 | 0.00068615 | 0.00068597 | 0.00068615 | 0.97298 | -0.52203 | 0.97299 | -0.52171 | 0.1885
89 | 0.029203 | 0.007329 | -0.029184 | -0.0073194 | 1.9458e-05 | 9.5477e-06 | 0.044664 | 0.044665 | 0.044665 | 0.97299 | -0.52171 | 0.97228 | -0.53569 | 4.0902
90 | -0.043545 | -0.010964 | 0.043767 | 0.011091 | 0.00022283 | 0.00012727 | 0.066304 | 0.066299 | 0.066304 | 0.97751 | -0.43293 | 0.98297 | -0.32643 | 6.0718
91 | 0.001004 | 0.00025161 | -0.001004 | -0.00025162 | 7.2969e-10 | -9.9799e-09 | 0.0015283 | 0.0015283 | 0.0015283 | 0.97751 | -0.43293 | 0.97751 | -0.43294 | 0.41987
92 | 0.026592 | 0.0066723 | -0.026574 | -0.0066616 | 1.7346e-05 | 1.0728e-05 | 0.039928 | 0.039928 | 0.039928 | 0.99106 | -0.17124 | 0.99036 | -0.18493 | 10.9694
93 | 0.052281 | 0.013178 | -0.05223 | -0.013145 | 5.0726e-05 | 3.2182e-05 | 0.078523 | 0.078523 | 0.078523 | 0.99106 | -0.17124 | 0.99001 | -0.19154 | 21.5722
94 | 0.0099167 | 0.0024854 | -0.009916 | -0.002485 | 7.4428e-07 | 3.6131e-07 | 0.0149 | 0.0149 | 0.0149 | 0.99036 | -0.18493 | 0.99028 | -0.18651 | 4.0934
95 | 0.016658 | 0.0041762 | -0.016654 | -0.004174 | 3.8159e-06 | 2.2332e-06 | 0.025029 | 0.025029 | 0.025029 | 0.99036 | -0.18493 | 0.99011 | -0.18974 | 6.876
96 | 0.045611 | 0.011487 | -0.045537 | -0.01144 | 7.4067e-05 | 4.6864e-05 | 0.068574 | 0.068575 | 0.068575 | 0.99001 | -0.19154 | 0.98826 | -0.22556 | 18.8392
97 | -0.0080505 | -0.0020163 | 0.0080507 | 0.0020164 | 1.7032e-07 | 6.9624e-08 | 0.012139 | 0.012139 | 0.012139 | 0.98683 | -0.25337 | 0.98685 | -0.25292 | 3.3348
98 | 0.018662 | 0.0046782 | -0.018659 | -0.0046763 | 3.1566e-06 | 1.885e-06 | 0.028171 | 0.028171 | 0.028171 | 0.98575 | -0.27443 | 0.98557 | -0.27798 | 7.7394
99 | -0.043086 | -0.010824 | 0.04309 | 0.010826 | 3.9826e-06 | 2.5166e-06 | 0.06489 | 0.06489 | 0.06489 | 0.98816 | -0.2275 | 0.98826 | -0.22556 | 17.827
100 | 0.011345 | 0.0028443 | -0.011342 | -0.0028428 | 2.7608e-06 | 1.4473e-06 | 0.017129 | 0.01713 | 0.01713 | 0.98557 | -0.27798 | 0.9853 | -0.28309 | 4.7059
101 | 0.0073137 | 0.001832 | -0.0073134 | -0.0018319 | 3.041e-07 | 1.0987e-07 | 0.011042 | 0.011042 | 0.011042 | 0.98557 | -0.27798 | 0.98552 | -0.27886 | 3.0335
102 | 0.048837 | 0.012391 | -0.048797 | -0.012368 | 3.9584e-05 | 2.3117e-05 | 0.073826 | 0.073827 | 0.073827 | 0.98507 | -0.28588 | 0.98419 | -0.30275 | 6.7607
103 | 0.047819 | 0.012123 | -0.047817 | -0.012122 | 1.5196e-06 | 8.8402e-07 | 0.072347 | 0.072347 | 0.072347 | 0.98419 | -0.30275 | 0.98416 | -0.30341 | 6.6252
104 | 0.047244 | 0.011978 | -0.047228 | -0.011969 | 1.5656e-05 | 9.0855e-06 | 0.07148 | 0.071481 | 0.071481 | 0.98416 | -0.30341 | 0.9838 | -0.31031 | 6.5458
105 | 0.045421 | 0.011516 | -0.045406 | -0.011508 | 1.4464e-05 | 8.3247e-06 | 0.068747 | 0.068747 | 0.068747 | 0.9838 | -0.31031 | 0.98346 | -0.31694 | 6.2956
106 | 0.044136 | 0.01119 | -0.044116 | -0.011178 | 2.0129e-05 | 1.151e-05 | 0.066826 | 0.066826 | 0.066826 | 0.98346 | -0.31694 | 0.98297 | -0.32643 | 6.1196
107 | 0.00034871 | 8.7014e-05 | -0.00034871 | -8.7395e-05 | 3.159e-09 | -3.8129e-07 | 0.00052774 | 0.00052788 | 0.00052788 | 0.98297 | -0.32643 | 0.98296 | -0.32662 | 0.14502
108 | 0.0058433 | 0.0014644 | -0.005843 | -0.0014644 | 2.7472e-07 | 5.3571e-08 | 0.0087802 | 0.0087803 | 0.0087803 | 0.99028 | -0.18651 | 0.99023 | -0.18749 | 2.4122
109 | 0.0040727 | 0.0010206 | -0.0040725 | -0.0010207 | 2.4076e-07 | -6.645e-08 | 0.0061197 | 0.0061198 | 0.0061198 | 0.99028 | -0.18651 | 0.99021 | -0.18775 | 1.6813
110 | 0.013431 | 0.0033663 | -0.013431 | -0.0033661 | 4.406e-07 | 2.449e-07 | 0.020186 | 0.020186 | 0.020186 | 0.99011 | -0.18974 | 0.99008 | -0.19043 | 5.5455
111 | 0.008987 | 0.0022528 | -0.0089849 | -0.0022518 | 2.0705e-06 | 9.4345e-07 | 0.013572 | 0.013573 | 0.013573 | 0.9853 | -0.28309 | 0.98506 | -0.28793 | 3.7287
112 | 0.0023554 | 0.00059006 | -0.0023553 | -0.00059029 | 1.1488e-07 | -2.3483e-07 | 0.0035571 | 0.0035572 | 0.0035572 | 0.9853 | -0.28309 | 0.98525 | -0.28412 | 0.97725
113 | -0.0022748 | -0.00057013 | 0.002275 | 0.00056979 | 1.6412e-07 | -3.4179e-07 | 0.0034835 | 0.0034834 | 0.0034835 | 0.97171 | -0.54703 | 0.97179 | -0.54551 | 0.95702
114 | 0.025402 | 0.0063692 | -0.025399 | -0.0063675 | 3.7416e-06 | 1.6594e-06 | 0.038897 | 0.038898 | 0.038898 | 0.97179 | -0.54551 | 0.97163 | -0.5486 | 3.5621
115 | -0.028338 | -0.0071045 | 0.028346 | 0.0071083 | 7.9423e-06 | 3.8284e-06 | 0.043392 | 0.043392 | 0.043392 | 0.97179 | -0.54551 | 0.97209 | -0.53963 | 3.9736
116 | 0.021649 | 0.0054279 | -0.021646 | -0.0054267 | 3.1195e-06 | 1.1531e-06 | 0.033156 | 0.033156 | 0.033156 | 0.97163 | -0.5486 | 0.97148 | -0.55163 | 3.0363
117 | -0.028763 | -0.0072128 | 0.028769 | 0.0072154 | 5.4076e-06 | 2.6308e-06 | 0.044031 | 0.04403 | 0.044031 | 0.97209 | -0.53963 | 0.97228 | -0.53569 | 4.0321
118 | 0.00041741 | 0.00010446 | -0.00041741 | -0.00010461 | 1.8829e-09 | -1.5128e-07 | 0.00063889 | 0.00063895 | 0.00063895 | 0.97209 | -0.53963 | 0.97208 | -0.53973 | 0.17553
119 | 0.020718 | 0.0051941 | -0.020714 | -0.0051926 | 4.1795e-06 | 1.4419e-06 | 0.031734 | 0.031735 | 0.031735 | 0.97148 | -0.55163 | 0.97126 | -0.55586 | 2.9061
120 | 0.020714 | 0.0051926 | -0.020703 | -0.0051887 | 1.1279e-05 | 3.8942e-06 | 0.031735 | 0.031736 | 0.031736 | 0.97126 | -0.55586 | 0.97069 | -0.56729 | 2.9062
121 | 0.018546 | 0.0046487 | -0.018543 | -0.004648 | 2.5133e-06 | 6.8615e-07 | 0.02843 | 0.02843 | 0.02843 | 0.97069 | -0.56729 | 0.97054 | -0.57014 | 2.6035
122 | 0.00096247 | 0.00024072 | -0.00096246 | -0.0002409 | 1.301e-08 | -1.8872e-07 | 0.0014752 | 0.0014753 | 0.0014753 | 0.97069 | -0.56729 | 0.97067 | -0.56758 | 0.4053
123 | -0.00096243 | -0.00024121 | 0.00096246 | 0.0002409 | 2.0963e-08 | -3.0403e-07 | 0.0014754 | 0.0014753 | 0.0014754 | 0.97065 | -0.56804 | 0.97067 | -0.56758 | 0.40534
124 | 0.017284 | 0.0043325 | -0.017282 | -0.0043314 | 2.2735e-06 | 1.0283e-06 | 0.0265 | 0.0265 | 0.0265 | 0.97054 | -0.57014 | 0.9704 | -0.5729 | 3.6401
125 | 0.015474 | 0.0038783 | -0.015473 | -0.003878 | 5.5244e-07 | 3.2124e-07 | 0.023728 | 0.023728 | 0.023728 | 0.9704 | -0.5729 | 0.97037 | -0.57365 | 6.5186

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.25219 | 0.06379

## res_load
| p_mw | q_mvar
0 | 0.0026583 | 0.00066622
1 | 0.00069512 | 0.00017421
2 | 0.002369 | 0.00059373
3 | 0.0025292 | 0.00063387
4 | 0.00042676 | 0.00010696
5 | 0.00036332 | 9.1058e-05
6 | 0.00037975 | 9.5173e-05
7 | 0.0068226 | 0.0017099
8 | 0.0018256 | 0.00045755
9 | 0.0053025 | 0.0013289
10 | 0.0082379 | 0.0020646
11 | 0.0017077 | 0.000428
12 | 0.0031391 | 0.00078674
13 | 0.0065694 | 0.0016464
14 | 0.001197 | 0.0003
15 | 0.0028201 | 0.00070679
16 | 0.0014812 | 0.00037123
17 | 0.0015718 | 0.00039394
18 | 0.0022112 | 0.00055417
19 | 0.0017674 | 0.00044296
20 | 0.00098863 | 0.00024777
21 | 0.0013679 | 0.00034283
22 | 0.0011769 | 0.00029495
23 | 0.00099893 | 0.00025036
24 | 0.0012942 | 0.00032435
25 | 0.00093707 | 0.00023485
26 | 0.0017601 | 0.00044113
27 | 0.0028247 | 0.00070793
28 | 0.0014542 | 0.00036446
29 | 0.0056092 | 0.0014058
30 | 0.0011696 | 0.00029312
31 | 0.0014933 | 0.00037425
32 | 0.00098797 | 0.00024761
33 | 0.00094923 | 0.0002379
34 | 0.0048935 | 0.0012264
35 | 0.0011704 | 0.00029332
36 | 0.0043057 | 0.0010791
37 | 0.0015097 | 0.00037838
38 | 0.0014214 | 0.00035624
39 | 0.0014028 | 0.00035159
40 | 0.0043692 | 0.001095
41 | 0.0012333 | 0.00030909
42 | 0.0061489 | 0.0015411
43 | 0.0033901 | 0.00084965
44 | 0.00036302 | 9.098e-05
45 | 0.00066664 | 0.00016708
46 | 0.00037973 | 9.517e-05
47 | 0.0024946 | 0.0006252
48 | 0.0029258 | 0.00073328
49 | 0.0020971 | 0.00052557
50 | 0.0094 | 0.0023559
51 | 0.00071929 | 0.00018027
52 | 0.00085143 | 0.00021339
53 | 0.0063676 | 0.0015959
54 | 0.0036339 | 0.00091075
55 | 0.00075076 | 0.00018816
56 | 0.0010852 | 0.00027198
57 | 0.00042037 | 0.00010535
58 | 0.0010831 | 0.00027145
59 | 0.00050254 | 0.00012595
60 | 0.00094963 | 0.000238
61 | 0.0021096 | 0.00052872
62 | 0.00049585 | 0.00012427
63 | 0.00044866 | 0.00011244
64 | 0.0023776 | 0.00059587
65 | 0.0063076 | 0.0015808
66 | 0.0066189 | 0.0016589
67 | 0.001899 | 0.00047594
68 | 0.0059955 | 0.0015026
69 | 0.002929 | 0.00073408
70 | 0.0024469 | 0.00061326
71 | 0.0014465 | 0.00036253
72 | 0.00097868 | 0.00024528
73 | 0.0005735 | 0.00014373
74 | 0.0018072 | 0.00045293
75 | 0.0012701 | 0.00031831
76 | 0.00034871 | 8.7395e-05
77 | 0.001004 | 0.00025162
78 | 0.0032226 | 0.00080765
79 | 0.005843 | 0.0014644
80 | 0.0040725 | 0.0010207
81 | 0.013431 | 0.0033661
82 | 0.0022748 | 0.00057013
83 | 0.00066042 | 0.00016552
84 | 0.0037493 | 0.00093967
85 | 0.00041741 | 0.00010461
86 | 0.00092821 | 0.00023263
87 | 0.00041507 | 0.00010403
88 | 0.0011944 | 0.00029934
89 | 0.00096243 | 0.00024121
90 | 0.0012589 | 0.00031552
91 | 0.001808 | 0.00045312
92 | 0.015473 | 0.003878
93 | 0.0089849 | 0.0022518
94 | 0.0023553 | 0.00059029

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1