## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1349-7_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1349-7_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1349-7_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1349-7_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1349-7_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1349-7_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1349-7_0_5_node_24 | 0.4 | n |  | TRUE
7 | bus_LV_1349-7_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1349-7_0_5_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1349-7_0_5_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_1349-7_0_5_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_1349-7_0_5_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_1349-7_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1349-7_0_5_node_122 | 0.4 | n |  | TRUE
14 | bus_LV_1349-7_0_5_node_123 | 0.4 | n |  | TRUE
15 | bus_LV_1349-7_0_5_node_17 | 0.4 | n |  | TRUE
16 | bus_LV_1349-7_0_5_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1349-7_0_5_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1349-7_0_5_node_109 | 0.4 | n |  | TRUE
19 | bus_LV_1349-7_0_5_node_111 | 0.4 | n |  | TRUE
20 | bus_LV_1349-7_0_5_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1349-7_0_5_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1349-7_0_5_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1349-7_0_5_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1349-7_0_5_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1349-7_0_5_node_110 | 0.4 | n |  | TRUE
26 | bus_LV_1349-7_0_5_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_1349-7_0_5_node_96 | 0.4 | n |  | TRUE
28 | bus_LV_1349-7_0_5_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_1349-7_0_5_node_95 | 0.4 | n |  | TRUE
30 | bus_LV_1349-7_0_5_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_1349-7_0_5_node_67 | 0.4 | n |  | TRUE
32 | bus_LV_1349-7_0_5_node_66 | 0.4 | n |  | TRUE
33 | bus_LV_1349-7_0_5_node_68 | 0.4 | n |  | TRUE
34 | bus_LV_1349-7_0_5_node_64 | 0.4 | n |  | TRUE
35 | bus_LV_1349-7_0_5_node_124 | 0.4 | n |  | TRUE
36 | bus_LV_1349-7_0_5_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_1349-7_0_5_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_1349-7_0_5_node_74 | 0.4 | n |  | TRUE
39 | bus_LV_1349-7_0_5_node_70 | 0.4 | n |  | TRUE
40 | bus_LV_1349-7_0_5_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_1349-7_0_5_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_1349-7_0_5_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_1349-7_0_5_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_1349-7_0_5_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_1349-7_0_5_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_1349-7_0_5_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_1349-7_0_5_node_118 | 0.4 | n |  | TRUE
48 | bus_LV_1349-7_0_5_node_32 | 0.4 | n |  | TRUE
49 | bus_LV_1349-7_0_5_node_119 | 0.4 | n |  | TRUE
50 | bus_LV_1349-7_0_5_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_1349-7_0_5_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_1349-7_0_5_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_1349-7_0_5_node_37 | 0.4 | n |  | TRUE
54 | bus_LV_1349-7_0_5_node_63 | 0.4 | n |  | TRUE
55 | bus_LV_1349-7_0_5_node_65 | 0.4 | n |  | TRUE
56 | bus_LV_1349-7_0_5_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_1349-7_0_5_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_1349-7_0_5_node_55 | 0.4 | n |  | TRUE
59 | bus_LV_1349-7_0_5_node_41 | 0.4 | n |  | TRUE
60 | bus_LV_1349-7_0_5_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_1349-7_0_5_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_1349-7_0_5_node_42 | 0.4 | n |  | TRUE
63 | bus_LV_1349-7_0_5_node_43 | 0.4 | n |  | TRUE
64 | bus_LV_1349-7_0_5_node_121 | 0.4 | n |  | TRUE
65 | bus_LV_1349-7_0_5_node_45 | 0.4 | n |  | TRUE
66 | bus_LV_1349-7_0_5_node_115 | 0.4 | n |  | TRUE
67 | bus_LV_1349-7_0_5_node_46 | 0.4 | n |  | TRUE
68 | bus_LV_1349-7_0_5_node_47 | 0.4 | n |  | TRUE
69 | bus_LV_1349-7_0_5_node_53 | 0.4 | n |  | TRUE
70 | bus_LV_1349-7_0_5_node_48 | 0.4 | n |  | TRUE
71 | bus_LV_1349-7_0_5_node_50 | 0.4 | n |  | TRUE
72 | bus_LV_1349-7_0_5_node_49 | 0.4 | n |  | TRUE
73 | bus_LV_1349-7_0_5_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_1349-7_0_5_node_108 | 0.4 | n |  | TRUE
75 | bus_LV_1349-7_0_5_node_57 | 0.4 | n |  | TRUE
76 | bus_LV_1349-7_0_5_node_58 | 0.4 | n |  | TRUE
77 | bus_LV_1349-7_0_5_node_116 | 0.4 | n |  | TRUE
78 | bus_LV_1349-7_0_5_node_114 | 0.4 | n |  | TRUE
79 | bus_LV_1349-7_0_5_node_52 | 0.4 | n |  | TRUE
80 | bus_LV_1349-7_0_5_node_54 | 0.4 | n |  | TRUE
81 | bus_LV_1349-7_0_5_node_56 | 0.4 | n |  | TRUE
82 | bus_LV_1349-7_0_5_node_61 | 0.4 | n |  | TRUE
83 | bus_LV_1349-7_0_5_node_62 | 0.4 | n |  | TRUE
84 | bus_LV_1349-7_0_5_node_59 | 0.4 | n |  | TRUE
85 | bus_LV_1349-7_0_5_node_60 | 0.4 | n |  | TRUE
86 | bus_LV_1349-7_0_5_node_79 | 0.4 | n |  | TRUE
87 | bus_LV_1349-7_0_5_node_80 | 0.4 | n |  | TRUE
88 | bus_LV_1349-7_0_5_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_1349-7_0_5_node_72 | 0.4 | n |  | TRUE
90 | bus_LV_1349-7_0_5_node_69 | 0.4 | n |  | TRUE
91 | bus_LV_1349-7_0_5_node_73 | 0.4 | n |  | TRUE
92 | bus_LV_1349-7_0_5_node_75 | 0.4 | n |  | TRUE
93 | bus_LV_1349-7_0_5_node_76 | 0.4 | n |  | TRUE
94 | bus_LV_1349-7_0_5_node_77 | 0.4 | n |  | TRUE
95 | bus_LV_1349-7_0_5_node_78 | 0.4 | n |  | TRUE
96 | bus_LV_1349-7_0_5_node_83 | 0.4 | n |  | TRUE
97 | bus_LV_1349-7_0_5_node_84 | 0.4 | n |  | TRUE
98 | bus_LV_1349-7_0_5_node_82 | 0.4 | n |  | TRUE
99 | bus_LV_1349-7_0_5_node_107 | 0.4 | n |  | TRUE
100 | bus_LV_1349-7_0_5_node_106 | 0.4 | n |  | TRUE
101 | bus_LV_1349-7_0_5_node_81 | 0.4 | n |  | TRUE
102 | bus_LV_1349-7_0_5_node_85 | 0.4 | n |  | TRUE
103 | bus_LV_1349-7_0_5_node_86 | 0.4 | n |  | TRUE
104 | bus_LV_1349-7_0_5_node_87 | 0.4 | n |  | TRUE
105 | bus_LV_1349-7_0_5_node_94 | 0.4 | n |  | TRUE
106 | bus_LV_1349-7_0_5_node_93 | 0.4 | n |  | TRUE
107 | bus_LV_1349-7_0_5_node_99 | 0.4 | n |  | TRUE
108 | bus_LV_1349-7_0_5_node_91 | 0.4 | n |  | TRUE
109 | bus_LV_1349-7_0_5_node_88 | 0.4 | n |  | TRUE
110 | bus_LV_1349-7_0_5_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_1349-7_0_5_node_90 | 0.4 | n |  | TRUE
112 | bus_LV_1349-7_0_5_node_92 | 0.4 | n |  | TRUE
113 | bus_LV_1349-7_0_5_node_103 | 0.4 | n |  | TRUE
114 | bus_LV_1349-7_0_5_node_105 | 0.4 | n |  | TRUE
115 | bus_LV_1349-7_0_5_node_98 | 0.4 | n |  | TRUE
116 | bus_LV_1349-7_0_5_node_97 | 0.4 | n |  | TRUE
117 | bus_LV_1349-7_0_5_node_100 | 0.4 | n |  | TRUE
118 | bus_LV_1349-7_0_5_node_101 | 0.4 | n |  | TRUE
119 | bus_LV_1349-7_0_5_node_102 | 0.4 | n |  | TRUE
120 | bus_LV_1349-7_0_5_node_104 | 0.4 | n |  | TRUE
121 | bus_LV_1349-7_0_5_node_112 | 0.4 | n |  | TRUE
122 | bus_LV_1349-7_0_5_node_113 | 0.4 | n |  | TRUE
123 | bus_LV_1349-7_0_5_node_120 | 0.4 | n |  | TRUE
124 | bus_MV_19_0_node_131 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1349-7_0_5_load_0 | 0 | 0.021175 | 0.0053069 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1349-7_0_5_load_24 | 6 | 0.0187 | 0.0046867 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1349-7_0_5_load_7 | 7 | 0.0074204 | 0.0018597 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1349-7_0_5_load_6 | 8 | 0.0019977 | 0.00050068 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1349-7_0_5_load_16 | 10 | 0.015278 | 0.0038291 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1349-7_0_5_load_25 | 11 | 0.01869 | 0.0046841 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1349-7_0_5_load_122 | 13 | 0.018728 | 0.0046938 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1349-7_0_5_load_9 | 16 | 0.0029746 | 0.0007455 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1349-7_0_5_load_10 | 17 | 0.0026156 | 0.00065553 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1349-7_0_5_load_109 | 18 | 0.0019891 | 0.00049851 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1349-7_0_5_load_111 | 19 | 0.0011752 | 0.00029453 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1349-7_0_5_load_11 | 20 | 0.0027227 | 0.00068238 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1349-7_0_5_load_12 | 21 | 0.0031089 | 0.00077917 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1349-7_0_5_load_14 | 23 | 0.0026044 | 0.00065272 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1349-7_0_5_load_110 | 25 | 0.0050817 | 0.0012736 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1349-7_0_5_load_21 | 26 | 0.0020032 | 0.00050204 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1349-7_0_5_load_96 | 27 | 0.0021158 | 0.00053027 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1349-7_0_5_load_20 | 28 | 0.0021937 | 0.0005498 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1349-7_0_5_load_95 | 29 | 0.0020786 | 0.00052093 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1349-7_0_5_load_67 | 31 | 0.0020019 | 0.00050172 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1349-7_0_5_load_66 | 32 | 0.0026896 | 0.00067409 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1349-7_0_5_load_68 | 33 | 0.0063347 | 0.0015876 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1349-7_0_5_load_64 | 34 | 0.001501 | 0.00037619 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1349-7_0_5_load_124 | 35 | 0.018729 | 0.004694 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1349-7_0_5_load_22 | 36 | 0.0048405 | 0.0012132 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1349-7_0_5_load_23 | 37 | 0.0030758 | 0.00077087 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1349-7_0_5_load_74 | 38 | 0.0050923 | 0.0012763 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1349-7_0_5_load_70 | 39 | 0.0058183 | 0.0014582 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1349-7_0_5_load_26 | 40 | 0.0071506 | 0.0017921 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1349-7_0_5_load_27 | 41 | 0.0025311 | 0.00063435 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1349-7_0_5_load_30 | 44 | 0.028344 | 0.0071038 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1349-7_0_5_load_33 | 46 | 0.0045977 | 0.0011523 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1349-7_0_5_load_118 | 47 | 0.0033067 | 0.00082874 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1349-7_0_5_load_32 | 48 | 0.018568 | 0.0046537 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1349-7_0_5_load_35 | 51 | 0.0031659 | 0.00079345 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1349-7_0_5_load_36 | 52 | 0.0015682 | 0.00039302 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1349-7_0_5_load_37 | 53 | 0.0023338 | 0.0005849 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1349-7_0_5_load_65 | 55 | 0.0033089 | 0.00082929 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1349-7_0_5_load_38 | 56 | 0.0020785 | 0.00052093 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1349-7_0_5_load_55 | 58 | 0.001831 | 0.00045888 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1349-7_0_5_load_39 | 60 | 0.0018983 | 0.00047576 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1349-7_0_5_load_40 | 61 | 0.0095233 | 0.0023868 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1349-7_0_5_load_42 | 62 | 0.011519 | 0.0028869 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1349-7_0_5_load_43 | 63 | 0.010874 | 0.0027254 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1349-7_0_5_load_121 | 64 | 0.0014585 | 0.00036554 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1349-7_0_5_load_115 | 66 | 0.0013397 | 0.00033576 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1349-7_0_5_load_46 | 67 | 0.0012245 | 0.0003069 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1349-7_0_5_load_47 | 68 | 0.0015266 | 0.0003826 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1349-7_0_5_load_53 | 69 | 0.0015266 | 0.00038259 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1349-7_0_5_load_48 | 70 | 0.0015778 | 0.00039544 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1349-7_0_5_load_49 | 72 | 0.0040357 | 0.0010114 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1349-7_0_5_load_51 | 73 | 0.0024048 | 0.00060269 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1349-7_0_5_load_108 | 74 | 0.0097958 | 0.0024551 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1349-7_0_5_load_57 | 75 | 0.0012158 | 0.00030472 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1349-7_0_5_load_58 | 76 | 0.0018638 | 0.00046712 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1349-7_0_5_load_116 | 77 | 0.0075996 | 0.0019046 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1349-7_0_5_load_114 | 78 | 0.0032469 | 0.00081374 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1349-7_0_5_load_52 | 79 | 0.0065805 | 0.0016492 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1349-7_0_5_load_54 | 80 | 0.0049671 | 0.0012449 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1349-7_0_5_load_56 | 81 | 0.0032574 | 0.00081639 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1349-7_0_5_load_61 | 82 | 0.0038577 | 0.00096683 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1349-7_0_5_load_62 | 83 | 0.002872 | 0.0007198 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1349-7_0_5_load_59 | 84 | 0.0022454 | 0.00056274 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1349-7_0_5_load_60 | 85 | 0.0016405 | 0.00041116 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1349-7_0_5_load_79 | 86 | 0.00095964 | 0.00024051 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1349-7_0_5_load_80 | 87 | 0.0020801 | 0.00052131 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1349-7_0_5_load_71 | 88 | 0.0046616 | 0.0011683 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1349-7_0_5_load_72 | 89 | 0.0061012 | 0.0015291 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1349-7_0_5_load_69 | 90 | 0.0028179 | 0.00070623 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1349-7_0_5_load_73 | 91 | 0.0042176 | 0.001057 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1349-7_0_5_load_75 | 92 | 0.0028873 | 0.00072363 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1349-7_0_5_load_76 | 93 | 0.0046908 | 0.0011756 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1349-7_0_5_load_77 | 94 | 0.0024701 | 0.00061906 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1349-7_0_5_load_78 | 95 | 0.0029631 | 0.00074263 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1349-7_0_5_load_84 | 97 | 0.0044536 | 0.0011162 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1349-7_0_5_load_82 | 98 | 0.0029015 | 0.00072717 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1349-7_0_5_load_107 | 99 | 0.003613 | 0.0009055 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1349-7_0_5_load_106 | 100 | 0.0023816 | 0.00059689 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1349-7_0_5_load_81 | 101 | 0.0030304 | 0.0007595 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1349-7_0_5_load_85 | 102 | 0.0024565 | 0.00061565 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1349-7_0_5_load_86 | 103 | 0.0036806 | 0.00092245 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1349-7_0_5_load_94 | 105 | 0.003643 | 0.00091303 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1349-7_0_5_load_93 | 106 | 0.0011288 | 0.0002829 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1349-7_0_5_load_99 | 107 | 0.001988 | 0.00049825 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1349-7_0_5_load_91 | 108 | 0.00097892 | 0.00024534 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1349-7_0_5_load_88 | 109 | 0.0018084 | 0.00045323 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1349-7_0_5_load_89 | 110 | 0.0013298 | 0.00033329 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1349-7_0_5_load_90 | 111 | 0.0016248 | 0.0004072 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1349-7_0_5_load_103 | 113 | 0.002228 | 0.00055838 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1349-7_0_5_load_105 | 114 | 0.0027626 | 0.00069236 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1349-7_0_5_load_98 | 115 | 0.0029367 | 0.00073601 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1349-7_0_5_load_100 | 117 | 0.0043426 | 0.0010883 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1349-7_0_5_load_102 | 119 | 0.0030096 | 0.00075428 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1349-7_0_5_load_104 | 120 | 0.0017727 | 0.00044427 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1349-7_0_5_load_112 | 121 | 0.0038092 | 0.00095469 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1349-7_0_5_load_113 | 122 | 0.006997 | 0.0017536 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1349-7_0_5_load_120 | 123 | 0.026499 | 0.0066414 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1349-7_0_5_line_0 |  | 0 | 1 | 0.027566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1349-7_0_5_line_1 |  | 0 | 2 | 0.021619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1349-7_0_5_line_2 |  | 1 | 3 | 0.029091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1349-7_0_5_line_3 |  | 2 | 4 | 0.02031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1349-7_0_5_line_4 |  | 2 | 5 | 0.037245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1349-7_0_5_line_5 |  | 3 | 7 | 0.023278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1349-7_0_5_line_6 |  | 3 | 8 | 0.012414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1349-7_0_5_line_7 |  | 4 | 6 | 0.047493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1349-7_0_5_line_8 |  | 5 | 9 | 0.018233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1349-7_0_5_line_9 |  | 5 | 10 | 0.001658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1349-7_0_5_line_10 |  | 6 | 11 | 0.024785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1349-7_0_5_line_11 |  | 7 | 12 | 0.01883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1349-7_0_5_line_12 |  | 9 | 13 | 0.004536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1349-7_0_5_line_13 |  | 9 | 14 | 0.024162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1349-7_0_5_line_14 |  | 10 | 15 | 0.026396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1349-7_0_5_line_15 |  | 12 | 16 | 0.015116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1349-7_0_5_line_16 |  | 12 | 17 | 0.037558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1349-7_0_5_line_17 |  | 14 | 35 | 0.004941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1349-7_0_5_line_18 |  | 15 | 30 | 0.024695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1349-7_0_5_line_19 |  | 16 | 18 | 0.013339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1349-7_0_5_line_20 |  | 17 | 19 | 0.025509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1349-7_0_5_line_21 |  | 20 | 21 | 0.02129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1349-7_0_5_line_22 |  | 20 | 22 | 0.018475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1349-7_0_5_line_23 |  | 21 | 23 | 0.019899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1349-7_0_5_line_24 |  | 22 | 24 | 0.0223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1349-7_0_5_line_25 |  | 23 | 25 | 0.0033986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1349-7_0_5_line_26 |  | 24 | 26 | 0.024854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1349-7_0_5_line_27 |  | 24 | 27 | 0.021618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_1349-7_0_5_line_28 |  | 26 | 28 | 0.00085034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1349-7_0_5_line_29 |  | 27 | 29 | 0.0091112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_1349-7_0_5_line_30 |  | 28 | 36 | 0.0082782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_1349-7_0_5_line_31 |  | 29 | 116 | 0.017645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_1349-7_0_5_line_32 |  | 30 | 31 | 0.004039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1349-7_0_5_line_33 |  | 30 | 32 | 0.015735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1349-7_0_5_line_34 |  | 31 | 33 | 0.021335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_1349-7_0_5_line_35 |  | 32 | 34 | 0.015712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1349-7_0_5_line_36 |  | 33 | 90 | 0.016783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_1349-7_0_5_line_37 |  | 34 | 54 | 0.0085363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1349-7_0_5_line_38 |  | 36 | 37 | 0.014833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_1349-7_0_5_line_39 |  | 37 | 38 | 0.019142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_1349-7_0_5_line_40 |  | 38 | 39 | 0.016518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_1349-7_0_5_line_41 |  | 39 | 90 | 0.018405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_1349-7_0_5_line_42 |  | 40 | 41 | 0.0055045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1349-7_0_5_line_43 |  | 40 | 42 | 0.005297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1349-7_0_5_line_44 |  | 41 | 43 | 0.011599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1349-7_0_5_line_45 |  | 42 | 44 | 0.009748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1349-7_0_5_line_46 |  | 42 | 45 | 0.03125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1349-7_0_5_line_47 |  | 43 | 46 | 0.0045856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1349-7_0_5_line_48 |  | 45 | 47 | 0.010731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1349-7_0_5_line_49 |  | 46 | 48 | 0.0090736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1349-7_0_5_line_50 |  | 47 | 49 | 0.011151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1349-7_0_5_line_51 |  | 48 | 50 | 0.010774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1349-7_0_5_line_52 |  | 49 | 123 | 0.015457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1349-7_0_5_line_53 |  | 50 | 51 | 0.011734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1349-7_0_5_line_54 |  | 50 | 52 | 0.020449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1349-7_0_5_line_55 |  | 51 | 53 | 0.00038408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1349-7_0_5_line_56 |  | 52 | 54 | 0.0085664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1349-7_0_5_line_57 |  | 54 | 55 | 0.023485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1349-7_0_5_line_58 |  | 56 | 57 | 0.014328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1349-7_0_5_line_59 |  | 57 | 58 | 0.016426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_1349-7_0_5_line_60 |  | 57 | 59 | 0.021506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_1349-7_0_5_line_61 |  | 58 | 69 | 0.025168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_1349-7_0_5_line_62 |  | 59 | 63 | 0.0047692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1349-7_0_5_line_63 |  | 59 | 60 | 0.012455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_1349-7_0_5_line_64 |  | 60 | 61 | 0.015402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_1349-7_0_5_line_65 |  | 61 | 62 | 0.021515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_1349-7_0_5_line_66 |  | 62 | 64 | 0.0054795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_1349-7_0_5_line_67 |  | 63 | 65 | 0.018847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1349-7_0_5_line_68 |  | 64 | 66 | 0.31451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_1349-7_0_5_line_69 |  | 65 | 67 | 0.012508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1349-7_0_5_line_70 |  | 65 | 68 | 0.0060615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1349-7_0_5_line_71 |  | 66 | 122 | 0.036187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_1349-7_0_5_line_72 |  | 67 | 70 | 0.024277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1349-7_0_5_line_73 |  | 68 | 71 | 0.087122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1349-7_0_5_line_74 |  | 69 | 79 | 0.0035544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_1349-7_0_5_line_75 |  | 70 | 72 | 0.0077775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1349-7_0_5_line_76 |  | 71 | 73 | 0.015758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1349-7_0_5_line_77 |  | 72 | 75 | 0.013372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1349-7_0_5_line_78 |  | 73 | 74 | 0.031899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1349-7_0_5_line_79 |  | 75 | 76 | 0.012379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1349-7_0_5_line_80 |  | 76 | 84 | 0.014602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1349-7_0_5_line_81 |  | 77 | 78 | 0.0078489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1349-7_0_5_line_82 |  | 78 | 121 | 0.0066922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1349-7_0_5_line_83 |  | 79 | 80 | 0.02256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_1349-7_0_5_line_84 |  | 80 | 81 | 0.0081314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_1349-7_0_5_line_85 |  | 81 | 82 | 0.015126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_1349-7_0_5_line_86 |  | 82 | 83 | 0.010031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_1349-7_0_5_line_87 |  | 83 | 88 | 0.0148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_1349-7_0_5_line_88 |  | 84 | 85 | 0.015525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1349-7_0_5_line_89 |  | 85 | 86 | 0.026136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1349-7_0_5_line_90 |  | 86 | 87 | 0.021803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1349-7_0_5_line_91 |  | 88 | 89 | 0.0090132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
92 | LV_1349-7_0_5_line_92 |  | 89 | 91 | 0.0094704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_1349-7_0_5_line_93 |  | 91 | 92 | 0.011535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_1349-7_0_5_line_94 |  | 92 | 93 | 0.0061233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_1349-7_0_5_line_95 |  | 93 | 94 | 0.016484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_1349-7_0_5_line_96 |  | 94 | 95 | 0.00072595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_1349-7_0_5_line_97 |  | 95 | 96 | 0.01454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_1349-7_0_5_line_98 |  | 96 | 97 | 0.0015469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_1349-7_0_5_line_99 |  | 96 | 98 | 0.043058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1349-7_0_5_line_100 |  | 97 | 102 | 0.012685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_1349-7_0_5_line_101 |  | 98 | 101 | 0.001037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1349-7_0_5_line_102 |  | 99 | 100 | 0.030208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1349-7_0_5_line_103 |  | 100 | 112 | 0.077832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1349-7_0_5_line_104 |  | 102 | 103 | 0.0030876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_1349-7_0_5_line_105 |  | 103 | 104 | 0.024155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_1349-7_0_5_line_106 |  | 104 | 105 | 0.0036345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_1349-7_0_5_line_107 |  | 104 | 106 | 0.0075992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1349-7_0_5_line_108 |  | 105 | 107 | 0.015426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_1349-7_0_5_line_109 |  | 106 | 108 | 0.030389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1349-7_0_5_line_110 |  | 107 | 115 | 0.0087429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_1349-7_0_5_line_111 |  | 108 | 110 | 0.01426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1349-7_0_5_line_112 |  | 109 | 110 | 0.0024972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1349-7_0_5_line_113 |  | 109 | 111 | 0.027636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1349-7_0_5_line_114 |  | 111 | 112 | 0.016131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1349-7_0_5_line_115 |  | 112 | 113 | 0.012628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1349-7_0_5_line_116 |  | 113 | 114 | 0.023018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1349-7_0_5_line_117 |  | 114 | 120 | 0.0045262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1349-7_0_5_line_118 |  | 115 | 116 | 0.023687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_1349-7_0_5_line_119 |  | 117 | 118 | 0.036308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1349-7_0_5_line_120 |  | 118 | 119 | 0.015324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1349-7_0_5_line_121 |  | 119 | 120 | 0.023798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1349-7_0_5_line_122 |  | 121 | 122 | 0.0051667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1349-7_0_5_trafo_18 | 0.63 MVA 20/0.4 kV | 124 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2710500.7023 | 1227533.0643 | 2710503.3073 | 1227528.3091 | 2710484.0389 | 1227517.3958
1 | 2710464.7752 | 1227512.9374 | 2710471.5399 | 1227510.3166 | 2710484.0389 | 1227517.3958
2 | 2710500.7023 | 1227533.0643 | 2710515.9015 | 1227541.1639 | 2710527.3661 | 1227544.2348
3 | 2710473.4735 | 1227526.5982 | 2710467.498 | 1227524.2744 | 2710469.7481 | 1227520.669 | 2710465.3252 | 1227516.3836 | 2710464.7752 | 1227512.9374
4 | 2710435.5374 | 1227508.5135 | 2710449.695 | 1227515.9709 | 2710454.6193 | 1227507.5559 | 2710464.7752 | 1227512.9374
5 | 2710527.3661 | 1227544.2348 | 2710537.3874 | 1227543.3981 | 2710549.1809 | 1227537.4202
6 | 2710527.3661 | 1227544.2348 | 2710529.6254 | 1227556.4416
7 | 2710473.4735 | 1227526.5982 | 2710450.7686 | 1227568.3123
8 | 2710435.5374 | 1227508.5135 | 2710427.0435 | 1227524.657
9 | 2710435.5374 | 1227508.5135 | 2710434.0707 | 1227507.7404
10 | 2710438.9199 | 1227590.0812 | 2710450.7686 | 1227568.3123
11 | 2710565.9761 | 1227528.9072 | 2710549.1809 | 1227537.4202
12 | 2710427.0435 | 1227524.657 | 2710422.9648 | 1227522.6465
13 | 2710415.6413 | 1227545.9727 | 2710427.0435 | 1227524.657
14 | 2710410.7205 | 1227495.4319 | 2710434.0707 | 1227507.7404
15 | 2710565.9761 | 1227528.9072 | 2710559.7895 | 1227515.1151
16 | 2710565.9761 | 1227528.9072 | 2710595.5063 | 1227513.9335 | 2710599.6359 | 1227512.2806
17 | 2710415.6413 | 1227545.9727 | 2710411.3749 | 1227543.4583
18 | 2710389.3388 | 1227483.0813 | 2710394.2432 | 1227486.7529 | 2710410.7205 | 1227495.4319
19 | 2710547.5394 | 1227511.0732 | 2710556.4602 | 1227512.3511 | 2710559.7895 | 1227515.1151
20 | 2710599.6359 | 1227512.2806 | 2710623.3179 | 1227502.8017
21 | 2710543.6243 | 1227467.4227 | 2710555.954 | 1227467.8301 | 2710564.5533 | 1227465.338
22 | 2710525.1594 | 1227466.8127 | 2710543.6243 | 1227467.4227
23 | 2710564.5533 | 1227465.338 | 2710567.3478 | 1227464.5282 | 2710583.0541 | 1227458.0507
24 | 2710529.2585 | 1227444.8944 | 2710525.1594 | 1227466.8127
25 | 2710583.0541 | 1227458.0507 | 2710586.196 | 1227456.755
26 | 2710529.2585 | 1227444.8944 | 2710505.2815 | 1227451.4382
27 | 2710529.2585 | 1227444.8944 | 2710531.6836 | 1227423.4125
28 | 2710505.2815 | 1227451.4382 | 2710504.4612 | 1227451.6621
29 | 2710532.7057 | 1227414.3588 | 2710531.6836 | 1227423.4125
30 | 2710504.4612 | 1227451.6621 | 2710496.4751 | 1227453.8417
31 | 2710534.6851 | 1227396.8254 | 2710532.7057 | 1227414.3588
32 | 2710389.3388 | 1227483.0813 | 2710393.2353 | 1227482.0179
33 | 2710389.3388 | 1227483.0813 | 2710373.9151 | 1227486.1951
34 | 2710393.2353 | 1227482.0179 | 2710413.8178 | 1227476.4005
35 | 2710358.514 | 1227489.3044 | 2710373.9151 | 1227486.1951
36 | 2710413.8178 | 1227476.4005 | 2710430.0087 | 1227471.9817
37 | 2710350.1466 | 1227490.9936 | 2710358.514 | 1227489.3044
38 | 2710482.1657 | 1227457.747 | 2710496.4751 | 1227453.8417
39 | 2710463.699 | 1227462.7869 | 2710482.1657 | 1227457.747
40 | 2710447.7642 | 1227467.1358 | 2710463.699 | 1227462.7869
41 | 2710430.0087 | 1227471.9817 | 2710447.7642 | 1227467.1358
42 | 2710334.8339 | 1227536.8081 | 2710332.612 | 1227531.772
43 | 2710336.972 | 1227541.6544 | 2710334.8339 | 1227536.8081
44 | 2710327.9303 | 1227521.1601 | 2710332.612 | 1227531.772
45 | 2710336.972 | 1227541.6544 | 2710346.0517 | 1227538.0423
46 | 2710336.972 | 1227541.6544 | 2710344.5424 | 1227558.919 | 2710345.4936 | 1227561.1717 | 2710349.4934 | 1227570.2862
47 | 2710327.9303 | 1227521.1601 | 2710326.2177 | 1227516.9062
48 | 2710349.4934 | 1227570.2862 | 2710353.749 | 1227580.1372
49 | 2710322.829 | 1227508.4892 | 2710326.2177 | 1227516.9062
50 | 2710358.1711 | 1227590.3735 | 2710353.749 | 1227580.1372
51 | 2710321.9291 | 1227497.7532 | 2710322.829 | 1227508.4892
52 | 2710358.1711 | 1227590.3735 | 2710372.7971 | 1227585.252
53 | 2710321.9291 | 1227497.7532 | 2710316.2635 | 1227493.4338 | 2710314.2621 | 1227489.2809
54 | 2710321.9291 | 1227497.7532 | 2710341.8158 | 1227492.9893
55 | 2710314.0954 | 1227488.9349 | 2710314.2621 | 1227489.2809
56 | 2710350.1466 | 1227490.9936 | 2710341.8158 | 1227492.9893
57 | 2710350.1466 | 1227490.9936 | 2710352.0413 | 1227498.768 | 2710358.2149 | 1227512.9675
58 | 2710296.9062 | 1227453.2666 | 2710303.1264 | 1227466.1739
59 | 2710296.9062 | 1227453.2666 | 2710312.4377 | 1227447.9212
60 | 2710296.9062 | 1227453.2666 | 2710287.5095 | 1227433.9111
61 | 2710336.2356 | 1227439.7306 | 2710312.4377 | 1227447.9212
62 | 2710287.5095 | 1227433.9111 | 2710285.4029 | 1227429.6324
63 | 2710287.5095 | 1227433.9111 | 2710276.2688 | 1227438.7731 | 2710276.076 | 1227438.8498
64 | 2710276.076 | 1227438.8498 | 2710268.2275 | 1227441.9709 | 2710261.8686 | 1227444.7886
65 | 2710261.8686 | 1227444.7886 | 2710261.8686 | 1227444.7886 | 2710259.5496 | 1227456.6101 | 2710250.7052 | 1227459.9889
66 | 2710245.5865 | 1227461.9443 | 2710250.7052 | 1227459.9889
67 | 2710277.0779 | 1227412.7239 | 2710285.4029 | 1227429.6324
68 | 2710245.5865 | 1227461.9443 | 2709931.1417 | 1227468.4574
69 | 2710277.0779 | 1227412.7239 | 2710288.4655 | 1227407.5497
70 | 2710277.0779 | 1227412.7239 | 2710274.352 | 1227407.31
71 | 2709931.1417 | 1227468.4574 | 2709916.5488 | 1227435.3435
72 | 2710288.4655 | 1227407.5497 | 2710310.568 | 1227397.507
73 | 2710274.352 | 1227407.31 | 2710235.1712 | 1227329.4953
74 | 2710339.5965 | 1227438.5739 | 2710336.2356 | 1227439.7306
75 | 2710317.6489 | 1227394.2896 | 2710310.568 | 1227397.507
76 | 2710235.1712 | 1227329.4953 | 2710249.5119 | 1227322.9649
77 | 2710317.6489 | 1227394.2896 | 2710329.8227 | 1227388.7582
78 | 2710278.5424 | 1227309.7452 | 2710249.5119 | 1227322.9649
79 | 2710341.0927 | 1227383.6374 | 2710329.8227 | 1227388.7582
80 | 2710341.0927 | 1227383.6374 | 2710354.387 | 1227377.5969
81 | 2709908.6013 | 1227417.3092 | 2709911.7665 | 1227424.4916
82 | 2709914.4652 | 1227430.6155 | 2709911.7665 | 1227424.4916
83 | 2710339.5965 | 1227438.5739 | 2710360.9283 | 1227431.2321
84 | 2710368.6171 | 1227428.5859 | 2710360.9283 | 1227431.2321
85 | 2710368.6171 | 1227428.5859 | 2710382.9199 | 1227423.6633
86 | 2710382.9199 | 1227423.6633 | 2710392.4048 | 1227420.3989
87 | 2710406.3994 | 1227415.5824 | 2710392.4048 | 1227420.3989
88 | 2710368.5215 | 1227371.1746 | 2710354.387 | 1227377.5969
89 | 2710368.5215 | 1227371.1746 | 2710392.316 | 1227360.363
90 | 2710392.316 | 1227360.363 | 2710412.1656 | 1227351.3439
91 | 2710406.3994 | 1227415.5824 | 2710414.922 | 1227412.6492
92 | 2710423.8769 | 1227409.5672 | 2710414.922 | 1227412.6492
93 | 2710423.8769 | 1227409.5672 | 2710434.7836 | 1227405.8134
94 | 2710440.5736 | 1227403.8207 | 2710434.7836 | 1227405.8134
95 | 2710440.5736 | 1227403.8207 | 2710456.1606 | 1227398.4561
96 | 2710456.8471 | 1227398.2198 | 2710456.1606 | 1227398.4561
97 | 2710470.5953 | 1227393.4881 | 2710456.8471 | 1227398.2198
98 | 2710470.5953 | 1227393.4881 | 2710472.0576 | 1227392.9836
99 | 2710470.5953 | 1227393.4881 | 2710452.3239 | 1227354.4986
100 | 2710484.0491 | 1227388.8464 | 2710472.0576 | 1227392.9836
101 | 2710451.8838 | 1227353.5596 | 2710452.3239 | 1227354.4986
102 | 2710397.5203 | 1227260.0119 | 2710388.2304 | 1227263.9388 | 2710378.9504 | 1227264.0223 | 2710369.0834 | 1227268.5154
103 | 2710469.2706 | 1227290.1739 | 2710397.5203 | 1227260.0119
104 | 2710484.0491 | 1227388.8464 | 2710486.9679 | 1227387.8394
105 | 2710509.8018 | 1227379.9615 | 2710486.9679 | 1227387.8394
106 | 2710509.8018 | 1227379.9615 | 2710513.2653 | 1227378.86
107 | 2710509.8018 | 1227379.9615 | 2710506.6752 | 1227373.0352
108 | 2710513.2653 | 1227378.86 | 2710527.9657 | 1227374.1851
109 | 2710506.6752 | 1227373.0352 | 2710494.1721 | 1227345.3376
110 | 2710536.6173 | 1227373.2211 | 2710529.4905 | 1227373.7002 | 2710527.9657 | 1227374.1851
111 | 2710494.1721 | 1227345.3376 | 2710488.305 | 1227332.3404
112 | 2710487.2776 | 1227330.0644 | 2710488.305 | 1227332.3404
113 | 2710487.2776 | 1227330.0644 | 2710475.9072 | 1227304.876
114 | 2710469.2706 | 1227290.1739 | 2710475.9072 | 1227304.876
115 | 2710469.2706 | 1227290.1739 | 2710476.2755 | 1227288.1024 | 2710481.5361 | 1227288.9164
116 | 2710481.5361 | 1227288.9164 | 2710504.2836 | 1227292.436
117 | 2710508.7566 | 1227293.1281 | 2710504.2836 | 1227292.436
118 | 2710536.6173 | 1227373.2211 | 2710534.6851 | 1227396.8254
119 | 2710547.4176 | 1227299.1099 | 2710542.1049 | 1227335.0267
120 | 2710547.4176 | 1227299.1099 | 2710532.2743 | 1227296.7669
121 | 2710508.7566 | 1227293.1281 | 2710532.2743 | 1227296.7669
122 | 2709914.4652 | 1227430.6155 | 2709916.5488 | 1227435.3435

## bus_geodata
| x | y | coords
0 | 2710484.0389 | 1227517.3958
1 | 2710500.7023 | 1227533.0643
2 | 2710464.7752 | 1227512.9374
3 | 2710527.3661 | 1227544.2348
4 | 2710473.4735 | 1227526.5982
5 | 2710435.5374 | 1227508.5135
6 | 2710450.7686 | 1227568.3123
7 | 2710549.1809 | 1227537.4202
8 | 2710529.6254 | 1227556.4416
9 | 2710427.0435 | 1227524.657
10 | 2710434.0707 | 1227507.7404
11 | 2710438.9199 | 1227590.0812
12 | 2710565.9761 | 1227528.9072
13 | 2710422.9648 | 1227522.6465
14 | 2710415.6413 | 1227545.9727
15 | 2710410.7205 | 1227495.4319
16 | 2710559.7895 | 1227515.1151
17 | 2710599.6359 | 1227512.2806
18 | 2710547.5394 | 1227511.0732
19 | 2710623.3179 | 1227502.8017
20 | 2710543.6243 | 1227467.4227
21 | 2710564.5533 | 1227465.338
22 | 2710525.1594 | 1227466.8127
23 | 2710583.0541 | 1227458.0507
24 | 2710529.2585 | 1227444.8944
25 | 2710586.196 | 1227456.755
26 | 2710505.2815 | 1227451.4382
27 | 2710531.6836 | 1227423.4125
28 | 2710504.4612 | 1227451.6621
29 | 2710532.7057 | 1227414.3588
30 | 2710389.3388 | 1227483.0813
31 | 2710393.2353 | 1227482.0179
32 | 2710373.9151 | 1227486.1951
33 | 2710413.8178 | 1227476.4005
34 | 2710358.514 | 1227489.3044
35 | 2710411.3749 | 1227543.4583
36 | 2710496.4751 | 1227453.8417
37 | 2710482.1657 | 1227457.747
38 | 2710463.699 | 1227462.7869
39 | 2710447.7642 | 1227467.1358
40 | 2710334.8339 | 1227536.8081
41 | 2710332.612 | 1227531.772
42 | 2710336.972 | 1227541.6544
43 | 2710327.9303 | 1227521.1601
44 | 2710346.0517 | 1227538.0423
45 | 2710349.4934 | 1227570.2862
46 | 2710326.2177 | 1227516.9062
47 | 2710353.749 | 1227580.1372
48 | 2710322.829 | 1227508.4892
49 | 2710358.1711 | 1227590.3735
50 | 2710321.9291 | 1227497.7532
51 | 2710314.2621 | 1227489.2809
52 | 2710341.8158 | 1227492.9893
53 | 2710314.0954 | 1227488.9349
54 | 2710350.1466 | 1227490.9936
55 | 2710358.2149 | 1227512.9675
56 | 2710303.1264 | 1227466.1739
57 | 2710296.9062 | 1227453.2666
58 | 2710312.4377 | 1227447.9212
59 | 2710287.5095 | 1227433.9111
60 | 2710276.076 | 1227438.8498
61 | 2710261.8686 | 1227444.7886
62 | 2710250.7052 | 1227459.9889
63 | 2710285.4029 | 1227429.6324
64 | 2710245.5865 | 1227461.9443
65 | 2710277.0779 | 1227412.7239
66 | 2709931.1417 | 1227468.4574
67 | 2710288.4655 | 1227407.5497
68 | 2710274.352 | 1227407.31
69 | 2710336.2356 | 1227439.7306
70 | 2710310.568 | 1227397.507
71 | 2710235.1712 | 1227329.4953
72 | 2710317.6489 | 1227394.2896
73 | 2710249.5119 | 1227322.9649
74 | 2710278.5424 | 1227309.7452
75 | 2710329.8227 | 1227388.7582
76 | 2710341.0927 | 1227383.6374
77 | 2709908.6013 | 1227417.3092
78 | 2709911.7665 | 1227424.4916
79 | 2710339.5965 | 1227438.5739
80 | 2710360.9283 | 1227431.2321
81 | 2710368.6171 | 1227428.5859
82 | 2710382.9199 | 1227423.6633
83 | 2710392.4048 | 1227420.3989
84 | 2710354.387 | 1227377.5969
85 | 2710368.5215 | 1227371.1746
86 | 2710392.316 | 1227360.363
87 | 2710412.1656 | 1227351.3439
88 | 2710406.3994 | 1227415.5824
89 | 2710414.922 | 1227412.6492
90 | 2710430.0087 | 1227471.9817
91 | 2710423.8769 | 1227409.5672
92 | 2710434.7836 | 1227405.8134
93 | 2710440.5736 | 1227403.8207
94 | 2710456.1606 | 1227398.4561
95 | 2710456.8471 | 1227398.2198
96 | 2710470.5953 | 1227393.4881
97 | 2710472.0576 | 1227392.9836
98 | 2710452.3239 | 1227354.4986
99 | 2710369.0834 | 1227268.5154
100 | 2710397.5203 | 1227260.0119
101 | 2710451.8838 | 1227353.5596
102 | 2710484.0491 | 1227388.8464
103 | 2710486.9679 | 1227387.8394
104 | 2710509.8018 | 1227379.9615
105 | 2710513.2653 | 1227378.86
106 | 2710506.6752 | 1227373.0352
107 | 2710527.9657 | 1227374.1851
108 | 2710494.1721 | 1227345.3376
109 | 2710487.2776 | 1227330.0644
110 | 2710488.305 | 1227332.3404
111 | 2710475.9072 | 1227304.876
112 | 2710469.2706 | 1227290.1739
113 | 2710481.5361 | 1227288.9164
114 | 2710504.2836 | 1227292.436
115 | 2710536.6173 | 1227373.2211
116 | 2710534.6851 | 1227396.8254
117 | 2710542.1049 | 1227335.0267
118 | 2710547.4176 | 1227299.1099
119 | 2710532.2743 | 1227296.7669
120 | 2710508.7566 | 1227293.1281
121 | 2709914.4652 | 1227430.6155
122 | 2709916.5488 | 1227435.3435
123 | 2710372.7971 | 1227585.252
124 | 2710410.7205 | 1227495.4319

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99037 | -0.18504 | 0.021175 | 0.0053069
1 | 0.98991 | -0.19395 | 0 | 0
2 | 0.99115 | -0.16993 | 0 | 0
3 | 0.98943 | -0.20336 | 0 | 0
4 | 0.99045 | -0.18341 | 0 | 0
5 | 0.99377 | -0.11935 | 0 | 0
6 | 0.98882 | -0.21502 | 0.0187 | 0.0046867
7 | 0.98908 | -0.21007 | 0.0074204 | 0.0018597
8 | 0.9894 | -0.2038 | 0.0019977 | 0.00050068
9 | 0.99315 | -0.13141 | 0 | 0
10 | 0.99394 | -0.11601 | 0.015278 | 0.0038291
11 | 0.9884 | -0.22328 | 0.01869 | 0.0046841
12 | 0.98893 | -0.213 | 0 | 0
13 | 0.99307 | -0.13291 | 0.018728 | 0.0046938
14 | 0.99273 | -0.13941 | 0 | 0
15 | 0.99707 | -0.055898 | 0 | 0
16 | 0.98886 | -0.21434 | 0.0029746 | 0.0007455
17 | 0.9888 | -0.21554 | 0.0026156 | 0.00065553
18 | 0.98884 | -0.21481 | 0.0019891 | 0.00049851
19 | 0.98877 | -0.21608 | 0.0011752 | 0.00029453
20 | 0.98918 | -0.20565 | 0.0027227 | 0.00068238
21 | 0.98897 | -0.20975 | 0.0031089 | 0.00077917
22 | 0.98941 | -0.20121 | 0 | 0
23 | 0.98883 | -0.21248 | 0.0026044 | 0.00065272
24 | 0.98969 | -0.19584 | 0 | 0
25 | 0.98882 | -0.21278 | 0.0050817 | 0.0012736
26 | 0.99133 | -0.16439 | 0.0020032 | 0.00050204
27 | 0.98835 | -0.22154 | 0.0021158 | 0.00053027
28 | 0.99139 | -0.16331 | 0.0021937 | 0.0005498
29 | 0.98779 | -0.23228 | 0.0020786 | 0.00052093
30 | 1 | 0 | -0.491 | -0.12514
31 | 0.99969 | -0.0058183 | 0.0020019 | 0.00050172
32 | 0.99848 | -0.028997 | 0.0026896 | 0.00067409
33 | 0.99807 | -0.036363 | 0.0063347 | 0.0015876
34 | 0.997 | -0.057299 | 0.001501 | 0.00037619
35 | 0.99265 | -0.14105 | 0.018729 | 0.004694
36 | 0.99195 | -0.15265 | 0.0048405 | 0.0012132
37 | 0.99297 | -0.13317 | 0.0030758 | 0.00077087
38 | 0.9943 | -0.10773 | 0.0050923 | 0.0012763
39 | 0.99548 | -0.085346 | 0.0058183 | 0.0014582
40 | 0.9908 | -0.17682 | 0.0071506 | 0.0017921
41 | 0.99113 | -0.17044 | 0.0025311 | 0.00063435
42 | 0.99051 | -0.18229 | 0 | 0
43 | 0.99185 | -0.15649 | 0 | 0
44 | 0.99026 | -0.1872 | 0.028344 | 0.0071038
45 | 0.98966 | -0.19885 | 0 | 0
46 | 0.99213 | -0.15098 | 0.0045977 | 0.0011523
47 | 0.98937 | -0.20455 | 0.0033067 | 0.00082874
48 | 0.99273 | -0.13935 | 0.018568 | 0.0046537
49 | 0.9891 | -0.20981 | 0 | 0
50 | 0.99363 | -0.12203 | 0 | 0
51 | 0.99357 | -0.12317 | 0.0031659 | 0.00079345
52 | 0.99544 | -0.087252 | 0.0015682 | 0.00039302
53 | 0.99357 | -0.12318 | 0.0023338 | 0.0005849
54 | 0.99621 | -0.072486 | 0 | 0
55 | 0.99614 | -0.073851 | 0.0033089 | 0.00082929
56 | 0.9751 | -0.47923 | 0.0020785 | 0.00052093
57 | 0.97513 | -0.47869 | 0 | 0
58 | 0.97559 | -0.46956 | 0.001831 | 0.00045888
59 | 0.97454 | -0.49037 | 0 | 0
60 | 0.97435 | -0.49399 | 0.0018983 | 0.00047576
61 | 0.97413 | -0.49828 | 0.0095233 | 0.0023868
62 | 0.97389 | -0.50303 | 0.011519 | 0.0028869
63 | 0.97435 | -0.494 | 0.010874 | 0.0027254
64 | 0.97385 | -0.50385 | 0.0014585 | 0.00036554
65 | 0.97381 | -0.50459 | 0 | 0
66 | 0.9716 | -0.54829 | 0.0013397 | 0.00033576
67 | 0.97362 | -0.50846 | 0.0012245 | 0.0003069
68 | 0.97374 | -0.50612 | 0.0015266 | 0.0003826
69 | 0.97632 | -0.45532 | 0.0015266 | 0.00038259
70 | 0.97327 | -0.51544 | 0.0015778 | 0.00039544
71 | 0.97275 | -0.52568 | 0 | 0
72 | 0.97316 | -0.51745 | 0.0040357 | 0.0010114
73 | 0.97257 | -0.52923 | 0.0024048 | 0.00060269
74 | 0.97228 | -0.53499 | 0.0097958 | 0.0024551
75 | 0.97304 | -0.51991 | 0.0012158 | 0.00030472
76 | 0.97294 | -0.52192 | 0.0018638 | 0.00046712
77 | 0.97116 | -0.55695 | 0.0075996 | 0.0019046
78 | 0.97122 | -0.55585 | 0.0032469 | 0.00081374
79 | 0.97642 | -0.45327 | 0.0065805 | 0.0016492
80 | 0.97713 | -0.43941 | 0.0049671 | 0.0012449
81 | 0.9774 | -0.43417 | 0.0032574 | 0.00081639
82 | 0.97791 | -0.42414 | 0.0038577 | 0.00096683
83 | 0.97826 | -0.41726 | 0.002872 | 0.0007198
84 | 0.97284 | -0.52378 | 0.0022454 | 0.00056274
85 | 0.97278 | -0.52512 | 0.0016405 | 0.00041116
86 | 0.9727 | -0.52658 | 0.00095964 | 0.00024051
87 | 0.97266 | -0.52742 | 0.0020801 | 0.00052131
88 | 0.97879 | -0.40685 | 0.0046616 | 0.0011683
89 | 0.97913 | -0.40026 | 0.0061012 | 0.0015291
90 | 0.99683 | -0.059839 | 0.0028179 | 0.00070623
91 | 0.9795 | -0.393 | 0.0042176 | 0.001057
92 | 0.97997 | -0.38386 | 0.0028873 | 0.00072363
93 | 0.98022 | -0.37891 | 0.0046908 | 0.0011756
94 | 0.98093 | -0.36512 | 0.0024701 | 0.00061906
95 | 0.98096 | -0.3645 | 0.0029631 | 0.00074263
96 | 0.98161 | -0.35188 | 0 | 0
97 | 0.98168 | -0.35049 | 0.0044536 | 0.0011162
98 | 0.98137 | -0.35651 | 0.0029015 | 0.00072717
99 | 0.98095 | -0.36498 | 0.003613 | 0.0009055
100 | 0.98106 | -0.36301 | 0.0023816 | 0.00059689
101 | 0.98137 | -0.35656 | 0.0030304 | 0.0007595
102 | 0.98229 | -0.3387 | 0.0024565 | 0.00061565
103 | 0.98244 | -0.33578 | 0.0036806 | 0.00092245
104 | 0.98364 | -0.31249 | 0 | 0
105 | 0.98385 | -0.3084 | 0.003643 | 0.00091303
106 | 0.98345 | -0.31619 | 0.0011288 | 0.0002829
107 | 0.98476 | -0.29073 | 0.001988 | 0.00049825
108 | 0.98272 | -0.33036 | 0.00097892 | 0.00024534
109 | 0.98234 | -0.33783 | 0.0018084 | 0.00045323
110 | 0.9824 | -0.33677 | 0.0013298 | 0.00033329
111 | 0.98179 | -0.34869 | 0.0016248 | 0.0004072
112 | 0.98149 | -0.35456 | 0 | 0
113 | 0.98132 | -0.35778 | 0.002228 | 0.00055838
114 | 0.98107 | -0.36274 | 0.0027626 | 0.00069236
115 | 0.98528 | -0.28063 | 0.0029367 | 0.00073601
116 | 0.98672 | -0.25289 | 0 | 0
117 | 0.98066 | -0.37072 | 0.0043426 | 0.0010883
118 | 0.98081 | -0.36786 | 0 | 0
119 | 0.98087 | -0.36666 | 0.0030096 | 0.00075428
120 | 0.98103 | -0.36349 | 0.0017727 | 0.00044427
121 | 0.97129 | -0.55451 | 0.0038092 | 0.00095469
122 | 0.97136 | -0.55311 | 0.006997 | 0.0017536
123 | 0.98872 | -0.21711 | 0.026499 | 0.0066414
124 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.018196 | 0.0045667 | -0.018188 | -0.0045621 | 7.7276e-06 | 4.5911e-06 | 0.027341 | 0.027341 | 0.027341 | 0.99037 | -0.18504 | 0.98991 | -0.19395 | 7.5113
1 | -0.03937 | -0.0098736 | 0.039399 | 0.0098914 | 2.837e-05 | 1.7878e-05 | 0.059156 | 0.059155 | 0.059156 | 0.99037 | -0.18504 | 0.99115 | -0.16993 | 16.2515
2 | 0.018188 | 0.0045621 | -0.01818 | -0.0045573 | 8.1552e-06 | 4.8455e-06 | 0.027341 | 0.027341 | 0.027341 | 0.98991 | -0.19395 | 0.98943 | -0.20336 | 7.5113
3 | 0.037478 | 0.0094258 | -0.037453 | -0.0094106 | 2.4121e-05 | 1.5176e-05 | 0.056277 | 0.056277 | 0.056277 | 0.99115 | -0.16993 | 0.99045 | -0.18341 | 15.4607
4 | -0.076876 | -0.019317 | 0.077062 | 0.019436 | 0.0001861 | 0.00011863 | 0.11543 | 0.11543 | 0.11543 | 0.99115 | -0.16993 | 0.99377 | -0.11935 | 31.7122
5 | 0.016182 | 0.0040567 | -0.016177 | -0.0040537 | 5.1702e-06 | 3.0101e-06 | 0.024337 | 0.024337 | 0.024337 | 0.98943 | -0.20336 | 0.98908 | -0.21007 | 6.686
6 | 0.0019978 | 0.00050055 | -0.0019977 | -0.00050068 | 4.2023e-08 | -1.3254e-07 | 0.0030045 | 0.0030045 | 0.0030045 | 0.98943 | -0.20336 | 0.9894 | -0.2038 | 0.82542
7 | 0.037453 | 0.0094106 | -0.037397 | -0.0093751 | 5.6406e-05 | 3.5489e-05 | 0.056277 | 0.056277 | 0.056277 | 0.99045 | -0.18341 | 0.98882 | -0.21502 | 15.4608
8 | 0.037489 | 0.0094073 | -0.037468 | -0.0093937 | 2.1548e-05 | 1.3555e-05 | 0.056138 | 0.056138 | 0.056138 | 0.99377 | -0.11935 | 0.99315 | -0.13141 | 15.4227
9 | -0.11455 | -0.028843 | 0.11457 | 0.028855 | 1.8302e-05 | 1.1692e-05 | 0.17157 | 0.17157 | 0.17157 | 0.99377 | -0.11935 | 0.99394 | -0.11601 | 47.1348
10 | 0.018697 | 0.0046885 | -0.01869 | -0.0046841 | 7.3581e-06 | 4.3914e-06 | 0.028137 | 0.028137 | 0.028137 | 0.98882 | -0.21502 | 0.9884 | -0.22328 | 7.7299
11 | 0.0087565 | 0.002194 | -0.0087553 | -0.0021934 | 1.2254e-06 | 5.4262e-07 | 0.013173 | 0.013174 | 0.013174 | 0.98908 | -0.21007 | 0.98893 | -0.213 | 3.6191
12 | 0.01873 | 0.0046946 | -0.018728 | -0.0046938 | 1.3396e-06 | 7.9864e-07 | 0.028063 | 0.028063 | 0.028063 | 0.99315 | -0.13141 | 0.99307 | -0.13291 | 7.7096
13 | 0.018738 | 0.0046991 | -0.018731 | -0.0046949 | 7.1421e-06 | 4.2584e-06 | 0.028076 | 0.028076 | 0.028076 | 0.99315 | -0.13141 | 0.99273 | -0.13941 | 7.7131
14 | -0.12985 | -0.032684 | 0.13022 | 0.032923 | 0.00037424 | 0.00023917 | 0.19444 | 0.19444 | 0.19444 | 0.99394 | -0.11601 | 0.99707 | -0.055898 | 53.4186
15 | 0.004964 | 0.0012439 | -0.0049637 | -0.0012439 | 3.1624e-07 | 8.4609e-09 | 0.0074691 | 0.0074692 | 0.0074692 | 0.98893 | -0.213 | 0.98886 | -0.21434 | 2.052
16 | 0.0037913 | 0.00094956 | -0.0037908 | -0.00094975 | 4.5831e-07 | -1.885e-07 | 0.0057044 | 0.0057046 | 0.0057046 | 0.98893 | -0.213 | 0.9888 | -0.21554 | 1.5672
17 | 0.018731 | 0.0046949 | -0.018729 | -0.004694 | 1.4605e-06 | 8.7086e-07 | 0.028076 | 0.028076 | 0.028076 | 0.99273 | -0.13941 | 0.99265 | -0.14105 | 7.7131
18 | -0.13022 | -0.032923 | 0.13057 | 0.033147 | 0.00035013 | 0.00022376 | 0.19444 | 0.19444 | 0.19444 | 0.99707 | -0.055898 | 1 | 0 | 53.4186
19 | 0.0019891 | 0.00049837 | -0.0019891 | -0.00049851 | 4.4814e-08 | -1.4244e-07 | 0.0029931 | 0.0029932 | 0.0029932 | 0.98886 | -0.21434 | 0.98884 | -0.21481 | 0.82231
20 | 0.0011752 | 0.00029422 | -0.0011752 | -0.00029453 | 2.9917e-08 | -3.0804e-07 | 0.0017684 | 0.0017685 | 0.0017685 | 0.9888 | -0.21554 | 0.98877 | -0.21608 | 0.48586
21 | 0.010798 | 0.0027069 | -0.010796 | -0.0027059 | 2.1066e-06 | 1.075e-06 | 0.016244 | 0.016244 | 0.016244 | 0.98918 | -0.20565 | 0.98897 | -0.20975 | 4.4626
22 | -0.013521 | -0.0033893 | 0.013524 | 0.0033909 | 2.8661e-06 | 1.5971e-06 | 0.02034 | 0.020339 | 0.02034 | 0.98918 | -0.20565 | 0.98941 | -0.20121 | 5.5878
23 | 0.0076871 | 0.0019267 | -0.0076861 | -0.0019263 | 9.9826e-07 | 3.8359e-07 | 0.011566 | 0.011566 | 0.011566 | 0.98897 | -0.20975 | 0.98883 | -0.21248 | 3.1775
24 | -0.013524 | -0.0033909 | 0.013527 | 0.0033928 | 3.4595e-06 | 1.9276e-06 | 0.020339 | 0.020339 | 0.020339 | 0.98941 | -0.20121 | 0.98969 | -0.19584 | 5.5878
25 | 0.0050818 | 0.0012736 | -0.0050817 | -0.0012736 | 7.4531e-08 | 4.1029e-09 | 0.0076471 | 0.0076472 | 0.0076472 | 0.98883 | -0.21248 | 0.98882 | -0.21278 | 2.1009
26 | -0.21595 | -0.055008 | 0.21628 | 0.055217 | 0.00032816 | 0.00020906 | 0.32501 | 0.32501 | 0.32501 | 0.98969 | -0.19584 | 0.99133 | -0.16439 | 29.7625
27 | 0.20243 | 0.051615 | -0.20218 | -0.051456 | 0.00025083 | 0.0001597 | 0.30467 | 0.30467 | 0.30467 | 0.98969 | -0.19584 | 0.98835 | -0.22154 | 27.9
28 | -0.21828 | -0.055719 | 0.2183 | 0.055727 | 1.1436e-05 | 7.2863e-06 | 0.32801 | 0.32801 | 0.32801 | 0.99133 | -0.16439 | 0.99139 | -0.16331 | 30.0378
29 | 0.20006 | 0.050926 | -0.19996 | -0.05086 | 0.00010352 | 6.5901e-05 | 0.30148 | 0.30148 | 0.30148 | 0.98835 | -0.22154 | 0.98779 | -0.23228 | 27.6083
30 | -0.22049 | -0.056277 | 0.2206 | 0.056349 | 0.00011358 | 7.2371e-05 | 0.33131 | 0.33131 | 0.33131 | 0.99139 | -0.16331 | 0.99195 | -0.15265 | 30.3393
31 | 0.19788 | 0.050339 | -0.19768 | -0.050214 | 0.00019633 | 0.00012497 | 0.29835 | 0.29835 | 0.29835 | 0.98779 | -0.23228 | 0.98672 | -0.25289 | 27.3216
32 | 0.25235 | 0.064989 | -0.25228 | -0.064943 | 7.1423e-05 | 4.5552e-05 | 0.37612 | 0.37612 | 0.37612 | 1 | 0 | 0.99969 | -0.0058183 | 34.4434
33 | 0.10643 | 0.027006 | -0.10628 | -0.026912 | 0.00014821 | 9.4646e-05 | 0.15848 | 0.15848 | 0.15848 | 1 | 0 | 0.99848 | -0.028997 | 43.5397
34 | 0.25028 | 0.064442 | -0.24991 | -0.064205 | 0.00037133 | 0.00023681 | 0.37314 | 0.37314 | 0.37314 | 0.99969 | -0.0058183 | 0.99807 | -0.036363 | 34.1706
35 | 0.10359 | 0.026238 | -0.10345 | -0.026148 | 0.0001406 | 8.9778e-05 | 0.15448 | 0.15448 | 0.15448 | 0.99848 | -0.028997 | 0.997 | -0.057299 | 42.4385
36 | 0.24357 | 0.062617 | -0.24329 | -0.06244 | 0.0002775 | 0.00017694 | 0.3637 | 0.3637 | 0.3637 | 0.99807 | -0.036363 | 0.99683 | -0.059839 | 33.3058
37 | 0.10195 | 0.025772 | -0.10187 | -0.025724 | 7.4188e-05 | 4.7369e-05 | 0.15224 | 0.15224 | 0.15224 | 0.997 | -0.057299 | 0.99621 | -0.072486 | 41.8231
38 | -0.22544 | -0.057562 | 0.22566 | 0.057697 | 0.00021253 | 0.00013544 | 0.33857 | 0.33857 | 0.33857 | 0.99195 | -0.15265 | 0.99297 | -0.13317 | 31.0043
39 | -0.22873 | -0.058468 | 0.22901 | 0.058648 | 0.00028179 | 0.0001796 | 0.34318 | 0.34318 | 0.34318 | 0.99297 | -0.13317 | 0.9943 | -0.10773 | 31.4264
40 | -0.23411 | -0.059924 | 0.23436 | 0.060086 | 0.00025408 | 0.00016197 | 0.3508 | 0.3508 | 0.3508 | 0.9943 | -0.10773 | 0.99548 | -0.085346 | 32.1242
41 | -0.24018 | -0.061544 | 0.24048 | 0.061734 | 0.00029732 | 0.00018957 | 0.35949 | 0.35949 | 0.35949 | 0.99548 | -0.085346 | 0.99683 | -0.059839 | 32.9206
42 | -0.06537 | -0.016409 | 0.06539 | 0.016422 | 1.9899e-05 | 1.2665e-05 | 0.098185 | 0.098185 | 0.098185 | 0.9908 | -0.17682 | 0.99113 | -0.17044 | 26.9739
43 | 0.05822 | 0.014617 | -0.058205 | -0.014608 | 1.5189e-05 | 9.653e-06 | 0.087446 | 0.087446 | 0.087446 | 0.9908 | -0.17682 | 0.99051 | -0.18229 | 24.0236
44 | -0.067921 | -0.017056 | 0.067967 | 0.017085 | 4.5239e-05 | 2.8803e-05 | 0.10198 | 0.10198 | 0.10198 | 0.99113 | -0.17044 | 0.99185 | -0.15649 | 28.0179
45 | 0.028351 | 0.0071079 | -0.028344 | -0.0071038 | 6.6313e-06 | 4.1186e-06 | 0.042592 | 0.042592 | 0.042592 | 0.99051 | -0.18229 | 0.99026 | -0.1872 | 11.701
46 | 0.029854 | 0.0074996 | -0.02983 | -0.007485 | 2.3577e-05 | 1.4688e-05 | 0.044854 | 0.044854 | 0.044854 | 0.99051 | -0.18229 | 0.98966 | -0.19885 | 12.3226
47 | -0.067967 | -0.017085 | 0.067985 | 0.017097 | 1.7886e-05 | 1.1388e-05 | 0.10198 | 0.10198 | 0.10198 | 0.99185 | -0.15649 | 0.99213 | -0.15098 | 28.0178
48 | 0.02983 | 0.007485 | -0.029822 | -0.0074799 | 8.0962e-06 | 5.0437e-06 | 0.044854 | 0.044854 | 0.044854 | 0.98966 | -0.19885 | 0.98937 | -0.20455 | 12.3227
49 | -0.072582 | -0.018249 | 0.072623 | 0.018275 | 4.0338e-05 | 2.5699e-05 | 0.10888 | 0.10888 | 0.10888 | 0.99213 | -0.15098 | 0.99273 | -0.13935 | 29.9123
50 | 0.026515 | 0.0066512 | -0.026509 | -0.0066471 | 6.6507e-06 | 4.1133e-06 | 0.039881 | 0.039881 | 0.039881 | 0.98937 | -0.20455 | 0.9891 | -0.20981 | 10.9564
51 | -0.091191 | -0.022928 | 0.091266 | 0.022976 | 7.5511e-05 | 4.8188e-05 | 0.13671 | 0.13671 | 0.13671 | 0.99273 | -0.13935 | 0.99363 | -0.12203 | 37.5585
52 | 0.026509 | 0.0066471 | -0.026499 | -0.0066414 | 9.2192e-06 | 5.702e-06 | 0.039881 | 0.039881 | 0.039881 | 0.9891 | -0.20981 | 0.98872 | -0.21711 | 10.9564
53 | 0.0055 | 0.0013784 | -0.0054997 | -0.0013783 | 2.9852e-07 | 3.9071e-08 | 0.0082365 | 0.0082365 | 0.0082365 | 0.99363 | -0.12203 | 0.99357 | -0.12317 | 2.2628
54 | -0.096766 | -0.024355 | 0.096928 | 0.024458 | 0.00016112 | 0.00010285 | 0.14495 | 0.14495 | 0.14495 | 0.99363 | -0.12203 | 0.99544 | -0.087252 | 39.8212
55 | 0.0023338 | 0.00058489 | -0.0023338 | -0.0005849 | 1.7592e-09 | -3.8479e-09 | 0.0034952 | 0.0034952 | 0.0034952 | 0.99357 | -0.12317 | 0.99357 | -0.12318 | 0.96021
56 | -0.098496 | -0.024851 | 0.098565 | 0.024895 | 6.9694e-05 | 4.4493e-05 | 0.14729 | 0.14729 | 0.14729 | 0.99544 | -0.087252 | 0.99621 | -0.072486 | 40.4652
57 | 0.0033091 | 0.00082912 | -0.0033089 | -0.00082929 | 2.1516e-07 | -1.6805e-07 | 0.0049427 | 0.0049428 | 0.0049428 | 0.99621 | -0.072486 | 0.99614 | -0.073851 | 1.3579
58 | -0.0020785 | -0.00052093 | 0.0020786 | 0.00052079 | 5.4055e-08 | -1.4414e-07 | 0.0031719 | 0.0031718 | 0.0031719 | 0.9751 | -0.47923 | 0.97513 | -0.47869 | 0.8714
59 | -0.0911 | -0.022883 | 0.091139 | 0.022908 | 3.9689e-05 | 2.4786e-05 | 0.13903 | 0.13903 | 0.13903 | 0.97513 | -0.47869 | 0.97559 | -0.46956 | 12.732
60 | 0.089021 | 0.022363 | -0.088971 | -0.022332 | 4.9621e-05 | 3.0953e-05 | 0.13586 | 0.13586 | 0.13586 | 0.97513 | -0.47869 | 0.97454 | -0.49037 | 12.4416
61 | -0.09297 | -0.023367 | 0.093034 | 0.023407 | 6.328e-05 | 3.9556e-05 | 0.14183 | 0.14183 | 0.14183 | 0.97559 | -0.46956 | 0.97632 | -0.45532 | 12.9877
62 | 0.041498 | 0.010417 | -0.04149 | -0.010412 | 7.1816e-06 | 4.5368e-06 | 0.063368 | 0.063369 | 0.063369 | 0.97454 | -0.49037 | 0.97435 | -0.494 | 17.4089
63 | 0.047474 | 0.011915 | -0.047466 | -0.01191 | 8.1817e-06 | 4.7708e-06 | 0.072494 | 0.072494 | 0.072494 | 0.97454 | -0.49037 | 0.97435 | -0.49399 | 6.6386
64 | 0.045567 | 0.011434 | -0.045558 | -0.011429 | 9.3246e-06 | 5.3924e-06 | 0.069595 | 0.069595 | 0.069595 | 0.97435 | -0.49399 | 0.97413 | -0.49828 | 6.3732
65 | 0.036035 | 0.0090421 | -0.036027 | -0.0090377 | 8.1494e-06 | 4.4123e-06 | 0.055048 | 0.055048 | 0.055048 | 0.97413 | -0.49828 | 0.97389 | -0.50303 | 5.041
66 | 0.024508 | 0.0061508 | -0.024507 | -0.0061504 | 9.6055e-07 | 4.1021e-07 | 0.037449 | 0.037449 | 0.037449 | 0.97389 | -0.50303 | 0.97385 | -0.50385 | 3.4294
67 | 0.030616 | 0.007687 | -0.030601 | -0.0076773 | 1.5454e-05 | 9.656e-06 | 0.046761 | 0.046761 | 0.046761 | 0.97435 | -0.494 | 0.97381 | -0.50459 | 12.8465
68 | 0.023048 | 0.0057849 | -0.022999 | -0.0057654 | 4.8773e-05 | 1.9502e-05 | 0.03522 | 0.035224 | 0.035224 | 0.97385 | -0.50385 | 0.9716 | -0.54829 | 3.2257
69 | 0.016856 | 0.0042277 | -0.016853 | -0.0042259 | 3.112e-06 | 1.8361e-06 | 0.025758 | 0.025758 | 0.025758 | 0.97381 | -0.50459 | 0.97362 | -0.50846 | 7.0763
70 | 0.013744 | 0.0034496 | -0.013743 | -0.003449 | 1.0028e-06 | 5.6636e-07 | 0.021004 | 0.021004 | 0.021004 | 0.97381 | -0.50459 | 0.97374 | -0.50612 | 5.7702
71 | 0.02166 | 0.0054296 | -0.021655 | -0.0054278 | 4.9776e-06 | 1.8415e-06 | 0.033173 | 0.033173 | 0.033173 | 0.9716 | -0.54829 | 0.97136 | -0.55311 | 3.0378
72 | 0.015629 | 0.003919 | -0.015623 | -0.003916 | 5.1943e-06 | 3.0226e-06 | 0.023886 | 0.023887 | 0.023887 | 0.97362 | -0.50846 | 0.97327 | -0.51544 | 6.5622
73 | 0.012217 | 0.0030664 | -0.012205 | -0.0030602 | 1.1389e-05 | 6.2064e-06 | 0.018671 | 0.018671 | 0.018671 | 0.97374 | -0.50612 | 0.97275 | -0.52568 | 5.1294
74 | -0.09456 | -0.023789 | 0.094569 | 0.023795 | 9.2325e-06 | 5.7755e-06 | 0.14415 | 0.14415 | 0.14415 | 0.97632 | -0.45532 | 0.97642 | -0.45327 | 13.2008
75 | 0.014046 | 0.0035205 | -0.014044 | -0.0035198 | 1.345e-06 | 7.6413e-07 | 0.021474 | 0.021474 | 0.021474 | 0.97327 | -0.51544 | 0.97316 | -0.51745 | 5.8995
76 | 0.012205 | 0.0030602 | -0.012203 | -0.0030591 | 2.06e-06 | 1.1228e-06 | 0.018671 | 0.018671 | 0.018671 | 0.97275 | -0.52568 | 0.97257 | -0.52923 | 5.1294
77 | 0.010008 | 0.0025083 | -0.010007 | -0.0025077 | 1.1743e-06 | 5.8547e-07 | 0.015303 | 0.015304 | 0.015304 | 0.97316 | -0.51745 | 0.97304 | -0.51991 | 4.2043
78 | 0.0097985 | 0.0024564 | -0.0097958 | -0.0024551 | 2.6886e-06 | 1.325e-06 | 0.014992 | 0.014992 | 0.014992 | 0.97257 | -0.52923 | 0.97228 | -0.53499 | 4.1187
79 | 0.0087915 | 0.002203 | -0.0087906 | -0.0022026 | 8.3904e-07 | 3.8324e-07 | 0.013444 | 0.013444 | 0.013444 | 0.97304 | -0.51991 | 0.97294 | -0.52192 | 3.6935
80 | 0.0069268 | 0.0017355 | -0.0069262 | -0.0017353 | 6.1455e-07 | 2.1198e-07 | 0.010594 | 0.010594 | 0.010594 | 0.97294 | -0.52192 | 0.97284 | -0.52378 | 2.9104
81 | -0.0075996 | -0.0019046 | 0.0076 | 0.0019048 | 3.9907e-07 | 1.5828e-07 | 0.011644 | 0.011644 | 0.011644 | 0.97116 | -0.55695 | 0.97122 | -0.55585 | 3.1989
82 | -0.010847 | -0.0027185 | 0.010848 | 0.0027189 | 6.9309e-07 | 3.6076e-07 | 0.016619 | 0.016619 | 0.016619 | 0.97122 | -0.55585 | 0.97129 | -0.55451 | 4.5656
83 | -0.10115 | -0.025444 | 0.10122 | 0.025486 | 6.7036e-05 | 4.2056e-05 | 0.15418 | 0.15418 | 0.15418 | 0.97642 | -0.45327 | 0.97713 | -0.43941 | 14.1191
84 | -0.10618 | -0.026731 | 0.10621 | 0.026748 | 2.6591e-05 | 1.6712e-05 | 0.16174 | 0.16174 | 0.16174 | 0.97713 | -0.43941 | 0.9774 | -0.43417 | 14.8118
85 | -0.10947 | -0.027564 | 0.10952 | 0.027597 | 5.2545e-05 | 3.306e-05 | 0.1667 | 0.1667 | 0.1667 | 0.9774 | -0.43417 | 0.97791 | -0.42414 | 15.2659
86 | -0.11338 | -0.028564 | 0.11342 | 0.028588 | 3.7342e-05 | 2.3521e-05 | 0.17257 | 0.17257 | 0.17257 | 0.97791 | -0.42414 | 0.97826 | -0.41726 | 15.8034
87 | -0.11629 | -0.029307 | 0.11635 | 0.029344 | 5.7921e-05 | 3.6512e-05 | 0.17694 | 0.17694 | 0.17694 | 0.97826 | -0.41726 | 0.97879 | -0.40685 | 16.2035
88 | 0.0046808 | 0.0011726 | -0.0046805 | -0.0011726 | 2.9842e-07 | -1.7653e-09 | 0.0071594 | 0.0071595 | 0.0071595 | 0.97284 | -0.52378 | 0.97278 | -0.52512 | 1.9669
89 | 0.00304 | 0.00076142 | -0.0030398 | -0.0007616 | 2.1192e-07 | -1.8881e-07 | 0.00465 | 0.0046501 | 0.0046501 | 0.97278 | -0.52512 | 0.9727 | -0.52658 | 1.2775
90 | 0.0020801 | 0.0005211 | -0.0020801 | -0.00052131 | 8.2789e-08 | -2.1763e-07 | 0.0031821 | 0.0031822 | 0.0031822 | 0.9727 | -0.52658 | 0.97266 | -0.52742 | 0.87422
91 | -0.12101 | -0.030512 | 0.12105 | 0.030536 | 3.8156e-05 | 2.408e-05 | 0.18403 | 0.18403 | 0.18403 | 0.97879 | -0.40685 | 0.97913 | -0.40026 | 16.8524
92 | -0.12715 | -0.032065 | 0.12719 | 0.032093 | 4.4233e-05 | 2.7951e-05 | 0.1933 | 0.1933 | 0.1933 | 0.97913 | -0.40026 | 0.9795 | -0.393 | 17.7015
93 | -0.13141 | -0.03315 | 0.13147 | 0.033187 | 5.7505e-05 | 3.6367e-05 | 0.19971 | 0.19971 | 0.19971 | 0.9795 | -0.393 | 0.97997 | -0.38386 | 18.2882
94 | -0.13435 | -0.03391 | 0.13438 | 0.033931 | 3.1882e-05 | 2.0173e-05 | 0.20409 | 0.20409 | 0.20409 | 0.97997 | -0.38386 | 0.98022 | -0.37891 | 18.6897
95 | -0.13908 | -0.035106 | 0.13917 | 0.035164 | 9.1922e-05 | 5.8207e-05 | 0.21121 | 0.21121 | 0.21121 | 0.98022 | -0.37891 | 0.98093 | -0.36512 | 19.3418
96 | -0.14164 | -0.035784 | 0.14164 | 0.035786 | 4.193e-06 | 2.656e-06 | 0.21496 | 0.21496 | 0.21496 | 0.98093 | -0.36512 | 0.98096 | -0.3645 | 19.6849
97 | -0.14461 | -0.036529 | 0.14469 | 0.036584 | 8.7529e-05 | 5.5467e-05 | 0.21945 | 0.21945 | 0.21945 | 0.98096 | -0.3645 | 0.98161 | -0.35188 | 20.0965
98 | -0.15063 | -0.038071 | 0.15064 | 0.038078 | 1.0091e-05 | 6.3996e-06 | 0.22845 | 0.22845 | 0.22845 | 0.98161 | -0.35188 | 0.98168 | -0.35049 | 20.9201
99 | 0.0059332 | 0.001487 | -0.0059319 | -0.0014867 | 1.3062e-06 | 2.9179e-07 | 0.0089941 | 0.0089943 | 0.0089943 | 0.98161 | -0.35188 | 0.98137 | -0.35651 | 2.471
100 | -0.15509 | -0.039194 | 0.15518 | 0.039249 | 8.7715e-05 | 5.5656e-05 | 0.2352 | 0.2352 | 0.2352 | 0.98168 | -0.35049 | 0.98229 | -0.3387 | 21.5383
101 | 0.0030304 | 0.00075949 | -0.0030304 | -0.0007595 | 8.2105e-09 | -7.848e-09 | 0.0045949 | 0.0045949 | 0.0045949 | 0.98137 | -0.35651 | 0.98137 | -0.35656 | 1.2623
102 | -0.003613 | -0.0009055 | 0.0036133 | 0.00090534 | 3.4025e-07 | -1.6364e-07 | 0.0054806 | 0.0054804 | 0.0054806 | 0.98095 | -0.36498 | 0.98106 | -0.36301 | 1.5057
103 | -0.005995 | -0.0015022 | 0.0059974 | 0.0015028 | 2.413e-06 | 5.6114e-07 | 0.0090928 | 0.0090924 | 0.0090928 | 0.98106 | -0.36301 | 0.98149 | -0.35456 | 2.498
104 | -0.15763 | -0.039865 | 0.15766 | 0.039879 | 2.2031e-05 | 1.3983e-05 | 0.23892 | 0.23892 | 0.23892 | 0.98229 | -0.3387 | 0.98244 | -0.33578 | 21.8791
105 | -0.16134 | -0.040802 | 0.16152 | 0.040916 | 0.00018049 | 0.00011459 | 0.24449 | 0.24449 | 0.24449 | 0.98244 | -0.33578 | 0.98364 | -0.31249 | 22.3896
106 | -0.18856 | -0.047711 | 0.18859 | 0.047735 | 3.7006e-05 | 2.3545e-05 | 0.2854 | 0.2854 | 0.2854 | 0.98364 | -0.31249 | 0.98385 | -0.3084 | 26.1358
107 | 0.027039 | 0.006795 | -0.027034 | -0.0067921 | 4.7693e-06 | 2.9559e-06 | 0.04091 | 0.04091 | 0.04091 | 0.98364 | -0.31249 | 0.98345 | -0.31619 | 11.239
108 | -0.19224 | -0.048648 | 0.1924 | 0.048752 | 0.00016319 | 0.00010385 | 0.29091 | 0.29091 | 0.29091 | 0.98385 | -0.3084 | 0.98476 | -0.29073 | 26.6404
109 | 0.025905 | 0.0065092 | -0.025888 | -0.0064984 | 1.7513e-05 | 1.0823e-05 | 0.039202 | 0.039202 | 0.039202 | 0.98345 | -0.31619 | 0.98272 | -0.33036 | 10.7698
110 | -0.19439 | -0.04925 | 0.19448 | 0.04931 | 9.4409e-05 | 6.0088e-05 | 0.29392 | 0.29392 | 0.29392 | 0.98476 | -0.29073 | 0.98528 | -0.28063 | 26.9155
111 | 0.024909 | 0.006253 | -0.024901 | -0.0062483 | 7.6084e-06 | 4.6888e-06 | 0.03772 | 0.03772 | 0.03772 | 0.98272 | -0.33036 | 0.9824 | -0.33677 | 10.3626
112 | -0.02357 | -0.0059143 | 0.023571 | 0.005915 | 1.1939e-06 | 7.3245e-07 | 0.035706 | 0.035706 | 0.035706 | 0.98234 | -0.33783 | 0.9824 | -0.33677 | 9.8092
113 | 0.021762 | 0.0054611 | -0.02175 | -0.0054542 | 1.1263e-05 | 6.8585e-06 | 0.032966 | 0.032966 | 0.032966 | 0.98234 | -0.33783 | 0.98179 | -0.34869 | 9.0567
114 | 0.020126 | 0.005047 | -0.02012 | -0.0050436 | 5.6285e-06 | 3.3983e-06 | 0.030504 | 0.030504 | 0.030504 | 0.98179 | -0.34869 | 0.98149 | -0.35456 | 8.3802
115 | 0.014123 | 0.0035408 | -0.01412 | -0.0035396 | 2.171e-06 | 1.2299e-06 | 0.021412 | 0.021412 | 0.021412 | 0.98149 | -0.35456 | 0.98132 | -0.35778 | 5.8823
116 | 0.011892 | 0.0029812 | -0.01189 | -0.0029797 | 2.8071e-06 | 1.5058e-06 | 0.018033 | 0.018033 | 0.018033 | 0.98132 | -0.35778 | 0.98107 | -0.36274 | 4.9542
117 | 0.0091271 | 0.0022873 | -0.0091268 | -0.0022872 | 3.2527e-07 | 1.5102e-07 | 0.013843 | 0.013843 | 0.013843 | 0.98107 | -0.36274 | 0.98103 | -0.36349 | 3.8031
118 | -0.19742 | -0.050046 | 0.19768 | 0.050214 | 0.00026356 | 0.00016777 | 0.29835 | 0.29835 | 0.29835 | 0.98528 | -0.28063 | 0.98672 | -0.25289 | 27.3216
119 | -0.0043426 | -0.0010883 | 0.0043431 | 0.0010883 | 5.9113e-07 | -7.9828e-08 | 0.0065892 | 0.0065891 | 0.0065892 | 0.98066 | -0.37072 | 0.98081 | -0.36786 | 1.8102
120 | -0.0043431 | -0.0010883 | 0.0043434 | 0.0010882 | 2.4948e-07 | -3.3738e-08 | 0.0065891 | 0.006589 | 0.0065891 | 0.98081 | -0.36786 | 0.98087 | -0.36666 | 1.8102
121 | -0.007353 | -0.0018425 | 0.0073541 | 0.0018429 | 1.1104e-06 | 4.1022e-07 | 0.011155 | 0.011155 | 0.011155 | 0.98087 | -0.36666 | 0.98103 | -0.36349 | 3.0645
122 | -0.014657 | -0.0036736 | 0.014658 | 0.0036741 | 9.7688e-07 | 5.6125e-07 | 0.022454 | 0.022454 | 0.022454 | 0.97129 | -0.55451 | 0.97136 | -0.55311 | 6.1688

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.491 | 0.12514

## res_load
| p_mw | q_mvar
0 | 0.021175 | 0.0053069
1 | 0.0187 | 0.0046867
2 | 0.0074204 | 0.0018597
3 | 0.0019977 | 0.00050068
4 | 0.015278 | 0.0038291
5 | 0.01869 | 0.0046841
6 | 0.018728 | 0.0046938
7 | 0.0029746 | 0.0007455
8 | 0.0026156 | 0.00065553
9 | 0.0019891 | 0.00049851
10 | 0.0011752 | 0.00029453
11 | 0.0027227 | 0.00068238
12 | 0.0031089 | 0.00077917
13 | 0.0026044 | 0.00065272
14 | 0.0050817 | 0.0012736
15 | 0.0020032 | 0.00050204
16 | 0.0021158 | 0.00053027
17 | 0.0021937 | 0.0005498
18 | 0.0020786 | 0.00052093
19 | 0.0020019 | 0.00050172
20 | 0.0026896 | 0.00067409
21 | 0.0063347 | 0.0015876
22 | 0.001501 | 0.00037619
23 | 0.018729 | 0.004694
24 | 0.0048405 | 0.0012132
25 | 0.0030758 | 0.00077087
26 | 0.0050923 | 0.0012763
27 | 0.0058183 | 0.0014582
28 | 0.0071506 | 0.0017921
29 | 0.0025311 | 0.00063435
30 | 0.028344 | 0.0071038
31 | 0.0045977 | 0.0011523
32 | 0.0033067 | 0.00082874
33 | 0.018568 | 0.0046537
34 | 0.0031659 | 0.00079345
35 | 0.0015682 | 0.00039302
36 | 0.0023338 | 0.0005849
37 | 0.0033089 | 0.00082929
38 | 0.0020785 | 0.00052093
39 | 0.001831 | 0.00045888
40 | 0.0018983 | 0.00047576
41 | 0.0095233 | 0.0023868
42 | 0.011519 | 0.0028869
43 | 0.010874 | 0.0027254
44 | 0.0014585 | 0.00036554
45 | 0.0013397 | 0.00033576
46 | 0.0012245 | 0.0003069
47 | 0.0015266 | 0.0003826
48 | 0.0015266 | 0.00038259
49 | 0.0015778 | 0.00039544
50 | 0.0040357 | 0.0010114
51 | 0.0024048 | 0.00060269
52 | 0.0097958 | 0.0024551
53 | 0.0012158 | 0.00030472
54 | 0.0018638 | 0.00046712
55 | 0.0075996 | 0.0019046
56 | 0.0032469 | 0.00081374
57 | 0.0065805 | 0.0016492
58 | 0.0049671 | 0.0012449
59 | 0.0032574 | 0.00081639
60 | 0.0038577 | 0.00096683
61 | 0.002872 | 0.0007198
62 | 0.0022454 | 0.00056274
63 | 0.0016405 | 0.00041116
64 | 0.00095964 | 0.00024051
65 | 0.0020801 | 0.00052131
66 | 0.0046616 | 0.0011683
67 | 0.0061012 | 0.0015291
68 | 0.0028179 | 0.00070623
69 | 0.0042176 | 0.001057
70 | 0.0028873 | 0.00072363
71 | 0.0046908 | 0.0011756
72 | 0.0024701 | 0.00061906
73 | 0.0029631 | 0.00074263
74 | 0.0044536 | 0.0011162
75 | 0.0029015 | 0.00072717
76 | 0.003613 | 0.0009055
77 | 0.0023816 | 0.00059689
78 | 0.0030304 | 0.0007595
79 | 0.0024565 | 0.00061565
80 | 0.0036806 | 0.00092245
81 | 0.003643 | 0.00091303
82 | 0.0011288 | 0.0002829
83 | 0.001988 | 0.00049825
84 | 0.00097892 | 0.00024534
85 | 0.0018084 | 0.00045323
86 | 0.0013298 | 0.00033329
87 | 0.0016248 | 0.0004072
88 | 0.002228 | 0.00055838
89 | 0.0027626 | 0.00069236
90 | 0.0029367 | 0.00073601
91 | 0.0043426 | 0.0010883
92 | 0.0030096 | 0.00075428
93 | 0.0017727 | 0.00044427
94 | 0.0038092 | 0.00095469
95 | 0.006997 | 0.0017536
96 | 0.026499 | 0.0066414

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1