## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1362-14_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1362-14_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1362-14_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1362-14_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1362-14_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1362-14_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1362-14_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1362-14_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1362-14_0_5_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1362-14_0_5_node_128 | 0.4 | n |  | TRUE
10 | bus_LV_1362-14_0_5_node_129 | 0.4 | n |  | TRUE
11 | bus_LV_1362-14_0_5_node_125 | 0.4 | n |  | TRUE
12 | bus_LV_1362-14_0_5_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1362-14_0_5_node_152 | 0.4 | n |  | TRUE
14 | bus_LV_1362-14_0_5_node_191 | 0.4 | n |  | TRUE
15 | bus_LV_1362-14_0_5_node_126 | 0.4 | n |  | TRUE
16 | bus_LV_1362-14_0_5_node_120 | 0.4 | n |  | TRUE
17 | bus_LV_1362-14_0_5_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1362-14_0_5_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1362-14_0_5_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1362-14_0_5_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1362-14_0_5_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1362-14_0_5_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1362-14_0_5_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1362-14_0_5_node_116 | 0.4 | n |  | TRUE
25 | bus_LV_1362-14_0_5_node_117 | 0.4 | n |  | TRUE
26 | bus_LV_1362-14_0_5_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1362-14_0_5_node_118 | 0.4 | n |  | TRUE
28 | bus_LV_1362-14_0_5_node_119 | 0.4 | n |  | TRUE
29 | bus_LV_1362-14_0_5_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_1362-14_0_5_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_1362-14_0_5_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1362-14_0_5_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_1362-14_0_5_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_1362-14_0_5_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_1362-14_0_5_node_48 | 0.4 | n |  | TRUE
36 | bus_LV_1362-14_0_5_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_1362-14_0_5_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_1362-14_0_5_node_105 | 0.4 | n |  | TRUE
39 | bus_LV_1362-14_0_5_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_1362-14_0_5_node_90 | 0.4 | n |  | TRUE
41 | bus_LV_1362-14_0_5_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_1362-14_0_5_node_87 | 0.4 | n |  | TRUE
43 | bus_LV_1362-14_0_5_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_1362-14_0_5_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_1362-14_0_5_node_235 | 0.4 | n |  | TRUE
46 | bus_LV_1362-14_0_5_node_236 | 0.4 | n |  | TRUE
47 | bus_LV_1362-14_0_5_node_25 | 0.4 | n |  | TRUE
48 | bus_LV_1362-14_0_5_node_245 | 0.4 | n |  | TRUE
49 | bus_LV_1362-14_0_5_node_244 | 0.4 | n |  | TRUE
50 | bus_LV_1362-14_0_5_node_26 | 0.4 | n |  | TRUE
51 | bus_LV_1362-14_0_5_node_31 | 0.4 | n |  | TRUE
52 | bus_LV_1362-14_0_5_node_34 | 0.4 | n |  | TRUE
53 | bus_LV_1362-14_0_5_node_56 | 0.4 | n |  | TRUE
54 | bus_LV_1362-14_0_5_node_27 | 0.4 | n |  | TRUE
55 | bus_LV_1362-14_0_5_node_92 | 0.4 | n |  | TRUE
56 | bus_LV_1362-14_0_5_node_93 | 0.4 | n |  | TRUE
57 | bus_LV_1362-14_0_5_node_30 | 0.4 | n |  | TRUE
58 | bus_LV_1362-14_0_5_node_58 | 0.4 | n |  | TRUE
59 | bus_LV_1362-14_0_5_node_71 | 0.4 | n |  | TRUE
60 | bus_LV_1362-14_0_5_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_1362-14_0_5_node_69 | 0.4 | n |  | TRUE
62 | bus_LV_1362-14_0_5_node_99 | 0.4 | n |  | TRUE
63 | bus_LV_1362-14_0_5_node_43 | 0.4 | n |  | TRUE
64 | bus_LV_1362-14_0_5_node_76 | 0.4 | n |  | TRUE
65 | bus_LV_1362-14_0_5_node_32 | 0.4 | n |  | TRUE
66 | bus_LV_1362-14_0_5_node_75 | 0.4 | n |  | TRUE
67 | bus_LV_1362-14_0_5_node_74 | 0.4 | n |  | TRUE
68 | bus_LV_1362-14_0_5_node_249 | 0.4 | n |  | TRUE
69 | bus_LV_1362-14_0_5_node_247 | 0.4 | n |  | TRUE
70 | bus_LV_1362-14_0_5_node_252 | 0.4 | n |  | TRUE
71 | bus_LV_1362-14_0_5_node_37 | 0.4 | n |  | TRUE
72 | bus_LV_1362-14_0_5_node_57 | 0.4 | n |  | TRUE
73 | bus_LV_1362-14_0_5_node_161 | 0.4 | n |  | TRUE
74 | bus_LV_1362-14_0_5_node_72 | 0.4 | n |  | TRUE
75 | bus_LV_1362-14_0_5_node_41 | 0.4 | n |  | TRUE
76 | bus_LV_1362-14_0_5_node_40 | 0.4 | n |  | TRUE
77 | bus_LV_1362-14_0_5_node_64 | 0.4 | n |  | TRUE
78 | bus_LV_1362-14_0_5_node_60 | 0.4 | n |  | TRUE
79 | bus_LV_1362-14_0_5_node_42 | 0.4 | n |  | TRUE
80 | bus_LV_1362-14_0_5_node_96 | 0.4 | n |  | TRUE
81 | bus_LV_1362-14_0_5_node_95 | 0.4 | n |  | TRUE
82 | bus_LV_1362-14_0_5_node_44 | 0.4 | n |  | TRUE
83 | bus_LV_1362-14_0_5_node_108 | 0.4 | n |  | TRUE
84 | bus_LV_1362-14_0_5_node_107 | 0.4 | n |  | TRUE
85 | bus_LV_1362-14_0_5_node_45 | 0.4 | n |  | TRUE
86 | bus_LV_1362-14_0_5_node_97 | 0.4 | n |  | TRUE
87 | bus_LV_1362-14_0_5_node_46 | 0.4 | n |  | TRUE
88 | bus_LV_1362-14_0_5_node_85 | 0.4 | n |  | TRUE
89 | bus_LV_1362-14_0_5_node_47 | 0.4 | n |  | TRUE
90 | bus_LV_1362-14_0_5_node_104 | 0.4 | n |  | TRUE
91 | bus_LV_1362-14_0_5_node_186 | 0.4 | n |  | TRUE
92 | bus_LV_1362-14_0_5_node_88 | 0.4 | n |  | TRUE
93 | bus_LV_1362-14_0_5_node_234 | 0.4 | n |  | TRUE
94 | bus_LV_1362-14_0_5_node_181 | 0.4 | n |  | TRUE
95 | bus_LV_1362-14_0_5_node_246 | 0.4 | n |  | TRUE
96 | bus_LV_1362-14_0_5_node_194 | 0.4 | n |  | TRUE
97 | bus_LV_1362-14_0_5_node_243 | 0.4 | n |  | TRUE
98 | bus_LV_1362-14_0_5_node_94 | 0.4 | n |  | TRUE
99 | bus_LV_1362-14_0_5_node_70 | 0.4 | n |  | TRUE
100 | bus_LV_1362-14_0_5_node_106 | 0.4 | n |  | TRUE
101 | bus_LV_1362-14_0_5_node_73 | 0.4 | n |  | TRUE
102 | bus_LV_1362-14_0_5_node_248 | 0.4 | n |  | TRUE
103 | bus_LV_1362-14_0_5_node_101 | 0.4 | n |  | TRUE
104 | bus_LV_1362-14_0_5_node_110 | 0.4 | n |  | TRUE
105 | bus_LV_1362-14_0_5_node_54 | 0.4 | n |  | TRUE
106 | bus_LV_1362-14_0_5_node_52 | 0.4 | n |  | TRUE
107 | bus_LV_1362-14_0_5_node_61 | 0.4 | n |  | TRUE
108 | bus_LV_1362-14_0_5_node_109 | 0.4 | n |  | TRUE
109 | bus_LV_1362-14_0_5_node_98 | 0.4 | n |  | TRUE
110 | bus_LV_1362-14_0_5_node_81 | 0.4 | n |  | TRUE
111 | bus_LV_1362-14_0_5_node_103 | 0.4 | n |  | TRUE
112 | bus_LV_1362-14_0_5_node_49 | 0.4 | n |  | TRUE
113 | bus_LV_1362-14_0_5_node_50 | 0.4 | n |  | TRUE
114 | bus_LV_1362-14_0_5_node_51 | 0.4 | n |  | TRUE
115 | bus_LV_1362-14_0_5_node_53 | 0.4 | n |  | TRUE
116 | bus_LV_1362-14_0_5_node_55 | 0.4 | n |  | TRUE
117 | bus_LV_1362-14_0_5_node_66 | 0.4 | n |  | TRUE
118 | bus_LV_1362-14_0_5_node_67 | 0.4 | n |  | TRUE
119 | bus_LV_1362-14_0_5_node_165 | 0.4 | n |  | TRUE
120 | bus_LV_1362-14_0_5_node_163 | 0.4 | n |  | TRUE
121 | bus_LV_1362-14_0_5_node_62 | 0.4 | n |  | TRUE
122 | bus_LV_1362-14_0_5_node_63 | 0.4 | n |  | TRUE
123 | bus_LV_1362-14_0_5_node_65 | 0.4 | n |  | TRUE
124 | bus_LV_1362-14_0_5_node_100 | 0.4 | n |  | TRUE
125 | bus_LV_1362-14_0_5_node_226 | 0.4 | n |  | TRUE
126 | bus_LV_1362-14_0_5_node_68 | 0.4 | n |  | TRUE
127 | bus_LV_1362-14_0_5_node_82 | 0.4 | n |  | TRUE
128 | bus_LV_1362-14_0_5_node_79 | 0.4 | n |  | TRUE
129 | bus_LV_1362-14_0_5_node_77 | 0.4 | n |  | TRUE
130 | bus_LV_1362-14_0_5_node_78 | 0.4 | n |  | TRUE
131 | bus_LV_1362-14_0_5_node_80 | 0.4 | n |  | TRUE
132 | bus_LV_1362-14_0_5_node_83 | 0.4 | n |  | TRUE
133 | bus_LV_1362-14_0_5_node_84 | 0.4 | n |  | TRUE
134 | bus_LV_1362-14_0_5_node_86 | 0.4 | n |  | TRUE
135 | bus_LV_1362-14_0_5_node_115 | 0.4 | n |  | TRUE
136 | bus_LV_1362-14_0_5_node_121 | 0.4 | n |  | TRUE
137 | bus_LV_1362-14_0_5_node_114 | 0.4 | n |  | TRUE
138 | bus_LV_1362-14_0_5_node_122 | 0.4 | n |  | TRUE
139 | bus_LV_1362-14_0_5_node_89 | 0.4 | n |  | TRUE
140 | bus_LV_1362-14_0_5_node_91 | 0.4 | n |  | TRUE
141 | bus_LV_1362-14_0_5_node_218 | 0.4 | n |  | TRUE
142 | bus_LV_1362-14_0_5_node_216 | 0.4 | n |  | TRUE
143 | bus_LV_1362-14_0_5_node_225 | 0.4 | n |  | TRUE
144 | bus_LV_1362-14_0_5_node_102 | 0.4 | n |  | TRUE
145 | bus_LV_1362-14_0_5_node_111 | 0.4 | n |  | TRUE
146 | bus_LV_1362-14_0_5_node_112 | 0.4 | n |  | TRUE
147 | bus_LV_1362-14_0_5_node_113 | 0.4 | n |  | TRUE
148 | bus_LV_1362-14_0_5_node_193 | 0.4 | n |  | TRUE
149 | bus_LV_1362-14_0_5_node_195 | 0.4 | n |  | TRUE
150 | bus_LV_1362-14_0_5_node_123 | 0.4 | n |  | TRUE
151 | bus_LV_1362-14_0_5_node_124 | 0.4 | n |  | TRUE
152 | bus_LV_1362-14_0_5_node_130 | 0.4 | n |  | TRUE
153 | bus_LV_1362-14_0_5_node_131 | 0.4 | n |  | TRUE
154 | bus_LV_1362-14_0_5_node_127 | 0.4 | n |  | TRUE
155 | bus_LV_1362-14_0_5_node_142 | 0.4 | n |  | TRUE
156 | bus_LV_1362-14_0_5_node_141 | 0.4 | n |  | TRUE
157 | bus_LV_1362-14_0_5_node_151 | 0.4 | n |  | TRUE
158 | bus_LV_1362-14_0_5_node_189 | 0.4 | n |  | TRUE
159 | bus_LV_1362-14_0_5_node_132 | 0.4 | n |  | TRUE
160 | bus_LV_1362-14_0_5_node_133 | 0.4 | n |  | TRUE
161 | bus_LV_1362-14_0_5_node_134 | 0.4 | n |  | TRUE
162 | bus_LV_1362-14_0_5_node_135 | 0.4 | n |  | TRUE
163 | bus_LV_1362-14_0_5_node_136 | 0.4 | n |  | TRUE
164 | bus_LV_1362-14_0_5_node_137 | 0.4 | n |  | TRUE
165 | bus_LV_1362-14_0_5_node_139 | 0.4 | n |  | TRUE
166 | bus_LV_1362-14_0_5_node_140 | 0.4 | n |  | TRUE
167 | bus_LV_1362-14_0_5_node_147 | 0.4 | n |  | TRUE
168 | bus_LV_1362-14_0_5_node_138 | 0.4 | n |  | TRUE
169 | bus_LV_1362-14_0_5_node_146 | 0.4 | n |  | TRUE
170 | bus_LV_1362-14_0_5_node_143 | 0.4 | n |  | TRUE
171 | bus_LV_1362-14_0_5_node_145 | 0.4 | n |  | TRUE
172 | bus_LV_1362-14_0_5_node_148 | 0.4 | n |  | TRUE
173 | bus_LV_1362-14_0_5_node_150 | 0.4 | n |  | TRUE
174 | bus_LV_1362-14_0_5_node_153 | 0.4 | n |  | TRUE
175 | bus_LV_1362-14_0_5_node_154 | 0.4 | n |  | TRUE
176 | bus_LV_1362-14_0_5_node_155 | 0.4 | n |  | TRUE
177 | bus_LV_1362-14_0_5_node_156 | 0.4 | n |  | TRUE
178 | bus_LV_1362-14_0_5_node_157 | 0.4 | n |  | TRUE
179 | bus_LV_1362-14_0_5_node_158 | 0.4 | n |  | TRUE
180 | bus_LV_1362-14_0_5_node_159 | 0.4 | n |  | TRUE
181 | bus_LV_1362-14_0_5_node_183 | 0.4 | n |  | TRUE
182 | bus_LV_1362-14_0_5_node_184 | 0.4 | n |  | TRUE
183 | bus_LV_1362-14_0_5_node_179 | 0.4 | n |  | TRUE
184 | bus_LV_1362-14_0_5_node_162 | 0.4 | n |  | TRUE
185 | bus_LV_1362-14_0_5_node_164 | 0.4 | n |  | TRUE
186 | bus_LV_1362-14_0_5_node_166 | 0.4 | n |  | TRUE
187 | bus_LV_1362-14_0_5_node_169 | 0.4 | n |  | TRUE
188 | bus_LV_1362-14_0_5_node_251 | 0.4 | n |  | TRUE
189 | bus_LV_1362-14_0_5_node_167 | 0.4 | n |  | TRUE
190 | bus_LV_1362-14_0_5_node_168 | 0.4 | n |  | TRUE
191 | bus_LV_1362-14_0_5_node_176 | 0.4 | n |  | TRUE
192 | bus_LV_1362-14_0_5_node_177 | 0.4 | n |  | TRUE
193 | bus_LV_1362-14_0_5_node_171 | 0.4 | n |  | TRUE
194 | bus_LV_1362-14_0_5_node_174 | 0.4 | n |  | TRUE
195 | bus_LV_1362-14_0_5_node_178 | 0.4 | n |  | TRUE
196 | bus_LV_1362-14_0_5_node_170 | 0.4 | n |  | TRUE
197 | bus_LV_1362-14_0_5_node_172 | 0.4 | n |  | TRUE
198 | bus_LV_1362-14_0_5_node_173 | 0.4 | n |  | TRUE
199 | bus_LV_1362-14_0_5_node_182 | 0.4 | n |  | TRUE
200 | bus_LV_1362-14_0_5_node_250 | 0.4 | n |  | TRUE
201 | bus_LV_1362-14_0_5_node_185 | 0.4 | n |  | TRUE
202 | bus_LV_1362-14_0_5_node_187 | 0.4 | n |  | TRUE
203 | bus_LV_1362-14_0_5_node_188 | 0.4 | n |  | TRUE
204 | bus_LV_1362-14_0_5_node_190 | 0.4 | n |  | TRUE
205 | bus_LV_1362-14_0_5_node_192 | 0.4 | n |  | TRUE
206 | bus_LV_1362-14_0_5_node_196 | 0.4 | n |  | TRUE
207 | bus_LV_1362-14_0_5_node_197 | 0.4 | n |  | TRUE
208 | bus_LV_1362-14_0_5_node_198 | 0.4 | n |  | TRUE
209 | bus_LV_1362-14_0_5_node_199 | 0.4 | n |  | TRUE
210 | bus_LV_1362-14_0_5_node_200 | 0.4 | n |  | TRUE
211 | bus_LV_1362-14_0_5_node_201 | 0.4 | n |  | TRUE
212 | bus_LV_1362-14_0_5_node_202 | 0.4 | n |  | TRUE
213 | bus_LV_1362-14_0_5_node_203 | 0.4 | n |  | TRUE
214 | bus_LV_1362-14_0_5_node_204 | 0.4 | n |  | TRUE
215 | bus_LV_1362-14_0_5_node_205 | 0.4 | n |  | TRUE
216 | bus_LV_1362-14_0_5_node_206 | 0.4 | n |  | TRUE
217 | bus_LV_1362-14_0_5_node_207 | 0.4 | n |  | TRUE
218 | bus_LV_1362-14_0_5_node_224 | 0.4 | n |  | TRUE
219 | bus_LV_1362-14_0_5_node_214 | 0.4 | n |  | TRUE
220 | bus_LV_1362-14_0_5_node_212 | 0.4 | n |  | TRUE
221 | bus_LV_1362-14_0_5_node_208 | 0.4 | n |  | TRUE
222 | bus_LV_1362-14_0_5_node_209 | 0.4 | n |  | TRUE
223 | bus_LV_1362-14_0_5_node_210 | 0.4 | n |  | TRUE
224 | bus_LV_1362-14_0_5_node_211 | 0.4 | n |  | TRUE
225 | bus_LV_1362-14_0_5_node_213 | 0.4 | n |  | TRUE
226 | bus_LV_1362-14_0_5_node_215 | 0.4 | n |  | TRUE
227 | bus_LV_1362-14_0_5_node_217 | 0.4 | n |  | TRUE
228 | bus_LV_1362-14_0_5_node_219 | 0.4 | n |  | TRUE
229 | bus_LV_1362-14_0_5_node_220 | 0.4 | n |  | TRUE
230 | bus_LV_1362-14_0_5_node_221 | 0.4 | n |  | TRUE
231 | bus_LV_1362-14_0_5_node_222 | 0.4 | n |  | TRUE
232 | bus_LV_1362-14_0_5_node_223 | 0.4 | n |  | TRUE
233 | bus_LV_1362-14_0_5_node_227 | 0.4 | n |  | TRUE
234 | bus_LV_1362-14_0_5_node_228 | 0.4 | n |  | TRUE
235 | bus_LV_1362-14_0_5_node_229 | 0.4 | n |  | TRUE
236 | bus_LV_1362-14_0_5_node_230 | 0.4 | n |  | TRUE
237 | bus_LV_1362-14_0_5_node_231 | 0.4 | n |  | TRUE
238 | bus_LV_1362-14_0_5_node_232 | 0.4 | n |  | TRUE
239 | bus_LV_1362-14_0_5_node_233 | 0.4 | n |  | TRUE
240 | bus_LV_1362-14_0_5_node_237 | 0.4 | n |  | TRUE
241 | bus_LV_1362-14_0_5_node_238 | 0.4 | n |  | TRUE
242 | bus_LV_1362-14_0_5_node_239 | 0.4 | n |  | TRUE
243 | bus_LV_1362-14_0_5_node_240 | 0.4 | n |  | TRUE
244 | bus_LV_1362-14_0_5_node_241 | 0.4 | n |  | TRUE
245 | bus_LV_1362-14_0_5_node_242 | 0.4 | n |  | TRUE
246 | bus_MV_1_0_node_81 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1362-14_0_5_load_0 | 0 | 0.00014278 | 3.5785e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1362-14_0_5_load_1 | 1 | 0.00043273 | 0.00010845 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1362-14_0_5_load_2 | 2 | 4.8707e-05 | 1.2207e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1362-14_0_5_load_3 | 3 | 0.00027723 | 6.948e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1362-14_0_5_load_5 | 5 | 0.00036227 | 9.0794e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1362-14_0_5_load_7 | 7 | 0.00040958 | 0.00010265 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1362-14_0_5_load_8 | 8 | 8.997e-05 | 2.2549e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1362-14_0_5_load_128 | 9 | 0.00041665 | 0.00010442 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1362-14_0_5_load_129 | 10 | 0.00011624 | 2.9133e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1362-14_0_5_load_9 | 12 | 0.0022068 | 0.00055308 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1362-14_0_5_load_191 | 14 | 0.00011416 | 2.861e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1362-14_0_5_load_126 | 15 | 0.00041212 | 0.00010329 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1362-14_0_5_load_120 | 16 | 0.001182 | 0.00029624 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1362-14_0_5_load_10 | 17 | 0.0001589 | 3.9823e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1362-14_0_5_load_11 | 18 | 0.00042025 | 0.00010533 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1362-14_0_5_load_12 | 19 | 0.00042263 | 0.00010592 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1362-14_0_5_load_13 | 20 | 0.00016839 | 4.2201e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1362-14_0_5_load_14 | 21 | 0.00049265 | 0.00012347 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1362-14_0_5_load_16 | 23 | 0.00042105 | 0.00010553 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1362-14_0_5_load_117 | 25 | 0.0011934 | 0.00029908 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1362-14_0_5_load_17 | 26 | 0.0008095 | 0.00020288 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1362-14_0_5_load_119 | 28 | 0.00025013 | 6.2688e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1362-14_0_5_load_18 | 29 | 0.0017178 | 0.00043053 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1362-14_0_5_load_19 | 30 | 0.0042913 | 0.0010755 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1362-14_0_5_load_105 | 38 | 0.0038998 | 0.00097738 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1362-14_0_5_load_90 | 40 | 0.0047679 | 0.0011949 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1362-14_0_5_load_87 | 42 | 0.0039554 | 0.00099132 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1362-14_0_5_load_235 | 45 | 0.00022498 | 5.6385e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1362-14_0_5_load_244 | 49 | 0.00099456 | 0.00024926 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1362-14_0_5_load_56 | 53 | 0.010561 | 0.0026468 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1362-14_0_5_load_93 | 56 | 0.00054497 | 0.00013658 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1362-14_0_5_load_58 | 58 | 0.01291 | 0.0032356 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1362-14_0_5_load_71 | 59 | 0.011401 | 0.0028573 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1362-14_0_5_load_69 | 61 | 0.012864 | 0.0032241 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1362-14_0_5_load_99 | 62 | 0.0092291 | 0.002313 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1362-14_0_5_load_76 | 64 | 0.0045782 | 0.0011474 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1362-14_0_5_load_75 | 66 | 0.0022712 | 0.00056923 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1362-14_0_5_load_74 | 67 | 0.0047082 | 0.00118 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1362-14_0_5_load_249 | 68 | 0.001757 | 0.00044035 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1362-14_0_5_load_247 | 69 | 0.0074727 | 0.0018728 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1362-14_0_5_load_252 | 70 | 0.0027361 | 0.00068574 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1362-14_0_5_load_57 | 72 | 0.0092681 | 0.0023228 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1362-14_0_5_load_161 | 73 | 0.0010786 | 0.00027032 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1362-14_0_5_load_72 | 74 | 0.0035715 | 0.00089511 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1362-14_0_5_load_64 | 77 | 0.005382 | 0.0013489 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1362-14_0_5_load_60 | 78 | 0.010312 | 0.0025845 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1362-14_0_5_load_96 | 80 | 0.0050491 | 0.0012654 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1362-14_0_5_load_95 | 81 | 0.0059908 | 0.0015014 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1362-14_0_5_load_108 | 83 | 0.002419 | 0.00060627 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1362-14_0_5_load_107 | 84 | 0.0056159 | 0.0014075 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1362-14_0_5_load_97 | 86 | 0.0064538 | 0.0016175 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1362-14_0_5_load_85 | 88 | 0.0069478 | 0.0017413 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1362-14_0_5_load_104 | 90 | 0.007159 | 0.0017942 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1362-14_0_5_load_186 | 91 | 0.00017268 | 4.3278e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1362-14_0_5_load_88 | 92 | 0.0049237 | 0.001234 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1362-14_0_5_load_234 | 93 | 0.00021069 | 5.2805e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1362-14_0_5_load_246 | 95 | 0.00051762 | 0.00012973 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1362-14_0_5_load_194 | 96 | 0.00070819 | 0.00017749 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1362-14_0_5_load_243 | 97 | 0.00060427 | 0.00015144 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1362-14_0_5_load_94 | 98 | 0.021992 | 0.0055118 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1362-14_0_5_load_70 | 99 | 0.0074879 | 0.0018766 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1362-14_0_5_load_106 | 100 | 0.0092575 | 0.0023202 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1362-14_0_5_load_73 | 101 | 0.0070718 | 0.0017724 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1362-14_0_5_load_248 | 102 | 0.007473 | 0.0018729 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1362-14_0_5_load_101 | 103 | 0.0053175 | 0.0013327 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1362-14_0_5_load_110 | 104 | 0.0017432 | 0.0004369 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1362-14_0_5_load_54 | 105 | 0.0026582 | 0.00066621 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1362-14_0_5_load_52 | 106 | 0.0030726 | 0.00077007 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1362-14_0_5_load_61 | 107 | 0.01523 | 0.003817 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1362-14_0_5_load_109 | 108 | 0.0025173 | 0.0006309 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1362-14_0_5_load_98 | 109 | 0.0040159 | 0.0010065 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1362-14_0_5_load_81 | 110 | 0.0044581 | 0.0011173 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1362-14_0_5_load_103 | 111 | 0.0028878 | 0.00072374 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1362-14_0_5_load_49 | 112 | 0.0026437 | 0.00066257 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1362-14_0_5_load_50 | 113 | 0.0024341 | 0.00061003 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1362-14_0_5_load_51 | 114 | 0.0046625 | 0.0011685 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1362-14_0_5_load_53 | 115 | 0.0011051 | 0.00027697 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1362-14_0_5_load_55 | 116 | 0.0020976 | 0.0005257 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1362-14_0_5_load_66 | 117 | 0.0027861 | 0.00069827 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1362-14_0_5_load_67 | 118 | 0.0025135 | 0.00062994 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1362-14_0_5_load_165 | 119 | 0.0037016 | 0.00092771 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1362-14_0_5_load_62 | 121 | 0.0030387 | 0.00076158 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1362-14_0_5_load_63 | 122 | 0.0031447 | 0.00078814 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1362-14_0_5_load_65 | 123 | 0.0036227 | 0.00090793 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1362-14_0_5_load_100 | 124 | 0.003871 | 0.00097017 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1362-14_0_5_load_226 | 125 | 0.0024813 | 0.00062186 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1362-14_0_5_load_68 | 126 | 0.004224 | 0.0010586 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1362-14_0_5_load_82 | 127 | 0.0027047 | 0.00067786 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1362-14_0_5_load_77 | 129 | 0.0068666 | 0.0017209 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1362-14_0_5_load_78 | 130 | 0.0029406 | 0.00073697 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1362-14_0_5_load_83 | 132 | 0.0038546 | 0.00096606 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1362-14_0_5_load_84 | 133 | 0.0069116 | 0.0017322 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1362-14_0_5_load_115 | 135 | 0.0067623 | 0.0016948 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1362-14_0_5_load_121 | 136 | 0.0028992 | 0.00072662 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1362-14_0_5_load_122 | 138 | 0.0021014 | 0.00052666 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1362-14_0_5_load_89 | 139 | 0.00025112 | 6.2937e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1362-14_0_5_load_91 | 140 | 0.0047765 | 0.0011971 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1362-14_0_5_load_218 | 141 | 0.00024717 | 6.1947e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1362-14_0_5_load_216 | 142 | 0.0027444 | 0.0006878 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1362-14_0_5_load_225 | 143 | 0.0074279 | 0.0018616 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1362-14_0_5_load_102 | 144 | 0.0070184 | 0.001759 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1362-14_0_5_load_111 | 145 | 0.0039998 | 0.0010024 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1362-14_0_5_load_112 | 146 | 0.0039539 | 0.00099095 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1362-14_0_5_load_193 | 148 | 0.00050826 | 0.00012738 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1362-14_0_5_load_195 | 149 | 0.00020668 | 5.1799e-05 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1362-14_0_5_load_123 | 150 | 0.0026166 | 0.00065577 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1362-14_0_5_load_124 | 151 | 0.005337 | 0.0013376 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1362-14_0_5_load_130 | 152 | 0.0070964 | 0.0017785 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1362-14_0_5_load_131 | 153 | 0.0011042 | 0.00027674 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1362-14_0_5_load_142 | 155 | 0.00065355 | 0.00016379 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1362-14_0_5_load_141 | 156 | 0.00017664 | 4.4271e-05 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1362-14_0_5_load_132 | 159 | 0.00038292 | 9.5969e-05 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1362-14_0_5_load_133 | 160 | 0.00040141 | 0.0001006 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1362-14_0_5_load_134 | 161 | 0.00013322 | 3.3388e-05 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_1362-14_0_5_load_136 | 163 | 0.00021744 | 5.4496e-05 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_1362-14_0_5_load_140 | 166 | 0.00021362 | 5.3538e-05 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_1362-14_0_5_load_147 | 167 | 0.00029066 | 7.2847e-05 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_1362-14_0_5_load_146 | 169 | 0.0019729 | 0.00049447 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_1362-14_0_5_load_145 | 171 | 0.00021492 | 5.3863e-05 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_1362-14_0_5_load_148 | 172 | 0.0020195 | 0.00050614 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_1362-14_0_5_load_150 | 173 | 0.001308 | 0.00032782 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_1362-14_0_5_load_153 | 174 | 0.00028808 | 7.22e-05 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_1362-14_0_5_load_156 | 177 | 0.00025368 | 6.3578e-05 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_1362-14_0_5_load_159 | 180 | 0.00037346 | 9.3598e-05 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_1362-14_0_5_load_183 | 181 | 0.00050606 | 0.00012683 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_1362-14_0_5_load_162 | 184 | 0.0039146 | 0.00098108 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_1362-14_0_5_load_251 | 188 | 0.011766 | 0.0029488 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_1362-14_0_5_load_176 | 191 | 0.0047367 | 0.0011871 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_1362-14_0_5_load_177 | 192 | 0.0042706 | 0.0010703 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_1362-14_0_5_load_171 | 193 | 0.0087175 | 0.0021848 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_1362-14_0_5_load_170 | 196 | 0.0050663 | 0.0012697 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_1362-14_0_5_load_173 | 198 | 6.5451e-05 | 1.6404e-05 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_1362-14_0_5_load_182 | 199 | 0.00032835 | 8.2293e-05 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_1362-14_0_5_load_250 | 200 | 0.0066972 | 0.0016785 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_1362-14_0_5_load_187 | 202 | 0.00059207 | 0.00014839 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_1362-14_0_5_load_192 | 205 | 0.00043157 | 0.00010816 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_1362-14_0_5_load_196 | 206 | 0.00055888 | 0.00014007 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_1362-14_0_5_load_197 | 207 | 0.00044336 | 0.00011112 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_1362-14_0_5_load_198 | 208 | 0.00031627 | 7.9265e-05 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_1362-14_0_5_load_199 | 209 | 0.0033819 | 0.00084758 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_1362-14_0_5_load_200 | 210 | 0.0025683 | 0.00064367 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_1362-14_0_5_load_202 | 212 | 0.0030655 | 0.00076828 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_1362-14_0_5_load_203 | 213 | 0.0026776 | 0.00067108 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_1362-14_0_5_load_204 | 214 | 0.0020301 | 0.0005088 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_1362-14_0_5_load_205 | 215 | 0.0024435 | 0.00061241 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_1362-14_0_5_load_206 | 216 | 0.0013726 | 0.00034401 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_1362-14_0_5_load_207 | 217 | 0.0027155 | 0.00068057 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_1362-14_0_5_load_224 | 218 | 0.0056645 | 0.0014197 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_1362-14_0_5_load_214 | 219 | 0.0022902 | 0.00057399 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_1362-14_0_5_load_212 | 220 | 0.0025578 | 0.00064104 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_1362-14_0_5_load_208 | 221 | 0.0017519 | 0.00043907 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_1362-14_0_5_load_209 | 222 | 0.0030666 | 0.00076857 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_1362-14_0_5_load_210 | 223 | 0.004905 | 0.0012293 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_1362-14_0_5_load_211 | 224 | 0.0012815 | 0.00032117 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_1362-14_0_5_load_213 | 225 | 0.0043575 | 0.0010921 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_1362-14_0_5_load_215 | 226 | 0.0022134 | 0.00055472 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_1362-14_0_5_load_217 | 227 | 0.0026616 | 0.00066705 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_1362-14_0_5_load_219 | 228 | 0.0028364 | 0.00071086 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_1362-14_0_5_load_220 | 229 | 0.0025468 | 0.00063829 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_1362-14_0_5_load_221 | 230 | 0.0028014 | 0.00070211 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_1362-14_0_5_load_222 | 231 | 0.0033549 | 0.00084082 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_1362-14_0_5_load_223 | 232 | 0.0023706 | 0.00059412 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_1362-14_0_5_load_227 | 233 | 0.0021311 | 0.0005341 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_1362-14_0_5_load_228 | 234 | 0.002893 | 0.00072505 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_1362-14_0_5_load_230 | 236 | 0.0060178 | 0.0015082 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_1362-14_0_5_load_231 | 237 | 0.00049433 | 0.00012389 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_1362-14_0_5_load_232 | 238 | 0.0004394 | 0.00011012 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_1362-14_0_5_load_233 | 239 | 0.00033836 | 8.48e-05 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_1362-14_0_5_load_237 | 240 | 0.0012734 | 0.00031915 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_1362-14_0_5_load_238 | 241 | 0.00086585 | 0.000217 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_1362-14_0_5_load_239 | 242 | 0.0012109 | 0.00030348 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_1362-14_0_5_load_240 | 243 | 0.00075782 | 0.00018993 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_1362-14_0_5_load_241 | 244 | 0.0011414 | 0.00028607 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_1362-14_0_5_load_242 | 245 | 0.00047864 | 0.00011996 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1362-14_0_5_line_0 |  | 0 | 1 | 0.016279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1362-14_0_5_line_1 |  | 0 | 2 | 0.091857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1362-14_0_5_line_2 |  | 1 | 3 | 0.0090459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1362-14_0_5_line_3 |  | 2 | 4 | 0.012589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1362-14_0_5_line_4 |  | 3 | 5 | 0.025889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1362-14_0_5_line_5 |  | 4 | 6 | 0.2722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1362-14_0_5_line_6 |  | 4 | 7 | 0.14388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1362-14_0_5_line_7 |  | 5 | 8 | 0.0062252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1362-14_0_5_line_8 |  | 6 | 9 | 0.34058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1362-14_0_5_line_9 |  | 6 | 10 | 0.13699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1362-14_0_5_line_10 |  | 7 | 11 | 0.076092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1362-14_0_5_line_11 |  | 8 | 12 | 0.0057592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1362-14_0_5_line_12 |  | 9 | 13 | 0.021735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1362-14_0_5_line_13 |  | 10 | 14 | 0.075124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1362-14_0_5_line_14 |  | 11 | 15 | 0.014443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1362-14_0_5_line_15 |  | 11 | 16 | 0.062763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1362-14_0_5_line_16 |  | 13 | 157 | 0.049594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1362-14_0_5_line_17 |  | 14 | 158 | 0.087642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1362-14_0_5_line_18 |  | 15 | 154 | 0.13996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1362-14_0_5_line_19 |  | 16 | 25 | 0.06231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1362-14_0_5_line_20 |  | 17 | 18 | 0.027447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1362-14_0_5_line_21 |  | 17 | 19 | 0.034649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1362-14_0_5_line_22 |  | 18 | 20 | 0.042586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1362-14_0_5_line_23 |  | 19 | 21 | 0.030067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1362-14_0_5_line_24 |  | 20 | 22 | 0.010147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1362-14_0_5_line_25 |  | 21 | 23 | 0.035456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1362-14_0_5_line_26 |  | 22 | 24 | 0.0353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1362-14_0_5_line_27 |  | 22 | 25 | 0.0063737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1362-14_0_5_line_28 |  | 23 | 26 | 0.057528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1362-14_0_5_line_29 |  | 24 | 27 | 0.018703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1362-14_0_5_line_30 |  | 24 | 28 | 0.037756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1362-14_0_5_line_31 |  | 27 | 148 | 0.015874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1362-14_0_5_line_32 |  | 27 | 96 | 0.020643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1362-14_0_5_line_33 |  | 29 | 30 | 0.039817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1362-14_0_5_line_34 |  | 29 | 31 | 0.023094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1362-14_0_5_line_35 |  | 31 | 32 | 0.045558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1362-14_0_5_line_36 |  | 31 | 33 | 0.15205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_1362-14_0_5_line_37 |  | 31 | 34 | 0.1531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_1362-14_0_5_line_38 |  | 32 | 35 | 0.15196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1362-14_0_5_line_39 |  | 33 | 70 | 0.018221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1362-14_0_5_line_40 |  | 33 | 47 | 0.11412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1362-14_0_5_line_41 |  | 34 | 73 | 0.044619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1362-14_0_5_line_42 |  | 34 | 43 | 0.20937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_1362-14_0_5_line_43 |  | 35 | 91 | 0.028513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1362-14_0_5_line_44 |  | 36 | 37 | 0.0073494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1362-14_0_5_line_45 |  | 36 | 38 | 0.015818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1362-14_0_5_line_46 |  | 37 | 57 | 0.061874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1362-14_0_5_line_47 |  | 37 | 58 | 0.03905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1362-14_0_5_line_48 |  | 39 | 40 | 0.039835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_1362-14_0_5_line_49 |  | 39 | 41 | 0.019989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_1362-14_0_5_line_50 |  | 39 | 42 | 0.044659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_1362-14_0_5_line_51 |  | 40 | 54 | 0.028644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_1362-14_0_5_line_52 |  | 41 | 59 | 0.023219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1362-14_0_5_line_53 |  | 41 | 60 | 0.005247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_1362-14_0_5_line_54 |  | 41 | 61 | 0.025348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1362-14_0_5_line_55 |  | 42 | 92 | 0.043611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1362-14_0_5_line_56 |  | 43 | 44 | 0.030262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_1362-14_0_5_line_57 |  | 43 | 45 | 0.018965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1362-14_0_5_line_58 |  | 43 | 46 | 0.014802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_1362-14_0_5_line_59 |  | 44 | 54 | 0.081514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_1362-14_0_5_line_60 |  | 45 | 93 | 0.0053989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1362-14_0_5_line_61 |  | 46 | 94 | 0.01305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_1362-14_0_5_line_62 |  | 47 | 48 | 0.008334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1362-14_0_5_line_63 |  | 47 | 49 | 0.018556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1362-14_0_5_line_64 |  | 48 | 95 | 0.087047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1362-14_0_5_line_65 |  | 48 | 96 | 0.014252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1362-14_0_5_line_66 |  | 49 | 97 | 0.038131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1362-14_0_5_line_67 |  | 50 | 51 | 0.039909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1362-14_0_5_line_68 |  | 50 | 52 | 0.028902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1362-14_0_5_line_69 |  | 50 | 53 | 0.010512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1362-14_0_5_line_70 |  | 51 | 64 | 0.019491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1362-14_0_5_line_71 |  | 52 | 68 | 0.013264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1362-14_0_5_line_72 |  | 52 | 69 | 0.0054402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1362-14_0_5_line_73 |  | 53 | 71 | 0.011401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1362-14_0_5_line_74 |  | 54 | 55 | 0.006064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1362-14_0_5_line_75 |  | 54 | 56 | 0.047621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1362-14_0_5_line_76 |  | 55 | 98 | 0.041447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1362-14_0_5_line_77 |  | 57 | 62 | 0.03623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1362-14_0_5_line_78 |  | 57 | 63 | 0.044099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1362-14_0_5_line_79 |  | 58 | 71 | 0.023659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1362-14_0_5_line_80 |  | 60 | 74 | 0.011955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_1362-14_0_5_line_81 |  | 60 | 75 | 0.017006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_1362-14_0_5_line_82 |  | 61 | 99 | 0.054323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1362-14_0_5_line_83 |  | 62 | 100 | 0.045927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1362-14_0_5_line_84 |  | 63 | 80 | 0.043165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1362-14_0_5_line_85 |  | 64 | 65 | 0.0095813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1362-14_0_5_line_86 |  | 65 | 66 | 0.013232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1362-14_0_5_line_87 |  | 65 | 67 | 0.0092441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1362-14_0_5_line_88 |  | 67 | 101 | 0.023737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1362-14_0_5_line_89 |  | 69 | 102 | 0.01785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1362-14_0_5_line_90 |  | 71 | 72 | 0.019235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1362-14_0_5_line_91 |  | 74 | 103 | 0.022044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_1362-14_0_5_line_92 |  | 75 | 78 | 0.022725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1362-14_0_5_line_93 |  | 75 | 76 | 0.032755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_1362-14_0_5_line_94 |  | 76 | 77 | 0.030459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_1362-14_0_5_line_95 |  | 77 | 104 | 0.023788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_1362-14_0_5_line_96 |  | 78 | 107 | 0.00022683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1362-14_0_5_line_97 |  | 79 | 80 | 0.015924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
98 | LV_1362-14_0_5_line_98 |  | 79 | 81 | 0.019501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_1362-14_0_5_line_99 |  | 81 | 85 | 0.028502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_1362-14_0_5_line_100 |  | 82 | 83 | 0.010132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1362-14_0_5_line_101 |  | 82 | 84 | 0.0049648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1362-14_0_5_line_102 |  | 83 | 108 | 0.022062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1362-14_0_5_line_103 |  | 84 | 87 | 0.014542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1362-14_0_5_line_104 |  | 85 | 86 | 0.023033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_1362-14_0_5_line_105 |  | 86 | 109 | 0.022938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_1362-14_0_5_line_106 |  | 87 | 88 | 0.026562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1362-14_0_5_line_107 |  | 87 | 89 | 0.12898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1362-14_0_5_line_108 |  | 88 | 110 | 0.019815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1362-14_0_5_line_109 |  | 89 | 90 | 0.047495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1362-14_0_5_line_110 |  | 90 | 111 | 0.014161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1362-14_0_5_line_111 |  | 92 | 139 | 0.011641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1362-14_0_5_line_112 |  | 93 | 238 | 0.025615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1362-14_0_5_line_113 |  | 94 | 183 | 0.007604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_1362-14_0_5_line_114 |  | 94 | 180 | 0.010883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1362-14_0_5_line_115 |  | 97 | 245 | 0.023142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1362-14_0_5_line_116 |  | 103 | 109 | 0.007899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_1362-14_0_5_line_117 |  | 104 | 108 | 0.028263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1362-14_0_5_line_118 |  | 105 | 106 | 0.010264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1362-14_0_5_line_119 |  | 106 | 113 | 0.0089157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1362-14_0_5_line_120 |  | 107 | 121 | 0.02618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1362-14_0_5_line_121 |  | 110 | 128 | 0.020084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1362-14_0_5_line_122 |  | 111 | 144 | 0.015563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1362-14_0_5_line_123 |  | 112 | 113 | 0.0066851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1362-14_0_5_line_124 |  | 112 | 114 | 0.0066113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1362-14_0_5_line_125 |  | 114 | 115 | 0.0060943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1362-14_0_5_line_126 |  | 115 | 116 | 0.010804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1362-14_0_5_line_127 |  | 116 | 117 | 0.0055697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1362-14_0_5_line_128 |  | 117 | 118 | 0.012562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1362-14_0_5_line_129 |  | 118 | 126 | 0.0077817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1362-14_0_5_line_130 |  | 119 | 120 | 0.048709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1362-14_0_5_line_131 |  | 120 | 186 | 0.15584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1362-14_0_5_line_132 |  | 120 | 184 | 0.017419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1362-14_0_5_line_133 |  | 121 | 122 | 0.0045299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1362-14_0_5_line_134 |  | 122 | 123 | 0.0030916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1362-14_0_5_line_135 |  | 123 | 124 | 0.0030217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1362-14_0_5_line_136 |  | 124 | 125 | 0.012099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1362-14_0_5_line_137 |  | 125 | 143 | 0.0069325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1362-14_0_5_line_138 |  | 126 | 127 | 0.022597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1362-14_0_5_line_139 |  | 127 | 128 | 0.0063013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1362-14_0_5_line_140 |  | 128 | 132 | 0.030491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1362-14_0_5_line_141 |  | 128 | 129 | 0.023345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_1362-14_0_5_line_142 |  | 129 | 130 | 0.0112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_1362-14_0_5_line_143 |  | 130 | 131 | 0.0046124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_1362-14_0_5_line_144 |  | 131 | 133 | 0.009166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_1362-14_0_5_line_145 |  | 132 | 134 | 0.018411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_1362-14_0_5_line_146 |  | 134 | 135 | 0.01232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_1362-14_0_5_line_147 |  | 134 | 136 | 0.017213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_1362-14_0_5_line_148 |  | 135 | 137 | 0.012929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_1362-14_0_5_line_149 |  | 136 | 138 | 0.012436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_1362-14_0_5_line_150 |  | 137 | 147 | 0.031298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_1362-14_0_5_line_151 |  | 138 | 150 | 0.010031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_1362-14_0_5_line_152 |  | 139 | 140 | 0.014212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_1362-14_0_5_line_153 |  | 140 | 141 | 0.024149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_1362-14_0_5_line_154 |  | 141 | 142 | 0.014633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_1362-14_0_5_line_155 |  | 142 | 226 | 0.0053781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_1362-14_0_5_line_156 |  | 143 | 217 | 0.014091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_1362-14_0_5_line_157 |  | 145 | 146 | 0.011401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_1362-14_0_5_line_158 |  | 145 | 147 | 0.03383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_1362-14_0_5_line_159 |  | 148 | 149 | 0.0079711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_1362-14_0_5_line_160 |  | 149 | 206 | 0.029238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_1362-14_0_5_line_161 |  | 150 | 151 | 0.0090485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_1362-14_0_5_line_162 |  | 151 | 152 | 0.020339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_1362-14_0_5_line_163 |  | 152 | 153 | 0.00036785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_1362-14_0_5_line_164 |  | 154 | 155 | 0.40984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_1362-14_0_5_line_165 |  | 155 | 156 | 0.025512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_1362-14_0_5_line_166 |  | 156 | 170 | 0.041494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_1362-14_0_5_line_167 |  | 157 | 173 | 0.034861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_1362-14_0_5_line_168 |  | 158 | 204 | 0.097897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_1362-14_0_5_line_169 |  | 158 | 203 | 0.24894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_1362-14_0_5_line_170 |  | 159 | 160 | 0.014411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_1362-14_0_5_line_171 |  | 159 | 161 | 0.0061162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_1362-14_0_5_line_172 |  | 160 | 162 | 0.20544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_1362-14_0_5_line_173 |  | 161 | 163 | 0.0050852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_1362-14_0_5_line_174 |  | 162 | 164 | 0.3531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_1362-14_0_5_line_175 |  | 162 | 165 | 0.28137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_1362-14_0_5_line_176 |  | 163 | 166 | 0.040235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_1362-14_0_5_line_177 |  | 164 | 167 | 0.0031002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_1362-14_0_5_line_178 |  | 165 | 171 | 0.024082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_1362-14_0_5_line_179 |  | 165 | 170 | 0.01098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_1362-14_0_5_line_180 |  | 167 | 172 | 0.031177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_1362-14_0_5_line_181 |  | 168 | 169 | 0.035533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_1362-14_0_5_line_182 |  | 168 | 170 | 0.03515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_1362-14_0_5_line_183 |  | 174 | 175 | 0.017386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_1362-14_0_5_line_184 |  | 175 | 176 | 0.023211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_1362-14_0_5_line_185 |  | 175 | 177 | 0.0090306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_1362-14_0_5_line_186 |  | 176 | 178 | 0.12402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_1362-14_0_5_line_187 |  | 177 | 179 | 0.028436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_1362-14_0_5_line_188 |  | 178 | 180 | 0.026317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
189 | LV_1362-14_0_5_line_189 |  | 179 | 181 | 0.092814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
190 | LV_1362-14_0_5_line_190 |  | 181 | 182 | 0.087727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
191 | LV_1362-14_0_5_line_191 |  | 182 | 201 | 0.14079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
192 | LV_1362-14_0_5_line_192 |  | 183 | 199 | 0.008908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
193 | LV_1362-14_0_5_line_193 |  | 183 | 195 | 0.054598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
194 | LV_1362-14_0_5_line_194 |  | 184 | 185 | 0.052453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
195 | LV_1362-14_0_5_line_195 |  | 185 | 187 | 0.16262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
196 | LV_1362-14_0_5_line_196 |  | 186 | 188 | 0.047788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
197 | LV_1362-14_0_5_line_197 |  | 187 | 193 | 0.09767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
198 | LV_1362-14_0_5_line_198 |  | 189 | 190 | 0.17452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
199 | LV_1362-14_0_5_line_199 |  | 189 | 191 | 0.097405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
200 | LV_1362-14_0_5_line_200 |  | 190 | 192 | 0.0015794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
201 | LV_1362-14_0_5_line_201 |  | 191 | 194 | 0.0084947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
202 | LV_1362-14_0_5_line_202 |  | 192 | 195 | 0.055126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
203 | LV_1362-14_0_5_line_203 |  | 193 | 196 | 0.017969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
204 | LV_1362-14_0_5_line_204 |  | 194 | 197 | 0.13243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
205 | LV_1362-14_0_5_line_205 |  | 196 | 197 | 0.035463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
206 | LV_1362-14_0_5_line_206 |  | 197 | 198 | 0.026684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
207 | LV_1362-14_0_5_line_207 |  | 200 | 201 | 0.055165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
208 | LV_1362-14_0_5_line_208 |  | 202 | 203 | 0.15739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
209 | LV_1362-14_0_5_line_209 |  | 204 | 205 | 0.32387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
210 | LV_1362-14_0_5_line_210 |  | 206 | 207 | 0.015473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
211 | LV_1362-14_0_5_line_211 |  | 207 | 208 | 0.011343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
212 | LV_1362-14_0_5_line_212 |  | 209 | 210 | 0.0071986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
213 | LV_1362-14_0_5_line_213 |  | 209 | 211 | 0.013442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
214 | LV_1362-14_0_5_line_214 |  | 210 | 212 | 0.0044654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
215 | LV_1362-14_0_5_line_215 |  | 211 | 213 | 0.018566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
216 | LV_1362-14_0_5_line_216 |  | 211 | 214 | 0.011896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
217 | LV_1362-14_0_5_line_217 |  | 212 | 215 | 0.0056514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
218 | LV_1362-14_0_5_line_218 |  | 213 | 216 | 0.0057173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
219 | LV_1362-14_0_5_line_219 |  | 214 | 217 | 0.0015227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
220 | LV_1362-14_0_5_line_220 |  | 215 | 218 | 0.0097649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
221 | LV_1362-14_0_5_line_221 |  | 216 | 219 | 0.035154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
222 | LV_1362-14_0_5_line_222 |  | 219 | 220 | 0.0082644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
223 | LV_1362-14_0_5_line_223 |  | 220 | 223 | 0.0094491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
224 | LV_1362-14_0_5_line_224 |  | 221 | 222 | 0.0063261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
225 | LV_1362-14_0_5_line_225 |  | 221 | 223 | 0.0066876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
226 | LV_1362-14_0_5_line_226 |  | 222 | 224 | 0.0012678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
227 | LV_1362-14_0_5_line_227 |  | 224 | 225 | 0.0072698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
228 | LV_1362-14_0_5_line_228 |  | 226 | 227 | 0.012858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
229 | LV_1362-14_0_5_line_229 |  | 227 | 228 | 0.0053343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
230 | LV_1362-14_0_5_line_230 |  | 228 | 229 | 0.013072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
231 | LV_1362-14_0_5_line_231 |  | 229 | 230 | 0.011995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
232 | LV_1362-14_0_5_line_232 |  | 230 | 231 | 0.011396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
233 | LV_1362-14_0_5_line_233 |  | 231 | 232 | 0.014917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
234 | LV_1362-14_0_5_line_234 |  | 232 | 233 | 0.007531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
235 | LV_1362-14_0_5_line_235 |  | 233 | 234 | 0.020788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
236 | LV_1362-14_0_5_line_236 |  | 234 | 235 | 0.10575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
237 | LV_1362-14_0_5_line_237 |  | 235 | 236 | 0.054759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
238 | LV_1362-14_0_5_line_238 |  | 237 | 238 | 0.0016793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
239 | LV_1362-14_0_5_line_239 |  | 237 | 239 | 0.035877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
240 | LV_1362-14_0_5_line_240 |  | 240 | 241 | 0.025043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
241 | LV_1362-14_0_5_line_241 |  | 241 | 242 | 0.021341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
242 | LV_1362-14_0_5_line_242 |  | 242 | 243 | 0.018797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
243 | LV_1362-14_0_5_line_243 |  | 243 | 244 | 0.016504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
244 | LV_1362-14_0_5_line_244 |  | 244 | 245 | 0.020925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1362-14_0_5_trafo_87 | 0.63 MVA 20/0.4 kV | 246 | 42 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40
0 | 2685507.544 | 1211609.5735 | 2685491.2852 | 1211610.3838
1 | 2685507.544 | 1211609.5735 | 2685507.544 | 1211609.5735 | 2685532.0025 | 1211624.1448 | 2685548.6033 | 1211646.1195 | 2685552.3492 | 1211681.7701
2 | 2685491.2852 | 1211610.3838 | 2685482.2505 | 1211610.8341
3 | 2685553.6647 | 1211694.2905 | 2685552.3492 | 1211681.7701
4 | 2685460.3581 | 1211624.1882 | 2685466.4474 | 1211618.535 | 2685482.2505 | 1211610.8341 | 2685482.2505 | 1211610.8341
5 | 2685553.6647 | 1211694.2905 | 2685556.1999 | 1211693.4374 | 2685570.2232 | 1211693.2495 | 2685588.3275 | 1211699.4021 | 2685610.1253 | 1211708.7099 | 2685631.1258 | 1211719.5517 | 2685647.4246 | 1211732.3497 | 2685659.2583 | 1211742.2817 | 2685669.167 | 1211756.0775 | 2685676.157 | 1211767.7967 | 2685691.0929 | 1211799.799 | 2685695.6552 | 1211807.0026 | 2685702.5434 | 1211814.6955 | 2685712.2319 | 1211822.1174 | 2685728.0198 | 1211827.6145 | 2685761.5481 | 1211832.2884 | 2685767.1252 | 1211833.914
6 | 2685553.6647 | 1211694.2905 | 2685544.9517 | 1211697.2341 | 2685536.6379 | 1211703.608 | 2685524.9768 | 1211717.6501 | 2685508.0717 | 1211739.1552 | 2685487.0417 | 1211758.978 | 2685465.9797 | 1211772.0293 | 2685443.1284 | 1211781.9816
7 | 2685460.3581 | 1211624.1882 | 2685455.7959 | 1211628.4237
8 | 2685767.1252 | 1211833.914 | 2685780.1518 | 1211836.4363 | 2685806.8918 | 1211848.1286 | 2685836.2902 | 1211858.3249 | 2685872.5718 | 1211865.9743 | 2685938.9892 | 1211876.3931 | 2685965.7421 | 1211876.6232 | 2686097.6386 | 1211865.0398 | 2686101.1511 | 1211864.6063
9 | 2685767.1252 | 1211833.914 | 2685767.128 | 1211829.5001 | 2685769.6825 | 1211822.0207 | 2685768.6918 | 1211819.5716 | 2685774.1102 | 1211811.6331 | 2685774.9423 | 1211810.3109 | 2685778.814 | 1211810.5778 | 2685782.7455 | 1211806.1648 | 2685786.8458 | 1211804.8006 | 2685792.8422 | 1211803.6972 | 2685798.9735 | 1211794.8018 | 2685813.6772 | 1211786.3966 | 2685818.8202 | 1211763.8112 | 2685821.2224 | 1211752.6607 | 2685817.2962 | 1211742.453 | 2685814.9064 | 1211735.8476 | 2685810.5458 | 1211726.4346
10 | 2685377.4066 | 1211819.0809 | 2685394.6069 | 1211804.5064 | 2685405.1796 | 1211798.5093 | 2685443.1284 | 1211781.9816
11 | 2685451.5752 | 1211632.3421 | 2685455.7959 | 1211628.4237
12 | 2686122.7222 | 1211861.9443 | 2686101.1511 | 1211864.6063
13 | 2685810.5458 | 1211726.4346 | 2685805.8115 | 1211716.215 | 2685796.7809 | 1211692.1137 | 2685782.4664 | 1211667.1136 | 2685779.2481 | 1211658.3723
14 | 2685377.4066 | 1211819.0809 | 2685391.4701 | 1211822.3693
15 | 2685377.4066 | 1211819.0809 | 2685368.5021 | 1211819.4982 | 2685354.8922 | 1211822.6833 | 2685319.2429 | 1211840.5403
16 | 2686122.7222 | 1211861.9443 | 2686171.2475 | 1211851.06
17 | 2685744.553 | 1211579.9667 | 2685743.9972 | 1211592.189 | 2685753.9948 | 1211606.153 | 2685765.1553 | 1211623.7917 | 2685773.4415 | 1211642.601 | 2685779.2481 | 1211658.3723
18 | 2685500.6433 | 1211781.2987 | 2685488.6811 | 1211798.3385 | 2685475.3957 | 1211821.8081 | 2685468.9805 | 1211831.4558 | 2685461.9922 | 1211834.9691 | 2685452.4113 | 1211836.9888 | 2685439.7811 | 1211836.4965 | 2685392.501 | 1211822.6104 | 2685391.4701 | 1211822.3693
19 | 2685263.1491 | 1211867.6606 | 2685295.7197 | 1211852.3232 | 2685319.2429 | 1211840.5403
20 | 2685316.5441 | 1211816.909 | 2685305.672 | 1211826.4707 | 2685295.4738 | 1211834.4812
21 | 2685342.5624 | 1211794.0268 | 2685316.5441 | 1211816.909
22 | 2685263.513 | 1211862.2903 | 2685268.5822 | 1211855.6041 | 2685295.4738 | 1211834.4812
23 | 2685342.5624 | 1211794.0268 | 2685344.0363 | 1211792.7305 | 2685367.7387 | 1211777.6291
24 | 2685257.3827 | 1211870.376 | 2685263.513 | 1211862.2903
25 | 2685400.9765 | 1211767.1738 | 2685377.7956 | 1211771.2216 | 2685367.7387 | 1211777.6291
26 | 2685257.3827 | 1211870.376 | 2685225.373 | 1211885.4507
27 | 2685257.3827 | 1211870.376 | 2685263.1491 | 1211867.6606
28 | 2685400.9765 | 1211767.1738 | 2685430.5212 | 1211762.0148 | 2685439.7053 | 1211756.943 | 2685440.6026 | 1211739.9222
29 | 2685225.373 | 1211885.4507 | 2685207.5608 | 1211891.3113
30 | 2685225.373 | 1211885.4507 | 2685239.5804 | 1211906.9012 | 2685251.0488 | 1211910.5259
31 | 2685207.5608 | 1211891.3113 | 2685216.5733 | 1211904.3791
32 | 2685207.5608 | 1211891.3113 | 2685187.9491 | 1211897.7547
33 | 2685108.4729 | 1211859.3868 | 2685099.434 | 1211880.7276 | 2685084.0283 | 1211874.4358
34 | 2685062.6488 | 1211865.7042 | 2685084.0283 | 1211874.4358
35 | 2685062.6488 | 1211865.7042 | 2685079.9153 | 1211823.5338
36 | 2685062.6488 | 1211865.7042 | 2685048.1464 | 1211901.1096 | 2685047.9881 | 1211912.7373 | 2685100.9786 | 1211908.2678 | 2685101.1196 | 1211896.7956 | 2685102.1849 | 1211894.5649 | 2685110.8332 | 1211876.4207 | 2685117.6342 | 1211863.1201
37 | 2685016.0266 | 1211981.5047 | 2685015.325 | 1211941.713 | 2685015.2698 | 1211938.6546 | 2685015.1933 | 1211934.4285 | 2685015.0727 | 1211927.4333 | 2685014.7903 | 1211911.53 | 2685032.2168 | 1211912.4456 | 2685047.9881 | 1211912.7373 | 2685048.1464 | 1211901.1096 | 2685062.6488 | 1211865.7042
38 | 2685079.9153 | 1211823.5338 | 2685094.0323 | 1211789.0681 | 2685120.2641 | 1211706.5881 | 2685123.2087 | 1211695.1559 | 2685136.9681 | 1211686.302
39 | 2685117.6342 | 1211863.1201 | 2685135.9061 | 1211862.8473
40 | 2685165.8641 | 1211902.5566 | 2685130.1493 | 1211905.7267 | 2685100.9786 | 1211908.2678 | 2685101.1196 | 1211896.7956 | 2685102.1849 | 1211894.5649 | 2685110.8332 | 1211876.4207 | 2685117.6342 | 1211863.1201
41 | 2685016.0266 | 1211981.5047 | 2685016.8134 | 1212026.1165
42 | 2684883.9027 | 1211911.7663 | 2684885.17 | 1211910.2834 | 2684887.8366 | 1211904.462 | 2684890.1658 | 1211899.3806 | 2684896.568 | 1211901.2396 | 2684908.1316 | 1211903.5168 | 2684922.3904 | 1211905.4321 | 2684929.4895 | 1211905.8446 | 2685002.5397 | 1211910.5436 | 2685014.7903 | 1211911.53 | 2685015.0727 | 1211927.4333 | 2685015.1933 | 1211934.4285 | 2685015.2698 | 1211938.6546 | 2685015.325 | 1211941.713 | 2685016.0266 | 1211981.5047
43 | 2685136.9681 | 1211686.302 | 2685149.6187 | 1211691.775 | 2685156.4866 | 1211692.9627 | 2685163.7862 | 1211690.3319
44 | 2684630.5637 | 1211745.6692 | 2684632.2404 | 1211743.1802 | 2684634.6777 | 1211739.5791
45 | 2684634.6777 | 1211739.5791 | 2684648.1413 | 1211747.8813
46 | 2684599.7205 | 1211789.4605 | 2684608.7124 | 1211771.0981 | 2684623.2215 | 1211741.4845 | 2684630.5637 | 1211745.6692
47 | 2684630.5637 | 1211745.6692 | 2684660.5127 | 1211765.4182 | 2684663.1712 | 1211767.1544
48 | 2684748.4062 | 1211868.4448 | 2684766.876 | 1211861.2025 | 2684784.4158 | 1211857.9051 | 2684786.557 | 1211858.0836
49 | 2684732.8809 | 1211865.2778 | 2684734.6848 | 1211869.3505 | 2684744.9606 | 1211865.4717 | 2684748.4062 | 1211868.4448
50 | 2684748.4062 | 1211868.4448 | 2684771.0013 | 1211887.9898 | 2684781.5858 | 1211898.3106
51 | 2684813.9177 | 1211865.7407 | 2684810.3149 | 1211863.6659 | 2684801.154 | 1211860.7449 | 2684791.3303 | 1211858.4816 | 2684786.557 | 1211858.0836
52 | 2684718.8696 | 1211848.0786 | 2684727.5571 | 1211853.2943 | 2684732.8809 | 1211865.2778
53 | 2684728.0488 | 1211867.355 | 2684732.8809 | 1211865.2778
54 | 2684732.8809 | 1211865.2778 | 2684756.1617 | 1211855.2518
55 | 2684802.923 | 1211934.2016 | 2684801.0887 | 1211929.4447 | 2684798.5755 | 1211914.8771 | 2684781.5858 | 1211898.3106
56 | 2684881.2418 | 1211890.5034 | 2684879.5292 | 1211896.0382 | 2684877.8485 | 1211901.4734 | 2684887.8366 | 1211904.462 | 2684885.17 | 1211910.2834 | 2684883.9027 | 1211911.7663
57 | 2684883.9027 | 1211911.7663 | 2684871.5426 | 1211926.1504
58 | 2684898.3855 | 1211915.019 | 2684883.9027 | 1211911.7663
59 | 2684813.9177 | 1211865.7407 | 2684815.7937 | 1211862.5987 | 2684821.7755 | 1211865.708 | 2684848.569 | 1211881.2325 | 2684859.0495 | 1211886.9965 | 2684865.2776 | 1211889.887 | 2684870.2675 | 1211892.2039 | 2684879.5292 | 1211896.0382 | 2684881.2418 | 1211890.5034
60 | 2684871.5426 | 1211926.1504 | 2684870.9059 | 1211926.8914 | 2684867.5668 | 1211929.7904
61 | 2684898.3855 | 1211915.019 | 2684900.8897 | 1211920.6028 | 2684900.5175 | 1211927.5242
62 | 2685165.8641 | 1211902.5566 | 2685174.0423 | 1211900.8389
63 | 2685165.8641 | 1211902.5566 | 2685162.7913 | 1211920.8561
64 | 2685211.9542 | 1211837.5275 | 2685208.8403 | 1211853.8938 | 2685178.3229 | 1211866.0994 | 2685172.5274 | 1211872.3096 | 2685170.6606 | 1211889.1496 | 2685174.0423 | 1211900.8389
65 | 2685174.0423 | 1211900.8389 | 2685186.6108 | 1211898.1944 | 2685187.9491 | 1211897.7547
66 | 2685156.4767 | 1211958.461 | 2685162.7913 | 1211920.8561
67 | 2684701.3211 | 1211792.0816 | 2684704.2348 | 1211793.9909 | 2684706.5032 | 1211791.0434 | 2684708.9497 | 1211792.6792 | 2684709.6272 | 1211793.1335 | 2684718.3663 | 1211799.0059 | 2684730.546 | 1211807.1398 | 2684732.6724 | 1211804.0235
68 | 2684697.9165 | 1211813.4917 | 2684693.1746 | 1211810.289 | 2684704.2348 | 1211793.9909 | 2684701.3211 | 1211792.0816
69 | 2684701.3211 | 1211792.0816 | 2684692.5228 | 1211786.3297
70 | 2684732.6724 | 1211804.0235 | 2684749.0232 | 1211814.632
71 | 2684691.5427 | 1211825.1311 | 2684697.9165 | 1211813.4917
72 | 2684697.9165 | 1211813.4917 | 2684702.5277 | 1211816.3782
73 | 2684682.98 | 1211780.0911 | 2684692.5228 | 1211786.3297
74 | 2684813.9177 | 1211865.7407 | 2684810.9547 | 1211871.0354
75 | 2684813.9177 | 1211865.7407 | 2684855.2131 | 1211889.4558
76 | 2684810.9547 | 1211871.0354 | 2684832.7665 | 1211883.6649 | 2684824.3439 | 1211897.5531
77 | 2684599.7205 | 1211789.4605 | 2684631.5214 | 1211805.0773 | 2684631.9632 | 1211804.4082
78 | 2684599.7205 | 1211789.4605 | 2684589.1757 | 1211811.2252 | 2684587.2535 | 1211816.557 | 2684585.8423 | 1211821.2178 | 2684583.6686 | 1211830.3486
79 | 2684682.98 | 1211780.0911 | 2684663.1712 | 1211767.1544
80 | 2684728.0488 | 1211867.355 | 2684716.8837 | 1211871.6297
81 | 2684723.1492 | 1211878.4593 | 2684721.9326 | 1211874.2393 | 2684729.7647 | 1211871.2041 | 2684728.0488 | 1211867.355
82 | 2684756.1617 | 1211855.2518 | 2684764.4963 | 1211851.6624 | 2684767.5473 | 1211847.125 | 2684768.2942 | 1211841.0872 | 2684765.3884 | 1211835.42 | 2684751.9648 | 1211826.0565 | 2684742.8947 | 1211819.9021
83 | 2684665.9623 | 1211807.0784 | 2684640.8251 | 1211790.9889 | 2684631.9632 | 1211804.4082
84 | 2684583.6686 | 1211830.3486 | 2684621.901 | 1211840.9422 | 2684621.6102 | 1211844.4217
85 | 2684757.0609 | 1211819.847 | 2684749.0232 | 1211814.632
86 | 2684757.0609 | 1211819.847 | 2684764.2556 | 1211808.7308
87 | 2684757.0609 | 1211819.847 | 2684759.7715 | 1211821.6089 | 2684764.8288 | 1211824.8581
88 | 2684784.7992 | 1211837.6887 | 2684764.8288 | 1211824.8581
89 | 2684702.5277 | 1211816.3782 | 2684717.658 | 1211825.8494
90 | 2684682.98 | 1211780.0911 | 2684674.1306 | 1211792.6849 | 2684670.8924 | 1211790.6153
91 | 2684716.8837 | 1211871.6297 | 2684696.297 | 1211879.5116
92 | 2684723.1492 | 1211878.4593 | 2684729.4605 | 1211900.2907
93 | 2684692.6269 | 1211890.5673 | 2684723.1492 | 1211878.4593
94 | 2684692.6269 | 1211890.5673 | 2684664.1255 | 1211901.311
95 | 2684641.8662 | 1211909.7018 | 2684664.1255 | 1211901.311
96 | 2684729.4605 | 1211900.2907 | 2684729.5235 | 1211900.5087
97 | 2684618.6016 | 1211859.7855 | 2684620.6378 | 1211856.0564 | 2684621.6102 | 1211844.4217
98 | 2684618.6016 | 1211859.7855 | 2684633.3177 | 1211863.2187 | 2684635.4642 | 1211867.0474
99 | 2684647.5181 | 1211892.8063 | 2684641.6999 | 1211878.1697 | 2684635.4642 | 1211867.0474
100 | 2684585.2951 | 1211931.0266 | 2684594.7758 | 1211927.4528
101 | 2684585.2951 | 1211931.0266 | 2684580.6292 | 1211932.7234
102 | 2684594.7758 | 1211927.4528 | 2684615.4197 | 1211919.671
103 | 2684566.9631 | 1211937.6933 | 2684580.6292 | 1211932.7234
104 | 2684647.5181 | 1211892.8063 | 2684651.5616 | 1211891.1403 | 2684653.233 | 1211894.3773 | 2684656.9537 | 1211894.5747 | 2684667.4984 | 1211890.5375
105 | 2684688.9202 | 1211882.3359 | 2684667.4984 | 1211890.5375
106 | 2684566.9631 | 1211937.6933 | 2684578.1873 | 1211961.767
107 | 2684470.2462 | 1211981.5408 | 2684466.3869 | 1211983.0871 | 2684464.0581 | 1211976.3609 | 2684462.8424 | 1211972.5967 | 2684494.5923 | 1211960.6718 | 2684536.2279 | 1211945.0292 | 2684540.3761 | 1211943.4758 | 2684565.1267 | 1211933.7647 | 2684566.9631 | 1211937.6933
108 | 2684578.1873 | 1211961.767 | 2684586.1147 | 1211978.7696 | 2684586.2973 | 1211979.8087
109 | 2684470.2462 | 1211981.5408 | 2684471.8967 | 1211976.6053 | 2684474.8755 | 1211973.3787 | 2684510.1503 | 1211959.5192
110 | 2684510.1503 | 1211959.5192 | 2684523.33 | 1211954.3409
111 | 2684802.923 | 1211934.2016 | 2684807.1113 | 1211945.0634
112 | 2684848.9427 | 1211947.2087 | 2684850.8092 | 1211944.3392 | 2684867.5668 | 1211929.7904
113 | 2684907.931 | 1211928.8084 | 2684905.7259 | 1211927.843 | 2684900.5175 | 1211927.5242
114 | 2684900.5175 | 1211927.5242 | 2684895.3739 | 1211929.5968 | 2684890.7269 | 1211932.2225
115 | 2685152.6444 | 1211981.2834 | 2685156.4767 | 1211958.461
116 | 2684688.9202 | 1211882.3359 | 2684696.297 | 1211879.5116
117 | 2684641.8662 | 1211909.7018 | 2684615.4197 | 1211919.671
118 | 2684660.114 | 1211940.4681 | 2684664.5368 | 1211935.8205 | 2684666.9778 | 1211932.8454
119 | 2684653.9678 | 1211946.9267 | 2684660.114 | 1211940.4681
120 | 2684729.5235 | 1211900.5087 | 2684736.7941 | 1211925.6588
121 | 2684587.7624 | 1211999.74 | 2684588.0131 | 1211989.5702 | 2684586.2973 | 1211979.8087
122 | 2684523.33 | 1211954.3409 | 2684537.8151 | 1211948.6497
123 | 2684649.3592 | 1211951.7695 | 2684653.9678 | 1211946.9267
124 | 2684649.3592 | 1211951.7695 | 2684644.8016 | 1211956.5588
125 | 2684644.8016 | 1211956.5588 | 2684640.8703 | 1211960.6899 | 2684640.5695 | 1211960.9406
126 | 2684632.2702 | 1211967.8581 | 2684640.5695 | 1211960.9406
127 | 2684632.2702 | 1211967.8581 | 2684627.9917 | 1211971.4242
128 | 2684618.2347 | 1211979.3234 | 2684619.6617 | 1211978.3673 | 2684627.9917 | 1211971.4242
129 | 2684618.2347 | 1211979.3234 | 2684611.77 | 1211983.6548
130 | 2684765.0871 | 1211667.9391 | 2684753.7132 | 1211665.6426 | 2684749.7601 | 1211660.4053 | 2684750.5937 | 1211651.4779 | 2684753.998 | 1211646.6787 | 2684765.5259 | 1211636.0304
131 | 2684765.0871 | 1211667.9391 | 2684754.5082 | 1211679.2184 | 2684745.8067 | 1211684.5872 | 2684735.6853 | 1211690.9476 | 2684733.5464 | 1211700.29 | 2684731.8964 | 1211711.5851 | 2684728.8046 | 1211721.1364 | 2684737.8213 | 1211725.6563 | 2684741.5186 | 1211725.909 | 2684744.5339 | 1211729.2206 | 2684749.284 | 1211732.3902 | 2684778.6605 | 1211722.9014 | 2684789.4141 | 1211720.7083 | 2684801.0571 | 1211715.2924 | 2684805.8062 | 1211710.5124 | 2684807.3604 | 1211709.7006
132 | 2684765.0871 | 1211667.9391 | 2684773.3044 | 1211666.1547 | 2684781.3086 | 1211662.0183
133 | 2684738.0522 | 1211930.0105 | 2684736.7941 | 1211925.6588
134 | 2684738.9949 | 1211932.9545 | 2684738.2506 | 1211930.697 | 2684738.0522 | 1211930.0105
135 | 2684739.941 | 1211935.8242 | 2684738.9949 | 1211932.9545
136 | 2684739.941 | 1211935.8242 | 2684743.7291 | 1211947.3148
137 | 2684745.8997 | 1211953.8987 | 2684745.8997 | 1211953.8987 | 2684743.7291 | 1211947.3148
138 | 2684611.77 | 1211983.6548 | 2684592.9973 | 1211996.2326
139 | 2684587.7624 | 1211999.74 | 2684592.9973 | 1211996.2326
140 | 2684587.7624 | 1211999.74 | 2684588.5292 | 1212017.4625 | 2684592.7025 | 1212029.5119
141 | 2684587.7624 | 1211999.74 | 2684565.6872 | 1212007.3349
142 | 2684565.6872 | 1212007.3349 | 2684555.0965 | 1212010.9785
143 | 2684550.7351 | 1212012.4791 | 2684555.0965 | 1212010.9785
144 | 2684542.0891 | 1212015.5919 | 2684550.7351 | 1212012.4791
145 | 2684595.2601 | 1212047.5666 | 2684594.7559 | 1212035.4404 | 2684592.7025 | 1212029.5119
146 | 2684595.2601 | 1212047.5666 | 2684594.7036 | 1212059.8739
147 | 2684595.2601 | 1212047.5666 | 2684611.9817 | 1212043.4822
148 | 2684594.1195 | 1212072.7893 | 2684594.7036 | 1212059.8739
149 | 2684611.9817 | 1212043.4822 | 2684624.0626 | 1212040.5313
150 | 2684594.1195 | 1212072.7893 | 2684601.2859 | 1212103.2553
151 | 2684624.0626 | 1212040.5313 | 2684633.8074 | 1212038.151
152 | 2684812.0015 | 1211958.3953 | 2684811.4952 | 1211956.4325 | 2684807.1113 | 1211945.0634
153 | 2684812.0015 | 1211958.3953 | 2684813.3029 | 1211963.4406 | 2684809.8609 | 1211972.4976 | 2684802.8173 | 1211978.493
154 | 2684802.8173 | 1211978.493 | 2684802.7304 | 1211978.5669 | 2684792.4385 | 1211980.3885 | 2684789.3675 | 1211983.0544
155 | 2684785.3063 | 1211986.5801 | 2684785.3063 | 1211986.5801 | 2684789.3675 | 1211983.0544
156 | 2684745.8997 | 1211953.8987 | 2684747.6443 | 1211964.8084 | 2684746.9757 | 1211967.7769
157 | 2684645.2 | 1212092.4191 | 2684634.1308 | 1212095.1505
158 | 2684601.2859 | 1212103.2553 | 2684634.1308 | 1212095.1505
159 | 2685221.3772 | 1211910.7389 | 2685216.9858 | 1211904.9771 | 2685216.5733 | 1211904.3791
160 | 2685221.3772 | 1211910.7389 | 2685225.5189 | 1211916.173 | 2685229.0952 | 1211920.0934 | 2685229.6839 | 1211924.0933 | 2685228.2519 | 1211927.5196 | 2685225.1472 | 1211931.0108 | 2685221.3337 | 1211933.7071
161 | 2684642.5976 | 1212036.0039 | 2684633.8074 | 1212038.151
162 | 2684642.5976 | 1212036.0039 | 2684662.3554 | 1212031.1778
163 | 2684662.7127 | 1212031.0905 | 2684662.3554 | 1212031.1778
164 | 2685500.6433 | 1211781.2987 | 2685513.6703 | 1211768.9662 | 2685521.846 | 1211766.3817 | 2685531.7045 | 1211765.1556 | 2685542.421 | 1211767.6887 | 2685551.5996 | 1211774.6582 | 2685577.2946 | 1211813.141 | 2685595.5024 | 1211833.7602 | 2685625.2102 | 1211854.7114 | 2685645.05 | 1211871.7296 | 2685668.1681 | 1211898.5681 | 2685691.011 | 1211918.1091 | 2685740.7218 | 1211952.5683 | 2685767.0657 | 1211970.6367 | 2685774.5549 | 1211977.2042 | 2685780.4736 | 1211985.1835 | 2685798.0491 | 1212017.4819
165 | 2685810.2429 | 1212039.8906 | 2685798.0491 | 1212017.4819
166 | 2685830.1197 | 1212076.3132 | 2685828.1047 | 1212072.7152 | 2685810.2429 | 1212039.8906
167 | 2686169.3291 | 1211882.8422 | 2686164.1576 | 1211872.6163 | 2686164.2941 | 1211863.1676 | 2686171.2475 | 1211851.06
168 | 2685744.553 | 1211579.9667 | 2685717.1632 | 1211567.3871 | 2685672.4907 | 1211549.1 | 2685656.275 | 1211537.882
169 | 2685980.48 | 1211660.871 | 2685946.5722 | 1211650.3088 | 2685939.485 | 1211649.0503 | 2685857.0655 | 1211618.2545 | 2685786.4478 | 1211595.8572 | 2685744.553 | 1211579.9667
170 | 2685648.0239 | 1212219.357 | 2685646.2102 | 1212216.2401 | 2685641.5899 | 1212211.504 | 2685638.087 | 1212209.2087
171 | 2685649.546 | 1212225.2272 | 2685649.546 | 1212225.2272 | 2685648.598 | 1212220.3437 | 2685648.0239 | 1212219.357
172 | 2685670.1219 | 1212058.2125 | 2685668.2136 | 1212060.9203 | 2685665.7293 | 1212063.5307 | 2685660.7725 | 1212067.9291 | 2685655.3926 | 1212073.7446 | 2685653.7038 | 1212077.5784 | 2685652.9151 | 1212090.1643 | 2685653.0425 | 1212095.0471 | 2685655.0131 | 1212100.1566 | 2685658.0118 | 1212104.0578 | 2685660.6049 | 1212108.1533 | 2685661.1572 | 1212112.0193 | 2685661.2863 | 1212117.3135 | 2685659.3942 | 1212121.5447 | 2685655.6956 | 1212123.5262 | 2685649.958 | 1212125.6786 | 2685634.3974 | 1212130.3361 | 2685628.657 | 1212132.6885 | 2685624.9438 | 1212135.6817 | 2685620.6053 | 1212139.8888 | 2685617.8724 | 1212145.5311 | 2685616.9835 | 1212150.8107 | 2685616.4817 | 1212157.7081 | 2685618.3922 | 1212166.4746 | 2685619.1264 | 1212171.9665 | 2685618.8716 | 1212175.4207 | 2685616.7657 | 1212180.2603 | 2685613.8158 | 1212186.7223 | 2685611.7011 | 1212192.1733 | 2685612.4544 | 1212196.865 | 2685614.0219 | 1212200.9457 | 2685617.454 | 1212203.2298 | 2685621.7079 | 1212204.9142 | 2685627.201 | 1212206.016 | 2685632.8947 | 1212206.9094 | 2685637.1485 | 1212208.5938 | 2685638.087 | 1212209.2087
173 | 2685648.0477 | 1212230.0867 | 2685648.0477 | 1212230.0867 | 2685649.546 | 1212225.2272
174 | 2685670.1219 | 1212058.2125 | 2685700.3923 | 1212066.8864 | 2685718.359 | 1212073.0041 | 2685716.3233 | 1212074.0088 | 2685714.8676 | 1212076.4229 | 2685715.4286 | 1212079.6886 | 2685718.8317 | 1212083.9959 | 2685725.6552 | 1212091.41 | 2685729.0405 | 1212096.9512 | 2685731.3816 | 1212104.3008 | 2685732.4967 | 1212111.8329 | 2685732.5417 | 1212119.2718 | 2685733.6771 | 1212125.3921 | 2685737.4261 | 1212134.174 | 2685740.9973 | 1212140.5295 | 2685746.2007 | 1212147.5089 | 2685751.6305 | 1212156.1927 | 2685756.143 | 1212164.7187 | 2685759.4873 | 1212173.1057 | 2685761.4066 | 1212181.2498 | 2685762.2989 | 1212190.0017 | 2685763.8258 | 1212211.1598 | 2685765.5474 | 1212219.3122 | 2685769.9098 | 1212227.7027 | 2685780.5762 | 1212240.52 | 2685786.6215 | 1212245.488 | 2685792.8404 | 1212248.9575 | 2685803.5859 | 1212252.57 | 2685813.7384 | 1212255.1511 | 2685819.0149 | 1212257.0505 | 2685828.9967 | 1212260.93 | 2685840.0858 | 1212265.4814 | 2685845.001 | 1212267.6647 | 2685847.4386 | 1212268.3002 | 2685850.6426 | 1212268.4798 | 2685853.3173 | 1212266.895 | 2685863.7948 | 1212261.1531 | 2685868.764 | 1212259.0566 | 2685874.8419 | 1212258.0657 | 2685886.6687 | 1212257.8247 | 2685887.9374 | 1212257.8429
175 | 2685670.1219 | 1212058.2125 | 2685700.3923 | 1212066.8864 | 2685718.359 | 1212073.0041 | 2685724.8572 | 1212072.9196 | 2685735.197 | 1212076.2371 | 2685743.2711 | 1212080.7005 | 2685753.2154 | 1212087.2144 | 2685794.7167 | 1212118.0537 | 2685836.0857 | 1212142.2203 | 2685843.4924 | 1212144.9954 | 2685851.0104 | 1212145.326 | 2685861.1154 | 1212140.1347 | 2685866.3551 | 1212135.0957 | 2685862.0711 | 1212131.8096 | 2685858.0458 | 1212127.4488 | 2685853.3089 | 1212121.321 | 2685847.8939 | 1212112.1482 | 2685843.9368 | 1212104.1081 | 2685835.1463 | 1212086.0809
176 | 2685648.0477 | 1212230.0867 | 2685644.528 | 1212233.8942 | 2685639.3826 | 1212237.6784 | 2685632.6049 | 1212240.8388 | 2685627.6706 | 1212244.2146 | 2685622.0957 | 1212248.8043 | 2685616.6654 | 1212254.6582
177 | 2685887.9374 | 1212257.8429 | 2685890.7847 | 1212256.6164
178 | 2685812.7887 | 1212080.411 | 2685816.5681 | 1212083.9121 | 2685820.2611 | 1212085.4997 | 2685826.9866 | 1212086.5082 | 2685835.1463 | 1212086.0809
179 | 2685835.1463 | 1212086.0809 | 2685830.1197 | 1212076.3132
180 | 2685918.5648 | 1212242.7184 | 2685908.2256 | 1212246.7611 | 2685901.857 | 1212250.5274 | 2685895.5299 | 1212254.5723 | 2685890.7847 | 1212256.6164
181 | 2685862.0501 | 1212087.3689 | 2685879.8989 | 1212095.8536 | 2685888.9327 | 1212100.1532 | 2685894.3206 | 1212102.2052
182 | 2685862.0501 | 1212087.3689 | 2685836.706 | 1212074.8626 | 2685832.999 | 1212074.7758 | 2685830.1197 | 1212076.3132
183 | 2684855.1654 | 1212018.4054 | 2684858.3527 | 1212020.8412 | 2684861.2631 | 1212022.9729 | 2684863.5473 | 1212025.318 | 2684868.1473 | 1212027.2625 | 2684869.646 | 1212027.2839
184 | 2684855.1654 | 1212018.4054 | 2684862.5411 | 1212011.1277 | 2684869.8699 | 1212006.6068 | 2684874.0331 | 1212005.6098
185 | 2684855.1654 | 1212018.4054 | 2684852.2432 | 1212021.3769 | 2684850.7936 | 1212026.0188
186 | 2684874.0331 | 1212005.6098 | 2684877.4894 | 1212006.2261 | 2684881.0139 | 1212009.5228 | 2684884.5457 | 1212012.8419 | 2684889.9457 | 1212017.2995 | 2684890.6584 | 1212017.4097 | 2684890.3286 | 1212009.6221 | 2684889.3867 | 1212004.2607 | 2684886.231 | 1211998.0117 | 2684881.0172 | 1211992.7452 | 2684876.1785 | 1211990.486 | 2684869.4324 | 1211990.3677 | 2684867.1157 | 1211987.0992 | 2684866.7868 | 1211982.9807 | 2684868.4002 | 1211980.1352 | 2684870.9303 | 1211979.0927 | 2684873.8268 | 1211979.5342 | 2684884.4198 | 1211983.7877 | 2684888.373 | 1211983.1324 | 2684890.0182 | 1211979.6535 | 2684886.1249 | 1211972.3711 | 2684881.6404 | 1211963.9129 | 2684879.2235 | 1211954.8725
187 | 2684851.3129 | 1212054.1741 | 2684852.6266 | 1212041.4177 | 2684851.0396 | 1212032.2669 | 2684850.4837 | 1212027.0111 | 2684850.7936 | 1212026.0188
188 | 2684879.2235 | 1211954.8725 | 2684880.0678 | 1211949.481 | 2684882.2924 | 1211943.7422 | 2684884.2805 | 1211938.6005 | 2684888.5024 | 1211933.4794 | 2684890.7269 | 1211932.2225
189 | 2684851.3129 | 1212054.1741 | 2684849.6422 | 1212061.0437 | 2684849.1515 | 1212067.7523 | 2684852.4402 | 1212072.1353 | 2684857.7421 | 1212074.4122 | 2684861.9006 | 1212076.406 | 2684869.2092 | 1212083.9816 | 2684873.9516 | 1212097.2689 | 2684875.741 | 1212103.9432 | 2684879.7663 | 1212113.1621 | 2684889.6952 | 1212122.9431 | 2684896.0025 | 1212127.2101
190 | 2684963.0885 | 1212181.2263 | 2684954.8621 | 1212170.3576 | 2684947.6111 | 1212162.4936 | 2684939.4731 | 1212155.5509 | 2684928.2492 | 1212150.2654 | 2684916.204 | 1212145.5575 | 2684900.7587 | 1212130.4277 | 2684896.0025 | 1212127.2101
191 | 2684963.0885 | 1212181.2263 | 2684966.4224 | 1212185.6211 | 2684979.8169 | 1212198.009 | 2684984.0073 | 1212199.8921 | 2684987.1245 | 1212204.0281 | 2684995.9971 | 1212212.7381 | 2685006.291 | 1212221.4127 | 2685019.0311 | 1212227.4649 | 2685022.8429 | 1212226.0516 | 2685022.4893 | 1212221.0099 | 2685023.1749 | 1212202.7743 | 2685023.5742 | 1212189.16 | 2685020.0062 | 1212174.0103 | 2685016.2433 | 1212163.9945
192 | 2684907.931 | 1211928.8084 | 2684908.46 | 1211923.6792 | 2684909.1999 | 1211920.0013
193 | 2684907.931 | 1211928.8084 | 2684914.4935 | 1211931.6814 | 2684919.4856 | 1211934.9102 | 2684921.1171 | 1211946.8079 | 2684926.7114 | 1211955.2375 | 2684929.639 | 1211959.3597 | 2684932.2216 | 1211964.7667 | 2684935.7439 | 1211968.7528 | 2684938.7126 | 1211969.4622
194 | 2684812.8512 | 1211622.8661 | 2684808.3244 | 1211626.9711 | 2684800.8092 | 1211641.8963 | 2684787.9474 | 1211652.3203 | 2684786.6633 | 1211659.2511 | 2684781.3086 | 1211662.0183
195 | 2684812.8512 | 1211622.8661 | 2684820.6498 | 1211615.8056 | 2684825.38 | 1211614.4943 | 2684834.9431 | 1211629.7625 | 2684850.6795 | 1211641.0937 | 2684863.21 | 1211647.554 | 2684877.4026 | 1211647.756 | 2684872.7651 | 1211636.1491 | 2684867.2198 | 1211625.3186 | 2684865.6297 | 1211615.8342 | 2684870.3375 | 1211610.7645 | 2684879.4648 | 1211608.5929 | 2684882.4075 | 1211607.4007 | 2684887.0018 | 1211595.3582 | 2684901.213 | 1211591.0575
196 | 2684807.3604 | 1211709.7006 | 2684801.9624 | 1211700.2621 | 2684796.1441 | 1211694.7313 | 2684789.5947 | 1211690.3798 | 2684784.8268 | 1211690.0674 | 2684780.3724 | 1211691.2271 | 2684769.9754 | 1211696.6607
197 | 2684901.213 | 1211591.0575 | 2684900.6038 | 1211582.61 | 2684905.933 | 1211577.6604 | 2684912.9039 | 1211578.0376 | 2684944.178 | 1211568.243 | 2684948.6881 | 1211569.0522 | 2684951.8342 | 1211571.721 | 2684960.0305 | 1211579.9653 | 2684968.8985 | 1211589.0643 | 2684972.286 | 1211597.5491
198 | 2684944.0275 | 1211822.0298 | 2684944.287 | 1211825.6804 | 2684944.9026 | 1211834.2058 | 2684949.8165 | 1211846.6618 | 2684960.818 | 1211847.33 | 2684967.8374 | 1211850.1429 | 2684971.2664 | 1211853.216 | 2684968.3356 | 1211856.7766 | 2684962.5886 | 1211858.5292 | 2684960.2471 | 1211858.5959 | 2684961.6301 | 1211879.396 | 2684965.1065 | 1211878.6005 | 2684969.7449 | 1211879.456 | 2684976.4621 | 1211883.2097 | 2684980.7342 | 1211887.3733 | 2684982.8025 | 1211891.5388 | 2684982.842 | 1211898.8998 | 2684980.9777 | 1211903.8765 | 2684977.6865 | 1211907.1318 | 2684986.5457 | 1211912.0167 | 2684987.4416 | 1211919.5344 | 2684970.2927 | 1211919.4012 | 2684968.5486 | 1211932.4738
199 | 2684944.0275 | 1211822.0298 | 2684956.3189 | 1211816.9682 | 2684965.4589 | 1211812.2842 | 2684976.743 | 1211815.5248 | 2684994.0075 | 1211808.6329 | 2684997.6044 | 1211805.7933 | 2685003.939 | 1211795.3434 | 2685020.6992 | 1211775.8694 | 2685021.2174 | 1211774.9954
200 | 2684968.5486 | 1211932.4738 | 2684967.4397 | 1211933.5985
201 | 2685025.5501 | 1211767.6887 | 2685021.2174 | 1211774.9954
202 | 2684938.7126 | 1211969.4622 | 2684938.4276 | 1211954.7929 | 2684938.9768 | 1211946.6509 | 2684942.9379 | 1211942.7714 | 2684953.2414 | 1211937.4813 | 2684965.5107 | 1211935.5548 | 2684967.4397 | 1211933.5985
203 | 2684981.9276 | 1211612.2031 | 2684975.8764 | 1211606.5418 | 2684972.286 | 1211597.5491
204 | 2685003.0314 | 1211637.8047 | 2685019.0501 | 1211726.3134 | 2685023.8724 | 1211741.4587 | 2685026.5867 | 1211752.5491 | 2685025.5501 | 1211767.6887
205 | 2685003.0314 | 1211637.8047 | 2684995.0018 | 1211633.8766 | 2684991.0732 | 1211626.9272 | 2684990.2001 | 1211619.4098 | 2684983.7207 | 1211613.8806 | 2684981.9276 | 1211612.2031
206 | 2685003.0314 | 1211637.8047 | 2685014.8606 | 1211632.681 | 2685027.1748 | 1211626.4678
207 | 2685016.2433 | 1212163.9945 | 2685018.2291 | 1212158.4858 | 2685019.9889 | 1212154.9753 | 2685022.9206 | 1212148.6796 | 2685022.7098 | 1212138.4143 | 2685019.1689 | 1212126.6894 | 2685018.5887 | 1212110.7782
208 | 2685980.48 | 1211660.871 | 2685976.1859 | 1211664.0668 | 2685968.5036 | 1211671.4054 | 2685958.5556 | 1211685.1489 | 2685950.4161 | 1211695.7386 | 2685939.3006 | 1211703.4947 | 2685933.7102 | 1211706.4717 | 2685924.1488 | 1211708.1573 | 2685917.8042 | 1211709.6892 | 2685914.4775 | 1211714.311 | 2685911.4351 | 1211727.6871 | 2685906.5601 | 1211740.6143 | 2685897.4972 | 1211749.901 | 2685886.1327 | 1211760.7112 | 2685882.9315 | 1211767.7031 | 2685883.3428 | 1211773.0707
209 | 2685384.7184 | 1211389.692 | 2685390.8183 | 1211387.7558 | 2685401.7882 | 1211387.5016 | 2685415.9781 | 1211388.9946 | 2685457.2151 | 1211403.7392 | 2685476.5523 | 1211404.539 | 2685490.4777 | 1211402.2147 | 2685502.1109 | 1211404.9944 | 2685604.8644 | 1211497.6844 | 2685617.5578 | 1211508.6404 | 2685656.275 | 1211537.882
210 | 2685208.7072 | 1211941.8943 | 2685208.7072 | 1211941.8943 | 2685211.1849 | 1211938.672 | 2685217.3325 | 1211936.5362 | 2685221.3337 | 1211933.7071
211 | 2685213.9539 | 1211950.8285 | 2685213.5041 | 1211948.1336 | 2685209.2942 | 1211945.4828 | 2685208.7072 | 1211941.8943
212 | 2684730.9214 | 1211979.3476 | 2684724.6144 | 1211975.8775
213 | 2684744.027 | 1211980.8676 | 2684733.2853 | 1211980.6482 | 2684730.9214 | 1211979.3476
214 | 2684721.8482 | 1211972.3721 | 2684724.6144 | 1211975.8775 | 2684724.6144 | 1211975.8775
215 | 2684744.027 | 1211980.8676 | 2684742.85 | 1211986.1543 | 2684742.1193 | 1211996.3951 | 2684742.7192 | 1211999.2152
216 | 2684744.027 | 1211980.8676 | 2684746.6411 | 1211969.2624
217 | 2684721.8482 | 1211972.3721 | 2684718.3472 | 1211967.9357
218 | 2684742.7192 | 1211999.2152 | 2684743.9087 | 1212004.8074
219 | 2684746.9757 | 1211967.7769 | 2684746.6411 | 1211969.2624
220 | 2684712.2981 | 1211960.2701 | 2684718.3472 | 1211967.9357
221 | 2684740.7138 | 1212037.0019 | 2684746.3113 | 1212031.8558 | 2684747.6965 | 1212022.6138 | 2684743.9087 | 1212004.8074
222 | 2684732.4816 | 1212037.7298 | 2684740.7138 | 1212037.0019 | 2684740.7138 | 1212037.0019
223 | 2684732.4816 | 1212037.7298 | 2684732.4816 | 1212037.7298 | 2684723.6463 | 1212034.3799
224 | 2684720.4165 | 1212028.524 | 2684717.3613 | 1212022.9846
225 | 2684720.4165 | 1212028.524 | 2684723.6463 | 1212034.3799 | 2684723.6463 | 1212034.3799
226 | 2684717.3613 | 1212022.9846 | 2684716.749 | 1212021.8744
227 | 2684713.2381 | 1212015.5086 | 2684716.749 | 1212021.8744
228 | 2684785.3063 | 1211986.5801 | 2684780.7318 | 1211997.2665 | 2684780.4529 | 1211998.4687
229 | 2684779.2475 | 1212003.665 | 2684780.4529 | 1211998.4687
230 | 2684777.7135 | 1212016.6172 | 2684778.449 | 1212007.1072 | 2684779.2475 | 1212003.665
231 | 2684777.7135 | 1212016.6172 | 2684776.7887 | 1212028.5765
232 | 2684776.7887 | 1212028.5765 | 2684775.91 | 1212039.9389
233 | 2684775.91 | 1212039.9389 | 2684774.7599 | 1212054.8115
234 | 2684774.7599 | 1212054.8115 | 2684774.1792 | 1212062.3201
235 | 2684772.5764 | 1212083.0466 | 2684774.1792 | 1212062.3201
236 | 2684759.7883 | 1212184.403 | 2684765.3396 | 1212170.2059 | 2684768.0333 | 1212154.9786 | 2684761.6675 | 1212130.2608 | 2684762.5881 | 1212110.939 | 2684771.7824 | 1212093.3136 | 2684772.5764 | 1212083.0466
237 | 2684759.7883 | 1212184.403 | 2684770.9521 | 1212180.0255 | 2684798.6654 | 1212147.3534
238 | 2684848.027 | 1211948.6164 | 2684848.9427 | 1211947.2087
239 | 2684836.0906 | 1211982.2214 | 2684844.532 | 1211953.9896 | 2684848.027 | 1211948.6164
240 | 2685132.4853 | 1212081.7103 | 2685133.8401 | 1212064.9953 | 2685135.3874 | 1212056.8683
241 | 2685135.3874 | 1212056.8683 | 2685139.3789 | 1212035.9041
242 | 2685139.3789 | 1212035.9041 | 2685140.7899 | 1212028.4927 | 2685143.567 | 1212017.5884
243 | 2685143.567 | 1212017.5884 | 2685147.6402 | 1212001.5949
244 | 2685147.6402 | 1212001.5949 | 2685152.318 | 1211983.2274 | 2685152.6444 | 1211981.2834

## bus_geodata
| x | y | coords
0 | 2685507.544 | 1211609.5735
1 | 2685491.2852 | 1211610.3838
2 | 2685552.3492 | 1211681.7701
3 | 2685482.2505 | 1211610.8341
4 | 2685553.6647 | 1211694.2905
5 | 2685460.3581 | 1211624.1882
6 | 2685767.1252 | 1211833.914
7 | 2685443.1284 | 1211781.9816
8 | 2685455.7959 | 1211628.4237
9 | 2686101.1511 | 1211864.6063
10 | 2685810.5457 | 1211726.4346
11 | 2685377.4066 | 1211819.0809
12 | 2685451.5752 | 1211632.3421
13 | 2686122.7222 | 1211861.9443
14 | 2685779.2481 | 1211658.3723
15 | 2685391.4701 | 1211822.3693
16 | 2685319.2429 | 1211840.5403
17 | 2685316.5441 | 1211816.909
18 | 2685295.4738 | 1211834.4812
19 | 2685342.5624 | 1211794.0268
20 | 2685263.513 | 1211862.2903
21 | 2685367.7387 | 1211777.6291
22 | 2685257.3827 | 1211870.376
23 | 2685400.9765 | 1211767.1739
24 | 2685225.373 | 1211885.4507
25 | 2685263.1491 | 1211867.6606
26 | 2685440.6026 | 1211739.9222
27 | 2685207.5608 | 1211891.3113
28 | 2685251.0488 | 1211910.5259
29 | 2685084.0283 | 1211874.4358
30 | 2685108.4729 | 1211859.3868
31 | 2685062.6488 | 1211865.7042
32 | 2685079.9153 | 1211823.5338
33 | 2685117.6342 | 1211863.1201
34 | 2685016.0266 | 1211981.5047
35 | 2685136.9681 | 1211686.302
36 | 2684634.6777 | 1211739.5791
37 | 2684630.5637 | 1211745.6692
38 | 2684648.1413 | 1211747.8813
39 | 2684748.4062 | 1211868.4448
40 | 2684786.557 | 1211858.0836
41 | 2684732.8809 | 1211865.2778
42 | 2684781.5858 | 1211898.3106
43 | 2684883.9027 | 1211911.7663
44 | 2684881.2418 | 1211890.5034
45 | 2684871.5426 | 1211926.1504
46 | 2684898.3855 | 1211915.019
47 | 2685165.8641 | 1211902.5566
48 | 2685174.0423 | 1211900.8389
49 | 2685162.7913 | 1211920.8561
50 | 2684701.3211 | 1211792.0816
51 | 2684732.6724 | 1211804.0235
52 | 2684697.9165 | 1211813.4917
53 | 2684692.5228 | 1211786.3297
54 | 2684813.9177 | 1211865.7407
55 | 2684810.9547 | 1211871.0354
56 | 2684855.2131 | 1211889.4558
57 | 2684599.7205 | 1211789.4605
58 | 2684663.1712 | 1211767.1544
59 | 2684718.8696 | 1211848.0786
60 | 2684728.0488 | 1211867.355
61 | 2684756.1617 | 1211855.2518
62 | 2684631.9632 | 1211804.4082
63 | 2684583.6686 | 1211830.3486
64 | 2684749.0232 | 1211814.632
65 | 2684757.0609 | 1211819.847
66 | 2684764.2556 | 1211808.7308
67 | 2684764.8288 | 1211824.8581
68 | 2684691.5427 | 1211825.1311
69 | 2684702.5277 | 1211816.3782
70 | 2685135.9061 | 1211862.8473
71 | 2684682.98 | 1211780.0911
72 | 2684670.8924 | 1211790.6153
73 | 2685016.8134 | 1212026.1165
74 | 2684716.8837 | 1211871.6297
75 | 2684723.1492 | 1211878.4593
76 | 2684692.6269 | 1211890.5673
77 | 2684664.1255 | 1211901.311
78 | 2684729.4605 | 1211900.2907
79 | 2684618.6016 | 1211859.7855
80 | 2684621.6102 | 1211844.4217
81 | 2684635.4642 | 1211867.0474
82 | 2684585.2951 | 1211931.0266
83 | 2684594.7758 | 1211927.4528
84 | 2684580.6292 | 1211932.7234
85 | 2684647.5181 | 1211892.8063
86 | 2684667.4984 | 1211890.5375
87 | 2684566.9631 | 1211937.6933
88 | 2684578.1873 | 1211961.767
89 | 2684470.2462 | 1211981.5408
90 | 2684510.1503 | 1211959.5192
91 | 2685163.7862 | 1211690.3319
92 | 2684802.923 | 1211934.2016
93 | 2684867.5668 | 1211929.7904
94 | 2684900.5175 | 1211927.5242
95 | 2685211.9542 | 1211837.5275
96 | 2685187.9491 | 1211897.7547
97 | 2685156.4767 | 1211958.461
98 | 2684824.3439 | 1211897.5531
99 | 2684742.8947 | 1211819.9021
100 | 2684665.9623 | 1211807.0784
101 | 2684784.7992 | 1211837.6887
102 | 2684717.658 | 1211825.8494
103 | 2684696.297 | 1211879.5116
104 | 2684641.8662 | 1211909.7018
105 | 2684666.9778 | 1211932.8454
106 | 2684660.114 | 1211940.4681
107 | 2684729.5235 | 1211900.5087
108 | 2684615.4197 | 1211919.671
109 | 2684688.9202 | 1211882.3359
110 | 2684586.2973 | 1211979.8087
111 | 2684523.33 | 1211954.3409
112 | 2684649.3592 | 1211951.7695
113 | 2684653.9678 | 1211946.9267
114 | 2684644.8016 | 1211956.5588
115 | 2684640.5695 | 1211960.9406
116 | 2684632.2702 | 1211967.8581
117 | 2684627.9917 | 1211971.4242
118 | 2684618.2347 | 1211979.3234
119 | 2684765.5259 | 1211636.0304
120 | 2684765.0871 | 1211667.9391
121 | 2684736.7941 | 1211925.6588
122 | 2684738.0522 | 1211930.0105
123 | 2684738.9949 | 1211932.9545
124 | 2684739.941 | 1211935.8242
125 | 2684743.7291 | 1211947.3148
126 | 2684611.77 | 1211983.6548
127 | 2684592.9973 | 1211996.2326
128 | 2684587.7624 | 1211999.74
129 | 2684565.6872 | 1212007.3349
130 | 2684555.0965 | 1212010.9785
131 | 2684550.7351 | 1212012.4791
132 | 2684592.7025 | 1212029.5119
133 | 2684542.0891 | 1212015.5919
134 | 2684595.2601 | 1212047.5666
135 | 2684594.7036 | 1212059.8739
136 | 2684611.9817 | 1212043.4822
137 | 2684594.1195 | 1212072.7893
138 | 2684624.0626 | 1212040.5313
139 | 2684807.1113 | 1211945.0634
140 | 2684812.0015 | 1211958.3953
141 | 2684802.8173 | 1211978.493
142 | 2684789.3675 | 1211983.0544
143 | 2684745.8997 | 1211953.8987
144 | 2684537.8151 | 1211948.6497
145 | 2684634.1308 | 1212095.1505
146 | 2684645.2 | 1212092.4191
147 | 2684601.2859 | 1212103.2553
148 | 2685216.5733 | 1211904.379
149 | 2685221.3772 | 1211910.7389
150 | 2684633.8074 | 1212038.151
151 | 2684642.5976 | 1212036.0039
152 | 2684662.3554 | 1212031.1778
153 | 2684662.7127 | 1212031.0905
154 | 2685500.6433 | 1211781.2987
155 | 2685798.0491 | 1212017.4819
156 | 2685810.2429 | 1212039.8906
157 | 2686171.2475 | 1211851.06
158 | 2685744.553 | 1211579.9667
159 | 2685648.0239 | 1212219.357
160 | 2685638.087 | 1212209.2087
161 | 2685649.546 | 1212225.2272
162 | 2685670.1219 | 1212058.2125
163 | 2685648.0477 | 1212230.0867
164 | 2685887.9374 | 1212257.8429
165 | 2685835.1463 | 1212086.0809
166 | 2685616.6654 | 1212254.6582
167 | 2685890.7847 | 1212256.6164
168 | 2685862.0501 | 1212087.3689
169 | 2685894.3206 | 1212102.2052
170 | 2685830.1197 | 1212076.3132
171 | 2685812.7887 | 1212080.411
172 | 2685918.5648 | 1212242.7184
173 | 2686169.3291 | 1211882.8422
174 | 2684869.646 | 1212027.2839
175 | 2684855.1654 | 1212018.4054
176 | 2684874.0331 | 1212005.6098
177 | 2684850.7936 | 1212026.0188
178 | 2684879.2235 | 1211954.8725
179 | 2684851.3129 | 1212054.1741
180 | 2684890.7269 | 1211932.2225
181 | 2684896.0025 | 1212127.2101
182 | 2684963.0885 | 1212181.2263
183 | 2684907.931 | 1211928.8084
184 | 2684781.3086 | 1211662.0183
185 | 2684812.8512 | 1211622.8661
186 | 2684807.3604 | 1211709.7006
187 | 2684901.213 | 1211591.0575
188 | 2684769.9754 | 1211696.6607
189 | 2684944.0275 | 1211822.0298
190 | 2684968.5486 | 1211932.4738
191 | 2685021.2174 | 1211774.9954
192 | 2684967.4397 | 1211933.5985
193 | 2684972.286 | 1211597.5491
194 | 2685025.5501 | 1211767.6887
195 | 2684938.7126 | 1211969.4622
196 | 2684981.9276 | 1211612.2031
197 | 2685003.0314 | 1211637.8047
198 | 2685027.1748 | 1211626.4678
199 | 2684909.1999 | 1211920.0013
200 | 2685018.5887 | 1212110.7782
201 | 2685016.2433 | 1212163.9945
202 | 2685883.3428 | 1211773.0707
203 | 2685980.48 | 1211660.871
204 | 2685656.275 | 1211537.882
205 | 2685384.7184 | 1211389.692
206 | 2685221.3337 | 1211933.7071
207 | 2685208.7072 | 1211941.8943
208 | 2685213.9539 | 1211950.8285
209 | 2684730.9214 | 1211979.3476
210 | 2684724.6144 | 1211975.8775
211 | 2684744.027 | 1211980.8676
212 | 2684721.8482 | 1211972.3721
213 | 2684742.7192 | 1211999.2152
214 | 2684746.6411 | 1211969.2624
215 | 2684718.3472 | 1211967.9357
216 | 2684743.9087 | 1212004.8074
217 | 2684746.9757 | 1211967.7769
218 | 2684712.2981 | 1211960.2701
219 | 2684740.7138 | 1212037.0019
220 | 2684732.4816 | 1212037.7298
221 | 2684720.4165 | 1212028.524
222 | 2684717.3613 | 1212022.9846
223 | 2684723.6463 | 1212034.3799
224 | 2684716.749 | 1212021.8744
225 | 2684713.2381 | 1212015.5086
226 | 2684785.3063 | 1211986.5801
227 | 2684780.4529 | 1211998.4687
228 | 2684779.2475 | 1212003.665
229 | 2684777.7135 | 1212016.6172
230 | 2684776.7887 | 1212028.5765
231 | 2684775.91 | 1212039.9389
232 | 2684774.7599 | 1212054.8115
233 | 2684774.1792 | 1212062.3201
234 | 2684772.5764 | 1212083.0466
235 | 2684759.7883 | 1212184.403
236 | 2684798.6654 | 1212147.3534
237 | 2684848.027 | 1211948.6164
238 | 2684848.9427 | 1211947.2087
239 | 2684836.0906 | 1211982.2214
240 | 2685132.4853 | 1212081.7103
241 | 2685135.3874 | 1212056.8683
242 | 2685139.3789 | 1212035.9041
243 | 2685143.567 | 1212017.5884
244 | 2685147.6402 | 1212001.5949
245 | 2685152.6444 | 1211981.2834
246 | 2684781.5858 | 1211898.3106

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97496 | -0.48484 | 0.00014278 | 3.5785e-05
1 | 0.97491 | -0.48584 | 0.00043273 | 0.00010845
2 | 0.97526 | -0.47892 | 4.8707e-05 | 1.2207e-05
3 | 0.97489 | -0.48633 | 0.00027723 | 6.948e-05
4 | 0.97531 | -0.4781 | 0 | 0
5 | 0.97483 | -0.48759 | 0.00036227 | 9.0794e-05
6 | 0.97455 | -0.49324 | 0 | 0
7 | 0.97618 | -0.4607 | 0.00040958 | 0.00010265
8 | 0.97481 | -0.48786 | 8.997e-05 | 2.2549e-05
9 | 0.97401 | -0.50408 | 0.00041665 | 0.00010442
10 | 0.9744 | -0.49647 | 0.00011624 | 2.9133e-05
11 | 0.97667 | -0.45093 | 0 | 0
12 | 0.9748 | -0.48809 | 0.0022068 | 0.00055308
13 | 0.97398 | -0.5046 | 0 | 0
14 | 0.97432 | -0.49809 | 0.00011416 | 2.861e-05
15 | 0.97658 | -0.45282 | 0.00041212 | 0.00010329
16 | 0.97749 | -0.4347 | 0.001182 | 0.00029624
17 | 0.97828 | -0.41916 | 0.0001589 | 3.9823e-05
18 | 0.97833 | -0.41801 | 0.00042025 | 0.00010533
19 | 0.97821 | -0.42052 | 0.00042263 | 0.00010592
20 | 0.97844 | -0.41589 | 0.00016839 | 4.2201e-05
21 | 0.97816 | -0.42146 | 0.00049265 | 0.00012347
22 | 0.97847 | -0.41535 | 0 | 0
23 | 0.97812 | -0.42226 | 0.00042105 | 0.00010553
24 | 0.9791 | -0.40287 | 0 | 0
25 | 0.97837 | -0.41727 | 0.0011934 | 0.00029908
26 | 0.97808 | -0.42311 | 0.0008095 | 0.00020288
27 | 0.97944 | -0.39617 | 0 | 0
28 | 0.97909 | -0.40304 | 0.00025013 | 6.2688e-05
29 | 0.98571 | -0.27358 | 0.0017178 | 0.00043053
30 | 0.98555 | -0.27665 | 0.0042913 | 0.0010755
31 | 0.98584 | -0.27109 | 0 | 0
32 | 0.98583 | -0.27124 | 0 | 0
33 | 0.98352 | -0.31625 | 0 | 0
34 | 0.98861 | -0.21737 | 0 | 0
35 | 0.98581 | -0.27172 | 0 | 0
36 | 0.97702 | -0.44107 | 0 | 0
37 | 0.97705 | -0.44054 | 0 | 0
38 | 0.97696 | -0.44219 | 0.0038998 | 0.00097738
39 | 0.99482 | -0.098121 | 0 | 0
40 | 0.99372 | -0.11922 | 0.0047679 | 0.0011949
41 | 0.99305 | -0.13175 | 0 | 0
42 | 1 | 0 | -0.55486 | -0.14208
43 | 0.99056 | -0.17979 | 0 | 0
44 | 0.99121 | -0.16732 | 0 | 0
45 | 0.99053 | -0.18036 | 0.00022498 | 5.6385e-05
46 | 0.99038 | -0.18313 | 0 | 0
47 | 0.98033 | -0.37875 | 0 | 0
48 | 0.98015 | -0.38222 | 0 | 0
49 | 0.9802 | -0.38122 | 0.00099456 | 0.00024926
50 | 0.97252 | -0.52966 | 0 | 0
51 | 0.97182 | -0.54337 | 0 | 0
52 | 0.97207 | -0.53856 | 0 | 0
53 | 0.97286 | -0.52282 | 0.010561 | 0.0026468
54 | 0.99295 | -0.13382 | 0 | 0
55 | 0.99283 | -0.13617 | 0 | 0
56 | 0.99293 | -0.13427 | 0.00054497 | 0.00013658
57 | 0.9812 | -0.35957 | 0 | 0
58 | 0.97457 | -0.4892 | 0.01291 | 0.0032356
59 | 0.99281 | -0.13643 | 0.011401 | 0.0028573
60 | 0.99263 | -0.13986 | 0 | 0
61 | 0.99258 | -0.14087 | 0.012864 | 0.0032241
62 | 0.98058 | -0.3717 | 0.0092291 | 0.002313
63 | 0.98492 | -0.28761 | 0 | 0
64 | 0.97148 | -0.55008 | 0.0045782 | 0.0011474
65 | 0.97136 | -0.55257 | 0 | 0
66 | 0.97133 | -0.55312 | 0.0022712 | 0.00056923
67 | 0.97126 | -0.55458 | 0.0047082 | 0.00118
68 | 0.97204 | -0.53899 | 0.001757 | 0.00044035
69 | 0.97199 | -0.54006 | 0.0074727 | 0.0018728
70 | 0.98347 | -0.31714 | 0.0027361 | 0.00068574
71 | 0.97335 | -0.51319 | 0 | 0
72 | 0.97319 | -0.51647 | 0.0092681 | 0.0023228
73 | 0.98857 | -0.21823 | 0.0010786 | 0.00027032
74 | 0.99229 | -0.14626 | 0.0035715 | 0.00089511
75 | 0.99173 | -0.15708 | 0 | 0
76 | 0.99071 | -0.17648 | 0 | 0
77 | 0.98976 | -0.19455 | 0.005382 | 0.0013489
78 | 0.98974 | -0.19553 | 0.010312 | 0.0025845
79 | 0.98926 | -0.20415 | 0 | 0
80 | 0.98855 | -0.2177 | 0.0050491 | 0.0012654
81 | 0.98969 | -0.19586 | 0.0059908 | 0.0015014
82 | 0.98131 | -0.35713 | 0 | 0
83 | 0.98246 | -0.33488 | 0.002419 | 0.00060627
84 | 0.98075 | -0.36805 | 0.0056159 | 0.0014075
85 | 0.99037 | -0.183 | 0 | 0
86 | 0.99091 | -0.17261 | 0.0064538 | 0.0016175
87 | 0.97918 | -0.39862 | 0 | 0
88 | 0.97673 | -0.44643 | 0.0069478 | 0.0017413
89 | 0.97714 | -0.43873 | 0 | 0
90 | 0.97638 | -0.45354 | 0.007159 | 0.0017942
91 | 0.9858 | -0.27181 | 0.00017268 | 4.3278e-05
92 | 0.9983 | -0.032574 | 0.0049237 | 0.001234
93 | 0.99052 | -0.18051 | 0.00021069 | 5.2805e-05
94 | 0.99023 | -0.18607 | 0 | 0
95 | 0.98011 | -0.38304 | 0.00051762 | 0.00012973
96 | 0.97986 | -0.38802 | 0.00070819 | 0.00017749
97 | 0.97998 | -0.3856 | 0.00060427 | 0.00015144
98 | 0.992 | -0.1523 | 0.021992 | 0.0055118
99 | 0.99221 | -0.14807 | 0.0074879 | 0.0018766
100 | 0.98019 | -0.37942 | 0.0092575 | 0.0023202
101 | 0.9711 | -0.55768 | 0.0070718 | 0.0017724
102 | 0.97187 | -0.54252 | 0.007473 | 0.0018729
103 | 0.99169 | -0.15771 | 0.0053175 | 0.0013327
104 | 0.98834 | -0.22171 | 0.0017432 | 0.0004369
105 | 0.97166 | -0.54641 | 0.0026582 | 0.00066621
106 | 0.97168 | -0.54591 | 0.0030726 | 0.00077007
107 | 0.98972 | -0.19587 | 0.01523 | 0.003817
108 | 0.98501 | -0.28566 | 0.0025173 | 0.0006309
109 | 0.99149 | -0.16163 | 0.0040159 | 0.0010065
110 | 0.97504 | -0.47973 | 0.0044581 | 0.0011173
111 | 0.97625 | -0.4561 | 0.0028878 | 0.00072374
112 | 0.97178 | -0.54395 | 0.0026437 | 0.00066257
113 | 0.97173 | -0.54496 | 0.0024341 | 0.00061003
114 | 0.97185 | -0.54264 | 0.0046625 | 0.0011685
115 | 0.97193 | -0.5409 | 0.0011051 | 0.00027697
116 | 0.9721 | -0.53759 | 0.0020976 | 0.0005257
117 | 0.9722 | -0.53567 | 0.0027861 | 0.00069827
118 | 0.97245 | -0.5307 | 0.0025135 | 0.00062994
119 | 0.97225 | -0.5356 | 0.0037016 | 0.00092771
120 | 0.97242 | -0.53228 | 0 | 0
121 | 0.98804 | -0.2284 | 0.0030387 | 0.00076158
122 | 0.98776 | -0.2338 | 0.0031447 | 0.00078814
123 | 0.98758 | -0.23731 | 0.0036227 | 0.00090793
124 | 0.98741 | -0.24055 | 0.003871 | 0.00097017
125 | 0.98679 | -0.25267 | 0.0024813 | 0.00062186
126 | 0.97262 | -0.52727 | 0.004224 | 0.0010586
127 | 0.97322 | -0.51553 | 0.0027047 | 0.00067786
128 | 0.9734 | -0.51195 | 0 | 0
129 | 0.97304 | -0.51913 | 0.0068666 | 0.0017209
130 | 0.97293 | -0.52116 | 0.0029406 | 0.00073697
131 | 0.9729 | -0.52175 | 0 | 0
132 | 0.97227 | -0.53426 | 0.0038546 | 0.00096606
133 | 0.97284 | -0.52292 | 0.0069116 | 0.0017322
134 | 0.97165 | -0.54645 | 0 | 0
135 | 0.97148 | -0.54979 | 0.0067623 | 0.0016948
136 | 0.97131 | -0.55317 | 0.0028992 | 0.00072662
137 | 0.97139 | -0.55169 | 0 | 0
138 | 0.9711 | -0.55737 | 0.0021014 | 0.00052666
139 | 0.9979 | -0.040284 | 0.00025112 | 6.2937e-05
140 | 0.99741 | -0.049643 | 0.0047765 | 0.0011971
141 | 0.99669 | -0.063543 | 0.00024717 | 6.1947e-05
142 | 0.99626 | -0.071911 | 0.0027444 | 0.0006878
143 | 0.98645 | -0.25932 | 0.0074279 | 0.0018616
144 | 0.97615 | -0.4581 | 0.0070184 | 0.001759
145 | 0.9709 | -0.56127 | 0.0039998 | 0.0010024
146 | 0.97086 | -0.5621 | 0.0039539 | 0.00099095
147 | 0.97115 | -0.55629 | 0 | 0
148 | 0.97941 | -0.39676 | 0.00050826 | 0.00012738
149 | 0.9794 | -0.39698 | 0.00020668 | 5.1799e-05
150 | 0.97095 | -0.56036 | 0.0026166 | 0.00065577
151 | 0.97083 | -0.56263 | 0.005337 | 0.0013376
152 | 0.97068 | -0.56571 | 0.0070964 | 0.0017785
153 | 0.97068 | -0.56572 | 0.0011042 | 0.00027674
154 | 0.9757 | -0.47004 | 0 | 0
155 | 0.97315 | -0.52059 | 0.00065355 | 0.00016379
156 | 0.97301 | -0.52343 | 0.00017664 | 4.4271e-05
157 | 0.97392 | -0.50579 | 0 | 0
158 | 0.97423 | -0.49978 | 0 | 0
159 | 0.97152 | -0.55321 | 0.00038292 | 9.5969e-05
160 | 0.97153 | -0.55296 | 0.00040141 | 0.0001006
161 | 0.97151 | -0.55328 | 0.00013322 | 3.3388e-05
162 | 0.97179 | -0.54783 | 0 | 0
163 | 0.97151 | -0.55332 | 0.00021744 | 5.4496e-05
164 | 0.97103 | -0.56294 | 0 | 0
165 | 0.97275 | -0.52871 | 0 | 0
166 | 0.9715 | -0.55348 | 0.00021362 | 5.3538e-05
167 | 0.97102 | -0.56307 | 0.00029066 | 7.2847e-05
168 | 0.97272 | -0.5292 | 0 | 0
169 | 0.97266 | -0.53049 | 0.0019729 | 0.00049447
170 | 0.97279 | -0.52792 | 0 | 0
171 | 0.97274 | -0.52881 | 0.00021492 | 5.3863e-05
172 | 0.97096 | -0.56423 | 0.0020195 | 0.00050614
173 | 0.97388 | -0.50663 | 0.001308 | 0.00032782
174 | 0.98891 | -0.21171 | 0.00028808 | 7.22e-05
175 | 0.98891 | -0.21162 | 0 | 0
176 | 0.98908 | -0.20841 | 0 | 0
177 | 0.98885 | -0.21283 | 0.00025368 | 6.3578e-05
178 | 0.98996 | -0.19128 | 0 | 0
179 | 0.98866 | -0.21648 | 0 | 0
180 | 0.99015 | -0.18764 | 0.00037346 | 9.3598e-05
181 | 0.98805 | -0.22843 | 0.00050606 | 0.00012683
182 | 0.98751 | -0.23894 | 0 | 0
183 | 0.99015 | -0.18751 | 0 | 0
184 | 0.97267 | -0.52731 | 0.0039146 | 0.00098108
185 | 0.97362 | -0.50859 | 0 | 0
186 | 0.97071 | -0.56614 | 0 | 0
187 | 0.97657 | -0.45077 | 0 | 0
188 | 0.97018 | -0.57655 | 0.011766 | 0.0029488
189 | 0.98598 | -0.2677 | 0 | 0
190 | 0.98906 | -0.20842 | 0 | 0
191 | 0.98426 | -0.30093 | 0.0047367 | 0.0011871
192 | 0.98908 | -0.20816 | 0.0042706 | 0.0010703
193 | 0.97833 | -0.41621 | 0.0087175 | 0.0021848
194 | 0.984 | -0.30601 | 0 | 0
195 | 0.98962 | -0.19778 | 0 | 0
196 | 0.9788 | -0.40701 | 0.0050663 | 0.0012697
197 | 0.9799 | -0.38562 | 0 | 0
198 | 0.9799 | -0.38565 | 6.5451e-05 | 1.6404e-05
199 | 0.99015 | -0.18756 | 0.00032835 | 8.2293e-05
200 | 0.9863 | -0.26243 | 0.0066972 | 0.0016785
201 | 0.98664 | -0.25582 | 0 | 0
202 | 0.97401 | -0.50425 | 0.00059207 | 0.00014839
203 | 0.9741 | -0.50253 | 0 | 0
204 | 0.97419 | -0.50058 | 0 | 0
205 | 0.97406 | -0.50317 | 0.00043157 | 0.00010816
206 | 0.97937 | -0.39768 | 0.00055888 | 0.00014007
207 | 0.97935 | -0.39789 | 0.00044336 | 0.00011112
208 | 0.97935 | -0.39796 | 0.00031627 | 7.9265e-05
209 | 0.98512 | -0.28513 | 0.0033819 | 0.00084758
210 | 0.98503 | -0.28691 | 0.0025683 | 0.00064367
211 | 0.98533 | -0.281 | 0 | 0
212 | 0.98499 | -0.2878 | 0.0030655 | 0.00076828
213 | 0.98492 | -0.28909 | 0.0026776 | 0.00067108
214 | 0.98579 | -0.27216 | 0.0020301 | 0.0005088
215 | 0.98494 | -0.28863 | 0.0024435 | 0.00061241
216 | 0.98481 | -0.2913 | 0.0013726 | 0.00034401
217 | 0.98585 | -0.27097 | 0.0027155 | 0.00068057
218 | 0.98489 | -0.28962 | 0.0056645 | 0.0014197
219 | 0.98415 | -0.30408 | 0.0022902 | 0.00057399
220 | 0.98401 | -0.30675 | 0.0025578 | 0.00064104
221 | 0.98382 | -0.31062 | 0.0017519 | 0.00043907
222 | 0.98377 | -0.31161 | 0.0030666 | 0.00076857
223 | 0.98388 | -0.30936 | 0.004905 | 0.0012293
224 | 0.98376 | -0.31174 | 0.0012815 | 0.00032117
225 | 0.98373 | -0.31231 | 0.0043575 | 0.0010921
226 | 0.99611 | -0.074729 | 0.0022134 | 0.00055472
227 | 0.99579 | -0.08097 | 0.0026616 | 0.00066705
228 | 0.99567 | -0.083311 | 0.0028364 | 0.00071086
229 | 0.9954 | -0.088396 | 0.0025468 | 0.00063829
230 | 0.99519 | -0.092528 | 0.0028014 | 0.00070211
231 | 0.99501 | -0.095893 | 0.0033549 | 0.00084082
232 | 0.99483 | -0.099417 | 0.0023706 | 0.00059412
233 | 0.99476 | -0.10088 | 0.0021311 | 0.0005341
234 | 0.99459 | -0.10415 | 0.002893 | 0.00072505
235 | 0.99401 | -0.11537 | 0 | 0
236 | 0.99371 | -0.12119 | 0.0060178 | 0.0015082
237 | 0.99049 | -0.18111 | 0.00049433 | 0.00012389
238 | 0.99049 | -0.18109 | 0.0004394 | 0.00011012
239 | 0.99048 | -0.18133 | 0.00033836 | 8.48e-05
240 | 0.97956 | -0.39379 | 0.0012734 | 0.00031915
241 | 0.97959 | -0.39321 | 0.00086585 | 0.000217
242 | 0.97963 | -0.39238 | 0.0012109 | 0.00030348
243 | 0.97969 | -0.39123 | 0.00075782 | 0.00018993
244 | 0.97975 | -0.39 | 0.0011414 | 0.00028607
245 | 0.97986 | -0.38801 | 0.00047864 | 0.00011996
246 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0033694 | 0.00084385 | -0.0033693 | -0.00084395 | 1.6143e-07 | -9.9684e-08 | 0.0051423 | 0.0051424 | 0.0051424 | 0.97496 | -0.48484 | 0.97491 | -0.48584 | 1.4127
1 | -0.0035122 | -0.00087963 | 0.0035132 | 0.00087912 | 9.8964e-07 | -5.125e-07 | 0.0053602 | 0.0053598 | 0.0053602 | 0.97496 | -0.48484 | 0.97526 | -0.47892 | 1.4726
2 | 0.0029366 | 0.0007355 | -0.0029365 | -0.00073557 | 6.8142e-08 | -6.9182e-08 | 0.0044819 | 0.004482 | 0.004482 | 0.97491 | -0.48584 | 0.97489 | -0.48633 | 1.2313
3 | -0.0035619 | -0.00089133 | 0.0035621 | 0.00089126 | 1.3941e-07 | -6.7878e-08 | 0.0054341 | 0.0054341 | 0.0054341 | 0.97526 | -0.47892 | 0.97531 | -0.4781 | 1.4929
4 | 0.0026593 | 0.00066609 | -0.0026591 | -0.00066631 | 1.5994e-07 | -2.2042e-07 | 0.0040588 | 0.0040589 | 0.0040589 | 0.97489 | -0.48633 | 0.97483 | -0.48759 | 1.1151
5 | 0.0029824 | 0.0007259 | -0.0029803 | -0.00072794 | 2.1069e-06 | -2.0459e-06 | 0.0045426 | 0.0045437 | 0.0045437 | 0.97531 | -0.4781 | 0.97455 | -0.49324 | 1.2483
6 | -0.0065445 | -0.0016172 | 0.0065498 | 0.0016188 | 5.37e-06 | 1.6396e-06 | 0.0099766 | 0.0099759 | 0.0099766 | 0.97531 | -0.4781 | 0.97618 | -0.4607 | 2.7408
7 | 0.0022968 | 0.00057551 | -0.0022968 | -0.00057557 | 2.8694e-08 | -5.9244e-08 | 0.0035059 | 0.003506 | 0.003506 | 0.97483 | -0.48759 | 0.97481 | -0.48786 | 0.96318
8 | 0.0017257 | 0.00042734 | -0.0017248 | -0.00043102 | 8.8596e-07 | -3.6742e-06 | 0.0026331 | 0.0026346 | 0.0026346 | 0.97455 | -0.49324 | 0.97401 | -0.50408 | 0.72379
9 | 0.0012546 | 0.0003006 | -0.0012544 | -0.00030219 | 1.876e-07 | -1.5865e-06 | 0.0019107 | 0.0019113 | 0.0019113 | 0.97455 | -0.49324 | 0.9744 | -0.49647 | 0.52508
10 | -0.0069594 | -0.0017214 | 0.0069626 | 0.0017225 | 3.2062e-06 | 1.1002e-06 | 0.0106 | 0.0106 | 0.0106 | 0.97618 | -0.4607 | 0.97667 | -0.45093 | 2.9122
11 | 0.0022068 | 0.00055302 | -0.0022068 | -0.00055308 | 2.4508e-08 | -5.6112e-08 | 0.0033686 | 0.0033687 | 0.0033687 | 0.97481 | -0.48786 | 0.9748 | -0.48809 | 0.92545
12 | 0.0013082 | 0.0003266 | -0.0013081 | -0.00032684 | 3.254e-08 | -2.4968e-07 | 0.001998 | 0.0019981 | 0.0019981 | 0.97401 | -0.50408 | 0.97398 | -0.5046 | 0.54894
13 | 0.0011382 | 0.00027305 | -0.0011381 | -0.00027393 | 8.47e-08 | -8.8146e-07 | 0.0017338 | 0.0017341 | 0.0017341 | 0.9744 | -0.49647 | 0.97432 | -0.49809 | 0.47641
14 | 0.007119 | 0.0017751 | -0.0071184 | -0.0017748 | 6.3677e-07 | 2.2681e-07 | 0.010843 | 0.010843 | 0.010843 | 0.97667 | -0.45093 | 0.97658 | -0.45282 | 2.9789
15 | -0.014082 | -0.0034976 | 0.014092 | 0.0035038 | 1.0822e-05 | 6.1399e-06 | 0.021443 | 0.021443 | 0.021443 | 0.97667 | -0.45093 | 0.97749 | -0.4347 | 5.8909
16 | 0.0013081 | 0.00032684 | -0.001308 | -0.00032741 | 7.4261e-08 | -5.6966e-07 | 0.0019981 | 0.0019984 | 0.0019984 | 0.97398 | -0.5046 | 0.97392 | -0.50579 | 0.549
17 | 0.0010239 | 0.00024532 | -0.0010238 | -0.00024636 | 7.9979e-08 | -1.0402e-06 | 0.0015598 | 0.0015602 | 0.0015602 | 0.97432 | -0.49809 | 0.97423 | -0.49978 | 0.42862
18 | 0.0067063 | 0.0016716 | -0.0067008 | -0.0016698 | 5.4772e-06 | 1.7557e-06 | 0.010215 | 0.010216 | 0.010216 | 0.97658 | -0.45282 | 0.9757 | -0.47004 | 2.8065
19 | -0.015274 | -0.0038 | 0.015287 | 0.0038073 | 1.2622e-05 | 7.2964e-06 | 0.023242 | 0.023242 | 0.023242 | 0.97749 | -0.4347 | 0.97837 | -0.41727 | 6.3851
20 | -0.002305 | -0.00057583 | 0.0023051 | 0.00057556 | 1.2647e-07 | -2.6369e-07 | 0.0035054 | 0.0035053 | 0.0035054 | 0.97828 | -0.41916 | 0.97833 | -0.41801 | 0.96302
21 | 0.0021461 | 0.00053601 | -0.002146 | -0.00053635 | 1.3841e-07 | -3.4642e-07 | 0.0032637 | 0.0032639 | 0.0032639 | 0.97828 | -0.41916 | 0.97821 | -0.42052 | 0.89667
22 | -0.0027254 | -0.00068089 | 0.0027257 | 0.00068053 | 2.743e-07 | -3.5926e-07 | 0.0041445 | 0.0041443 | 0.0041445 | 0.97833 | -0.41801 | 0.97844 | -0.41589 | 1.1386
23 | 0.0017234 | 0.00043043 | -0.0017233 | -0.00043076 | 7.7459e-08 | -3.2786e-07 | 0.002621 | 0.0026211 | 0.0026211 | 0.97821 | -0.42052 | 0.97816 | -0.42146 | 0.72009
24 | -0.0028941 | -0.00072273 | 0.0028941 | 0.00072265 | 7.3677e-08 | -8.0291e-08 | 0.0044004 | 0.0044003 | 0.0044004 | 0.97844 | -0.41589 | 0.97847 | -0.41535 | 1.2089
25 | 0.0012306 | 0.00030729 | -0.0012306 | -0.0003077 | 4.6582e-08 | -4.1523e-07 | 0.0018717 | 0.0018718 | 0.0018718 | 0.97816 | -0.42146 | 0.97812 | -0.42226 | 0.51424
26 | -0.019376 | -0.0048299 | 0.019388 | 0.0048368 | 1.1486e-05 | 6.9075e-06 | 0.029457 | 0.029457 | 0.029457 | 0.97847 | -0.41535 | 0.9791 | -0.40287 | 8.0926
27 | 0.016482 | 0.0041072 | -0.01648 | -0.0041064 | 1.5006e-06 | 8.8035e-07 | 0.025057 | 0.025057 | 0.025057 | 0.97847 | -0.41535 | 0.97837 | -0.41727 | 6.8837
28 | 0.00080953 | 0.00020218 | -0.0008095 | -0.00020288 | 3.2713e-08 | -7.0109e-07 | 0.0012313 | 0.0012315 | 0.0012315 | 0.97812 | -0.42226 | 0.97808 | -0.42311 | 0.33834
29 | -0.019638 | -0.004899 | 0.019644 | 0.0049028 | 6.2437e-06 | 3.7607e-06 | 0.029837 | 0.029837 | 0.029837 | 0.9791 | -0.40287 | 0.97944 | -0.39617 | 8.1969
30 | 0.00025013 | 6.2215e-05 | -0.00025013 | -6.2688e-05 | 2.0451e-09 | -4.7354e-07 | 0.00037997 | 0.00038014 | 0.00038014 | 0.9791 | -0.40287 | 0.97909 | -0.40304 | 0.10443
31 | 0.0020336 | 0.00050871 | -0.0020335 | -0.00050887 | 5.6809e-08 | -1.6342e-07 | 0.0030892 | 0.0030892 | 0.0030892 | 0.97944 | -0.39617 | 0.97941 | -0.39676 | 0.84869
32 | -0.021677 | -0.0054115 | 0.021686 | 0.0054166 | 8.3922e-06 | 5.1111e-06 | 0.032926 | 0.032926 | 0.032926 | 0.97944 | -0.39617 | 0.97986 | -0.38802 | 9.0456
33 | 0.0042919 | 0.0010754 | -0.0042913 | -0.0010755 | 6.2679e-07 | -1.0633e-07 | 0.0064789 | 0.0064791 | 0.0064791 | 0.98571 | -0.27358 | 0.98555 | -0.27665 | 1.78
34 | -0.0060098 | -0.0015059 | 0.0060105 | 0.0015061 | 7.1276e-07 | 1.6175e-07 | 0.0090722 | 0.009072 | 0.0090722 | 0.98571 | -0.27358 | 0.98584 | -0.27109 | 2.4923
35 | 0.00017269 | 4.04e-05 | -0.00017269 | -4.098e-05 | 1.1528e-09 | -5.8014e-07 | 0.00025966 | 0.00025986 | 0.00025986 | 0.98584 | -0.27109 | 0.98583 | -0.27124 | 0.071389
36 | 0.03315 | 0.008349 | -0.033079 | -0.0083072 | 7.1423e-05 | 4.1842e-05 | 0.050051 | 0.050053 | 0.050053 | 0.98584 | -0.27109 | 0.98352 | -0.31625 | 6.8754
37 | -0.039334 | -0.0098955 | 0.039435 | 0.0099564 | 0.00010123 | 6.0869e-05 | 0.059383 | 0.059382 | 0.059383 | 0.98584 | -0.27109 | 0.98861 | -0.21737 | 8.157
38 | 0.00017269 | 4.098e-05 | -0.00017268 | -4.2915e-05 | 3.8578e-09 | -1.935e-06 | 0.00025986 | 0.00026053 | 0.00026053 | 0.98583 | -0.27124 | 0.98581 | -0.27172 | 0.071573
39 | 0.0027362 | 0.00068558 | -0.0027361 | -0.00068574 | 1.171e-07 | -1.5628e-07 | 0.0041397 | 0.0041398 | 0.0041398 | 0.98352 | -0.31625 | 0.98347 | -0.31714 | 1.1373
40 | 0.030343 | 0.0076216 | -0.030252 | -0.0075653 | 9.0213e-05 | 5.6293e-05 | 0.045913 | 0.045914 | 0.045914 | 0.98352 | -0.31625 | 0.98033 | -0.37875 | 12.6136
41 | 0.0010786 | 0.00026977 | -0.0010786 | -0.00027032 | 4.4097e-08 | -5.4386e-07 | 0.0016233 | 0.0016235 | 0.0016235 | 0.98861 | -0.21737 | 0.98857 | -0.21823 | 0.44602
42 | -0.040513 | -0.010226 | 0.040586 | 0.010262 | 7.3045e-05 | 3.5989e-05 | 0.061005 | 0.061001 | 0.061005 | 0.98861 | -0.21737 | 0.99056 | -0.17979 | 4.1899
43 | 0.00017268 | 4.2915e-05 | -0.00017268 | -4.3278e-05 | 7.2609e-10 | -3.6306e-07 | 0.00026053 | 0.00026066 | 0.00026066 | 0.98581 | -0.27172 | 0.9858 | -0.27181 | 0.071609
44 | -0.0039 | -0.00097732 | 0.0039001 | 0.00097729 | 9.7234e-08 | -2.9812e-08 | 0.0059397 | 0.0059397 | 0.0059397 | 0.97702 | -0.44107 | 0.97705 | -0.44054 | 1.6318
45 | 0.0039 | 0.00097732 | -0.0038998 | -0.00097738 | 2.0927e-07 | -6.4142e-08 | 0.0059397 | 0.0059398 | 0.0059398 | 0.97702 | -0.44107 | 0.97696 | -0.44219 | 1.6318
46 | -0.072258 | -0.018218 | 0.07254 | 0.018397 | 0.00028119 | 0.00017919 | 0.11009 | 0.11009 | 0.11009 | 0.97705 | -0.44054 | 0.9812 | -0.35957 | 30.2435
47 | 0.068358 | 0.017241 | -0.068199 | -0.017139 | 0.00015883 | 0.00010117 | 0.10415 | 0.10415 | 0.10415 | 0.97705 | -0.44054 | 0.97457 | -0.4892 | 28.6118
48 | 0.12129 | 0.030836 | -0.12117 | -0.030759 | 0.00012313 | 7.6735e-05 | 0.18158 | 0.18158 | 0.18158 | 0.99482 | -0.098121 | 0.99372 | -0.11922 | 12.471
49 | 0.38656 | 0.09887 | -0.38593 | -0.098469 | 0.00062803 | 0.0004009 | 0.57891 | 0.57891 | 0.57891 | 0.99482 | -0.098121 | 0.99305 | -0.13175 | 39.7603
50 | -0.50785 | -0.12971 | 0.51027 | 0.13125 | 0.0024214 | 0.0015474 | 0.76049 | 0.76049 | 0.76049 | 0.99482 | -0.098121 | 1 | 0 | 52.2313
51 | 0.1164 | 0.029564 | -0.11632 | -0.029513 | 8.1712e-05 | 5.0813e-05 | 0.17444 | 0.17444 | 0.17444 | 0.99372 | -0.11922 | 0.99295 | -0.13382 | 11.9807
52 | 0.011403 | 0.0028586 | -0.011401 | -0.0028573 | 2.5423e-06 | 1.3267e-06 | 0.017087 | 0.017087 | 0.017087 | 0.99305 | -0.13175 | 0.99281 | -0.13643 | 4.6943
53 | 0.35416 | 0.090504 | -0.35402 | -0.090415 | 0.00013886 | 8.8599e-05 | 0.53131 | 0.53131 | 0.53131 | 0.99305 | -0.13175 | 0.99263 | -0.13986 | 36.491
54 | 0.020363 | 0.005107 | -0.020355 | -0.0051016 | 8.8508e-06 | 5.3367e-06 | 0.030514 | 0.030514 | 0.030514 | 0.99305 | -0.13175 | 0.99258 | -0.14087 | 8.3831
55 | 0.042938 | 0.010822 | -0.042872 | -0.01078 | 6.6807e-05 | 4.2186e-05 | 0.063914 | 0.063915 | 0.063915 | 1 | 0 | 0.9983 | -0.032574 | 17.559
56 | -0.093554 | -0.023727 | 0.09361 | 0.023761 | 5.6113e-05 | 3.4353e-05 | 0.14064 | 0.14064 | 0.14064 | 0.99056 | -0.17979 | 0.99121 | -0.16732 | 9.6591
57 | 0.0017079 | 0.00042694 | -0.0017078 | -0.00042715 | 4.6798e-08 | -2.1417e-07 | 0.0025652 | 0.0025652 | 0.0025652 | 0.99056 | -0.17979 | 0.99053 | -0.18036 | 0.70474
58 | 0.051259 | 0.013038 | -0.051251 | -0.013033 | 8.2426e-06 | 4.5132e-06 | 0.07707 | 0.07707 | 0.07707 | 0.99056 | -0.17979 | 0.99038 | -0.18313 | 5.2933
59 | -0.09361 | -0.023761 | 0.093761 | 0.023854 | 0.00015114 | 9.2522e-05 | 0.14064 | 0.14063 | 0.14064 | 0.99121 | -0.16732 | 0.99295 | -0.13382 | 9.659
60 | 0.0014828 | 0.00037077 | -0.0014828 | -0.00037083 | 1.0044e-08 | -6.3066e-08 | 0.0022273 | 0.0022273 | 0.0022273 | 0.99053 | -0.18036 | 0.99052 | -0.18051 | 0.61189
61 | 0.051251 | 0.013033 | -0.051244 | -0.013029 | 7.267e-06 | 3.9793e-06 | 0.07707 | 0.077071 | 0.077071 | 0.99038 | -0.18313 | 0.99023 | -0.18607 | 5.2933
62 | 0.022922 | 0.0057288 | -0.022918 | -0.0057265 | 3.7819e-06 | 2.3154e-06 | 0.034787 | 0.034787 | 0.034787 | 0.98033 | -0.37875 | 0.98015 | -0.38222 | 9.5568
63 | 0.0073308 | 0.0018365 | -0.0073299 | -0.0018362 | 8.6152e-07 | 3.1745e-07 | 0.011127 | 0.011127 | 0.011127 | 0.98033 | -0.37875 | 0.9802 | -0.38122 | 3.0569
64 | 0.00051764 | 0.00012864 | -0.00051762 | -0.00012973 | 2.0149e-08 | -1.0842e-06 | 0.00078547 | 0.00078586 | 0.00078586 | 0.98015 | -0.38222 | 0.98011 | -0.38304 | 0.2159
65 | 0.0224 | 0.0055979 | -0.022394 | -0.0055941 | 6.1788e-06 | 3.7749e-06 | 0.034001 | 0.034001 | 0.034001 | 0.98015 | -0.38222 | 0.97986 | -0.38802 | 9.341
66 | 0.0063354 | 0.0015869 | -0.006334 | -0.0015865 | 1.3226e-06 | 3.6591e-07 | 0.0096172 | 0.0096174 | 0.0096174 | 0.9802 | -0.38122 | 0.97998 | -0.3856 | 2.6421
67 | 0.018651 | 0.0046817 | -0.018639 | -0.0046743 | 1.2191e-05 | 7.3073e-06 | 0.028541 | 0.028541 | 0.028541 | 0.97252 | -0.52966 | 0.97182 | -0.54337 | 7.8409
68 | 0.016712 | 0.0041911 | -0.016705 | -0.0041869 | 7.0871e-06 | 4.1773e-06 | 0.025571 | 0.025571 | 0.025571 | 0.97252 | -0.52966 | 0.97207 | -0.53856 | 7.0251
69 | -0.035363 | -0.0088728 | 0.035375 | 0.00888 | 1.1542e-05 | 7.2564e-06 | 0.054112 | 0.054112 | 0.054112 | 0.97252 | -0.52966 | 0.97286 | -0.52282 | 14.8659
70 | 0.018639 | 0.0046743 | -0.018633 | -0.0046708 | 5.9538e-06 | 3.569e-06 | 0.028541 | 0.028541 | 0.028541 | 0.97182 | -0.54337 | 0.97148 | -0.55008 | 7.8409
71 | 0.001757 | 0.00044021 | -0.001757 | -0.00044035 | 3.5982e-08 | -1.414e-07 | 0.0026896 | 0.0026896 | 0.0026896 | 0.97207 | -0.53856 | 0.97204 | -0.53899 | 0.73891
72 | 0.014948 | 0.0037467 | -0.014947 | -0.0037461 | 1.0681e-06 | 6.1617e-07 | 0.022882 | 0.022882 | 0.022882 | 0.97207 | -0.53856 | 0.97199 | -0.54006 | 6.2862
73 | -0.045936 | -0.011527 | 0.045957 | 0.01154 | 2.1108e-05 | 1.3368e-05 | 0.070265 | 0.070264 | 0.070265 | 0.97286 | -0.52282 | 0.97335 | -0.51319 | 19.3034
74 | 0.022012 | 0.0055236 | -0.022009 | -0.0055221 | 2.4747e-06 | 1.5054e-06 | 0.032989 | 0.032989 | 0.032989 | 0.99295 | -0.13382 | 0.99283 | -0.13617 | 9.0628
75 | 0.00054498 | 0.00013597 | -0.00054497 | -0.00013658 | 1.1908e-08 | -6.0834e-07 | 0.00081648 | 0.00081669 | 0.00081669 | 0.99295 | -0.13382 | 0.99293 | -0.13427 | 0.22437
76 | 0.022009 | 0.0055221 | -0.021992 | -0.0055118 | 1.6914e-05 | 1.029e-05 | 0.032989 | 0.032989 | 0.032989 | 0.99283 | -0.13617 | 0.992 | -0.1523 | 9.0628
77 | 0.018501 | 0.0046412 | -0.01849 | -0.0046348 | 1.0696e-05 | 6.3883e-06 | 0.028058 | 0.028059 | 0.028059 | 0.9812 | -0.35957 | 0.98058 | -0.3717 | 7.7084
78 | -0.09104 | -0.023038 | 0.091356 | 0.02324 | 0.00031559 | 0.00020142 | 0.13814 | 0.13814 | 0.13814 | 0.9812 | -0.35957 | 0.98492 | -0.28761 | 37.9518
79 | 0.055289 | 0.013904 | -0.055226 | -0.013864 | 6.3252e-05 | 4.0187e-05 | 0.084435 | 0.084436 | 0.084436 | 0.97457 | -0.4892 | 0.97335 | -0.51319 | 23.1966
80 | 0.12246 | 0.031305 | -0.12243 | -0.031281 | 3.7865e-05 | 2.3616e-05 | 0.1838 | 0.1838 | 0.1838 | 0.99263 | -0.13986 | 0.99229 | -0.14626 | 12.6237
81 | 0.23156 | 0.05911 | -0.23137 | -0.058988 | 0.00019253 | 0.00012234 | 0.34751 | 0.34751 | 0.34751 | 0.99263 | -0.13986 | 0.99173 | -0.15708 | 23.8673
82 | 0.0074905 | 0.0018776 | -0.0074879 | -0.0018766 | 2.5688e-06 | 9.4215e-07 | 0.011229 | 0.01123 | 0.01123 | 0.99258 | -0.14087 | 0.99221 | -0.14807 | 3.0851
83 | 0.0092609 | 0.0023218 | -0.0092575 | -0.0023202 | 3.4016e-06 | 1.5979e-06 | 0.014054 | 0.014054 | 0.014054 | 0.98058 | -0.3717 | 0.98019 | -0.37942 | 3.8609
84 | -0.091356 | -0.02324 | 0.091665 | 0.023437 | 0.0003089 | 0.00019715 | 0.13814 | 0.13814 | 0.13814 | 0.98492 | -0.28761 | 0.98855 | -0.2177 | 37.9517
85 | 0.014055 | 0.0035234 | -0.014053 | -0.0035224 | 1.6652e-06 | 9.4714e-07 | 0.021528 | 0.021528 | 0.021528 | 0.97148 | -0.55008 | 0.97136 | -0.55257 | 5.9144
86 | 0.0022713 | 0.0005691 | -0.0022712 | -0.00056923 | 6.007e-08 | -1.2534e-07 | 0.0034793 | 0.0034794 | 0.0034794 | 0.97136 | -0.55257 | 0.97133 | -0.55312 | 0.95588
87 | 0.011782 | 0.0029533 | -0.011781 | -0.0029527 | 1.1293e-06 | 6.0833e-07 | 0.018049 | 0.018049 | 0.018049 | 0.97136 | -0.55257 | 0.97126 | -0.55458 | 4.9586
88 | 0.0070728 | 0.0017727 | -0.0070718 | -0.0017724 | 1.0452e-06 | 3.752e-07 | 0.010836 | 0.010836 | 0.010836 | 0.97126 | -0.55458 | 0.9711 | -0.55768 | 2.9769
89 | 0.0074739 | 0.0018733 | -0.007473 | -0.0018729 | 8.7633e-07 | 3.3963e-07 | 0.011442 | 0.011442 | 0.011442 | 0.97199 | -0.54006 | 0.97187 | -0.54252 | 3.1434
90 | 0.0092696 | 0.0023235 | -0.0092681 | -0.0023228 | 1.4485e-06 | 6.8803e-07 | 0.014171 | 0.014171 | 0.014171 | 0.97335 | -0.51319 | 0.97319 | -0.51647 | 3.8932
91 | 0.11886 | 0.030386 | -0.11879 | -0.030345 | 6.5808e-05 | 4.0978e-05 | 0.17845 | 0.17845 | 0.17845 | 0.99229 | -0.14626 | 0.99169 | -0.15771 | 12.2559
92 | 0.095712 | 0.024161 | -0.095536 | -0.024049 | 0.00017591 | 0.00011229 | 0.14367 | 0.14367 | 0.14367 | 0.99173 | -0.15708 | 0.98974 | -0.19553 | 39.47
93 | 0.13566 | 0.034827 | -0.13553 | -0.034747 | 0.00012759 | 7.997e-05 | 0.20384 | 0.20384 | 0.20384 | 0.99173 | -0.15708 | 0.99071 | -0.17648 | 13.9999
94 | 0.13553 | 0.034747 | -0.13541 | -0.034673 | 0.00011865 | 7.4368e-05 | 0.20384 | 0.20384 | 0.20384 | 0.99071 | -0.17648 | 0.98976 | -0.19455 | 14
95 | 0.13003 | 0.033324 | -0.12986 | -0.033215 | 0.00017091 | 0.00010877 | 0.19575 | 0.19575 | 0.19575 | 0.98976 | -0.19455 | 0.98834 | -0.22171 | 26.8885
96 | 0.085224 | 0.021464 | -0.085223 | -0.021463 | 1.3973e-06 | 8.9136e-07 | 0.12817 | 0.12817 | 0.12817 | 0.98974 | -0.19553 | 0.98972 | -0.19587 | 35.2107
97 | 0.096777 | 0.024742 | -0.096714 | -0.024702 | 6.3422e-05 | 4.0181e-05 | 0.14574 | 0.14574 | 0.14574 | 0.98926 | -0.20415 | 0.98855 | -0.2177 | 20.0198
98 | -0.096777 | -0.024742 | 0.096816 | 0.024766 | 3.8833e-05 | 2.3851e-05 | 0.14574 | 0.14574 | 0.14574 | 0.98926 | -0.20415 | 0.98969 | -0.19586 | 10.0099
99 | -0.10281 | -0.026268 | 0.10287 | 0.026307 | 6.3989e-05 | 3.9487e-05 | 0.15475 | 0.15475 | 0.15475 | 0.98969 | -0.19586 | 0.99037 | -0.183 | 10.6285
100 | -0.12235 | -0.031015 | 0.12248 | 0.031099 | 0.00013096 | 8.3689e-05 | 0.18566 | 0.18566 | 0.18566 | 0.98131 | -0.35713 | 0.98246 | -0.33488 | 51.0048
101 | 0.12235 | 0.031015 | -0.12229 | -0.030974 | 6.4174e-05 | 4.1009e-05 | 0.18566 | 0.18566 | 0.18566 | 0.98131 | -0.35713 | 0.98075 | -0.36805 | 51.0048
102 | -0.1249 | -0.031705 | 0.1252 | 0.031894 | 0.00029653 | 0.0001895 | 0.18932 | 0.18932 | 0.18932 | 0.98246 | -0.33488 | 0.98501 | -0.28566 | 52.0113
103 | 0.11667 | 0.029567 | -0.1165 | -0.029457 | 0.00017111 | 0.00010932 | 0.17714 | 0.17714 | 0.17714 | 0.98075 | -0.36805 | 0.97918 | -0.39862 | 48.664
104 | -0.10287 | -0.026307 | 0.10292 | 0.026339 | 5.1712e-05 | 3.1909e-05 | 0.15475 | 0.15475 | 0.15475 | 0.99037 | -0.183 | 0.99091 | -0.17261 | 10.6285
105 | -0.10938 | -0.027957 | 0.10943 | 0.027993 | 5.815e-05 | 3.6033e-05 | 0.16444 | 0.16444 | 0.16444 | 0.99091 | -0.17261 | 0.99149 | -0.16163 | 11.294
106 | 0.099391 | 0.025153 | -0.099164 | -0.025008 | 0.0002275 | 0.00014526 | 0.15113 | 0.15113 | 0.15113 | 0.97918 | -0.39862 | 0.97673 | -0.44643 | 41.5186
107 | 0.017112 | 0.0043042 | -0.017079 | -0.0042849 | 3.2721e-05 | 1.9322e-05 | 0.02601 | 0.02601 | 0.02601 | 0.97918 | -0.39862 | 0.97714 | -0.43873 | 7.1457
108 | 0.092216 | 0.023266 | -0.092069 | -0.023173 | 0.00014677 | 9.3686e-05 | 0.14054 | 0.14054 | 0.14054 | 0.97673 | -0.44643 | 0.97504 | -0.47973 | 38.6107
109 | 0.017079 | 0.0042849 | -0.017067 | -0.0042778 | 1.205e-05 | 7.1173e-06 | 0.02601 | 0.02601 | 0.02601 | 0.97714 | -0.43873 | 0.97638 | -0.45354 | 7.1457
110 | 0.009908 | 0.0024836 | -0.0099068 | -0.002483 | 1.2108e-06 | 5.9782e-07 | 0.0151 | 0.0151 | 0.0151 | 0.97638 | -0.45354 | 0.97625 | -0.4561 | 4.1484
111 | 0.037948 | 0.009546 | -0.037934 | -0.0095373 | 1.3973e-05 | 8.7907e-06 | 0.056576 | 0.056576 | 0.056576 | 0.9983 | -0.032574 | 0.9979 | -0.040284 | 15.5428
112 | 0.0012721 | 0.00031803 | -0.0012721 | -0.00031833 | 3.5073e-08 | -3.0725e-07 | 0.0019108 | 0.0019109 | 0.0019109 | 0.99052 | -0.18051 | 0.99049 | -0.18109 | 0.52497
113 | 0.043099 | 0.010986 | -0.043096 | -0.010984 | 2.9963e-06 | 1.5264e-06 | 0.064831 | 0.064831 | 0.064831 | 0.99023 | -0.18607 | 0.99015 | -0.18751 | 4.4527
114 | 0.0081447 | 0.0020435 | -0.008144 | -0.0020433 | 6.114e-07 | 2.5131e-07 | 0.01224 | 0.01224 | 0.01224 | 0.99023 | -0.18607 | 0.99015 | -0.18764 | 3.3626
115 | 0.0057298 | 0.0014351 | -0.0057291 | -0.001435 | 6.5684e-07 | 1.2884e-07 | 0.0086999 | 0.0087 | 0.0087 | 0.97998 | -0.3856 | 0.97986 | -0.38801 | 2.3901
116 | 0.11347 | 0.029012 | -0.11345 | -0.028999 | 2.1519e-05 | 1.3365e-05 | 0.17047 | 0.17047 | 0.17047 | 0.99169 | -0.15771 | 0.99149 | -0.16163 | 11.708
117 | 0.12811 | 0.032778 | -0.12772 | -0.032525 | 0.0003953 | 0.00025263 | 0.19312 | 0.19312 | 0.19312 | 0.98834 | -0.22171 | 0.98501 | -0.28566 | 53.056
118 | -0.0026582 | -0.00066621 | 0.0026583 | 0.00066613 | 6.3785e-08 | -8.6313e-08 | 0.0040709 | 0.0040708 | 0.0040709 | 0.97166 | -0.54641 | 0.97168 | -0.54591 | 1.1184
119 | -0.0057309 | -0.0014362 | 0.0057311 | 0.0014362 | 2.5751e-07 | 5.4364e-08 | 0.0087761 | 0.0087761 | 0.0087761 | 0.97168 | -0.54591 | 0.97173 | -0.54496 | 2.411
120 | 0.069993 | 0.017646 | -0.069884 | -0.017577 | 0.00010879 | 6.9292e-05 | 0.10527 | 0.10527 | 0.10527 | 0.98972 | -0.19587 | 0.98804 | -0.2284 | 28.9202
121 | 0.087611 | 0.022055 | -0.087476 | -0.02197 | 0.00013471 | 8.5965e-05 | 0.13374 | 0.13374 | 0.13374 | 0.97504 | -0.47973 | 0.9734 | -0.51195 | 36.7416
122 | 0.0070191 | 0.0017592 | -0.0070184 | -0.001759 | 6.6801e-07 | 2.3295e-07 | 0.010699 | 0.010699 | 0.010699 | 0.97625 | -0.4561 | 0.97615 | -0.4581 | 2.9392
123 | 0.0081656 | 0.0020464 | -0.0081652 | -0.0020463 | 3.9192e-07 | 1.6801e-07 | 0.012503 | 0.012503 | 0.012503 | 0.97178 | -0.54395 | 0.97173 | -0.54496 | 3.435
124 | -0.010809 | -0.002709 | 0.01081 | 0.0027094 | 6.7919e-07 | 3.5276e-07 | 0.016551 | 0.016551 | 0.016551 | 0.97178 | -0.54395 | 0.97185 | -0.54264 | 4.5471
125 | -0.015472 | -0.0038779 | 0.015474 | 0.0038787 | 1.2826e-06 | 7.4535e-07 | 0.02369 | 0.02369 | 0.02369 | 0.97185 | -0.54264 | 0.97193 | -0.5409 | 6.5083
126 | -0.016579 | -0.0041556 | 0.016581 | 0.0041572 | 2.6102e-06 | 1.5366e-06 | 0.025382 | 0.025382 | 0.025382 | 0.97193 | -0.5409 | 0.9721 | -0.53759 | 6.9731
127 | -0.018679 | -0.0046829 | 0.018681 | 0.0046839 | 1.7076e-06 | 1.0238e-06 | 0.028593 | 0.028593 | 0.028593 | 0.9721 | -0.53759 | 0.9722 | -0.53567 | 7.8552
128 | -0.021467 | -0.0053822 | 0.021472 | 0.0053853 | 5.0857e-06 | 3.099e-06 | 0.032857 | 0.032857 | 0.032857 | 0.9722 | -0.53567 | 0.97245 | -0.5307 | 9.0267
129 | -0.023985 | -0.0060152 | 0.023989 | 0.0060176 | 3.9311e-06 | 2.4193e-06 | 0.036703 | 0.036703 | 0.036703 | 0.97245 | -0.5307 | 0.97262 | -0.52727 | 10.0833
130 | -0.0037016 | -0.00092771 | 0.0037022 | 0.00092749 | 5.8622e-07 | -2.2897e-07 | 0.0056653 | 0.0056651 | 0.0056653 | 0.97225 | -0.5356 | 0.97242 | -0.53228 | 1.5564
131 | 0.011791 | 0.0029622 | -0.011772 | -0.0029519 | 1.903e-05 | 1.0249e-05 | 0.018045 | 0.018046 | 0.018046 | 0.97242 | -0.53228 | 0.97071 | -0.56614 | 4.9576
132 | -0.015493 | -0.0038897 | 0.015497 | 0.0038918 | 3.672e-06 | 2.134e-06 | 0.02371 | 0.02371 | 0.02371 | 0.97242 | -0.53228 | 0.97267 | -0.52731 | 6.5137
133 | 0.066845 | 0.016816 | -0.066828 | -0.016805 | 1.7223e-05 | 1.0965e-05 | 0.10069 | 0.10069 | 0.10069 | 0.98804 | -0.2284 | 0.98776 | -0.2338 | 27.6629
134 | 0.063683 | 0.016016 | -0.063672 | -0.01601 | 1.0675e-05 | 6.7923e-06 | 0.095956 | 0.095956 | 0.095956 | 0.98776 | -0.2338 | 0.98758 | -0.23731 | 26.3614
135 | 0.06005 | 0.015102 | -0.06004 | -0.015096 | 9.2801e-06 | 5.9006e-06 | 0.090497 | 0.090497 | 0.090497 | 0.98758 | -0.23731 | 0.98741 | -0.24055 | 24.8619
136 | 0.056169 | 0.014126 | -0.056137 | -0.014105 | 3.2521e-05 | 2.0659e-05 | 0.084664 | 0.084664 | 0.084664 | 0.98741 | -0.24055 | 0.98679 | -0.25267 | 23.2593
137 | 0.053656 | 0.013483 | -0.053639 | -0.013472 | 1.7024e-05 | 1.0807e-05 | 0.080922 | 0.080922 | 0.080922 | 0.98679 | -0.25267 | 0.98645 | -0.25932 | 22.2314
138 | -0.028213 | -0.0070762 | 0.028229 | 0.0070861 | 1.5789e-05 | 9.8242e-06 | 0.043165 | 0.043165 | 0.043165 | 0.97262 | -0.52727 | 0.97322 | -0.51553 | 11.8586
139 | -0.030934 | -0.0077639 | 0.030939 | 0.0077672 | 5.2868e-06 | 3.3053e-06 | 0.047301 | 0.047301 | 0.047301 | 0.97322 | -0.51553 | 0.9734 | -0.51195 | 12.9947
140 | 0.039811 | 0.010008 | -0.039769 | -0.0099814 | 4.2364e-05 | 2.6734e-05 | 0.060869 | 0.060869 | 0.060869 | 0.9734 | -0.51195 | 0.97227 | -0.53426 | 16.7224
141 | 0.016726 | 0.0041942 | -0.01672 | -0.0041908 | 5.7237e-06 | 3.3731e-06 | 0.02557 | 0.02557 | 0.02557 | 0.9734 | -0.51195 | 0.97304 | -0.51913 | 7.0246
142 | 0.0098537 | 0.0024699 | -0.0098527 | -0.0024694 | 9.5369e-07 | 4.7126e-07 | 0.015069 | 0.015069 | 0.015069 | 0.97304 | -0.51913 | 0.97293 | -0.52116 | 4.1398
143 | 0.0069122 | 0.0017324 | -0.006912 | -0.0017323 | 1.933e-07 | 6.6435e-08 | 0.010572 | 0.010572 | 0.010572 | 0.97293 | -0.52116 | 0.9729 | -0.52175 | 2.9043
144 | 0.006912 | 0.0017323 | -0.0069116 | -0.0017322 | 3.8414e-07 | 1.3204e-07 | 0.010572 | 0.010572 | 0.010572 | 0.9729 | -0.52175 | 0.97284 | -0.52292 | 2.9043
145 | 0.035914 | 0.0090154 | -0.035893 | -0.0090022 | 2.0862e-05 | 1.3124e-05 | 0.05497 | 0.05497 | 0.05497 | 0.97227 | -0.53426 | 0.97165 | -0.54645 | 15.1017
146 | 0.014723 | 0.0036913 | -0.014721 | -0.00369 | 2.3488e-06 | 1.3506e-06 | 0.022548 | 0.022548 | 0.022548 | 0.97165 | -0.54645 | 0.97148 | -0.54979 | 6.1944
147 | 0.02117 | 0.0053109 | -0.021163 | -0.0053068 | 6.7856e-06 | 4.1297e-06 | 0.032423 | 0.032423 | 0.032423 | 0.97165 | -0.54645 | 0.97131 | -0.55317 | 8.9073
148 | 0.0079582 | 0.0019952 | -0.0079575 | -0.0019949 | 7.2041e-07 | 3.01e-07 | 0.01219 | 0.01219 | 0.01219 | 0.97148 | -0.54979 | 0.97139 | -0.55169 | 3.3489
149 | 0.018264 | 0.0045802 | -0.018261 | -0.004578 | 3.6513e-06 | 2.1829e-06 | 0.027981 | 0.027981 | 0.027981 | 0.97131 | -0.55317 | 0.9711 | -0.55737 | 7.6871
150 | 0.0079575 | 0.0019949 | -0.0079558 | -0.0019941 | 1.744e-06 | 7.2882e-07 | 0.01219 | 0.01219 | 0.01219 | 0.97139 | -0.55169 | 0.97115 | -0.55629 | 3.3489
151 | 0.016159 | 0.0040513 | -0.016157 | -0.00405 | 2.3064e-06 | 1.352e-06 | 0.024761 | 0.024761 | 0.024761 | 0.9711 | -0.55737 | 0.97095 | -0.56036 | 6.8025
152 | 0.037683 | 0.0094743 | -0.037666 | -0.0094637 | 1.6834e-05 | 1.0588e-05 | 0.056201 | 0.056201 | 0.056201 | 0.9979 | -0.040284 | 0.99741 | -0.049643 | 15.4399
153 | 0.03289 | 0.0082666 | -0.032868 | -0.008253 | 2.181e-05 | 1.3644e-05 | 0.049075 | 0.049076 | 0.049076 | 0.99741 | -0.049643 | 0.99669 | -0.063543 | 13.4823
154 | 0.032621 | 0.008191 | -0.032608 | -0.0081829 | 1.3018e-05 | 8.1407e-06 | 0.048707 | 0.048707 | 0.048707 | 0.99669 | -0.063543 | 0.99626 | -0.071911 | 13.3809
155 | 0.029863 | 0.0074951 | -0.029859 | -0.0074926 | 4.0131e-06 | 2.4984e-06 | 0.044608 | 0.044608 | 0.044608 | 0.99626 | -0.071911 | 0.99611 | -0.074729 | 12.2548
156 | 0.046211 | 0.011611 | -0.046185 | -0.011594 | 2.5684e-05 | 1.6258e-05 | 0.069717 | 0.069717 | 0.069717 | 0.98645 | -0.25932 | 0.98585 | -0.27097 | 19.1532
157 | 0.0039541 | 0.00099091 | -0.0039539 | -0.00099095 | 1.5701e-07 | -4.0503e-08 | 0.00606 | 0.0060601 | 0.0060601 | 0.9709 | -0.56127 | 0.97086 | -0.5621 | 1.6649
158 | -0.0079539 | -0.0019934 | 0.0079558 | 0.0019941 | 1.8852e-06 | 7.8802e-07 | 0.01219 | 0.01219 | 0.01219 | 0.9709 | -0.56127 | 0.97115 | -0.55629 | 3.349
159 | 0.0015253 | 0.00038149 | -0.0015252 | -0.00038158 | 1.6048e-08 | -9.0041e-08 | 0.002317 | 0.0023171 | 0.0023171 | 0.97941 | -0.39676 | 0.9794 | -0.39698 | 0.63656
160 | 0.0013186 | 0.00032978 | -0.0013185 | -0.00033012 | 4.3994e-08 | -3.3977e-07 | 0.0020031 | 0.0020032 | 0.0020032 | 0.9794 | -0.39698 | 0.97937 | -0.39768 | 0.55033
161 | 0.01354 | 0.0033942 | -0.013539 | -0.0033934 | 1.4612e-06 | 8.2325e-07 | 0.020751 | 0.020751 | 0.020751 | 0.97095 | -0.56036 | 0.97083 | -0.56263 | 5.7009
162 | 0.0082018 | 0.0020558 | -0.0082006 | -0.0020553 | 1.2053e-06 | 5.1997e-07 | 0.012571 | 0.012571 | 0.012571 | 0.97083 | -0.56263 | 0.97068 | -0.56571 | 3.4536
163 | 0.0011042 | 0.00027674 | -0.0011042 | -0.00027674 | 3.9538e-10 | -4.2938e-09 | 0.0016927 | 0.0016927 | 0.0016927 | 0.97068 | -0.56571 | 0.97068 | -0.56572 | 0.46504
164 | 0.0067008 | 0.0016698 | -0.0066847 | -0.0016646 | 1.6042e-05 | 5.1615e-06 | 0.010216 | 0.010218 | 0.010218 | 0.9757 | -0.47004 | 0.97315 | -0.52059 | 2.807
165 | 0.0060312 | 0.0015008 | -0.0060304 | -0.0015006 | 8.1296e-07 | 2.0337e-07 | 0.0092182 | 0.0092183 | 0.0092183 | 0.97315 | -0.52059 | 0.97301 | -0.52343 | 2.5325
166 | 0.0058537 | 0.0014564 | -0.0058525 | -0.0014561 | 1.2459e-06 | 2.8213e-07 | 0.0089482 | 0.0089484 | 0.0089484 | 0.97301 | -0.52343 | 0.97279 | -0.52792 | 2.4583
167 | 0.001308 | 0.00032741 | -0.001308 | -0.00032782 | 5.221e-08 | -4.0038e-07 | 0.0019984 | 0.0019985 | 0.0019985 | 0.97392 | -0.50579 | 0.97388 | -0.50663 | 0.54905
168 | 0.00043164 | 0.00010296 | -0.00043162 | -0.00010416 | 1.5878e-08 | -1.2088e-06 | 0.00065744 | 0.00065786 | 0.00065786 | 0.97423 | -0.49978 | 0.97419 | -0.50058 | 0.18073
169 | 0.00059219 | 0.00014341 | -0.00059212 | -0.00014646 | 7.6165e-08 | -3.0506e-06 | 0.00090272 | 0.00090382 | 0.00090382 | 0.97423 | -0.49978 | 0.9741 | -0.50253 | 0.2483
170 | -0.00094721 | -0.00023676 | 0.00094722 | 0.00023659 | 1.137e-08 | -1.7117e-07 | 0.0014506 | 0.0014505 | 0.0014506 | 0.97152 | -0.55321 | 0.97153 | -0.55296 | 0.3985
171 | 0.00056429 | 0.00014079 | -0.00056429 | -0.00014086 | 1.7124e-09 | -7.4638e-08 | 0.00086406 | 0.00086409 | 0.00086409 | 0.97152 | -0.55321 | 0.97151 | -0.55328 | 0.23739
172 | -0.0013486 | -0.00033719 | 0.001349 | 0.00033486 | 3.2847e-07 | -2.3344e-06 | 0.0020653 | 0.0020644 | 0.0020653 | 0.97153 | -0.55296 | 0.97179 | -0.54783 | 0.56739
173 | 0.00043107 | 0.00010748 | -0.00043107 | -0.00010754 | 8.3079e-10 | -6.2436e-08 | 0.00066004 | 0.00066006 | 0.00066006 | 0.97151 | -0.55328 | 0.97151 | -0.55332 | 0.18134
174 | 0.002312 | 0.00057533 | -0.0023103 | -0.00057864 | 1.6588e-06 | -3.3096e-06 | 0.0035386 | 0.0035402 | 0.0035402 | 0.97179 | -0.54783 | 0.97103 | -0.56294 | 0.97259
175 | -0.0036609 | -0.00091019 | 0.0036642 | 0.00090882 | 3.3118e-06 | -1.3699e-06 | 0.005603 | 0.0056018 | 0.005603 | 0.97179 | -0.54783 | 0.97275 | -0.52871 | 1.5393
176 | 0.00021362 | 5.3041e-05 | -0.00021362 | -5.3538e-05 | 1.6144e-09 | -4.9717e-07 | 0.00032702 | 0.0003272 | 0.0003272 | 0.97151 | -0.55332 | 0.9715 | -0.55348 | 0.089889
177 | 0.0023103 | 0.00057864 | -0.0023103 | -0.00057867 | 1.4571e-08 | -2.9024e-08 | 0.0035402 | 0.0035402 | 0.0035402 | 0.97103 | -0.56294 | 0.97102 | -0.56307 | 0.97259
178 | 0.00021492 | 5.3565e-05 | -0.00021492 | -5.3863e-05 | 9.7576e-10 | -2.9833e-07 | 0.00032865 | 0.00032876 | 0.00032876 | 0.97275 | -0.52871 | 0.97274 | -0.52881 | 0.090319
179 | -0.0038792 | -0.00096238 | 0.0038793 | 0.00096234 | 1.4481e-07 | -4.3631e-08 | 0.0059304 | 0.0059304 | 0.0059304 | 0.97275 | -0.52871 | 0.97279 | -0.52792 | 1.6292
180 | 0.0020196 | 0.00050583 | -0.0020195 | -0.00050614 | 1.1198e-07 | -3.1396e-07 | 0.0030948 | 0.003095 | 0.003095 | 0.97102 | -0.56307 | 0.97096 | -0.56423 | 0.85026
181 | 0.0019731 | 0.0004941 | -0.0019729 | -0.00049447 | 1.2139e-07 | -3.6337e-07 | 0.0030181 | 0.0030183 | 0.0030183 | 0.97272 | -0.5292 | 0.97266 | -0.53049 | 0.8292
182 | -0.0019731 | -0.0004941 | 0.0019732 | 0.00049374 | 1.2006e-07 | -3.5952e-07 | 0.0030181 | 0.003018 | 0.0030181 | 0.97272 | -0.5292 | 0.97279 | -0.52792 | 0.82916
183 | -0.00028808 | -7.22e-05 | 0.00028808 | 7.1978e-05 | 1.2248e-09 | -2.2227e-07 | 0.00043348 | 0.0004334 | 0.00043348 | 0.98891 | -0.21171 | 0.98891 | -0.21162 | 0.11909
184 | -0.0077617 | -0.0019462 | 0.0077629 | 0.0019467 | 1.1873e-06 | 4.6203e-07 | 0.011679 | 0.011679 | 0.011679 | 0.98891 | -0.21162 | 0.98908 | -0.20841 | 3.2086
185 | 0.0074736 | 0.0018743 | -0.0074732 | -0.0018741 | 4.283e-07 | 1.5825e-07 | 0.011246 | 0.011246 | 0.011246 | 0.98891 | -0.21162 | 0.98885 | -0.21283 | 3.0896
186 | -0.0077629 | -0.0019467 | 0.0077692 | 0.0019492 | 6.3438e-06 | 2.4669e-06 | 0.011679 | 0.011679 | 0.011679 | 0.98908 | -0.20841 | 0.98996 | -0.19128 | 3.2086
187 | 0.0072195 | 0.0018105 | -0.0072183 | -0.0018101 | 1.2587e-06 | 4.4082e-07 | 0.010864 | 0.010864 | 0.010864 | 0.98885 | -0.21283 | 0.98866 | -0.21648 | 2.9847
188 | -0.0077692 | -0.0019492 | 0.0077706 | 0.0019497 | 1.346e-06 | 5.2303e-07 | 0.011679 | 0.011679 | 0.011679 | 0.98996 | -0.19128 | 0.99015 | -0.18764 | 3.2084
189 | 0.0072183 | 0.0018101 | -0.0072142 | -0.0018086 | 4.1084e-06 | 1.4399e-06 | 0.010864 | 0.010865 | 0.010865 | 0.98866 | -0.21648 | 0.98805 | -0.22843 | 2.9848
190 | 0.0067081 | 0.0016818 | -0.0067047 | -0.0016808 | 3.3578e-06 | 1.026e-06 | 0.010103 | 0.010103 | 0.010103 | 0.98805 | -0.22843 | 0.98751 | -0.23894 | 2.7756
191 | 0.0067047 | 0.0016808 | -0.0066993 | -0.0016791 | 5.3892e-06 | 1.6495e-06 | 0.010103 | 0.010104 | 0.010104 | 0.98751 | -0.23894 | 0.98664 | -0.25582 | 2.7758
192 | 0.00032835 | 8.2179e-05 | -0.00032835 | -8.2293e-05 | 8.1332e-10 | -1.1406e-07 | 0.00049341 | 0.00049345 | 0.00049345 | 0.99015 | -0.18751 | 0.99015 | -0.18756 | 0.13556
193 | 0.042768 | 0.010902 | -0.042747 | -0.010891 | 2.1188e-05 | 1.0753e-05 | 0.064338 | 0.064339 | 0.064339 | 0.99015 | -0.18751 | 0.98962 | -0.19778 | 4.4189
194 | -0.019411 | -0.0048729 | 0.019428 | 0.0048833 | 1.7349e-05 | 1.0452e-05 | 0.029698 | 0.029698 | 0.029698 | 0.97267 | -0.52731 | 0.97362 | -0.50859 | 8.1589
195 | -0.019428 | -0.0048833 | 0.019482 | 0.0049157 | 5.3786e-05 | 3.2394e-05 | 0.029698 | 0.029698 | 0.029698 | 0.97362 | -0.50859 | 0.97657 | -0.45077 | 8.1589
196 | 0.011772 | 0.0029519 | -0.011766 | -0.0029488 | 5.8358e-06 | 3.1445e-06 | 0.018046 | 0.018046 | 0.018046 | 0.97071 | -0.56614 | 0.97018 | -0.57655 | 4.9576
197 | -0.019482 | -0.0049157 | 0.019515 | 0.0049352 | 3.2302e-05 | 1.9449e-05 | 0.029698 | 0.029697 | 0.029698 | 0.97657 | -0.45077 | 0.97833 | -0.41621 | 8.1587
198 | -0.038344 | -0.0097441 | 0.038454 | 0.0098099 | 0.00010976 | 6.5779e-05 | 0.057916 | 0.057915 | 0.057916 | 0.98598 | -0.2677 | 0.98906 | -0.20842 | 7.9556
199 | 0.038344 | 0.0097441 | -0.038283 | -0.0097074 | 6.1262e-05 | 3.6727e-05 | 0.057916 | 0.057917 | 0.057917 | 0.98598 | -0.2677 | 0.98426 | -0.30093 | 7.9557
200 | -0.038454 | -0.0098099 | 0.038455 | 0.0098101 | 4.9664e-07 | 2.3677e-07 | 0.057915 | 0.057915 | 0.057915 | 0.98906 | -0.20842 | 0.98908 | -0.20816 | 3.9777
201 | 0.033547 | 0.0085203 | -0.033538 | -0.0085151 | 8.2065e-06 | 5.1443e-06 | 0.050756 | 0.050756 | 0.050756 | 0.98426 | -0.30093 | 0.984 | -0.30601 | 13.9441
202 | -0.042725 | -0.01088 | 0.042747 | 0.010891 | 2.1393e-05 | 1.086e-05 | 0.06434 | 0.064339 | 0.06434 | 0.98908 | -0.20816 | 0.98962 | -0.19778 | 4.4189
203 | -0.028232 | -0.00712 | 0.028244 | 0.0071277 | 1.2434e-05 | 7.7321e-06 | 0.042956 | 0.042956 | 0.042956 | 0.97833 | -0.41621 | 0.9788 | -0.40701 | 11.8011
204 | 0.033538 | 0.0085151 | -0.03341 | -0.0084349 | 0.00012794 | 8.0209e-05 | 0.050756 | 0.050757 | 0.050757 | 0.984 | -0.30601 | 0.9799 | -0.38562 | 13.9443
205 | -0.033311 | -0.0083975 | 0.033345 | 0.0084189 | 3.4128e-05 | 2.1395e-05 | 0.050658 | 0.050658 | 0.050658 | 0.9788 | -0.40701 | 0.9799 | -0.38562 | 13.917
206 | 6.5451e-05 | 1.6068e-05 | -6.5451e-05 | -1.6404e-05 | 9.8727e-11 | -3.3608e-07 | 9.9271e-05 | 9.939e-05 | 9.939e-05 | 0.9799 | -0.38562 | 0.9799 | -0.38565 | 0.027305
207 | -0.0066972 | -0.0016785 | 0.0066993 | 0.0016791 | 2.1119e-06 | 6.4732e-07 | 0.010104 | 0.010104 | 0.010104 | 0.9863 | -0.26243 | 0.98664 | -0.25582 | 2.7758
208 | -0.00059207 | -0.00014839 | 0.00059212 | 0.00014646 | 4.8249e-08 | -1.9281e-06 | 0.00090452 | 0.00090382 | 0.00090452 | 0.97401 | -0.50425 | 0.9741 | -0.50253 | 0.24849
209 | 0.00043162 | 0.00010416 | -0.00043157 | -0.00010816 | 5.2674e-08 | -3.9982e-06 | 0.00065786 | 0.00065928 | 0.00065928 | 0.97419 | -0.50058 | 0.97406 | -0.50317 | 0.18112
210 | 0.00075964 | 0.00019005 | -0.00075963 | -0.00019024 | 7.7284e-09 | -1.8976e-07 | 0.0011541 | 0.0011541 | 0.0011541 | 0.97937 | -0.39768 | 0.97935 | -0.39789 | 0.31707
211 | 0.00031627 | 7.9123e-05 | -0.00031627 | -7.9265e-05 | 9.8216e-10 | -1.4211e-07 | 0.00048049 | 0.00048054 | 0.00048054 | 0.97935 | -0.39789 | 0.97935 | -0.39796 | 0.13202
212 | 0.013744 | 0.0034451 | -0.013743 | -0.0034445 | 1.1635e-06 | 6.5297e-07 | 0.02076 | 0.02076 | 0.02076 | 0.98512 | -0.28513 | 0.98503 | -0.28691 | 5.7034
213 | -0.017126 | -0.0042927 | 0.017129 | 0.0042947 | 3.3732e-06 | 1.9877e-06 | 0.025869 | 0.025869 | 0.025869 | 0.98512 | -0.28513 | 0.98533 | -0.281 | 7.1068
214 | 0.011175 | 0.0028008 | -0.011174 | -0.0028005 | 4.7717e-07 | 2.4855e-07 | 0.016881 | 0.016881 | 0.016881 | 0.98503 | -0.28691 | 0.98499 | -0.2878 | 4.6376
215 | 0.02429 | 0.0060979 | -0.024281 | -0.0060921 | 9.3702e-06 | 5.7605e-06 | 0.036686 | 0.036686 | 0.036686 | 0.98533 | -0.281 | 0.98492 | -0.28909 | 10.0785
216 | -0.041419 | -0.010393 | 0.041437 | 0.010404 | 1.7456e-05 | 1.102e-05 | 0.062554 | 0.062554 | 0.062554 | 0.98533 | -0.281 | 0.98579 | -0.27216 | 17.1853
217 | 0.0081087 | 0.0020323 | -0.0081084 | -0.0020321 | 3.1801e-07 | 1.316e-07 | 0.01225 | 0.01225 | 0.01225 | 0.98499 | -0.2878 | 0.98494 | -0.28863 | 3.3653
218 | 0.021603 | 0.005421 | -0.021601 | -0.0054196 | 2.2842e-06 | 1.3891e-06 | 0.03264 | 0.03264 | 0.03264 | 0.98492 | -0.28909 | 0.98481 | -0.2913 | 8.9672
219 | -0.043467 | -0.010912 | 0.04347 | 0.010914 | 2.4586e-06 | 1.5541e-06 | 0.065619 | 0.065619 | 0.065619 | 0.98579 | -0.27216 | 0.98585 | -0.27097 | 18.0271
220 | 0.0056648 | 0.0014197 | -0.0056645 | -0.0014197 | 2.682e-07 | 4.7377e-08 | 0.0085582 | 0.0085582 | 0.0085582 | 0.98494 | -0.28863 | 0.98489 | -0.28962 | 2.3512
221 | 0.020228 | 0.0050756 | -0.020216 | -0.0050682 | 1.2317e-05 | 7.4357e-06 | 0.030566 | 0.030567 | 0.030567 | 0.98481 | -0.2913 | 0.98415 | -0.30408 | 8.3974
222 | 0.017926 | 0.0044942 | -0.017923 | -0.0044928 | 2.2767e-06 | 1.3521e-06 | 0.027104 | 0.027104 | 0.027104 | 0.98415 | -0.30408 | 0.98401 | -0.30675 | 7.4461
223 | 0.015366 | 0.0038518 | -0.015364 | -0.0038507 | 1.9131e-06 | 1.1044e-06 | 0.023236 | 0.023236 | 0.023236 | 0.98401 | -0.30675 | 0.98388 | -0.30936 | 6.3835
224 | 0.0087062 | 0.002182 | -0.0087058 | -0.0021818 | 4.1135e-07 | 1.8294e-07 | 0.013168 | 0.013168 | 0.013168 | 0.98382 | -0.31062 | 0.98377 | -0.31161 | 3.6176
225 | -0.010458 | -0.0026211 | 0.010459 | 0.0026214 | 6.2747e-07 | 3.1665e-07 | 0.015818 | 0.015818 | 0.015818 | 0.98382 | -0.31062 | 0.98388 | -0.30936 | 4.3456
226 | 0.0056391 | 0.0014133 | -0.0056391 | -0.0014132 | 3.459e-08 | 6.0404e-09 | 0.0085296 | 0.0085296 | 0.0085296 | 0.98377 | -0.31161 | 0.98376 | -0.31174 | 2.3433
227 | 0.0043576 | 0.0010921 | -0.0043575 | -0.0010921 | 1.1844e-07 | -1.6498e-08 | 0.0065913 | 0.0065913 | 0.0065913 | 0.98376 | -0.31174 | 0.98373 | -0.31231 | 1.8108
228 | 0.027646 | 0.0069379 | -0.027638 | -0.0069328 | 8.2252e-06 | 5.0968e-06 | 0.041301 | 0.041301 | 0.041301 | 0.99611 | -0.074729 | 0.99579 | -0.08097 | 11.3465
229 | 0.024976 | 0.0062657 | -0.024973 | -0.006264 | 2.7867e-06 | 1.7141e-06 | 0.037324 | 0.037324 | 0.037324 | 0.99579 | -0.08097 | 0.99567 | -0.083311 | 10.2539
230 | 0.022137 | 0.0055532 | -0.022131 | -0.0055499 | 5.3659e-06 | 3.2642e-06 | 0.033085 | 0.033085 | 0.033085 | 0.99567 | -0.083311 | 0.9954 | -0.088396 | 9.0894
231 | 0.019585 | 0.0049116 | -0.019581 | -0.0049093 | 3.8558e-06 | 2.3118e-06 | 0.029278 | 0.029278 | 0.029278 | 0.9954 | -0.088396 | 0.99519 | -0.092528 | 8.0434
232 | 0.016779 | 0.0042072 | -0.016777 | -0.0042056 | 2.6902e-06 | 1.5736e-06 | 0.025089 | 0.025089 | 0.025089 | 0.99519 | -0.092528 | 0.99501 | -0.095893 | 6.8927
233 | 0.013422 | 0.0033648 | -0.013419 | -0.0033635 | 2.2537e-06 | 1.2487e-06 | 0.020072 | 0.020072 | 0.020072 | 0.99501 | -0.095893 | 0.99483 | -0.099417 | 5.5144
234 | 0.011049 | 0.0027694 | -0.011048 | -0.002769 | 7.7134e-07 | 3.9588e-07 | 0.016526 | 0.016527 | 0.016527 | 0.99483 | -0.099417 | 0.99476 | -0.10088 | 4.5403
235 | 0.0089171 | 0.0022349 | -0.0089157 | -0.0022343 | 1.387e-06 | 6.1786e-07 | 0.013339 | 0.013339 | 0.013339 | 0.99476 | -0.10088 | 0.99459 | -0.10415 | 3.6645
236 | 0.0060227 | 0.0015092 | -0.0060195 | -0.0015086 | 3.22e-06 | 6.8915e-07 | 0.0090106 | 0.009011 | 0.009011 | 0.99459 | -0.10415 | 0.99401 | -0.11537 | 2.4756
237 | 0.0060195 | 0.0015086 | -0.0060178 | -0.0015082 | 1.6674e-06 | 3.5756e-07 | 0.009011 | 0.0090113 | 0.0090113 | 0.99401 | -0.11537 | 0.99371 | -0.12119 | 2.4756
238 | -0.00083269 | -0.00020823 | 0.00083269 | 0.00020821 | 9.8527e-10 | -2.0984e-08 | 0.0012508 | 0.0012508 | 0.0012508 | 0.99049 | -0.18111 | 0.99049 | -0.18109 | 0.34362
239 | 0.00033836 | 8.434e-05 | -0.00033836 | -8.48e-05 | 3.4752e-09 | -4.5954e-07 | 0.00050816 | 0.00050832 | 0.00050832 | 0.99049 | -0.18111 | 0.99048 | -0.18133 | 0.13965
240 | -0.0012734 | -0.00031915 | 0.0012735 | 0.00031886 | 3.5139e-08 | -2.9277e-07 | 0.0019344 | 0.0019343 | 0.0019344 | 0.97956 | -0.39379 | 0.97959 | -0.39321 | 0.53144
241 | -0.0021393 | -0.00053586 | 0.0021394 | 0.00053565 | 8.4504e-08 | -2.1459e-07 | 0.0032496 | 0.0032495 | 0.0032496 | 0.97959 | -0.39321 | 0.97963 | -0.39238 | 0.89273
242 | -0.0033503 | -0.00083913 | 0.0033505 | 0.00083901 | 1.8253e-07 | -1.1985e-07 | 0.0050888 | 0.0050887 | 0.0050888 | 0.97963 | -0.39238 | 0.97969 | -0.39123 | 1.398
243 | -0.0041083 | -0.0010289 | 0.0041086 | 0.0010289 | 2.4096e-07 | -5.3615e-08 | 0.0062397 | 0.0062396 | 0.0062397 | 0.97969 | -0.39123 | 0.97975 | -0.39 | 1.7142
244 | -0.00525 | -0.001315 | 0.0052505 | 0.001315 | 4.9883e-07 | 5.5708e-08 | 0.0079732 | 0.0079731 | 0.0079732 | 0.97975 | -0.39 | 0.97986 | -0.38801 | 2.1904

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.55881 | 0.14307

## res_load
| p_mw | q_mvar
0 | 0.00014278 | 3.5785e-05
1 | 0.00043273 | 0.00010845
2 | 4.8707e-05 | 1.2207e-05
3 | 0.00027723 | 6.948e-05
4 | 0.00036227 | 9.0794e-05
5 | 0.00040958 | 0.00010265
6 | 8.997e-05 | 2.2549e-05
7 | 0.00041665 | 0.00010442
8 | 0.00011624 | 2.9133e-05
9 | 0.0022068 | 0.00055308
10 | 0.00011416 | 2.861e-05
11 | 0.00041212 | 0.00010329
12 | 0.001182 | 0.00029624
13 | 0.0001589 | 3.9823e-05
14 | 0.00042025 | 0.00010533
15 | 0.00042263 | 0.00010592
16 | 0.00016839 | 4.2201e-05
17 | 0.00049265 | 0.00012347
18 | 0.00042105 | 0.00010553
19 | 0.0011934 | 0.00029908
20 | 0.0008095 | 0.00020288
21 | 0.00025013 | 6.2688e-05
22 | 0.0017178 | 0.00043053
23 | 0.0042913 | 0.0010755
24 | 0.0038998 | 0.00097738
25 | 0.0047679 | 0.0011949
26 | 0.0039554 | 0.00099132
27 | 0.00022498 | 5.6385e-05
28 | 0.00099456 | 0.00024926
29 | 0.010561 | 0.0026468
30 | 0.00054497 | 0.00013658
31 | 0.01291 | 0.0032356
32 | 0.011401 | 0.0028573
33 | 0.012864 | 0.0032241
34 | 0.0092291 | 0.002313
35 | 0.0045782 | 0.0011474
36 | 0.0022712 | 0.00056923
37 | 0.0047082 | 0.00118
38 | 0.001757 | 0.00044035
39 | 0.0074727 | 0.0018728
40 | 0.0027361 | 0.00068574
41 | 0.0092681 | 0.0023228
42 | 0.0010786 | 0.00027032
43 | 0.0035715 | 0.00089511
44 | 0.005382 | 0.0013489
45 | 0.010312 | 0.0025845
46 | 0.0050491 | 0.0012654
47 | 0.0059908 | 0.0015014
48 | 0.002419 | 0.00060627
49 | 0.0056159 | 0.0014075
50 | 0.0064538 | 0.0016175
51 | 0.0069478 | 0.0017413
52 | 0.007159 | 0.0017942
53 | 0.00017268 | 4.3278e-05
54 | 0.0049237 | 0.001234
55 | 0.00021069 | 5.2805e-05
56 | 0.00051762 | 0.00012973
57 | 0.00070819 | 0.00017749
58 | 0.00060427 | 0.00015144
59 | 0.021992 | 0.0055118
60 | 0.0074879 | 0.0018766
61 | 0.0092575 | 0.0023202
62 | 0.0070718 | 0.0017724
63 | 0.007473 | 0.0018729
64 | 0.0053175 | 0.0013327
65 | 0.0017432 | 0.0004369
66 | 0.0026582 | 0.00066621
67 | 0.0030726 | 0.00077007
68 | 0.01523 | 0.003817
69 | 0.0025173 | 0.0006309
70 | 0.0040159 | 0.0010065
71 | 0.0044581 | 0.0011173
72 | 0.0028878 | 0.00072374
73 | 0.0026437 | 0.00066257
74 | 0.0024341 | 0.00061003
75 | 0.0046625 | 0.0011685
76 | 0.0011051 | 0.00027697
77 | 0.0020976 | 0.0005257
78 | 0.0027861 | 0.00069827
79 | 0.0025135 | 0.00062994
80 | 0.0037016 | 0.00092771
81 | 0.0030387 | 0.00076158
82 | 0.0031447 | 0.00078814
83 | 0.0036227 | 0.00090793
84 | 0.003871 | 0.00097017
85 | 0.0024813 | 0.00062186
86 | 0.004224 | 0.0010586
87 | 0.0027047 | 0.00067786
88 | 0.0068666 | 0.0017209
89 | 0.0029406 | 0.00073697
90 | 0.0038546 | 0.00096606
91 | 0.0069116 | 0.0017322
92 | 0.0067623 | 0.0016948
93 | 0.0028992 | 0.00072662
94 | 0.0021014 | 0.00052666
95 | 0.00025112 | 6.2937e-05
96 | 0.0047765 | 0.0011971
97 | 0.00024717 | 6.1947e-05
98 | 0.0027444 | 0.0006878
99 | 0.0074279 | 0.0018616
100 | 0.0070184 | 0.001759
101 | 0.0039998 | 0.0010024
102 | 0.0039539 | 0.00099095
103 | 0.00050826 | 0.00012738
104 | 0.00020668 | 5.1799e-05
105 | 0.0026166 | 0.00065577
106 | 0.005337 | 0.0013376
107 | 0.0070964 | 0.0017785
108 | 0.0011042 | 0.00027674
109 | 0.00065355 | 0.00016379
110 | 0.00017664 | 4.4271e-05
111 | 0.00038292 | 9.5969e-05
112 | 0.00040141 | 0.0001006
113 | 0.00013322 | 3.3388e-05
114 | 0.00021744 | 5.4496e-05
115 | 0.00021362 | 5.3538e-05
116 | 0.00029066 | 7.2847e-05
117 | 0.0019729 | 0.00049447
118 | 0.00021492 | 5.3863e-05
119 | 0.0020195 | 0.00050614
120 | 0.001308 | 0.00032782
121 | 0.00028808 | 7.22e-05
122 | 0.00025368 | 6.3578e-05
123 | 0.00037346 | 9.3598e-05
124 | 0.00050606 | 0.00012683
125 | 0.0039146 | 0.00098108
126 | 0.011766 | 0.0029488
127 | 0.0047367 | 0.0011871
128 | 0.0042706 | 0.0010703
129 | 0.0087175 | 0.0021848
130 | 0.0050663 | 0.0012697
131 | 6.5451e-05 | 1.6404e-05
132 | 0.00032835 | 8.2293e-05
133 | 0.0066972 | 0.0016785
134 | 0.00059207 | 0.00014839
135 | 0.00043157 | 0.00010816
136 | 0.00055888 | 0.00014007
137 | 0.00044336 | 0.00011112
138 | 0.00031627 | 7.9265e-05
139 | 0.0033819 | 0.00084758
140 | 0.0025683 | 0.00064367
141 | 0.0030655 | 0.00076828
142 | 0.0026776 | 0.00067108
143 | 0.0020301 | 0.0005088
144 | 0.0024435 | 0.00061241
145 | 0.0013726 | 0.00034401
146 | 0.0027155 | 0.00068057
147 | 0.0056645 | 0.0014197
148 | 0.0022902 | 0.00057399
149 | 0.0025578 | 0.00064104
150 | 0.0017519 | 0.00043907
151 | 0.0030666 | 0.00076857
152 | 0.004905 | 0.0012293
153 | 0.0012815 | 0.00032117
154 | 0.0043575 | 0.0010921
155 | 0.0022134 | 0.00055472
156 | 0.0026616 | 0.00066705
157 | 0.0028364 | 0.00071086
158 | 0.0025468 | 0.00063829
159 | 0.0028014 | 0.00070211
160 | 0.0033549 | 0.00084082
161 | 0.0023706 | 0.00059412
162 | 0.0021311 | 0.0005341
163 | 0.002893 | 0.00072505
164 | 0.0060178 | 0.0015082
165 | 0.00049433 | 0.00012389
166 | 0.0004394 | 0.00011012
167 | 0.00033836 | 8.48e-05
168 | 0.0012734 | 0.00031915
169 | 0.00086585 | 0.000217
170 | 0.0012109 | 0.00030348
171 | 0.00075782 | 0.00018993
172 | 0.0011414 | 0.00028607
173 | 0.00047864 | 0.00011996

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1