## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1362-15_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1362-15_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1362-15_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1362-15_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1362-15_0_3_node_103 | 0.4 | n |  | TRUE
5 | bus_LV_1362-15_0_3_node_88 | 0.4 | n |  | TRUE
6 | bus_LV_1362-15_0_3_node_38 | 0.4 | n |  | TRUE
7 | bus_LV_1362-15_0_3_node_31 | 0.4 | n |  | TRUE
8 | bus_LV_1362-15_0_3_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_1362-15_0_3_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_1362-15_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1362-15_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1362-15_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1362-15_0_3_node_106 | 0.4 | n |  | TRUE
14 | bus_LV_1362-15_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1362-15_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1362-15_0_3_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_1362-15_0_3_node_63 | 0.4 | n |  | TRUE
18 | bus_LV_1362-15_0_3_node_105 | 0.4 | n |  | TRUE
19 | bus_LV_1362-15_0_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1362-15_0_3_node_81 | 0.4 | n |  | TRUE
21 | bus_LV_1362-15_0_3_node_62 | 0.4 | n |  | TRUE
22 | bus_LV_1362-15_0_3_node_76 | 0.4 | n |  | TRUE
23 | bus_LV_1362-15_0_3_node_74 | 0.4 | n |  | TRUE
24 | bus_LV_1362-15_0_3_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_1362-15_0_3_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_1362-15_0_3_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_1362-15_0_3_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_1362-15_0_3_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_1362-15_0_3_node_108 | 0.4 | n |  | TRUE
30 | bus_LV_1362-15_0_3_node_104 | 0.4 | n |  | TRUE
31 | bus_LV_1362-15_0_3_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_1362-15_0_3_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_1362-15_0_3_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_1362-15_0_3_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_1362-15_0_3_node_61 | 0.4 | n |  | TRUE
36 | bus_LV_1362-15_0_3_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_1362-15_0_3_node_18 | 0.4 | n |  | TRUE
38 | bus_LV_1362-15_0_3_node_19 | 0.4 | n |  | TRUE
39 | bus_LV_1362-15_0_3_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_1362-15_0_3_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_1362-15_0_3_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_1362-15_0_3_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_1362-15_0_3_node_27 | 0.4 | n |  | TRUE
44 | bus_LV_1362-15_0_3_node_109 | 0.4 | n |  | TRUE
45 | bus_LV_1362-15_0_3_node_23 | 0.4 | n |  | TRUE
46 | bus_LV_1362-15_0_3_node_24 | 0.4 | n |  | TRUE
47 | bus_LV_1362-15_0_3_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_1362-15_0_3_node_102 | 0.4 | n |  | TRUE
49 | bus_LV_1362-15_0_3_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_1362-15_0_3_node_37 | 0.4 | n |  | TRUE
51 | bus_LV_1362-15_0_3_node_110 | 0.4 | n |  | TRUE
52 | bus_LV_1362-15_0_3_node_39 | 0.4 | n |  | TRUE
53 | bus_LV_1362-15_0_3_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_1362-15_0_3_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_1362-15_0_3_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_1362-15_0_3_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_1362-15_0_3_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_1362-15_0_3_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_1362-15_0_3_node_73 | 0.4 | n |  | TRUE
60 | bus_LV_1362-15_0_3_node_70 | 0.4 | n |  | TRUE
61 | bus_LV_1362-15_0_3_node_80 | 0.4 | n |  | TRUE
62 | bus_LV_1362-15_0_3_node_65 | 0.4 | n |  | TRUE
63 | bus_LV_1362-15_0_3_node_77 | 0.4 | n |  | TRUE
64 | bus_LV_1362-15_0_3_node_69 | 0.4 | n |  | TRUE
65 | bus_LV_1362-15_0_3_node_49 | 0.4 | n |  | TRUE
66 | bus_LV_1362-15_0_3_node_64 | 0.4 | n |  | TRUE
67 | bus_LV_1362-15_0_3_node_46 | 0.4 | n |  | TRUE
68 | bus_LV_1362-15_0_3_node_47 | 0.4 | n |  | TRUE
69 | bus_LV_1362-15_0_3_node_48 | 0.4 | n |  | TRUE
70 | bus_LV_1362-15_0_3_node_52 | 0.4 | n |  | TRUE
71 | bus_LV_1362-15_0_3_node_54 | 0.4 | n |  | TRUE
72 | bus_LV_1362-15_0_3_node_50 | 0.4 | n |  | TRUE
73 | bus_LV_1362-15_0_3_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_1362-15_0_3_node_53 | 0.4 | n |  | TRUE
75 | bus_LV_1362-15_0_3_node_56 | 0.4 | n |  | TRUE
76 | bus_LV_1362-15_0_3_node_57 | 0.4 | n |  | TRUE
77 | bus_LV_1362-15_0_3_node_55 | 0.4 | n |  | TRUE
78 | bus_LV_1362-15_0_3_node_58 | 0.4 | n |  | TRUE
79 | bus_LV_1362-15_0_3_node_59 | 0.4 | n |  | TRUE
80 | bus_LV_1362-15_0_3_node_60 | 0.4 | n |  | TRUE
81 | bus_LV_1362-15_0_3_node_93 | 0.4 | n |  | TRUE
82 | bus_LV_1362-15_0_3_node_99 | 0.4 | n |  | TRUE
83 | bus_LV_1362-15_0_3_node_92 | 0.4 | n |  | TRUE
84 | bus_LV_1362-15_0_3_node_100 | 0.4 | n |  | TRUE
85 | bus_LV_1362-15_0_3_node_98 | 0.4 | n |  | TRUE
86 | bus_LV_1362-15_0_3_node_72 | 0.4 | n |  | TRUE
87 | bus_LV_1362-15_0_3_node_75 | 0.4 | n |  | TRUE
88 | bus_LV_1362-15_0_3_node_66 | 0.4 | n |  | TRUE
89 | bus_LV_1362-15_0_3_node_67 | 0.4 | n |  | TRUE
90 | bus_LV_1362-15_0_3_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_1362-15_0_3_node_71 | 0.4 | n |  | TRUE
92 | bus_LV_1362-15_0_3_node_78 | 0.4 | n |  | TRUE
93 | bus_LV_1362-15_0_3_node_79 | 0.4 | n |  | TRUE
94 | bus_LV_1362-15_0_3_node_82 | 0.4 | n |  | TRUE
95 | bus_LV_1362-15_0_3_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_1362-15_0_3_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_1362-15_0_3_node_85 | 0.4 | n |  | TRUE
98 | bus_LV_1362-15_0_3_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_1362-15_0_3_node_87 | 0.4 | n |  | TRUE
100 | bus_LV_1362-15_0_3_node_101 | 0.4 | n |  | TRUE
101 | bus_LV_1362-15_0_3_node_91 | 0.4 | n |  | TRUE
102 | bus_LV_1362-15_0_3_node_89 | 0.4 | n |  | TRUE
103 | bus_LV_1362-15_0_3_node_90 | 0.4 | n |  | TRUE
104 | bus_LV_1362-15_0_3_node_94 | 0.4 | n |  | TRUE
105 | bus_LV_1362-15_0_3_node_95 | 0.4 | n |  | TRUE
106 | bus_LV_1362-15_0_3_node_96 | 0.4 | n |  | TRUE
107 | bus_LV_1362-15_0_3_node_97 | 0.4 | n |  | TRUE
108 | bus_MV_0_node_102 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1362-15_0_3_load_0 | 0 | 0.00083396 | 0.00020901 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1362-15_0_3_load_1 | 1 | 0.0057745 | 0.0014472 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1362-15_0_3_load_2 | 2 | 0.0023649 | 0.00059271 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1362-15_0_3_load_103 | 4 | 0.00032812 | 8.2235e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1362-15_0_3_load_88 | 5 | 0.00087056 | 0.00021818 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1362-15_0_3_load_38 | 6 | 0.00073713 | 0.00018474 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1362-15_0_3_load_31 | 7 | 0.00059098 | 0.00014811 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1362-15_0_3_load_30 | 8 | 0.00024362 | 6.1057e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1362-15_0_3_load_4 | 9 | 0.00018729 | 4.6938e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1362-15_0_3_load_5 | 10 | 0.00027035 | 6.7755e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1362-15_0_3_load_106 | 13 | 0.00042448 | 0.00010639 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1362-15_0_3_load_22 | 16 | 0.00022526 | 5.6454e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1362-15_0_3_load_105 | 18 | 0.00034168 | 8.5634e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1362-15_0_3_load_81 | 20 | 9.9539e-05 | 2.4947e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1362-15_0_3_load_62 | 21 | 8.9939e-05 | 2.2541e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1362-15_0_3_load_74 | 23 | 0.00021186 | 5.3096e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1362-15_0_3_load_11 | 24 | 0.0016212 | 0.00040631 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1362-15_0_3_load_12 | 25 | 0.00079604 | 0.00019951 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1362-15_0_3_load_13 | 26 | 0.00035614 | 8.9256e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1362-15_0_3_load_14 | 27 | 0.00032072 | 8.0381e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1362-15_0_3_load_15 | 28 | 0.00032534 | 8.1538e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1362-15_0_3_load_108 | 29 | 0.004954 | 0.0012416 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1362-15_0_3_load_104 | 30 | 0.0013665 | 0.00034247 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1362-15_0_3_load_17 | 31 | 0.00021273 | 5.3316e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1362-15_0_3_load_28 | 32 | 0.00059179 | 0.00014832 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1362-15_0_3_load_18 | 37 | 0.00018024 | 4.5173e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1362-15_0_3_load_19 | 38 | 0.00050017 | 0.00012536 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1362-15_0_3_load_32 | 40 | 0.00075633 | 0.00018955 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1362-15_0_3_load_29 | 41 | 0.00044619 | 0.00011183 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1362-15_0_3_load_33 | 42 | 0.0003297 | 8.2631e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1362-15_0_3_load_27 | 43 | 0.00035001 | 8.7721e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1362-15_0_3_load_109 | 44 | 0.0038362 | 0.00096144 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1362-15_0_3_load_23 | 45 | 0.00036929 | 9.2552e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1362-15_0_3_load_24 | 46 | 0.00072452 | 0.00018158 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1362-15_0_3_load_26 | 47 | 0.00040891 | 0.00010248 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1362-15_0_3_load_102 | 48 | 0.0024778 | 0.00062098 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1362-15_0_3_load_34 | 49 | 0.00029288 | 7.3401e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1362-15_0_3_load_37 | 50 | 0.0010483 | 0.00026272 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1362-15_0_3_load_110 | 51 | 0.00060744 | 0.00015224 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1362-15_0_3_load_39 | 52 | 0.00034073 | 8.5394e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1362-15_0_3_load_42 | 55 | 0.00015063 | 3.7753e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1362-15_0_3_load_44 | 57 | 0.00027637 | 6.9265e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1362-15_0_3_load_45 | 58 | 0.00014536 | 3.643e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1362-15_0_3_load_73 | 59 | 0.00039748 | 9.9618e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1362-15_0_3_load_70 | 60 | 0.00047378 | 0.00011874 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1362-15_0_3_load_80 | 61 | 0.00080688 | 0.00020222 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1362-15_0_3_load_77 | 63 | 0.00022299 | 5.5887e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1362-15_0_3_load_69 | 64 | 0.00018305 | 4.5876e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1362-15_0_3_load_64 | 66 | 0.0023867 | 0.00059816 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1362-15_0_3_load_46 | 67 | 0.00034763 | 8.7124e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1362-15_0_3_load_47 | 68 | 0.0007309 | 0.00018318 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1362-15_0_3_load_48 | 69 | 0.00050321 | 0.00012612 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1362-15_0_3_load_54 | 71 | 0.00018506 | 4.6382e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1362-15_0_3_load_50 | 72 | 0.00026704 | 6.6926e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1362-15_0_3_load_51 | 73 | 0.00077457 | 0.00019413 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1362-15_0_3_load_53 | 74 | 0.00085763 | 0.00021494 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1362-15_0_3_load_57 | 76 | 0.00038976 | 9.7682e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1362-15_0_3_load_55 | 77 | 0.00033449 | 8.3832e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1362-15_0_3_load_59 | 79 | 0.00025958 | 6.5056e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1362-15_0_3_load_60 | 80 | 0.00038115 | 9.5524e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1362-15_0_3_load_93 | 81 | 0.00023486 | 5.8861e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1362-15_0_3_load_92 | 83 | 0.00013556 | 3.3975e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1362-15_0_3_load_100 | 84 | 0.0010245 | 0.00025677 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1362-15_0_3_load_98 | 85 | 0.0019271 | 0.00048297 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1362-15_0_3_load_72 | 86 | 0.00010514 | 2.6351e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1362-15_0_3_load_75 | 87 | 0.0004324 | 0.00010837 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1362-15_0_3_load_67 | 89 | 0.00099144 | 0.00024848 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1362-15_0_3_load_68 | 90 | 0.00051866 | 0.00012999 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1362-15_0_3_load_71 | 91 | 0.00010517 | 2.6358e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1362-15_0_3_load_78 | 92 | 0.00027901 | 6.9926e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1362-15_0_3_load_79 | 93 | 0.00033323 | 8.3515e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1362-15_0_3_load_82 | 94 | 0.00024192 | 6.0631e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1362-15_0_3_load_83 | 95 | 0.0002683 | 6.7241e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1362-15_0_3_load_84 | 96 | 0.00034886 | 8.7433e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1362-15_0_3_load_86 | 98 | 0.0008399 | 0.0002105 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1362-15_0_3_load_101 | 100 | 0.00078932 | 0.00019782 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1362-15_0_3_load_91 | 101 | 0.00020647 | 5.1746e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1362-15_0_3_load_89 | 102 | 0.00032352 | 8.1082e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1362-15_0_3_load_90 | 103 | 0.00061511 | 0.00015416 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1362-15_0_3_load_94 | 104 | 0.00069046 | 0.00017305 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1362-15_0_3_load_95 | 105 | 0.0002118 | 5.3082e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1362-15_0_3_load_96 | 106 | 0.0048825 | 0.0012237 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1362-15_0_3_load_97 | 107 | 0.0026423 | 0.00066223 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 48 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1362-15_0_3_line_0 |  | 0 | 1 | 0.025796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1362-15_0_3_line_1 |  | 0 | 2 | 0.011994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1362-15_0_3_line_2 |  | 1 | 3 | 0.041709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1362-15_0_3_line_3 |  | 3 | 6 | 0.14924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1362-15_0_3_line_4 |  | 3 | 7 | 0.059767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1362-15_0_3_line_5 |  | 4 | 5 | 0.26331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1362-15_0_3_line_6 |  | 5 | 97 | 0.0097132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1362-15_0_3_line_7 |  | 7 | 8 | 0.27736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1362-15_0_3_line_8 |  | 8 | 47 | 0.019525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1362-15_0_3_line_9 |  | 9 | 10 | 0.017832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1362-15_0_3_line_10 |  | 9 | 11 | 0.28334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1362-15_0_3_line_11 |  | 10 | 12 | 0.072973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1362-15_0_3_line_12 |  | 11 | 13 | 0.62559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1362-15_0_3_line_13 |  | 12 | 14 | 0.26873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1362-15_0_3_line_14 |  | 14 | 15 | 0.16276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1362-15_0_3_line_15 |  | 14 | 16 | 0.058648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1362-15_0_3_line_16 |  | 15 | 17 | 0.36354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1362-15_0_3_line_17 |  | 15 | 18 | 0.10321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1362-15_0_3_line_18 |  | 17 | 22 | 0.36104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1362-15_0_3_line_19 |  | 17 | 23 | 0.030834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1362-15_0_3_line_20 |  | 19 | 20 | 0.059651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1362-15_0_3_line_21 |  | 19 | 21 | 0.051609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1362-15_0_3_line_22 |  | 21 | 35 | 0.13686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1362-15_0_3_line_23 |  | 22 | 86 | 0.13881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1362-15_0_3_line_24 |  | 23 | 87 | 0.020196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1362-15_0_3_line_25 |  | 24 | 25 | 0.14763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1362-15_0_3_line_26 |  | 24 | 26 | 0.0046044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1362-15_0_3_line_27 |  | 25 | 27 | 0.02982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_1362-15_0_3_line_28 |  | 26 | 28 | 0.0074506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1362-15_0_3_line_29 |  | 27 | 31 | 0.13383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1362-15_0_3_line_30 |  | 27 | 29 | 0.15808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_1362-15_0_3_line_31 |  | 28 | 32 | 0.093338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_1362-15_0_3_line_32 |  | 29 | 30 | 0.089203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1362-15_0_3_line_33 |  | 30 | 84 | 0.014013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_1362-15_0_3_line_34 |  | 31 | 33 | 0.40272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1362-15_0_3_line_35 |  | 32 | 34 | 0.08709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_1362-15_0_3_line_36 |  | 33 | 36 | 0.24845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1362-15_0_3_line_37 |  | 34 | 43 | 0.39658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1362-15_0_3_line_38 |  | 34 | 48 | 0.34865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_1362-15_0_3_line_39 |  | 34 | 45 | 0.061199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1362-15_0_3_line_40 |  | 35 | 55 | 0.10474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1362-15_0_3_line_41 |  | 36 | 44 | 0.063642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1362-15_0_3_line_42 |  | 37 | 38 | 0.0092623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1362-15_0_3_line_43 |  | 38 | 39 | 0.16626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1362-15_0_3_line_44 |  | 39 | 40 | 0.023346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1362-15_0_3_line_45 |  | 39 | 41 | 0.0076162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1362-15_0_3_line_46 |  | 40 | 42 | 0.13573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1362-15_0_3_line_47 |  | 41 | 43 | 0.025909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1362-15_0_3_line_48 |  | 42 | 49 | 0.0020281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1362-15_0_3_line_49 |  | 45 | 46 | 0.010217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1362-15_0_3_line_50 |  | 46 | 47 | 0.010817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1362-15_0_3_line_51 |  | 49 | 50 | 0.021847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1362-15_0_3_line_52 |  | 50 | 51 | 0.42837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1362-15_0_3_line_53 |  | 52 | 53 | 0.29134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_1362-15_0_3_line_54 |  | 52 | 54 | 0.042241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_1362-15_0_3_line_55 |  | 53 | 55 | 0.22378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1362-15_0_3_line_56 |  | 53 | 56 | 0.076494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1362-15_0_3_line_57 |  | 53 | 57 | 0.070536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1362-15_0_3_line_58 |  | 54 | 58 | 0.028698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_1362-15_0_3_line_59 |  | 56 | 59 | 0.10219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1362-15_0_3_line_60 |  | 56 | 60 | 0.20916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1362-15_0_3_line_61 |  | 57 | 61 | 0.056329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1362-15_0_3_line_62 |  | 58 | 62 | 0.16109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_1362-15_0_3_line_63 |  | 59 | 63 | 0.090391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1362-15_0_3_line_64 |  | 60 | 64 | 0.039994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1362-15_0_3_line_65 |  | 62 | 65 | 0.24789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_1362-15_0_3_line_66 |  | 62 | 66 | 0.031554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1362-15_0_3_line_67 |  | 63 | 92 | 0.085121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1362-15_0_3_line_68 |  | 64 | 91 | 0.013975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1362-15_0_3_line_69 |  | 65 | 70 | 0.3799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_1362-15_0_3_line_70 |  | 65 | 69 | 0.084179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1362-15_0_3_line_71 |  | 66 | 88 | 0.030518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1362-15_0_3_line_72 |  | 67 | 68 | 0.045286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1362-15_0_3_line_73 |  | 67 | 69 | 0.011244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1362-15_0_3_line_74 |  | 70 | 71 | 0.11575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_1362-15_0_3_line_75 |  | 70 | 72 | 0.32166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1362-15_0_3_line_76 |  | 71 | 76 | 0.049969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_1362-15_0_3_line_77 |  | 72 | 73 | 0.0045715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1362-15_0_3_line_78 |  | 73 | 74 | 0.034323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1362-15_0_3_line_79 |  | 74 | 75 | 0.13656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1362-15_0_3_line_80 |  | 75 | 77 | 0.075718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1362-15_0_3_line_81 |  | 76 | 78 | 0.16405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_1362-15_0_3_line_82 |  | 78 | 79 | 0.0054122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1362-15_0_3_line_83 |  | 78 | 80 | 0.13479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_1362-15_0_3_line_84 |  | 79 | 81 | 0.0074227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1362-15_0_3_line_85 |  | 80 | 82 | 0.064925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_1362-15_0_3_line_86 |  | 81 | 83 | 0.01846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1362-15_0_3_line_87 |  | 82 | 84 | 0.2187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_1362-15_0_3_line_88 |  | 82 | 85 | 0.043384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1362-15_0_3_line_89 |  | 83 | 103 | 0.19439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1362-15_0_3_line_90 |  | 85 | 107 | 0.016846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1362-15_0_3_line_91 |  | 86 | 91 | 0.0051667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1362-15_0_3_line_92 |  | 88 | 89 | 0.016623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1362-15_0_3_line_93 |  | 89 | 90 | 0.04639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1362-15_0_3_line_94 |  | 92 | 93 | 0.071758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1362-15_0_3_line_95 |  | 94 | 95 | 0.24223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1362-15_0_3_line_96 |  | 94 | 96 | 0.072205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1362-15_0_3_line_97 |  | 95 | 97 | 0.0068386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1362-15_0_3_line_98 |  | 96 | 98 | 0.010916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1362-15_0_3_line_99 |  | 97 | 99 | 0.20188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1362-15_0_3_line_100 |  | 98 | 100 | 0.14401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1362-15_0_3_line_101 |  | 99 | 101 | 0.011806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1362-15_0_3_line_102 |  | 101 | 102 | 0.0095628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1362-15_0_3_line_103 |  | 102 | 103 | 0.097442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1362-15_0_3_line_104 |  | 104 | 105 | 0.06128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1362-15_0_3_line_105 |  | 104 | 106 | 0.03498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1362-15_0_3_line_106 |  | 105 | 107 | 0.12653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1362-15_0_3_trafo_102 | 0.63 MVA 20/0.4 kV | 108 | 48 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26
0 | 2682978.9233 | 1210448.9451 | 2682988.8971 | 1210443.7816 | 2682994.1476 | 1210440.0744 | 2682996.5941 | 1210435.7723 | 2682996.4744 | 1210432.5862
1 | 2682978.9233 | 1210448.9451 | 2682975.1777 | 1210450.8843 | 2682970.6556 | 1210453.045 | 2682968.1883 | 1210454.2928
2 | 2682985.4618 | 1210392.4226 | 2682996.3889 | 1210430.3103 | 2682996.4744 | 1210432.5862
3 | 2682913.3421 | 1210380.6236 | 2682919.7801 | 1210382.2585 | 2682924.1053 | 1210384.42 | 2682928.4036 | 1210387.971 | 2682931.2839 | 1210392.9142 | 2682931.4912 | 1210398.2317 | 2682930.0228 | 1210403.259 | 2682915.2087 | 1210418.0294 | 2682912.3599 | 1210421.203 | 2682912.4285 | 1210426.1071 | 2682914.3578 | 1210428.9357 | 2682918.6829 | 1210431.0972 | 2682922.1837 | 1210430.2342 | 2682939.7676 | 1210415.2355 | 2682954.7564 | 1210408.1281 | 2682967.7696 | 1210400.9822 | 2682985.4618 | 1210392.4226
4 | 2682985.4618 | 1210392.4226 | 2682994.7329 | 1210389.2829 | 2683025.8263 | 1210381.199 | 2683042.2062 | 1210374.1001
5 | 2682879.1168 | 1210835.6098 | 2682827.5242 | 1210777.1339 | 2682700.0547 | 1210642.6058
6 | 2682885.5431 | 1210842.8934 | 2682879.1168 | 1210835.6098
7 | 2683281.4195 | 1210358.0844 | 2683247.7458 | 1210339.964 | 2683181.5077 | 1210305.9182 | 2683169.7346 | 1210299.8724 | 2683158.4384 | 1210298.325 | 2683148.4941 | 1210299.5762 | 2683140.2923 | 1210303.4199 | 2683117.6299 | 1210319.5258 | 2683091.9387 | 1210339.1697 | 2683052.6302 | 1210367.3186 | 2683042.2062 | 1210374.1001
8 | 2683281.4195 | 1210358.0844 | 2683298.6131 | 1210367.3366
9 | 2681770.5794 | 1210848.7744 | 2681776.2684 | 1210851.7825 | 2681780.1915 | 1210855.005 | 2681779.951 | 1210861.3198
10 | 2681709.2824 | 1210732.3764 | 2681707.7172 | 1210748.432 | 2681710.9669 | 1210769.1899 | 2681714.6179 | 1210786.7291 | 2681720.4461 | 1210794.0247 | 2681726.755 | 1210806.1746 | 2681724.5378 | 1210816.0061 | 2681722.5866 | 1210825.8413 | 2681712.124 | 1210848.9241 | 2681710.2594 | 1210857.4263 | 2681714.841 | 1210867.5067 | 2681713.7642 | 1210877.3094 | 2681701.9153 | 1210905.621 | 2681702.6908 | 1210911.1463 | 2681727.7203 | 1210888.7969 | 2681750.9301 | 1210865.5887 | 2681760.9661 | 1210852.5622 | 2681768.9719 | 1210847.9244 | 2681770.5794 | 1210848.7744
11 | 2681779.2153 | 1210933.9428 | 2681777.3962 | 1210928.5921 | 2681778.0926 | 1210906.6319 | 2681778.9562 | 1210887.4424 | 2681779.951 | 1210861.3198
12 | 2681709.2824 | 1210732.3764 | 2681424.417 | 1210175.4109
13 | 2681779.2153 | 1210933.9428 | 2681779.1758 | 1210936.8219 | 2681779.0868 | 1210938.8775 | 2681778.7653 | 1210943.4761 | 2681778.1955 | 1210955.654 | 2681776.7715 | 1210970.2662 | 2681772.5406 | 1210981.1819 | 2681771.6105 | 1210989.708 | 2681770.7194 | 1210995.3884 | 2681770.9626 | 1211007.5774 | 2681772.7371 | 1211026.703 | 2681775.3803 | 1211041.7823 | 2681778.8888 | 1211053.6159 | 2681788.5586 | 1211062.2874 | 2681797.8551 | 1211067.6961 | 2681808.0112 | 1211070.2703 | 2681820.7367 | 1211063.9407 | 2681845.0592 | 1211044.3616 | 2681881.9848 | 1211027.3905 | 2681888.5286 | 1211026.2685 | 2681896.6424 | 1211007.6678
14 | 2681891.9928 | 1211160.2808 | 2681887.9272 | 1211159.1576 | 2681885.2976 | 1211157.4982 | 2681882.4826 | 1211154.402 | 2681879.6917 | 1211150.1053 | 2681877.5367 | 1211143.7717 | 2681876.6162 | 1211136.6433 | 2681875.5072 | 1211128.3004 | 2681874.2155 | 1211118.3207 | 2681874.1553 | 1211107.7574 | 2681875.9074 | 1211084.2107 | 2681888.5286 | 1211026.2685 | 2681896.6424 | 1211007.6678
15 | 2681896.6424 | 1211007.6678 | 2681898.3806 | 1210996.7624 | 2681904.3928 | 1210978.4552 | 2681919.0591 | 1210954.2099
16 | 2682043.8266 | 1211349.3672 | 2682039.9064 | 1211340.9967 | 2682028.7739 | 1211328.7802 | 2682020.3829 | 1211321.6713 | 2682010.2192 | 1211328.5249 | 2682004.5443 | 1211330.5927 | 2681998.9025 | 1211330.2483 | 2681989.5732 | 1211323.9493 | 2681970.737 | 1211304.9226 | 2681955.8874 | 1211289.4419 | 2681945.5015 | 1211282.05 | 2681933.7079 | 1211279.2084 | 2681920.4918 | 1211281.4395 | 2681908.0372 | 1211287.4391 | 2681899.709 | 1211273.5379 | 2681890.5658 | 1211257.5465 | 2681884.2458 | 1211240.1818 | 2681887.2942 | 1211222.9569 | 2681894.6036 | 1211202.0437 | 2681908.5502 | 1211179.8318 | 2681920.826 | 1211166.4028 | 2681924.3367 | 1211158.1345 | 2681923.22 | 1211149.8026 | 2681918.6315 | 1211146.3485 | 2681913.3811 | 1211146.2764 | 2681903.4236 | 1211151.3763 | 2681891.9928 | 1211160.2808
17 | 2681891.9928 | 1211160.2808 | 2681870.007 | 1211177.4124 | 2681847.2101 | 1211194.9554 | 2681833.8225 | 1211202.4767 | 2681818.4289 | 1211221.0554 | 2681814.8777 | 1211227.1925
18 | 2682043.8266 | 1211349.3672 | 2682046.296 | 1211352.1585 | 2682094.8554 | 1211422.9391 | 2682108.522 | 1211416.6675 | 2682118.5366 | 1211414.5706 | 2682129.8523 | 1211414.0149 | 2682114.7715 | 1211421.4344 | 2682114.0602 | 1211428.9406 | 2682117.2037 | 1211437.4116 | 2682101.7589 | 1211454.1655 | 2682086.8197 | 1211476.152 | 2682070.602 | 1211496.62 | 2682094.0256 | 1211497.5539 | 2682102.9032 | 1211497.9986 | 2682116.5768 | 1211503.3458 | 2682136.603 | 1211499.3522 | 2682158.8024 | 1211500.8811 | 2682175.0796 | 1211503.1401 | 2682194.4028 | 1211502.1834 | 2682195.5138 | 1211502.6212
19 | 2682043.8266 | 1211349.3672 | 2682042.3748 | 1211357.1189 | 2682038.7281 | 1211367.5311 | 2682032.4032 | 1211377.6284
20 | 2682073.8594 | 1211000.4648 | 2682071.7026 | 1211002.5587 | 2682069.3252 | 1211004.1159 | 2682066.1307 | 1211004.2943 | 2682063.7678 | 1211004.7955 | 2682059.7613 | 1211008.7541 | 2682054.0616 | 1211014.8129 | 2682050.3967 | 1211016.0411 | 2682047.278 | 1211016.2317 | 2682045.2316 | 1211015.8255 | 2682043.0728 | 1211018.0639 | 2682041.9278 | 1211023.952 | 2682039.9208 | 1211031.7295 | 2682035.9553 | 1211038.7906
21 | 2682073.8594 | 1211000.4648 | 2682095.9056 | 1211011.6087 | 2682116.6334 | 1210994.454
22 | 2682197.3876 | 1211088.8448 | 2682194.0927 | 1211085.286 | 2682188.9426 | 1211080.134 | 2682141.823 | 1211033.2547 | 2682137.3861 | 1211029.8358 | 2682133.5584 | 1211026.8812 | 2682129.2201 | 1211024.0307 | 2682113.9789 | 1211016.5383 | 2682119.7484 | 1211008.179 | 2682120.8943 | 1210999.478 | 2682116.7313 | 1210994.3729 | 2682116.6334 | 1210994.454
23 | 2682195.5138 | 1211502.6212 | 2682198.2775 | 1211497.2891 | 2682202.1918 | 1211486.7696 | 2682206.7684 | 1211477.2709 | 2682214.7434 | 1211469.876 | 2682226.4511 | 1211464.5783 | 2682238.2041 | 1211456.5573 | 2682252.7038 | 1211447.1955 | 2682268.5456 | 1211440.2539 | 2682286.0735 | 1211435.0367 | 2682297.3765 | 1211434.848 | 2682306.0506 | 1211432.7315
24 | 2682027.8324 | 1211357.9973 | 2682030.1566 | 1211365.2673 | 2682032.4032 | 1211377.6284
25 | 2683540.9137 | 1210487.0888 | 2683555.0603 | 1210499.8076 | 2683558.1977 | 1210506.4336 | 2683558.0899 | 1210514.126 | 2683555.9242 | 1210518.4318 | 2683549.8297 | 1210522.6826 | 2683502.8381 | 1210549.042 | 2683495.1539 | 1210556.6394 | 2683492.8028 | 1210563.8779 | 2683494.2435 | 1210571.1806 | 2683497.8359 | 1210575.7116 | 2683505.2266 | 1210579.3063 | 2683512.8086 | 1210579.0011
26 | 2683537.4898 | 1210484.0103 | 2683540.9137 | 1210487.0888
27 | 2683512.8086 | 1210579.0011 | 2683512.8086 | 1210579.0011 | 2683520.1408 | 1210577.0024 | 2683540.4559 | 1210567.9993
28 | 2683537.4898 | 1210484.0103 | 2683531.9493 | 1210479.029
29 | 2683655.955 | 1210501.5184 | 2683627.7619 | 1210521.9627 | 2683590.5057 | 1210545.6561 | 2683580.6035 | 1210550.9764 | 2683555.039 | 1210561.5364 | 2683540.4559 | 1210567.9993
30 | 2683599.7901 | 1210714.5185 | 2683540.4559 | 1210567.9993
31 | 2683531.9493 | 1210479.029 | 2683490.0265 | 1210441.337 | 2683470.8915 | 1210427.4937 | 2683458.3062 | 1210423.0556
32 | 2683599.8392 | 1210803.7218 | 2683599.7901 | 1210714.5185
33 | 2683599.8392 | 1210803.7218 | 2683609.3598 | 1210805.5341 | 2683613.1255 | 1210807.6548
34 | 2684022.8077 | 1210401.0889 | 2684018.2984 | 1210397.4564 | 2684011.1446 | 1210397.5557 | 2683960.542 | 1210414.0209 | 2683924.2331 | 1210419.9473 | 2683896.1977 | 1210428.303 | 2683855.9623 | 1210442.6691 | 2683826.0656 | 1210459.093 | 2683813.1319 | 1210470.252 | 2683801.4361 | 1210483.1072 | 2683796.3334 | 1210486.5378 | 2683788.5831 | 1210488.5303 | 2683781.8583 | 1210487.3128 | 2683766.7766 | 1210481.4973 | 2683743.0568 | 1210470.5239 | 2683733.9849 | 1210467.0387 | 2683726.6701 | 1210467.781 | 2683701.9878 | 1210475.5509 | 2683680.6482 | 1210485.6138 | 2683663.9367 | 1210495.7305 | 2683655.955 | 1210501.5184
35 | 2683376.1738 | 1210394.0922 | 2683458.3062 | 1210423.0556
36 | 2684022.8077 | 1210401.0889 | 2684078.506 | 1210391.4338 | 2684089.1414 | 1210389.1488 | 2684090.115 | 1210377.7773 | 2684067.8305 | 1210345.8759 | 2683987.0362 | 1210271.7009 | 2683977.1031 | 1210252.7043
37 | 2683376.1738 | 1210394.0922 | 2683375.6137 | 1210314.0101 | 2683375.4302 | 1210307.0141 | 2683376.7194 | 1210295.2689 | 2683380.4728 | 1210287.7609 | 2683386.7255 | 1210282.5337 | 2683405.3626 | 1210274.9559 | 2683443.9957 | 1210263.7443 | 2683458.3485 | 1210261.4212 | 2683475.4739 | 1210261.9389 | 2683522.5146 | 1210271.8369 | 2683559.5185 | 1210276.558 | 2683580.7638 | 1210283.5712 | 2683587.4891 | 1210284.2214 | 2683599.5921 | 1210282.4342 | 2683614.7885 | 1210280.1234 | 2683627.1256 | 1210281.6973 | 2683640.0136 | 1210283.5569 | 2683647.6214 | 1210281.9847 | 2683652.7221 | 1210278.6985 | 2683654.7077 | 1210271.2407
38 | 2683283.6646 | 1210730.2414 | 2683376.1738 | 1210394.0922
39 | 2683376.1738 | 1210394.0922 | 2683317.7838 | 1210375.7652
40 | 2682197.3876 | 1211088.8448 | 2682212.2201 | 1211103.9145 | 2682227.5595 | 1211116.3784 | 2682245.2709 | 1211127.1295 | 2682284.7346 | 1211144.4734
41 | 2683946.3321 | 1210303.0709 | 2683956.4007 | 1210280.042 | 2683963.9402 | 1210258.5007 | 2683968.1902 | 1210253.5684 | 2683973.6397 | 1210251.9773 | 2683977.1031 | 1210252.7043
42 | 2683498.7047 | 1210189.8531 | 2683489.973 | 1210186.7629
43 | 2683657.7867 | 1210237.8985 | 2683547.0096 | 1210206.9487 | 2683498.7047 | 1210189.8531
44 | 2683657.7867 | 1210237.8985 | 2683655.4481 | 1210224.7127 | 2683653.414 | 1210214.9683
45 | 2683657.7867 | 1210237.8985 | 2683657.1961 | 1210245.4918
46 | 2683653.414 | 1210214.9683 | 2683629.7498 | 1210101.6057 | 2683628.076 | 1210093.5881 | 2683626.8307 | 1210082.6525 | 2683626.9906 | 1210081.9406
47 | 2683654.7077 | 1210271.2407 | 2683655.3941 | 1210268.6628 | 2683657.1961 | 1210245.4918
48 | 2683627.435 | 1210079.9617 | 2683626.9906 | 1210081.9406
49 | 2683308.1383 | 1210372.4623 | 2683309.3667 | 1210373.1233 | 2683317.7838 | 1210375.7652
50 | 2683308.1383 | 1210372.4623 | 2683298.6131 | 1210367.3366
51 | 2683632.2222 | 1210058.6457 | 2683627.435 | 1210079.9617
52 | 2683632.2222 | 1210058.6457 | 2683570.2897 | 1209634.7803
53 | 2682490.8651 | 1211230.0535 | 2682505.0595 | 1211236.2315 | 2682525.9133 | 1211254.8876 | 2682554.8707 | 1211271.1766 | 2682576.3365 | 1211275.7989 | 2682593.5018 | 1211277.0706 | 2682633.4036 | 1211280.1029 | 2682645.8619 | 1211277.1846 | 2682653.1851 | 1211271.916 | 2682669.6241 | 1211250.4742 | 2682674.6419 | 1211247.0415 | 2682683.3543 | 1211245.7169 | 2682690.5611 | 1211248.2963 | 2682719.2128 | 1211271.7976 | 2682729.2973 | 1211275.6511 | 2682740.0724 | 1211275.1891 | 2682745.4332 | 1211274.245
54 | 2682786.5253 | 1211264.5265 | 2682752.7721 | 1211272.9526 | 2682745.4332 | 1211274.245
55 | 2682490.8651 | 1211230.0535 | 2682450.0989 | 1211217.5041 | 2682382.5271 | 1211192.9325 | 2682371.4798 | 1211187.2318 | 2682326.1593 | 1211162.6793 | 2682284.7346 | 1211144.4734
56 | 2682417.2643 | 1211228.2241 | 2682429.3431 | 1211223.0653 | 2682436.9107 | 1211220.446 | 2682444.4312 | 1211221.2282 | 2682458.757 | 1211224.506 | 2682483.304 | 1211231.6611 | 2682490.8651 | 1211230.0535
57 | 2682490.8651 | 1211230.0535 | 2682491.5352 | 1211221.1681 | 2682479.4606 | 1211166.132 | 2682477.9594 | 1211161.0698
58 | 2682786.5253 | 1211264.5265 | 2682802.1596 | 1211260.5742 | 2682813.8049 | 1211255.8365
59 | 2682417.2643 | 1211228.2241 | 2682337.0635 | 1211262.4057 | 2682323.9593 | 1211269.7296
60 | 2682417.2643 | 1211228.2241 | 2682421.1176 | 1211248.5461 | 2682424.2444 | 1211269.7475 | 2682427.0934 | 1211286.8535 | 2682426.2586 | 1211297.7602 | 2682425.4776 | 1211304.2314 | 2682419.4765 | 1211317.7906 | 2682413.8615 | 1211327.6083 | 2682406.2043 | 1211336.7196 | 2682398.6085 | 1211341.3955 | 2682393.105 | 1211343.6988 | 2682384.1887 | 1211344.9432 | 2682366 | 1211348.4499 | 2682348.0705 | 1211357.4082 | 2682332.5354 | 1211367.4337 | 2682325.8948 | 1211377.2373 | 2682325.2413 | 1211378.4961
61 | 2682466.2296 | 1211106.2102 | 2682468.7503 | 1211130.0161 | 2682477.9594 | 1211161.0698
62 | 2682915.668 | 1211225.65 | 2682901.2558 | 1211219.8571 | 2682892.8603 | 1211213.1361 | 2682872.0591 | 1211190.7659 | 2682865.0975 | 1211185.3101 | 2682857.6551 | 1211184.3728 | 2682853.0864 | 1211185.5545 | 2682848.2411 | 1211191.8803 | 2682838.2618 | 1211224.752 | 2682833.3314 | 1211236.658 | 2682827.1988 | 1211246.4792 | 2682815.9015 | 1211254.9835 | 2682813.8049 | 1211255.8365
63 | 2682266.1594 | 1211338.4261 | 2682277.9753 | 1211327.4439 | 2682290.9145 | 1211307.8318 | 2682300.7031 | 1211292.9461 | 2682312.8709 | 1211279.1272 | 2682323.9593 | 1211269.7296 | 2682323.9593 | 1211269.7296
64 | 2682315.8947 | 1211417.0816 | 2682318.382 | 1211400.6822 | 2682321.6711 | 1211385.3732 | 2682325.2413 | 1211378.4961
65 | 2683130.581 | 1211336.3348 | 2683121.1148 | 1211335.5803 | 2683111.2071 | 1211333.7855 | 2683073.5449 | 1211318.4065 | 2683052.9422 | 1211311.3151 | 2683039.0986 | 1211309.4656 | 2683026.6947 | 1211308.4701 | 2683019.4996 | 1211305.0678 | 2683007.4645 | 1211292.3143 | 2683001.7332 | 1211287.4869 | 2682983.6369 | 1211279.3966 | 2682972.3274 | 1211271.8344 | 2682949.4945 | 1211248.5907 | 2682934.5499 | 1211236.8308 | 2682917.7236 | 1211226.4791 | 2682915.668 | 1211225.65
66 | 2682915.668 | 1211225.65 | 2682922.2603 | 1211210.6541 | 2682929.702 | 1211197.4317
67 | 2682266.1594 | 1211338.4261 | 2682261.3315 | 1211342.9134 | 2682255.1771 | 1211342.8285 | 2682247.718 | 1211337.6 | 2682229.451 | 1211321.9936 | 2682213.1696 | 1211311.1956 | 2682199.567 | 1211304.5261 | 2682196.9048 | 1211300.8314
68 | 2682315.8947 | 1211417.0816 | 2682315.7484 | 1211418.0461 | 2682312.1946 | 1211427.203 | 2682309.9145 | 1211429.4159
69 | 2683130.581 | 1211336.3348 | 2683152.7936 | 1211334.7767 | 2683172.911 | 1211331.9664 | 2683182.0643 | 1211329.0032 | 2683188.9623 | 1211323.7292 | 2683194.4656 | 1211314.9336 | 2683196.4441 | 1211307.1227 | 2683195.5442 | 1211222.922 | 2683198.352 | 1211214.5001 | 2683204.2158 | 1211209.8343 | 2683211.8921 | 1211208.7073 | 2683220.3229 | 1211212.3273 | 2683257.6848 | 1211249.784 | 2683267.1286 | 1211254.8747 | 2683277.0354 | 1211257.2812 | 2683291.7228 | 1211257.4864 | 2683314.3079 | 1211255.9451 | 2683323.0435 | 1211252.9763 | 2683326.8503 | 1211247.0367 | 2683327.3576 | 1211240.6507 | 2683328.3179 | 1211216.5262 | 2683331.7386 | 1211208.313 | 2683339.5129 | 1211200.1719 | 2683343.531 | 1211196.5256
70 | 2683130.581 | 1211336.3348 | 2683124.9944 | 1211344.5735 | 2683084.72 | 1211338.3196 | 2683077.5466 | 1211371.0093
71 | 2682942.4592 | 1211169.7749 | 2682935.4294 | 1211187.2552 | 2682929.702 | 1211197.4317
72 | 2683075.1364 | 1211381.9924 | 2683075.1364 | 1211381.9924 | 2683111.3704 | 1211400.031 | 2683115.961 | 1211401.4663
73 | 2683075.1364 | 1211381.9924 | 2683077.5466 | 1211371.0093
74 | 2683343.531 | 1211196.5256 | 2683334.7514 | 1211196.1138 | 2683315.1412 | 1211188.1459 | 2683305.6337 | 1211179.4519 | 2683292.2801 | 1211161.009 | 2683263.2545 | 1211120.1196
75 | 2683343.531 | 1211196.5256 | 2683360.6552 | 1211183.3451 | 2683369.3157 | 1211171.0804 | 2683374.4476 | 1211158.9775 | 2683376.4967 | 1211145.5974 | 2683377.8262 | 1211124.9803 | 2683378.6888 | 1211070.3568 | 2683380.8248 | 1211058.3677 | 2683384.5274 | 1211045.222 | 2683391.2526 | 1211037.6777 | 2683397.7339 | 1211033.4322 | 2683406.0145 | 1211033.1366 | 2683413.0075 | 1211036.3254 | 2683428.7221 | 1211052.2332 | 2683488.6176 | 1211106.5175 | 2683502.3124 | 1211118.4725 | 2683503.2879 | 1211118.8197 | 2683504.2255 | 1211119.1524
76 | 2683238.1568 | 1211077.5104 | 2683244.3878 | 1211087.3815 | 2683245.5657 | 1211090.6556 | 2683250.0253 | 1211103.2817 | 2683254.8279 | 1211109.8529 | 2683262.2436 | 1211118.6955 | 2683263.2545 | 1211120.1196
77 | 2683504.2255 | 1211119.1524 | 2683508.5339 | 1211120.6808
78 | 2683542.5566 | 1211124.3949 | 2683533.0938 | 1211123.2287 | 2683511.3796 | 1211121.6904 | 2683508.5339 | 1211120.6808
79 | 2683639.3256 | 1211193.6407 | 2683632.4947 | 1211193.5448 | 2683627.5659 | 1211190.5849 | 2683622.1316 | 1211179.7795 | 2683611.2381 | 1211144.7595 | 2683605.7777 | 1211135.8105 | 2683595.4952 | 1211130.9188 | 2683542.5566 | 1211124.3949
80 | 2683639.3256 | 1211193.6407 | 2683645.7964 | 1211189.6065 | 2683649.3752 | 1211185.3205 | 2683652.1982 | 1211175.8651 | 2683657.0592 | 1211153.8633 | 2683660.9103 | 1211130.1796 | 2683662.6322 | 1211124.3129
81 | 2683349.1427 | 1210966.8654 | 2683348.8861 | 1210972.1764 | 2683347.3687 | 1210979.0597 | 2683344.8875 | 1210984.7509 | 2683341.762 | 1210989.7772 | 2683338.9422 | 1210994.6855 | 2683336.519 | 1210997.32 | 2683333.0141 | 1210999.5837 | 2683326.8489 | 1211002.9553 | 2683319.4907 | 1211004.687 | 2683309.5173 | 1211007.0159 | 2683304.1813 | 1211009.7877 | 2683293.6531 | 1211019.1913 | 2683283.0796 | 1211031.8408 | 2683273.9629 | 1211042.4872 | 2683261.5733 | 1211053.4881 | 2683249.9819 | 1211062.8436 | 2683244.767 | 1211071.1095 | 2683239.6173 | 1211074.6956 | 2683238.1568 | 1211077.5104
82 | 2683349.1427 | 1210966.8654 | 2683343.941 | 1210965.3707
83 | 2683349.1427 | 1210966.8654 | 2683358.086 | 1210967.5574 | 2683396.7232 | 1210958.9806 | 2683438.6258 | 1210883.6011
84 | 2683343.941 | 1210965.3707 | 2683338.8934 | 1210963.9203 | 2683337.0428 | 1210962.7853
85 | 2683474.1996 | 1210837.3069 | 2683463.377 | 1210835.6656 | 2683452.7715 | 1210858.1541 | 2683438.6258 | 1210883.6011
86 | 2683337.0428 | 1210962.7853 | 2683321.3065 | 1210953.1336
87 | 2683474.1996 | 1210837.3069 | 2683475.4291 | 1210824.9383 | 2683481.4162 | 1210818.0175 | 2683496.3375 | 1210815.7137 | 2683533.3145 | 1210822.1132 | 2683557.346 | 1210830.2883 | 2683585.7665 | 1210845.7965 | 2683597.2708 | 1210846.5137 | 2683622.2748 | 1210846.0304 | 2683629.9333 | 1210840.2562 | 2683631.7183 | 1210833.2878 | 2683631.2581 | 1210825.9988 | 2683618.552 | 1210810.7107 | 2683613.1255 | 1210807.6548
88 | 2683474.1996 | 1210837.3069 | 2683486.0612 | 1210839.1074 | 2683504.6773 | 1210864.3774
89 | 2683321.3065 | 1210953.1336 | 2683313.7021 | 1210948.4695 | 2683285.0192 | 1210878.2789 | 2683206.1974 | 1210822.1872 | 2683193.3943 | 1210823.8081
90 | 2683514.669 | 1210877.9405 | 2683504.6773 | 1210864.3774
91 | 2682309.9145 | 1211429.4159 | 2682306.6487 | 1211432.5855 | 2682306.0506 | 1211432.7315
92 | 2682942.4592 | 1211169.7749 | 2682947.041 | 1211158.3645 | 2682949.4545 | 1211154.7735
93 | 2682992.4458 | 1211171.2265 | 2682953.5378 | 1211154.619 | 2682949.4545 | 1211154.7735
94 | 2682141.3009 | 1211260.3838 | 2682145.6594 | 1211267.2705 | 2682157.6244 | 1211269.8036 | 2682163.5091 | 1211272.3752 | 2682177.076 | 1211278.3326 | 2682187.9714 | 1211288.4336 | 2682196.9048 | 1211300.8314
95 | 2682637.7037 | 1210841.1461 | 2682644.574 | 1210838.7706 | 2682711.1361 | 1210831.1546 | 2682878.7199 | 1210842.4342
96 | 2682637.7037 | 1210841.1461 | 2682583.2047 | 1210859.9902 | 2682568.6856 | 1210860.7779
97 | 2682885.5431 | 1210842.8934 | 2682878.7199 | 1210842.4342
98 | 2682568.6856 | 1210860.7779 | 2682557.7854 | 1210861.3692
99 | 2682885.5431 | 1210842.8934 | 2682931.884 | 1210846.006 | 2683051.3411 | 1210853.8949 | 2683087.6205 | 1210855.2786
100 | 2682417.2868 | 1210852.6915 | 2682447.6675 | 1210867.3429 | 2682557.7854 | 1210861.3692
101 | 2683087.6205 | 1210855.2786 | 2683098.3522 | 1210850.3582
102 | 2683107.7569 | 1210852.0897 | 2683098.3522 | 1210850.3582
103 | 2683107.7569 | 1210852.0897 | 2683134.8763 | 1210857.0825 | 2683151.5171 | 1210855.1686 | 2683187.9244 | 1210824.5006 | 2683193.3943 | 1210823.8081
104 | 2683618.1117 | 1210992.0244 | 2683609.2052 | 1210997.0569 | 2683590.9916 | 1211002.7498 | 2683582.9492 | 1211003.9491 | 2683575.5171 | 1211001.7213 | 2683571.9869 | 1210994.9452 | 2683572.3641 | 1210986.517
105 | 2683618.1117 | 1210992.0244 | 2683648.5663 | 1210974.8163
106 | 2683572.3641 | 1210986.517 | 2683573.1044 | 1210969.9779 | 2683569.6618 | 1210955.8649 | 2683559.2802 | 1210938.4971 | 2683514.669 | 1210877.9405

## bus_geodata
| x | y | coords
0 | 2682978.9233 | 1210448.9451
1 | 2682996.4744 | 1210432.5862
2 | 2682968.1883 | 1210454.2928
3 | 2682985.4618 | 1210392.4226
4 | 2682700.0547 | 1210642.6058
5 | 2682879.1168 | 1210835.6098
6 | 2682913.3421 | 1210380.6236
7 | 2683042.2062 | 1210374.1001
8 | 2683281.4195 | 1210358.0844
9 | 2681770.5794 | 1210848.7744
10 | 2681779.951 | 1210861.3198
11 | 2681709.2824 | 1210732.3764
12 | 2681779.2153 | 1210933.9428
13 | 2681424.417 | 1210175.4109
14 | 2681896.6424 | 1211007.6678
15 | 2681891.9928 | 1211160.2808
16 | 2681919.0591 | 1210954.2099
17 | 2682043.8266 | 1211349.3672
18 | 2681814.8777 | 1211227.1925
19 | 2682073.8594 | 1211000.4648
20 | 2682035.9553 | 1211038.7906
21 | 2682116.6334 | 1210994.454
22 | 2682195.5138 | 1211502.6212
23 | 2682032.4032 | 1211377.6284
24 | 2683540.9137 | 1210487.0888
25 | 2683512.8086 | 1210579.0011
26 | 2683537.4898 | 1210484.0103
27 | 2683540.4559 | 1210567.9993
28 | 2683531.9493 | 1210479.029
29 | 2683599.7901 | 1210714.5185
30 | 2683599.8392 | 1210803.7218
31 | 2683655.955 | 1210501.5184
32 | 2683458.3062 | 1210423.0556
33 | 2684022.8077 | 1210401.0889
34 | 2683376.1738 | 1210394.0922
35 | 2682197.3876 | 1211088.8448
36 | 2683977.1031 | 1210252.7043
37 | 2683489.973 | 1210186.7629
38 | 2683498.7047 | 1210189.8531
39 | 2683657.7867 | 1210237.8985
40 | 2683653.414 | 1210214.9683
41 | 2683657.1961 | 1210245.4918
42 | 2683626.9906 | 1210081.9406
43 | 2683654.7077 | 1210271.2407
44 | 2683946.3321 | 1210303.0709
45 | 2683317.7838 | 1210375.7652
46 | 2683308.1383 | 1210372.4623
47 | 2683298.6131 | 1210367.3366
48 | 2683283.6646 | 1210730.2414
49 | 2683627.435 | 1210079.9617
50 | 2683632.2222 | 1210058.6457
51 | 2683570.2897 | 1209634.7803
52 | 2682745.4332 | 1211274.245
53 | 2682490.8651 | 1211230.0535
54 | 2682786.5253 | 1211264.5265
55 | 2682284.7346 | 1211144.4734
56 | 2682417.2643 | 1211228.2241
57 | 2682477.9594 | 1211161.0698
58 | 2682813.8049 | 1211255.8365
59 | 2682323.9593 | 1211269.7296
60 | 2682325.2413 | 1211378.4961
61 | 2682466.2296 | 1211106.2102
62 | 2682915.668 | 1211225.65
63 | 2682266.1594 | 1211338.4261
64 | 2682315.8947 | 1211417.0816
65 | 2683130.581 | 1211336.3348
66 | 2682929.702 | 1211197.4317
67 | 2683075.1364 | 1211381.9924
68 | 2683115.961 | 1211401.4663
69 | 2683077.5466 | 1211371.0093
70 | 2683343.531 | 1211196.5256
71 | 2683263.2545 | 1211120.1196
72 | 2683504.2255 | 1211119.1524
73 | 2683508.5339 | 1211120.6808
74 | 2683542.5566 | 1211124.3949
75 | 2683639.3256 | 1211193.6407
76 | 2683238.1568 | 1211077.5104
77 | 2683662.6322 | 1211124.3129
78 | 2683349.1427 | 1210966.8654
79 | 2683343.941 | 1210965.3707
80 | 2683438.6258 | 1210883.6011
81 | 2683337.0428 | 1210962.7853
82 | 2683474.1996 | 1210837.3069
83 | 2683321.3065 | 1210953.1336
84 | 2683613.1255 | 1210807.6548
85 | 2683504.6773 | 1210864.3774
86 | 2682306.0506 | 1211432.7315
87 | 2682027.8324 | 1211357.9973
88 | 2682942.4592 | 1211169.7749
89 | 2682949.4545 | 1211154.7735
90 | 2682992.4458 | 1211171.2265
91 | 2682309.9145 | 1211429.4159
92 | 2682196.9048 | 1211300.8314
93 | 2682141.3009 | 1211260.3838
94 | 2682637.7037 | 1210841.1461
95 | 2682878.7199 | 1210842.4342
96 | 2682568.6856 | 1210860.7779
97 | 2682885.5431 | 1210842.8934
98 | 2682557.7854 | 1210861.3692
99 | 2683087.6205 | 1210855.2786
100 | 2682417.2868 | 1210852.6915
101 | 2683098.3522 | 1210850.3582
102 | 2683107.7569 | 1210852.0897
103 | 2683193.3943 | 1210823.8081
104 | 2683618.1117 | 1210992.0244
105 | 2683572.3641 | 1210986.517
106 | 2683648.5663 | 1210974.8163
107 | 2683514.669 | 1210877.9405
108 | 2683283.6646 | 1210730.2414

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98865 | -0.21887 | 0.00083396 | 0.00020901
1 | 0.98873 | -0.2174 | 0.0057745 | 0.0014472
2 | 0.98863 | -0.21938 | 0.0023649 | 0.00059271
3 | 0.98907 | -0.21073 | 0 | 0
4 | 0.97984 | -0.39277 | 0.00032812 | 8.2235e-05
5 | 0.97992 | -0.39118 | 0.00087056 | 0.00021818
6 | 0.98897 | -0.21269 | 0.00073713 | 0.00018474
7 | 0.98961 | -0.20038 | 0.00059098 | 0.00014811
8 | 0.99222 | -0.1496 | 0.00024362 | 6.1057e-05
9 | 0.97444 | -0.50302 | 0.00018729 | 4.6938e-05
10 | 0.97445 | -0.50281 | 0.00027035 | 6.7755e-05
11 | 0.97433 | -0.50536 | 0 | 0
12 | 0.97451 | -0.50159 | 0 | 0
13 | 0.97408 | -0.51035 | 0.00042448 | 0.00010639
14 | 0.97473 | -0.49706 | 0 | 0
15 | 0.9749 | -0.49362 | 0 | 0
16 | 0.97472 | -0.49731 | 0.00022526 | 5.6454e-05
17 | 0.97538 | -0.48359 | 0 | 0
18 | 0.97486 | -0.49427 | 0.00034168 | 8.5634e-05
19 | 0.97723 | -0.44585 | 0 | 0
20 | 0.97723 | -0.44596 | 9.9539e-05 | 2.4947e-05
21 | 0.97724 | -0.44576 | 8.9939e-05 | 2.2541e-05
22 | 0.97608 | -0.46929 | 0 | 0
23 | 0.97536 | -0.48395 | 0.00021186 | 5.3096e-05
24 | 0.99061 | -0.18107 | 0.0016212 | 0.00040631
25 | 0.98865 | -0.2192 | 0.00079604 | 0.00019951
26 | 0.99067 | -0.17983 | 0.00035614 | 8.9256e-05
27 | 0.98826 | -0.22677 | 0.00032072 | 8.0381e-05
28 | 0.99077 | -0.17783 | 0.00032534 | 8.1538e-05
29 | 0.98642 | -0.26288 | 0.004954 | 0.0012416
30 | 0.98551 | -0.28067 | 0.0013665 | 0.00034247
31 | 0.98777 | -0.23651 | 0.00021273 | 5.3316e-05
32 | 0.99208 | -0.15253 | 0.00059179 | 0.00014832
33 | 0.98634 | -0.26427 | 0 | 0
34 | 0.99331 | -0.12867 | 0 | 0
35 | 0.97726 | -0.44527 | 0 | 0
36 | 0.98547 | -0.28139 | 0 | 0
37 | 0.99144 | -0.16504 | 0.00018024 | 4.5173e-05
38 | 0.99145 | -0.16501 | 0.00050017 | 0.00012536
39 | 0.99155 | -0.163 | 0 | 0
40 | 0.99148 | -0.16426 | 0.00075633 | 0.00018955
41 | 0.99158 | -0.16249 | 0.00044619 | 0.00011183
42 | 0.9912 | -0.16979 | 0.0003297 | 8.2631e-05
43 | 0.99167 | -0.16057 | 0.00035001 | 8.7721e-05
44 | 0.98524 | -0.28577 | 0.0038362 | 0.00096144
45 | 0.99263 | -0.14173 | 0.00036929 | 9.2552e-05
46 | 0.99252 | -0.14385 | 0.00072452 | 0.00018158
47 | 0.99241 | -0.14595 | 0.00040891 | 0.00010248
48 | 1 | 0 | -0.065119 | -0.016044
49 | 0.9912 | -0.16986 | 0.00029288 | 7.3401e-05
50 | 0.99117 | -0.1705 | 0.0010483 | 0.00026272
51 | 0.99093 | -0.17518 | 0.00060744 | 0.00015224
52 | 0.9781 | -0.42816 | 0.00034073 | 8.5394e-05
53 | 0.97735 | -0.44344 | 0 | 0
54 | 0.97818 | -0.4266 | 0 | 0
55 | 0.97728 | -0.44489 | 0.00015063 | 3.7753e-05
56 | 0.97705 | -0.44944 | 0 | 0
57 | 0.97728 | -0.44484 | 0.00027637 | 6.9265e-05
58 | 0.97823 | -0.42554 | 0.00014536 | 3.643e-05
59 | 0.97693 | -0.45175 | 0.00039748 | 9.9618e-05
60 | 0.97648 | -0.46107 | 0.00047378 | 0.00011874
61 | 0.97723 | -0.44567 | 0.00080688 | 0.00020222
62 | 0.97854 | -0.41941 | 0 | 0
63 | 0.97686 | -0.45314 | 0.00022299 | 5.5887e-05
64 | 0.97639 | -0.46295 | 0.00018305 | 4.5876e-05
65 | 0.9793 | -0.40411 | 0 | 0
66 | 0.97842 | -0.42165 | 0.0023867 | 0.00059816
67 | 0.97917 | -0.40676 | 0.00034763 | 8.7124e-05
68 | 0.97914 | -0.40736 | 0.0007309 | 0.00018318
69 | 0.97918 | -0.40654 | 0.00050321 | 0.00012612
70 | 0.98066 | -0.377 | 0 | 0
71 | 0.98115 | -0.36716 | 0.00018506 | 4.6382e-05
72 | 0.97999 | -0.3901 | 0.00026704 | 6.6926e-05
73 | 0.97998 | -0.39027 | 0.00077457 | 0.00019413
74 | 0.97995 | -0.39102 | 0.00085763 | 0.00021494
75 | 0.9799 | -0.39186 | 0 | 0
76 | 0.98136 | -0.36286 | 0.00038976 | 9.7682e-05
77 | 0.97988 | -0.39232 | 0.00033449 | 8.3832e-05
78 | 0.98209 | -0.34835 | 0 | 0
79 | 0.98206 | -0.34889 | 0.00025958 | 6.5056e-05
80 | 0.98291 | -0.33197 | 0.00038115 | 9.5524e-05
81 | 0.98203 | -0.34959 | 0.00023486 | 5.8861e-05
82 | 0.98332 | -0.32394 | 0 | 0
83 | 0.98194 | -0.35126 | 0.00013556 | 3.3975e-05
84 | 0.98538 | -0.28335 | 0.0010245 | 0.00025677
85 | 0.9829 | -0.33205 | 0.0019271 | 0.00048297
86 | 0.97635 | -0.46378 | 0.00010514 | 2.6351e-05
87 | 0.97535 | -0.48411 | 0.0004324 | 0.00010837
88 | 0.97838 | -0.42249 | 0 | 0
89 | 0.97836 | -0.42295 | 0.00099144 | 0.00024848
90 | 0.97833 | -0.42339 | 0.00051866 | 0.00012999
91 | 0.97636 | -0.46356 | 0.00010517 | 2.6358e-05
92 | 0.97682 | -0.4541 | 0.00027901 | 6.9926e-05
93 | 0.97679 | -0.45454 | 0.00033323 | 8.3515e-05
94 | 0.97942 | -0.4011 | 0.00024192 | 6.0631e-05
95 | 0.97992 | -0.39128 | 0.0002683 | 6.7241e-05
96 | 0.97929 | -0.4037 | 0.00034886 | 8.7433e-05
97 | 0.97993 | -0.39097 | 0 | 0
98 | 0.97927 | -0.40402 | 0.0008399 | 0.0002105
99 | 0.98062 | -0.37737 | 0 | 0
100 | 0.97917 | -0.4061 | 0.00078932 | 0.00019782
101 | 0.98066 | -0.37657 | 0.00020647 | 5.1746e-05
102 | 0.9807 | -0.37589 | 0.00032352 | 8.1082e-05
103 | 0.98107 | -0.36839 | 0.00061511 | 0.00015416
104 | 0.98178 | -0.35402 | 0.00069046 | 0.00017305
105 | 0.9821 | -0.34784 | 0.0002118 | 5.3082e-05
106 | 0.98162 | -0.35711 | 0.0048825 | 0.0012237
107 | 0.98277 | -0.33461 | 0.0026423 | 0.00066223
108 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.003199 | -0.0008016 | 0.0031992 | 0.00080142 | 2.2424e-07 | -1.873e-07 | 0.0048147 | 0.0048146 | 0.0048147 | 0.98865 | -0.21887 | 0.98873 | -0.2174 | 1.3227
1 | 0.002365 | 0.00059259 | -0.0023649 | -0.00059271 | 5.699e-08 | -1.1733e-07 | 0.0035595 | 0.0035596 | 0.0035596 | 0.98865 | -0.21887 | 0.98863 | -0.21938 | 0.9779
2 | -0.0089736 | -0.0022486 | 0.0089765 | 0.0022499 | 2.8526e-06 | 1.2906e-06 | 0.013505 | 0.013505 | 0.013505 | 0.98873 | -0.2174 | 0.98907 | -0.21073 | 3.7102
3 | 0.0007372 | 0.00018287 | -0.00073713 | -0.00018474 | 6.8799e-08 | -1.8711e-06 | 0.0011084 | 0.0011091 | 0.0011091 | 0.98907 | -0.21073 | 0.98897 | -0.21269 | 0.30469
4 | -0.0097137 | -0.0024328 | 0.0097185 | 0.0024351 | 4.7861e-06 | 2.2956e-06 | 0.014613 | 0.014613 | 0.014613 | 0.98907 | -0.21073 | 0.98961 | -0.20038 | 4.0146
5 | -0.00032812 | -8.2235e-05 | 0.00032815 | 7.8934e-05 | 2.446e-08 | -3.3012e-06 | 0.0004983 | 0.00049713 | 0.0004983 | 0.97984 | -0.39277 | 0.97992 | -0.39118 | 0.13689
6 | -0.0011987 | -0.00029712 | 0.0011987 | 0.000297 | 1.2053e-08 | -1.1465e-07 | 0.0018191 | 0.001819 | 0.0018191 | 0.97992 | -0.39118 | 0.97993 | -0.39097 | 0.49974
7 | -0.010309 | -0.0025832 | 0.010334 | 0.0025956 | 2.4991e-05 | 1.2422e-05 | 0.015502 | 0.0155 | 0.015502 | 0.98961 | -0.20038 | 0.99222 | -0.1496 | 4.2587
8 | -0.010578 | -0.0026567 | 0.01058 | 0.0026576 | 1.843e-06 | 9.2731e-07 | 0.015866 | 0.015866 | 0.015866 | 0.99222 | -0.1496 | 0.99241 | -0.14595 | 4.3587
9 | -0.00061191 | -0.0001421 | 0.00061192 | 0.00014188 | 5.7893e-09 | -2.1843e-07 | 0.0009305 | 0.00093043 | 0.0009305 | 0.97444 | -0.50302 | 0.97445 | -0.50281 | 0.25563
10 | 0.00042463 | 9.5158e-05 | -0.00042458 | -9.8659e-05 | 4.4223e-08 | -3.5009e-06 | 0.00064457 | 0.00064573 | 0.00064573 | 0.97444 | -0.50302 | 0.97433 | -0.50536 | 0.1774
11 | -0.00088226 | -0.00020963 | 0.00088231 | 0.00020876 | 4.9361e-08 | -8.7753e-07 | 0.0013432 | 0.0013429 | 0.0013432 | 0.97445 | -0.50281 | 0.97451 | -0.50159 | 0.36901
12 | 0.00042458 | 9.8659e-05 | -0.00042448 | -0.00010639 | 9.8223e-08 | -7.7265e-06 | 0.00064573 | 0.00064844 | 0.00064844 | 0.97433 | -0.50536 | 0.97408 | -0.51035 | 0.17814
13 | -0.00088231 | -0.00020876 | 0.0008825 | 0.00020552 | 1.8158e-07 | -3.2327e-06 | 0.0013429 | 0.0013418 | 0.0013429 | 0.97451 | -0.50159 | 0.97473 | -0.49706 | 0.36893
14 | -0.0011078 | -0.00026125 | 0.0011079 | 0.00025933 | 1.733e-07 | -1.9182e-06 | 0.0016854 | 0.0016847 | 0.0016854 | 0.97473 | -0.49706 | 0.9749 | -0.49362 | 0.46301
15 | 0.00022526 | 5.5725e-05 | -0.00022526 | -5.6454e-05 | 2.5988e-09 | -7.2935e-07 | 0.00034362 | 0.00034388 | 0.00034388 | 0.97473 | -0.49706 | 0.97472 | -0.49731 | 0.094472
16 | -0.0014496 | -0.00034368 | 0.0014503 | 0.00033957 | 6.628e-07 | -4.111e-06 | 0.0022057 | 0.0022042 | 0.0022057 | 0.9749 | -0.49362 | 0.97538 | -0.48359 | 0.60597
17 | 0.00034169 | 8.4354e-05 | -0.00034168 | -8.5634e-05 | 1.0518e-08 | -1.2802e-06 | 0.00052108 | 0.00052154 | 0.00052154 | 0.9749 | -0.49362 | 0.97486 | -0.49427 | 0.14328
18 | -0.0020946 | -0.00050041 | 0.0020959 | 0.00049678 | 1.3743e-06 | -3.63e-06 | 0.0031868 | 0.0031852 | 0.0031868 | 0.97538 | -0.48359 | 0.97608 | -0.46929 | 0.87549
19 | 0.00064428 | 0.00016084 | -0.00064426 | -0.00016122 | 1.1167e-08 | -3.7769e-07 | 0.00098266 | 0.0009828 | 0.0009828 | 0.97538 | -0.48359 | 0.97536 | -0.48395 | 0.27
20 | 9.9539e-05 | 2.42e-05 | -9.9539e-05 | -2.4947e-05 | 5.1297e-10 | -7.4702e-07 | 0.0001513 | 0.00015157 | 0.00015157 | 0.97723 | -0.44585 | 0.97723 | -0.44596 | 0.041639
21 | -9.9539e-05 | -2.42e-05 | 9.954e-05 | 2.3553e-05 | 4.4239e-10 | -6.4631e-07 | 0.0001513 | 0.00015108 | 0.0001513 | 0.97723 | -0.44585 | 0.97724 | -0.44576 | 0.041567
22 | -0.00018948 | -4.6094e-05 | 0.00018948 | 4.4382e-05 | 4.2488e-09 | -1.712e-06 | 0.00028802 | 0.00028743 | 0.00028802 | 0.97724 | -0.44576 | 0.97726 | -0.44527 | 0.079127
23 | -0.0020959 | -0.00049678 | 0.0020965 | 0.00049538 | 5.2801e-07 | -1.3975e-06 | 0.0031852 | 0.0031846 | 0.0031852 | 0.97608 | -0.46929 | 0.97635 | -0.46378 | 0.87506
24 | 0.00043241 | 0.00010812 | -0.0004324 | -0.00010837 | 3.2954e-09 | -2.4995e-07 | 0.00065959 | 0.00065968 | 0.00065968 | 0.97536 | -0.48395 | 0.97535 | -0.48411 | 0.18123
25 | 0.043459 | 0.010857 | -0.04338 | -0.010813 | 7.8614e-05 | 4.4622e-05 | 0.065269 | 0.065271 | 0.065271 | 0.99061 | -0.18107 | 0.98865 | -0.2192 | 5.9772
26 | -0.04508 | -0.011264 | 0.045083 | 0.011265 | 2.6382e-06 | 1.5106e-06 | 0.067704 | 0.067704 | 0.067704 | 0.99061 | -0.18107 | 0.99067 | -0.17983 | 6.2
27 | 0.042584 | 0.010613 | -0.042569 | -0.010605 | 1.5303e-05 | 8.647e-06 | 0.064072 | 0.064073 | 0.064073 | 0.98865 | -0.2192 | 0.98826 | -0.22677 | 5.8675
28 | -0.045439 | -0.011354 | 0.045443 | 0.011357 | 4.3367e-06 | 2.4877e-06 | 0.068239 | 0.068239 | 0.068239 | 0.99067 | -0.17983 | 0.99077 | -0.17783 | 6.249
29 | 0.0040598 | 0.0010109 | -0.0040579 | -0.0010114 | 1.874e-06 | -5.1454e-07 | 0.0061105 | 0.0061111 | 0.0061111 | 0.98826 | -0.22677 | 0.98777 | -0.23651 | 1.6789
30 | 0.038188 | 0.0095133 | -0.038123 | -0.0094776 | 6.5286e-05 | 3.5718e-05 | 0.05748 | 0.057482 | 0.057482 | 0.98826 | -0.22677 | 0.98642 | -0.26288 | 5.2639
31 | -0.045769 | -0.011438 | 0.045824 | 0.01147 | 5.5108e-05 | 3.1659e-05 | 0.068727 | 0.068726 | 0.068727 | 0.99077 | -0.17783 | 0.99208 | -0.15253 | 6.2937
32 | 0.033169 | 0.008236 | -0.033141 | -0.0082216 | 2.7886e-05 | 1.4434e-05 | 0.050009 | 0.05001 | 0.05001 | 0.98642 | -0.26288 | 0.98551 | -0.28067 | 4.5797
33 | 0.031775 | 0.0078791 | -0.031771 | -0.0078771 | 4.0269e-06 | 2.0416e-06 | 0.047947 | 0.047947 | 0.047947 | 0.98551 | -0.28067 | 0.98538 | -0.28335 | 4.3907
34 | 0.0038452 | 0.00095807 | -0.0038401 | -0.00095998 | 5.0654e-06 | -1.9056e-06 | 0.0057906 | 0.0057924 | 0.0057924 | 0.98777 | -0.23651 | 0.98634 | -0.26427 | 1.5913
35 | -0.046416 | -0.011618 | 0.046468 | 0.011649 | 5.2754e-05 | 3.0385e-05 | 0.069614 | 0.069612 | 0.069614 | 0.99208 | -0.15253 | 0.99331 | -0.12867 | 6.3749
36 | 0.0038401 | 0.00095998 | -0.003837 | -0.00096115 | 3.1266e-06 | -1.1672e-06 | 0.0057924 | 0.0057935 | 0.0057935 | 0.98634 | -0.26427 | 0.98547 | -0.28139 | 1.5916
37 | 0.0045195 | 0.0011202 | -0.0045127 | -0.001121 | 6.8101e-06 | -7.6656e-07 | 0.0067661 | 0.0067679 | 0.0067679 | 0.99331 | -0.12867 | 0.99167 | -0.16057 | 1.8593
38 | -0.06308 | -0.015808 | 0.063469 | 0.016044 | 0.00038914 | 0.00023542 | 0.094497 | 0.094492 | 0.094497 | 0.99331 | -0.12867 | 1 | 0 | 8.6535
39 | 0.012092 | 0.0030394 | -0.012085 | -0.0030354 | 7.5337e-06 | 4.0299e-06 | 0.018118 | 0.018118 | 0.018118 | 0.99331 | -0.12867 | 0.99263 | -0.14173 | 4.9776
40 | -0.00018948 | -4.4382e-05 | 0.00018949 | 4.3072e-05 | 3.2399e-09 | -1.3102e-06 | 0.00028743 | 0.000287 | 0.00028743 | 0.97726 | -0.44527 | 0.97728 | -0.44489 | 0.078965
41 | 0.003837 | 0.00096115 | -0.0038362 | -0.00096144 | 8.011e-07 | -2.9796e-07 | 0.0057935 | 0.0057938 | 0.0057938 | 0.98547 | -0.28139 | 0.98524 | -0.28577 | 1.5917
42 | -0.00018024 | -4.5173e-05 | 0.00018024 | 4.5054e-05 | 2.5412e-10 | -1.1928e-07 | 0.00027052 | 0.00027048 | 0.00027052 | 0.99144 | -0.16504 | 0.99145 | -0.16501 | 0.074318
43 | -0.00068042 | -0.00017041 | 0.00068048 | 0.00016831 | 6.4966e-08 | -2.1027e-06 | 0.0010212 | 0.0010204 | 0.0010212 | 0.99145 | -0.16501 | 0.99155 | -0.163 | 0.28054
44 | 0.0030356 | 0.00075328 | -0.0030354 | -0.00075347 | 1.8148e-07 | -1.8496e-07 | 0.0045528 | 0.0045529 | 0.0045529 | 0.99155 | -0.163 | 0.99148 | -0.16426 | 1.2508
45 | -0.0037161 | -0.00092159 | 0.0037161 | 0.00092155 | 8.8713e-08 | -4.1464e-08 | 0.0055732 | 0.0055732 | 0.0055732 | 0.99155 | -0.163 | 0.99158 | -0.16249 | 1.5311
46 | 0.0022791 | 0.00056391 | -0.0022785 | -0.00056528 | 5.947e-07 | -1.3694e-06 | 0.0034178 | 0.0034185 | 0.0034185 | 0.99148 | -0.16426 | 0.9912 | -0.16979 | 0.93914
47 | -0.0041623 | -0.0010334 | 0.0041627 | 0.0010333 | 3.7864e-07 | -9.1903e-08 | 0.0062428 | 0.0062427 | 0.0062428 | 0.99158 | -0.16249 | 0.99167 | -0.16057 | 1.7151
48 | 0.0019488 | 0.00048265 | -0.0019488 | -0.00048267 | 6.5004e-09 | -2.1981e-08 | 0.0029235 | 0.0029235 | 0.0029235 | 0.9912 | -0.16979 | 0.9912 | -0.16986 | 0.80316
49 | 0.011716 | 0.0029429 | -0.011714 | -0.0029422 | 1.1821e-06 | 6.2447e-07 | 0.017565 | 0.017565 | 0.017565 | 0.99263 | -0.14173 | 0.99252 | -0.14385 | 4.8255
50 | 0.01099 | 0.0027607 | -0.010989 | -0.0027601 | 1.1015e-06 | 5.6517e-07 | 0.016479 | 0.016479 | 0.016479 | 0.99252 | -0.14385 | 0.99241 | -0.14595 | 4.5271
51 | 0.0016559 | 0.00040927 | -0.0016558 | -0.00040952 | 5.0546e-08 | -2.4923e-07 | 0.0024838 | 0.0024839 | 0.0024839 | 0.9912 | -0.16986 | 0.99117 | -0.1705 | 0.6824
52 | 0.00060757 | 0.0001468 | -0.00060744 | -0.00015224 | 1.3337e-07 | -5.4343e-06 | 0.00091023 | 0.00091215 | 0.00091215 | 0.99117 | -0.1705 | 0.99093 | -0.17518 | 0.25059
53 | 0.0056271 | 0.0013583 | -0.0056231 | -0.0013631 | 3.9873e-06 | -4.7557e-06 | 0.0085423 | 0.0085448 | 0.0085448 | 0.9781 | -0.42816 | 0.97735 | -0.44344 | 1.1737
54 | -0.0059678 | -0.0014437 | 0.0059682 | 0.0014424 | 4.3345e-07 | -1.3132e-06 | 0.0090606 | 0.0090601 | 0.0090606 | 0.9781 | -0.42816 | 0.97818 | -0.4266 | 0.82973
55 | 0.00034014 | 7.8035e-05 | -0.00034012 | -8.0825e-05 | 2.233e-08 | -2.7898e-06 | 0.00051538 | 0.00051633 | 0.00051633 | 0.97735 | -0.44344 | 0.97728 | -0.44489 | 0.14185
56 | 0.0041996 | 0.0010151 | -0.0041984 | -0.0010153 | 1.1679e-06 | -2.1084e-07 | 0.0063807 | 0.006381 | 0.006381 | 0.97735 | -0.44344 | 0.97705 | -0.44944 | 1.753
57 | 0.0010834 | 0.00026997 | -0.0010833 | -0.0002708 | 7.1927e-08 | -8.3783e-07 | 0.0016489 | 0.0016492 | 0.0016492 | 0.97735 | -0.44344 | 0.97728 | -0.44484 | 0.45307
58 | -0.0059682 | -0.0014424 | 0.0059685 | 0.0014415 | 2.9445e-07 | -8.9236e-07 | 0.0090601 | 0.0090597 | 0.0090601 | 0.97818 | -0.4266 | 0.97823 | -0.42554 | 0.82968
59 | 0.0012329 | 0.00030471 | -0.0012328 | -0.00030591 | 1.3493e-07 | -1.1934e-06 | 0.0018762 | 0.0018766 | 0.0018766 | 0.97705 | -0.44944 | 0.97693 | -0.45175 | 0.51556
60 | 0.0029655 | 0.00071056 | -0.0029639 | -0.00071216 | 1.592e-06 | -1.5991e-06 | 0.0045049 | 0.0045058 | 0.0045058 | 0.97705 | -0.44944 | 0.97648 | -0.46107 | 1.2378
61 | 0.00080691 | 0.00020154 | -0.00080688 | -0.00020222 | 3.188e-08 | -6.8537e-07 | 0.0012284 | 0.0012286 | 0.0012286 | 0.97728 | -0.44484 | 0.97723 | -0.44567 | 0.33753
62 | -0.0061139 | -0.0014779 | 0.0061156 | 0.001473 | 1.734e-06 | -4.9593e-06 | 0.0092808 | 0.0092787 | 0.0092808 | 0.97823 | -0.42554 | 0.97854 | -0.41941 | 0.84989
63 | 0.00083532 | 0.00020629 | -0.00083526 | -0.00020739 | 5.4794e-08 | -1.0966e-06 | 0.0012712 | 0.0012716 | 0.0012716 | 0.97693 | -0.45175 | 0.97686 | -0.45314 | 0.34935
64 | 0.0024901 | 0.00059342 | -0.0024899 | -0.00059379 | 2.1474e-07 | -3.6282e-07 | 0.0037838 | 0.003784 | 0.003784 | 0.97648 | -0.46107 | 0.97639 | -0.46295 | 1.0396
65 | -0.010013 | -0.0024484 | 0.01002 | 0.0024436 | 7.1617e-06 | -4.7658e-06 | 0.015205 | 0.015201 | 0.015205 | 0.97854 | -0.41941 | 0.9793 | -0.40411 | 1.3924
66 | 0.0038973 | 0.00097539 | -0.0038969 | -0.00097552 | 4.1554e-07 | -1.3039e-07 | 0.005926 | 0.0059261 | 0.0059261 | 0.97854 | -0.41941 | 0.97842 | -0.42165 | 1.6281
67 | 0.00061227 | 0.0001515 | -0.00061224 | -0.00015255 | 2.7735e-08 | -1.0479e-06 | 0.00093195 | 0.00093233 | 0.00093233 | 0.97686 | -0.45314 | 0.97682 | -0.4541 | 0.25613
68 | 0.0023069 | 0.00054791 | -0.0023068 | -0.00054804 | 6.4385e-08 | -1.3358e-07 | 0.0035051 | 0.0035051 | 0.0035051 | 0.97639 | -0.46295 | 0.97636 | -0.46356 | 0.96294
69 | -0.011602 | -0.0028384 | 0.011617 | 0.0028334 | 1.4713e-05 | -4.9431e-06 | 0.017604 | 0.017599 | 0.017604 | 0.9793 | -0.40411 | 0.98066 | -0.377 | 1.6121
70 | 0.0015819 | 0.00039479 | -0.0015818 | -0.00039573 | 1.8233e-07 | -9.423e-07 | 0.0024031 | 0.0024035 | 0.0024035 | 0.9793 | -0.40411 | 0.97918 | -0.40654 | 0.6603
71 | 0.0015102 | 0.00037736 | -0.0015101 | -0.0003777 | 6.0353e-08 | -3.4465e-07 | 0.0022964 | 0.0022965 | 0.0022965 | 0.97842 | -0.42165 | 0.97838 | -0.42249 | 0.6309
72 | 0.00073092 | 0.00018262 | -0.0007309 | -0.00018318 | 2.0949e-08 | -5.5619e-07 | 0.0011106 | 0.0011108 | 0.0011108 | 0.97917 | -0.40676 | 0.97914 | -0.40736 | 0.30516
73 | -0.0010785 | -0.00026975 | 0.0010786 | 0.00026961 | 1.1325e-08 | -1.3419e-07 | 0.0016388 | 0.0016388 | 0.0016388 | 0.97917 | -0.40676 | 0.97918 | -0.40654 | 0.45023
74 | -0.013852 | -0.003387 | 0.013858 | 0.0033867 | 6.3735e-06 | -3.0441e-07 | 0.020989 | 0.020987 | 0.020989 | 0.98066 | -0.377 | 0.98115 | -0.36716 | 1.922
75 | 0.0022352 | 0.00055354 | -0.0022338 | -0.00055671 | 1.3862e-06 | -3.1684e-06 | 0.0033893 | 0.0033907 | 0.0033907 | 0.98066 | -0.377 | 0.97999 | -0.3901 | 0.93151
76 | -0.014043 | -0.0034331 | 0.014046 | 0.003433 | 2.8252e-06 | -8.5549e-08 | 0.021268 | 0.021267 | 0.021268 | 0.98115 | -0.36716 | 0.98136 | -0.36286 | 1.9476
77 | 0.0019668 | 0.00048979 | -0.0019668 | -0.00048983 | 1.5277e-08 | -4.782e-08 | 0.0029852 | 0.0029852 | 0.0029852 | 0.97999 | -0.3901 | 0.97998 | -0.39027 | 0.82012
78 | 0.0011922 | 0.00029571 | -0.0011921 | -0.00029611 | 4.213e-08 | -4.0546e-07 | 0.0018091 | 0.0018093 | 0.0018093 | 0.97998 | -0.39027 | 0.97995 | -0.39102 | 0.49706
79 | 0.00033451 | 8.1171e-05 | -0.0003345 | -8.2883e-05 | 1.3179e-08 | -1.7119e-06 | 0.00050701 | 0.00050761 | 0.00050761 | 0.97995 | -0.39102 | 0.9799 | -0.39186 | 0.13945
80 | 0.0003345 | 8.2883e-05 | -0.00033449 | -8.3832e-05 | 7.3212e-09 | -9.4914e-07 | 0.00050761 | 0.00050795 | 0.00050795 | 0.9799 | -0.39186 | 0.97988 | -0.39232 | 0.13955
81 | -0.014436 | -0.0035307 | 0.014446 | 0.0035307 | 9.7964e-06 | 4.6834e-08 | 0.021858 | 0.021856 | 0.021858 | 0.98136 | -0.36286 | 0.98209 | -0.34835 | 2.0017
82 | 0.0054723 | 0.0013591 | -0.0054721 | -0.0013591 | 1.3938e-07 | 2.0721e-08 | 0.008287 | 0.008287 | 0.008287 | 0.98209 | -0.34835 | 0.98206 | -0.34889 | 2.2766
83 | -0.019918 | -0.0048898 | 0.019933 | 0.0048945 | 1.5308e-05 | 4.6759e-06 | 0.030143 | 0.030141 | 0.030143 | 0.98209 | -0.34835 | 0.98291 | -0.33197 | 2.7603
84 | 0.0052126 | 0.0012941 | -0.0052124 | -0.001294 | 1.7344e-07 | 1.7087e-08 | 0.0078937 | 0.0078937 | 0.0078937 | 0.98206 | -0.34889 | 0.98203 | -0.34959 | 2.1686
85 | -0.020315 | -0.00499 | 0.020322 | 0.0049925 | 7.6576e-06 | 2.4311e-06 | 0.030718 | 0.030717 | 0.030718 | 0.98291 | -0.33197 | 0.98332 | -0.32394 | 2.813
86 | 0.0049775 | 0.0012352 | -0.0049771 | -0.0012352 | 3.9334e-07 | 1.8199e-08 | 0.0075378 | 0.0075379 | 0.0075379 | 0.98203 | -0.34959 | 0.98194 | -0.35126 | 2.0709
87 | -0.030687 | -0.007591 | 0.030746 | 0.0076203 | 5.8858e-05 | 2.9329e-05 | 0.046403 | 0.0464 | 0.046403 | 0.98332 | -0.32394 | 0.98538 | -0.28335 | 4.2493
88 | 0.010365 | 0.0025985 | -0.010361 | -0.0025965 | 4.0029e-06 | 2.0117e-06 | 0.015686 | 0.015686 | 0.015686 | 0.98332 | -0.32394 | 0.9829 | -0.33205 | 4.3093
89 | 0.0048416 | 0.0012012 | -0.0048377 | -0.0012011 | 3.9198e-06 | 5.183e-08 | 0.0073325 | 0.0073334 | 0.0073334 | 0.98194 | -0.35126 | 0.98107 | -0.36839 | 2.0147
90 | 0.0084342 | 0.0021135 | -0.0084331 | -0.0021131 | 1.0299e-06 | 4.4566e-07 | 0.012768 | 0.012768 | 0.012768 | 0.9829 | -0.33205 | 0.98277 | -0.33461 | 3.5078
91 | -0.0022016 | -0.00052174 | 0.0022016 | 0.00052168 | 2.1677e-08 | -5.0742e-08 | 0.0033449 | 0.0033448 | 0.0033449 | 0.97635 | -0.46378 | 0.97636 | -0.46356 | 0.91892
92 | 0.0015101 | 0.0003777 | -0.0015101 | -0.00037789 | 3.2876e-08 | -1.877e-07 | 0.0022965 | 0.0022966 | 0.0022966 | 0.97838 | -0.42249 | 0.97836 | -0.42295 | 0.63092
93 | 0.00051867 | 0.00012941 | -0.00051866 | -0.00012999 | 1.0823e-08 | -5.7561e-07 | 0.00078866 | 0.00078887 | 0.00078887 | 0.97836 | -0.42295 | 0.97833 | -0.42339 | 0.21672
94 | 0.00033324 | 8.2622e-05 | -0.00033323 | -8.3515e-05 | 6.9298e-09 | -8.9381e-07 | 0.00050731 | 0.00050763 | 0.00050763 | 0.97682 | -0.4541 | 0.97679 | -0.45454 | 0.13946
95 | -0.0022203 | -0.00055375 | 0.0022214 | 0.00055136 | 1.0327e-06 | -2.389e-06 | 0.0033724 | 0.0033713 | 0.0033724 | 0.97942 | -0.4011 | 0.97992 | -0.39128 | 0.92647
96 | 0.0019784 | 0.00049312 | -0.0019782 | -0.00049387 | 2.445e-07 | -7.5209e-07 | 0.0030048 | 0.0030051 | 0.0030051 | 0.97942 | -0.4011 | 0.97929 | -0.4037 | 0.82559
97 | -0.0024897 | -0.0006186 | 0.0024897 | 0.00061854 | 3.6617e-08 | -6.2717e-08 | 0.0037787 | 0.0037787 | 0.0037787 | 0.97992 | -0.39128 | 0.97993 | -0.39097 | 1.0381
98 | 0.0016293 | 0.00040644 | -0.0016293 | -0.00040656 | 2.5077e-08 | -1.2129e-07 | 0.0024751 | 0.0024751 | 0.0024751 | 0.97929 | -0.4037 | 0.97927 | -0.40402 | 0.67997
99 | -0.0036884 | -0.00091554 | 0.0036908 | 0.00091451 | 2.3717e-06 | -1.0271e-06 | 0.0055977 | 0.0055968 | 0.0055977 | 0.97993 | -0.39097 | 0.98062 | -0.37737 | 1.5378
100 | 0.0007894 | 0.00019606 | -0.00078932 | -0.00019782 | 7.766e-08 | -1.7619e-06 | 0.0011989 | 0.0011995 | 0.0011995 | 0.97927 | -0.40402 | 0.97917 | -0.4061 | 0.32954
101 | -0.0036908 | -0.00091451 | 0.0036909 | 0.00091445 | 1.3868e-07 | -6.0193e-08 | 0.0055968 | 0.0055967 | 0.0055968 | 0.98062 | -0.37737 | 0.98066 | -0.37657 | 1.5376
102 | -0.0038974 | -0.0009662 | 0.0038975 | 0.00096616 | 1.2525e-07 | -4.0494e-08 | 0.00591 | 0.00591 | 0.00591 | 0.98066 | -0.37657 | 0.9807 | -0.37589 | 1.6236
103 | -0.0042211 | -0.0010472 | 0.0042226 | 0.001047 | 1.497e-06 | -2.7188e-07 | 0.0064009 | 0.0064004 | 0.0064009 | 0.9807 | -0.37589 | 0.98107 | -0.36839 | 1.7585
104 | -0.0055737 | -0.0013967 | 0.0055754 | 0.001397 | 1.6399e-06 | 2.7433e-07 | 0.0084476 | 0.0084474 | 0.0084476 | 0.98178 | -0.35402 | 0.9821 | -0.34784 | 2.3208
105 | 0.0048833 | 0.0012237 | -0.0048825 | -0.0012237 | 7.1855e-07 | 1.7601e-08 | 0.0074012 | 0.0074013 | 0.0074013 | 0.98178 | -0.35402 | 0.98162 | -0.35711 | 2.0333
106 | -0.0057872 | -0.0014501 | 0.0057908 | 0.0014508 | 3.6478e-06 | 7.3238e-07 | 0.0087683 | 0.0087677 | 0.0087683 | 0.9821 | -0.34784 | 0.98277 | -0.33461 | 2.4089

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.067597 | 0.016665

## res_load
| p_mw | q_mvar
0 | 0.00083396 | 0.00020901
1 | 0.0057745 | 0.0014472
2 | 0.0023649 | 0.00059271
3 | 0.00032812 | 8.2235e-05
4 | 0.00087056 | 0.00021818
5 | 0.00073713 | 0.00018474
6 | 0.00059098 | 0.00014811
7 | 0.00024362 | 6.1057e-05
8 | 0.00018729 | 4.6938e-05
9 | 0.00027035 | 6.7755e-05
10 | 0.00042448 | 0.00010639
11 | 0.00022526 | 5.6454e-05
12 | 0.00034168 | 8.5634e-05
13 | 9.9539e-05 | 2.4947e-05
14 | 8.9939e-05 | 2.2541e-05
15 | 0.00021186 | 5.3096e-05
16 | 0.0016212 | 0.00040631
17 | 0.00079604 | 0.00019951
18 | 0.00035614 | 8.9256e-05
19 | 0.00032072 | 8.0381e-05
20 | 0.00032534 | 8.1538e-05
21 | 0.004954 | 0.0012416
22 | 0.0013665 | 0.00034247
23 | 0.00021273 | 5.3316e-05
24 | 0.00059179 | 0.00014832
25 | 0.00018024 | 4.5173e-05
26 | 0.00050017 | 0.00012536
27 | 0.00075633 | 0.00018955
28 | 0.00044619 | 0.00011183
29 | 0.0003297 | 8.2631e-05
30 | 0.00035001 | 8.7721e-05
31 | 0.0038362 | 0.00096144
32 | 0.00036929 | 9.2552e-05
33 | 0.00072452 | 0.00018158
34 | 0.00040891 | 0.00010248
35 | 0.0024778 | 0.00062098
36 | 0.00029288 | 7.3401e-05
37 | 0.0010483 | 0.00026272
38 | 0.00060744 | 0.00015224
39 | 0.00034073 | 8.5394e-05
40 | 0.00015063 | 3.7753e-05
41 | 0.00027637 | 6.9265e-05
42 | 0.00014536 | 3.643e-05
43 | 0.00039748 | 9.9618e-05
44 | 0.00047378 | 0.00011874
45 | 0.00080688 | 0.00020222
46 | 0.00022299 | 5.5887e-05
47 | 0.00018305 | 4.5876e-05
48 | 0.0023867 | 0.00059816
49 | 0.00034763 | 8.7124e-05
50 | 0.0007309 | 0.00018318
51 | 0.00050321 | 0.00012612
52 | 0.00018506 | 4.6382e-05
53 | 0.00026704 | 6.6926e-05
54 | 0.00077457 | 0.00019413
55 | 0.00085763 | 0.00021494
56 | 0.00038976 | 9.7682e-05
57 | 0.00033449 | 8.3832e-05
58 | 0.00025958 | 6.5056e-05
59 | 0.00038115 | 9.5524e-05
60 | 0.00023486 | 5.8861e-05
61 | 0.00013556 | 3.3975e-05
62 | 0.0010245 | 0.00025677
63 | 0.0019271 | 0.00048297
64 | 0.00010514 | 2.6351e-05
65 | 0.0004324 | 0.00010837
66 | 0.00099144 | 0.00024848
67 | 0.00051866 | 0.00012999
68 | 0.00010517 | 2.6358e-05
69 | 0.00027901 | 6.9926e-05
70 | 0.00033323 | 8.3515e-05
71 | 0.00024192 | 6.0631e-05
72 | 0.0002683 | 6.7241e-05
73 | 0.00034886 | 8.7433e-05
74 | 0.0008399 | 0.0002105
75 | 0.00078932 | 0.00019782
76 | 0.00020647 | 5.1746e-05
77 | 0.00032352 | 8.1082e-05
78 | 0.00061511 | 0.00015416
79 | 0.00069046 | 0.00017305
80 | 0.0002118 | 5.3082e-05
81 | 0.0048825 | 0.0012237
82 | 0.0026423 | 0.00066223

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1