## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1362-1_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1362-1_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1362-1_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1362-1_0_2_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1362-1_0_2_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_1362-1_0_2_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1362-1_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1362-1_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1362-1_0_2_node_53 | 0.4 | n |  | TRUE
9 | bus_LV_1362-1_0_2_node_51 | 0.4 | n |  | TRUE
10 | bus_LV_1362-1_0_2_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_1362-1_0_2_node_55 | 0.4 | n |  | TRUE
12 | bus_LV_1362-1_0_2_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_1362-1_0_2_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1362-1_0_2_node_54 | 0.4 | n |  | TRUE
15 | bus_LV_1362-1_0_2_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_1362-1_0_2_node_31 | 0.4 | n |  | TRUE
17 | bus_LV_1362-1_0_2_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1362-1_0_2_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1362-1_0_2_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1362-1_0_2_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1362-1_0_2_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1362-1_0_2_node_37 | 0.4 | n |  | TRUE
23 | bus_LV_1362-1_0_2_node_38 | 0.4 | n |  | TRUE
24 | bus_LV_1362-1_0_2_node_40 | 0.4 | n |  | TRUE
25 | bus_LV_1362-1_0_2_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1362-1_0_2_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1362-1_0_2_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1362-1_0_2_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_1362-1_0_2_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_1362-1_0_2_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_1362-1_0_2_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_1362-1_0_2_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_1362-1_0_2_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_1362-1_0_2_node_58 | 0.4 | n |  | TRUE
35 | bus_LV_1362-1_0_2_node_56 | 0.4 | n |  | TRUE
36 | bus_LV_1362-1_0_2_node_52 | 0.4 | n |  | TRUE
37 | bus_LV_1362-1_0_2_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_1362-1_0_2_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_1362-1_0_2_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_1362-1_0_2_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_1362-1_0_2_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_1362-1_0_2_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_1362-1_0_2_node_27 | 0.4 | n |  | TRUE
44 | bus_LV_1362-1_0_2_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_1362-1_0_2_node_57 | 0.4 | n |  | TRUE
46 | bus_LV_1362-1_0_2_node_45 | 0.4 | n |  | TRUE
47 | bus_LV_1362-1_0_2_node_50 | 0.4 | n |  | TRUE
48 | bus_LV_1362-1_0_2_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_1362-1_0_2_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_1362-1_0_2_node_46 | 0.4 | n |  | TRUE
51 | bus_LV_1362-1_0_2_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_1362-1_0_2_node_49 | 0.4 | n |  | TRUE
53 | bus_LV_1362-1_0_2_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_1362-1_0_2_node_47 | 0.4 | n |  | TRUE
55 | bus_LV_1362-1_0_2_node_42 | 0.4 | n |  | TRUE
56 | bus_MV_1_0_node_101 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1362-1_0_2_load_0 | 0 | 0.019134 | 0.0047955 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1362-1_0_2_load_53 | 8 | 0.00096348 | 0.00024147 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1362-1_0_2_load_51 | 9 | 0.0024844 | 0.00062264 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1362-1_0_2_load_30 | 10 | 0.00085391 | 0.00021401 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1362-1_0_2_load_55 | 11 | 0.0012591 | 0.00031556 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1362-1_0_2_load_11 | 12 | 0.0027581 | 0.00069125 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1362-1_0_2_load_9 | 13 | 0.0045079 | 0.0011298 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1362-1_0_2_load_54 | 14 | 0.0028817 | 0.00072223 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1362-1_0_2_load_10 | 17 | 0.00080127 | 0.00020082 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1362-1_0_2_load_16 | 19 | 0.0027908 | 0.00069944 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1362-1_0_2_load_12 | 20 | 0.0098686 | 0.0024733 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1362-1_0_2_load_17 | 25 | 0.0076719 | 0.0019227 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1362-1_0_2_load_18 | 26 | 0.0010116 | 0.00025353 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1362-1_0_2_load_36 | 30 | 0.00087423 | 0.0002191 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1362-1_0_2_load_32 | 32 | 0.0014516 | 0.00036379 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1362-1_0_2_load_58 | 34 | 0.00099241 | 0.00024872 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1362-1_0_2_load_52 | 36 | 0.0006188 | 0.00015509 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1362-1_0_2_load_22 | 37 | 0.0028647 | 0.00071797 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1362-1_0_2_load_24 | 39 | 0.00070822 | 0.0001775 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1362-1_0_2_load_34 | 40 | 0.0004583 | 0.00011486 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1362-1_0_2_load_35 | 41 | 0.0020128 | 0.00050447 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1362-1_0_2_load_26 | 42 | 0.0043464 | 0.0010893 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1362-1_0_2_load_57 | 45 | 0.0012894 | 0.00032316 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1362-1_0_2_load_50 | 47 | 0.0010039 | 0.00025161 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1362-1_0_2_load_39 | 48 | 0.0041896 | 0.00105 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1362-1_0_2_load_46 | 50 | 0.0053574 | 0.0013427 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1362-1_0_2_load_49 | 52 | 0.0019241 | 0.00048223 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1362-1_0_2_load_47 | 54 | 0.00036903 | 9.2487e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1362-1_0_2_load_42 | 55 | 0.00055732 | 0.00013968 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1362-1_0_2_line_0 |  | 0 | 1 | 0.024361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1362-1_0_2_line_1 |  | 0 | 2 | 0.027219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1362-1_0_2_line_2 |  | 1 | 3 | 0.073039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1362-1_0_2_line_3 |  | 1 | 4 | 0.058877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1362-1_0_2_line_4 |  | 2 | 5 | 0.088333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1362-1_0_2_line_5 |  | 3 | 9 | 0.0036602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1362-1_0_2_line_6 |  | 4 | 12 | 0.032264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1362-1_0_2_line_7 |  | 4 | 13 | 0.048489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1362-1_0_2_line_8 |  | 5 | 6 | 0.006416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1362-1_0_2_line_9 |  | 5 | 7 | 0.061854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1362-1_0_2_line_10 |  | 5 | 8 | 0.018581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1362-1_0_2_line_11 |  | 6 | 11 | 0.016071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1362-1_0_2_line_12 |  | 7 | 10 | 0.11456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1362-1_0_2_line_13 |  | 8 | 14 | 0.018336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1362-1_0_2_line_14 |  | 9 | 15 | 0.020275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1362-1_0_2_line_15 |  | 10 | 16 | 0.076386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1362-1_0_2_line_16 |  | 13 | 17 | 0.063278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1362-1_0_2_line_17 |  | 15 | 21 | 0.072942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1362-1_0_2_line_18 |  | 16 | 28 | 0.61413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1362-1_0_2_line_19 |  | 18 | 19 | 0.45376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1362-1_0_2_line_20 |  | 18 | 20 | 0.05352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1362-1_0_2_line_21 |  | 19 | 22 | 0.0099486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1362-1_0_2_line_22 |  | 20 | 21 | 0.031365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1362-1_0_2_line_23 |  | 22 | 23 | 0.29115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1362-1_0_2_line_24 |  | 22 | 24 | 0.39085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1362-1_0_2_line_25 |  | 23 | 46 | 0.0277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1362-1_0_2_line_26 |  | 23 | 47 | 0.035102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1362-1_0_2_line_27 |  | 24 | 48 | 0.010029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1362-1_0_2_line_28 |  | 25 | 26 | 0.054385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1362-1_0_2_line_29 |  | 25 | 27 | 0.08772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1362-1_0_2_line_30 |  | 26 | 28 | 0.017302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1362-1_0_2_line_31 |  | 27 | 29 | 0.18063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1362-1_0_2_line_32 |  | 28 | 30 | 0.016088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1362-1_0_2_line_33 |  | 29 | 31 | 0.51113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1362-1_0_2_line_34 |  | 29 | 32 | 0.35269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1362-1_0_2_line_35 |  | 30 | 33 | 0.12892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1362-1_0_2_line_36 |  | 31 | 34 | 0.039079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1362-1_0_2_line_37 |  | 31 | 35 | 0.063474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1362-1_0_2_line_38 |  | 32 | 36 | 0.11226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1362-1_0_2_line_39 |  | 33 | 40 | 0.033889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1362-1_0_2_line_40 |  | 33 | 38 | 0.073133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1362-1_0_2_line_41 |  | 35 | 45 | 0.017893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1362-1_0_2_line_42 |  | 37 | 38 | 0.032691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1362-1_0_2_line_43 |  | 37 | 39 | 0.033788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1362-1_0_2_line_44 |  | 40 | 41 | 0.031265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1362-1_0_2_line_45 |  | 41 | 44 | 0.06915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1362-1_0_2_line_46 |  | 42 | 43 | 0.048528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1362-1_0_2_line_47 |  | 43 | 44 | 0.025041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1362-1_0_2_line_48 |  | 46 | 50 | 0.023463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1362-1_0_2_line_49 |  | 46 | 51 | 0.038209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1362-1_0_2_line_50 |  | 47 | 52 | 0.0099207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1362-1_0_2_line_51 |  | 48 | 49 | 0.58001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1362-1_0_2_line_52 |  | 49 | 53 | 0.62472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1362-1_0_2_line_53 |  | 51 | 55 | 0.19047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1362-1_0_2_line_54 |  | 53 | 54 | 0.012235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1362-1_0_2_trafo_53 | 0.63 MVA 20/0.4 kV | 56 | 8 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48 | x49 | y49 | x50 | y50 | x51 | y51 | x52 | y52 | x53 | y53 | x54 | y54 | x55 | y55 | x56 | y56 | x57 | y57 | x58 | y58 | x59 | y59 | x60 | y60 | x61 | y61 | x62 | y62 | x63 | y63 | x64 | y64 | x65 | y65 | x66 | y66 | x67 | y67 | x68 | y68 | x69 | y69 | x70 | y70 | x71 | y71 | x72 | y72 | x73 | y73 | x74 | y74 | x75 | y75 | x76 | y76 | x77 | y77 | x78 | y78 | x79 | y79 | x80 | y80 | x81 | y81 | x82 | y82 | x83 | y83 | x84 | y84 | x85 | y85 | x86 | y86 | x87 | y87 | x88 | y88 | x89 | y89 | x90 | y90 | x91 | y91
0 | 2679451.5416 | 1212165.3214 | 2679449.6139 | 1212168.5756 | 2679447.3383 | 1212168.2785 | 2679438.8488 | 1212165.0078 | 2679430.2275 | 1212161.8369
1 | 2679404.1122 | 1212155.6281 | 2679405.6538 | 1212156.2602 | 2679411.8358 | 1212158.7774 | 2679416.6531 | 1212158.786 | 2679422.9775 | 1212159.1704 | 2679430.2275 | 1212161.8369
2 | 2679452.1928 | 1212117.5993 | 2679450.9749 | 1212142.2768 | 2679436.0913 | 1212150.6951 | 2679430.356 | 1212156.8561 | 2679451.5416 | 1212165.3214
3 | 2679451.5416 | 1212165.3214 | 2679466.0625 | 1212155.0415 | 2679475.53 | 1212149.9199 | 2679496.2797 | 1212143.7813 | 2679504.8955 | 1212142.7065
4 | 2679374.8123 | 1212108.8525 | 2679420.8031 | 1212144.432 | 2679425.0523 | 1212148.8692 | 2679420.772 | 1212153.6153 | 2679416.5085 | 1212155.9489 | 2679405.7294 | 1212154.5823 | 2679404.1122 | 1212155.6281
5 | 2679452.1928 | 1212117.5993 | 2679449.4825 | 1212115.1394
6 | 2679504.8955 | 1212142.7065 | 2679514.8685 | 1212129.8867 | 2679522.5024 | 1212127.2312 | 2679530.4287 | 1212126.7819
7 | 2679504.8955 | 1212142.7065 | 2679537.6516 | 1212154.1617 | 2679547.4533 | 1212157.0275 | 2679551.0272 | 1212157.1408
8 | 2679368.4896 | 1212110.0469 | 2679374.8123 | 1212108.8525
9 | 2679374.8123 | 1212108.8525 | 2679369.8982 | 1212102.9834 | 2679362.5042 | 1212097.8928 | 2679355.3152 | 1212095.6735 | 2679317.4855 | 1212094.2807
10 | 2679374.8123 | 1212108.8525 | 2679379.3746 | 1212104.0435 | 2679391.1164 | 1212102.1763 | 2679391.1786 | 1212102.1673
11 | 2679368.4896 | 1212110.0469 | 2679352.7453 | 1212113.4842
12 | 2679317.4855 | 1212094.2807 | 2679307.3379 | 1212091.1215 | 2679298.8611 | 1212091.4535 | 2679268.4366 | 1212097.1751 | 2679260.1891 | 1212099.1223 | 2679252.859 | 1212102.9385 | 2679244.9803 | 1212108.5819 | 2679237.5549 | 1212112.1411 | 2679224.9861 | 1212115.065 | 2679215.5876 | 1212115.5738 | 2679208.5905 | 1212112.8434
13 | 2679409.327 | 1212099.5503 | 2679391.1786 | 1212102.1673
14 | 2679451.0898 | 1212096.0263 | 2679448.8203 | 1212098.1196 | 2679448.6442 | 1212101.0747 | 2679448.6485 | 1212105.3109 | 2679449.8204 | 1212109.7404 | 2679449.4825 | 1212115.1394
15 | 2679151.3417 | 1212064.6883 | 2679156.3601 | 1212065.5777 | 2679168.371 | 1212073.1975 | 2679187.283 | 1212094.4289 | 2679202.6385 | 1212110.5209 | 2679208.5905 | 1212112.8434
16 | 2679551.0272 | 1212157.1408 | 2679563.2134 | 1212157.5269 | 2679575.5895 | 1212159.3709 | 2679589.3206 | 1212163.8681 | 2679597.5237 | 1212168.0914 | 2679603.2643 | 1212173.5048 | 2679605.287 | 1212180.2139 | 2679605.287 | 1212180.2139
17 | 2679451.0898 | 1212096.0263 | 2679463.5689 | 1212097.5601 | 2679475.519 | 1212098.3087 | 2679486.4093 | 1212098.7541 | 2679495.5233 | 1212097.9305 | 2679507.5142 | 1212096.1892 | 2679523.614 | 1212092.8794
18 | 2678681.4973 | 1211915.2772 | 2678679.1662 | 1211916.8697 | 2678675.5405 | 1211920.413 | 2678672.489 | 1211924.1974 | 2678669.9383 | 1211929.2003 | 2678668.5855 | 1211934.9751 | 2678669.3844 | 1211948.1385 | 2678670.4357 | 1211955.4238 | 2678671.6725 | 1211957.8639 | 2678672.7109 | 1211959.2118 | 2678674.6901 | 1211960.6721 | 2678678.3682 | 1211961.7991 | 2678687.0745 | 1211962.5033 | 2678690.5143 | 1211963.2603 | 2678691.9084 | 1211964.1459 | 2678693.8053 | 1211966.0833 | 2678708.9377 | 1211989.9983 | 2678718.4765 | 1212001.8873 | 2678726.6637 | 1212010.8345 | 2678736.61 | 1212020.0605 | 2678743.4343 | 1212025.1761 | 2678755.7126 | 1212033.8882 | 2678758.7178 | 1212036.474 | 2678763.1587 | 1212040.8243 | 2678767.1248 | 1212046.0245 | 2678784.5506 | 1212072.883 | 2678788.2815 | 1212076.9015 | 2678792.5502 | 1212079.9043 | 2678796.3151 | 1212081.3549 | 2678800.6929 | 1212082.4245 | 2678805.0693 | 1212082.449 | 2678815.7926 | 1212081.1676 | 2678820.0713 | 1212079.9567 | 2678822.1313 | 1212078.1717 | 2678823.267 | 1212075.6073 | 2678825.9307 | 1212068.9715 | 2678827.6347 | 1212067.671 | 2678830.7937 | 1212067.2458 | 2678831.3694 | 1212065.0853 | 2678834.0679 | 1212062.7083 | 2678838.572 | 1212062.8457 | 2678844.1735 | 1212061.5967 | 2678849.4386 | 1212060.4989 | 2678854.1021 | 1212061.2277 | 2678859.5309 | 1212060.966 | 2678866.8666 | 1212060.7294 | 2678871.6357 | 1212059.7919 | 2678877.753 | 1212057.4602 | 2678884.5047 | 1212056.5711 | 2678888.9663 | 1212056.4745 | 2678893.8709 | 1212059.0743 | 2678906.1525 | 1212060.0485 | 2678921.8315 | 1212056.3646 | 2678942.7453 | 1212048.136 | 2678969.1132 | 1212041.1805 | 2678976.8974 | 1212042.0841 | 2678980.8735 | 1212042.5037 | 2678985.5589 | 1212046.7351 | 2678993.3211 | 1212053.8869 | 2679002.3237 | 1212058.031 | 2679007.3361 | 1212058.7979 | 2679013.9368 | 1212057.2621 | 2679021.9326 | 1212051.9424 | 2679032.4569 | 1212047.9125 | 2679042.3953 | 1212045.6538 | 2679048.898 | 1212045.7845 | 2679053.7026 | 1212042.7462 | 2679057.5281 | 1212042.4857 | 2679061.2414 | 1212043.8135 | 2679065.5673 | 1212044.7826 | 2679069.949 | 1212044.9852 | 2679072.7892 | 1212043.9666 | 2679075.4328 | 1212042.3006 | 2679077.9141 | 1212041.9889 | 2679080.5849 | 1212043.4252 | 2679085.916 | 1212047.0982 | 2679088.0188 | 1212048.3936 | 2679092.111 | 1212049.2262 | 2679103.1338 | 1212050.5732 | 2679115.0759 | 1212051.9324 | 2679125.9451 | 1212053.9779 | 2679140.4848 | 1212057.1394 | 2679147.3151 | 1212059.4871 | 2679149.5567 | 1212061.2068 | 2679151.3417 | 1212064.6883
19 | 2679606.6343 | 1212082.7245 | 2679627.962 | 1212089.091 | 2679647.3491 | 1212092.263 | 2679656.7616 | 1212092.9891 | 2679662.5858 | 1212090.999 | 2679667.7341 | 1212085.5753 | 2679668.0606 | 1212071.3816 | 2679665.8383 | 1212048.326 | 2679661.3683 | 1212033.6902 | 2679659.2071 | 1212021.9871 | 2679661.8627 | 1211998.3962 | 2679666.0685 | 1211988.4459 | 2679695.7485 | 1211944.136 | 2679707.323 | 1211924.6892 | 2679712.5719 | 1211902.0892 | 2679719.0841 | 1211891.2914 | 2679742.0708 | 1211863.4251 | 2679749.3411 | 1211855.0391 | 2679756.1462 | 1211851.8836 | 2679764.4932 | 1211852.1954 | 2679771.3175 | 1211850.4521 | 2679779.4423 | 1211840.6767 | 2679789.309 | 1211832.47 | 2679806.0431 | 1211826.1231 | 2679824.6695 | 1211823.1704 | 2679839.348 | 1211819.3865 | 2679850.9823 | 1211821.0544 | 2679864.9208 | 1211827.7009 | 2679868.0465 | 1211827.6047
20 | 2679606.6343 | 1212082.7245 | 2679597.2459 | 1212081.3317 | 2679576.7289 | 1212080.2684 | 2679553.6633 | 1212084.6826
21 | 2679877.6578 | 1211825.3365 | 2679870.7136 | 1211827.5227 | 2679868.0465 | 1211827.6047
22 | 2679523.614 | 1212092.8794 | 2679532.1408 | 1212088.8016 | 2679553.6633 | 1212084.6826
23 | 2679877.6578 | 1211825.3365 | 2679883.9216 | 1211825.1647 | 2679900.6758 | 1211828.1021 | 2679907.104 | 1211827.5656 | 2679922.6098 | 1211820.4576 | 2679943.9717 | 1211812.9834 | 2679959.0016 | 1211805.669 | 2679964.1762 | 1211801.7247 | 2679966.5171 | 1211795.4631 | 2679985.1478 | 1211752.5518 | 2679991.2269 | 1211744.6282 | 2680002.7958 | 1211752.8776 | 2680009.9821 | 1211762.6803 | 2680014.212 | 1211765.1497 | 2680020.0115 | 1211762.7704 | 2680021.386 | 1211758.8752 | 2680024.475 | 1211750.0999 | 2680032.6105 | 1211728.8063 | 2680035.1377 | 1211717.1661 | 2680038.5031 | 1211685.5352 | 2680040.2653 | 1211668.0476
24 | 2679877.6578 | 1211825.3365 | 2680078.4528 | 1212160.6672
25 | 2680040.2653 | 1211668.0476 | 2680044.7206 | 1211640.7119
26 | 2680040.2653 | 1211668.0476 | 2680058.8219 | 1211673.1665 | 2680073.2896 | 1211679.6461
27 | 2680078.4528 | 1212160.6672 | 2680088.0887 | 1212163.4469
28 | 2678691.8501 | 1211929.1399 | 2678693.011 | 1211930.6945 | 2678702.2253 | 1211944.158 | 2678738.3488 | 1211943.4682
29 | 2678820.0074 | 1211948.5713 | 2678812.2911 | 1211954.0173 | 2678804.4223 | 1211958.3606 | 2678792.8072 | 1211958.6852 | 2678781.8843 | 1211953.7822 | 2678766.3822 | 1211945.7946 | 2678751.4468 | 1211943.218 | 2678738.3488 | 1211943.4682
30 | 2678681.4973 | 1211915.2772 | 2678691.8501 | 1211929.1399
31 | 2678820.0074 | 1211948.5713 | 2678858.6607 | 1211934.8733 | 2678865.1872 | 1211931.4907 | 2678868.7113 | 1211928.7467 | 2678889.972 | 1211904.0897 | 2678894.7873 | 1211897.3712 | 2678902.3077 | 1211883.1949 | 2678907.6721 | 1211876.9063 | 2678914.4173 | 1211871.9256 | 2678920.7218 | 1211869.8188 | 2678931.7204 | 1211867.2848 | 2678943.5772 | 1211860.1927 | 2678960.2222 | 1211845.0032
32 | 2678681.4973 | 1211915.2772 | 2678672.3697 | 1211902.0288
33 | 2679382.4945 | 1211621.4406 | 2679376.8583 | 1211623.5447 | 2679355.2034 | 1211627.348 | 2679330.851 | 1211637.4195 | 2679316.7258 | 1211649.3061 | 2679300.478 | 1211652.8035 | 2679264.7971 | 1211646.7588 | 2679247.4866 | 1211645.5947 | 2679231.5125 | 1211656.5229 | 2679217.7006 | 1211658.5742 | 2679197.7964 | 1211656.453 | 2679188.827 | 1211658.9244 | 2679179.5097 | 1211658.9897 | 2679166.5659 | 1211666.0558 | 2679138.0498 | 1211681.2762 | 2679112.1672 | 1211695.0418 | 2679096.9599 | 1211703.7569 | 2679077.7934 | 1211716.4999 | 2679066.9752 | 1211731.7664 | 2679042.5974 | 1211772.4807 | 2679029.526 | 1211789.2071 | 2679022.84 | 1211801.7378 | 2679012.1106 | 1211810.3234 | 2679003.1957 | 1211821.9017 | 2678992.8092 | 1211832.7156 | 2678971.4317 | 1211843.7619 | 2678960.2222 | 1211845.0032
34 | 2678960.2222 | 1211845.0032 | 2678976.4654 | 1211830.3199 | 2678983.6943 | 1211823.2555 | 2678993.3883 | 1211807.9295 | 2679003.2687 | 1211782.5551 | 2679010.7234 | 1211760.7509 | 2679023.3632 | 1211708.3735 | 2679035.533 | 1211655.345 | 2679044.3358 | 1211632.1801 | 2679052.21 | 1211614.2951 | 2679064.2586 | 1211595.0869 | 2679079.2187 | 1211579.2416 | 2679124.4841 | 1211552.5357 | 2679126.6873 | 1211551.0768
35 | 2678617.2746 | 1211786.0586 | 2678650.8251 | 1211868.8985 | 2678658.3913 | 1211881.7398 | 2678672.3697 | 1211902.0288
36 | 2679419.3449 | 1211608.1447 | 2679395.0197 | 1211616.7376 | 2679382.4945 | 1211621.4406
37 | 2679382.4945 | 1211621.4406 | 2679392.7335 | 1211634.3407 | 2679398.1373 | 1211647.977 | 2679402.0399 | 1211663.0608 | 2679399.8303 | 1211674.9168 | 2679398.6902 | 1211679.4935
38 | 2679126.6873 | 1211551.0768 | 2679103.891 | 1211441.1526
39 | 2678617.2746 | 1211786.0586 | 2678615.2013 | 1211787.1208 | 2678611.2767 | 1211787.9697 | 2678587.0738 | 1211781.0797 | 2678585.2068 | 1211779.604
40 | 2678617.2746 | 1211786.0586 | 2678611.1263 | 1211754.9909 | 2678598.1687 | 1211721.6655 | 2678597.4532 | 1211715.9968
41 | 2679380.9278 | 1211682.0366 | 2679398.6902 | 1211679.4935
42 | 2678597.4532 | 1211715.9968 | 2678601.367 | 1211709.0551 | 2678610.5 | 1211693.5654 | 2678610.0035 | 1211686.8435
43 | 2678601.9168 | 1211656.3951 | 2678600.9028 | 1211666.4438 | 2678602.3443 | 1211679.3044 | 2678610.0035 | 1211686.8435
44 | 2678585.2068 | 1211779.604 | 2678582.2532 | 1211777.2693 | 2678575.6747 | 1211767.8766 | 2678569.0026 | 1211761.5514 | 2678563.682 | 1211757.255
45 | 2678507.6221 | 1211717.4261 | 2678517.1734 | 1211721.51 | 2678524.3452 | 1211725.6737 | 2678535.0185 | 1211733.4192 | 2678553.2279 | 1211748.8133 | 2678563.682 | 1211757.255
46 | 2678483.6358 | 1211713.1078 | 2678493.2726 | 1211725.7093 | 2678501.7084 | 1211739.4847 | 2678510.0785 | 1211753.7166
47 | 2678483.6358 | 1211713.1078 | 2678487.2719 | 1211711.6658 | 2678489.5566 | 1211711.8627 | 2678507.6221 | 1211717.4261
48 | 2680044.7206 | 1211640.7119 | 2680066.5627 | 1211649.28
49 | 2680044.7206 | 1211640.7119 | 2680047.8168 | 1211632.5371 | 2680054.817 | 1211626.2047 | 2680069.5291 | 1211612.6156
50 | 2680082.3437 | 1211683.7011 | 2680073.2896 | 1211679.6461
51 | 2680464.4919 | 1212166.9211 | 2680463.2582 | 1212167.1268 | 2680460.5905 | 1212168.3027 | 2680458.49 | 1212167.9853 | 2680456.4736 | 1212166.5016 | 2680455.0425 | 1212165.5706 | 2680453.6032 | 1212166.9298 | 2680451.0887 | 1212169.1418 | 2680446.6725 | 1212170.939 | 2680443.6959 | 1212169.6647 | 2680436.8536 | 1212161.4893 | 2680433.7771 | 1212159.1686 | 2680432.937 | 1212156.1108 | 2680431.4663 | 1212153.0446 | 2680429.5521 | 1212150.7395 | 2680427.9437 | 1212150.5621 | 2680427.4421 | 1212152.2565 | 2680427.7598 | 1212154.0508 | 2680426.8137 | 1212156.5953 | 2680425.6097 | 1212160.2258 | 2680425.6872 | 1212164.6186 | 2680423.9243 | 1212171.3881 | 2680422.5048 | 1212175.227 | 2680421.1382 | 1212176.2648 | 2680419.3661 | 1212175.8295 | 2680418.0314 | 1212173.9436 | 2680416.5009 | 1212171.3658 | 2680413.7816 | 1212169.0387 | 2680408.793 | 1212165.3914 | 2680405.2151 | 1212160.2509 | 2680402.5915 | 1212158.7146 | 2680400.9558 | 1212158.3034 | 2680398.646 | 1212158.2945 | 2680392.6579 | 1212155.512 | 2680389.5119 | 1212154.9692 | 2680386.7286 | 1212154.0089 | 2680385.346 | 1212154.5461 | 2680385.12 | 1212156.6556 | 2680384.0852 | 1212156.7639 | 2680382.4223 | 1212155.5518 | 2680379.4719 | 1212151.7652 | 2680376.2657 | 1212148.9202 | 2680374.2112 | 1212148.57 | 2680372.5949 | 1212148.4148 | 2680371.1224 | 1212147.7279 | 2680368.2738 | 1212144.2873 | 2680366.2241 | 1212141.8914 | 2680363.1308 | 1212141.3828 | 2680358.8037 | 1212141.6469 | 2680356.8277 | 1212140.5418 | 2680342.2127 | 1212131.7503 | 2680333.8543 | 1212132.883 | 2680328.0917 | 1212132.5385 | 2680320.2095 | 1212132.1654 | 2680314.9341 | 1212128.3697 | 2680305.7822 | 1212119.5853 | 2680298.1404 | 1212117.1586 | 2680296.823 | 1212113.9833 | 2680299.1248 | 1212103.8744 | 2680298.6312 | 1212100.4656 | 2680291.3096 | 1212109.8064 | 2680284.6671 | 1212120.624 | 2680281.4869 | 1212126.0069 | 2680276.4085 | 1212131.2753 | 2680275.1855 | 1212133.5047 | 2680269.3822 | 1212135.6169 | 2680260.4142 | 1212133.4949 | 2680254.2712 | 1212126.4076 | 2680252.5289 | 1212122.0592 | 2680248.303 | 1212118.1887 | 2680243.4249 | 1212118.1786 | 2680237.1067 | 1212119.5946 | 2680233.9663 | 1212123.1435 | 2680233.6378 | 1212129.4877 | 2680241.6774 | 1212148.6526 | 2680249.8541 | 1212162.1491 | 2680255.175 | 1212172.7276 | 2680256.7344 | 1212183.8891 | 2680255.1312 | 1212188.9597 | 2680246.1831 | 1212193.2643 | 2680240.1261 | 1212192.7825 | 2680232.7324 | 1212187.1684 | 2680209.8549 | 1212176.3315 | 2680199.2742 | 1212172.6535 | 2680178.0349 | 1212172.2122 | 2680170.7489 | 1212173.8376 | 2680156.8246 | 1212174.6954 | 2680138.8881 | 1212173.3091 | 2680123.4544 | 1212171.7119 | 2680111.8173 | 1212172.0003 | 2680089.4885 | 1212163.8507 | 2680088.0887 | 1212163.4469
52 | 2680464.4919 | 1212166.9211 | 2680796.7086 | 1211637.8575
53 | 2680069.5291 | 1211612.6156 | 2680065.4044 | 1211603.4321 | 2680055.8974 | 1211597.812 | 2680042.8519 | 1211597.6368 | 2680024.7815 | 1211599.8737 | 2680001.1437 | 1211599.0672 | 2679993.8582 | 1211602.872 | 2679988.7337 | 1211605.9053 | 2679984.7211 | 1211607.6192 | 2679979.6689 | 1211605.2611 | 2679978.9628 | 1211600.115 | 2679973.1562 | 1211582.0477 | 2679968.7989 | 1211567.5355 | 2679962.0869 | 1211565.4108 | 2679956.0021 | 1211562.9833 | 2679946.2193 | 1211555.8142 | 2679941.494 | 1211546.0669 | 2679935.3887 | 1211532.9537
54 | 2680796.7086 | 1211637.8575 | 2680798.9174 | 1211639.733 | 2680808.2342 | 1211639.1078

## bus_geodata
| x | y | coords
0 | 2679430.2275 | 1212161.8369
1 | 2679451.5416 | 1212165.3214
2 | 2679404.1122 | 1212155.6281
3 | 2679452.1928 | 1212117.5993
4 | 2679504.8955 | 1212142.7065
5 | 2679374.8123 | 1212108.8525
6 | 2679368.4896 | 1212110.0469
7 | 2679317.4855 | 1212094.2807
8 | 2679391.1786 | 1212102.1673
9 | 2679449.4825 | 1212115.1394
10 | 2679208.5905 | 1212112.8434
11 | 2679352.7453 | 1212113.4842
12 | 2679530.4287 | 1212126.7819
13 | 2679551.0272 | 1212157.1408
14 | 2679409.327 | 1212099.5503
15 | 2679451.0898 | 1212096.0263
16 | 2679151.3417 | 1212064.6883
17 | 2679605.287 | 1212180.2139
18 | 2679606.6343 | 1212082.7245
19 | 2679868.0465 | 1211827.6047
20 | 2679553.6633 | 1212084.6826
21 | 2679523.614 | 1212092.8794
22 | 2679877.6578 | 1211825.3365
23 | 2680040.2653 | 1211668.0476
24 | 2680078.4528 | 1212160.6672
25 | 2678738.3488 | 1211943.4682
26 | 2678691.8501 | 1211929.1399
27 | 2678820.0074 | 1211948.5713
28 | 2678681.4973 | 1211915.2772
29 | 2678960.2222 | 1211845.0032
30 | 2678672.3697 | 1211902.0288
31 | 2679382.4945 | 1211621.4406
32 | 2679126.6873 | 1211551.0768
33 | 2678617.2746 | 1211786.0586
34 | 2679419.3449 | 1211608.1447
35 | 2679398.6902 | 1211679.4935
36 | 2679103.891 | 1211441.1526
37 | 2678610.0035 | 1211686.8435
38 | 2678597.4532 | 1211715.9968
39 | 2678601.9168 | 1211656.3951
40 | 2678585.2068 | 1211779.604
41 | 2678563.682 | 1211757.255
42 | 2678510.0785 | 1211753.7166
43 | 2678483.6358 | 1211713.1078
44 | 2678507.6221 | 1211717.4261
45 | 2679380.9278 | 1211682.0366
46 | 2680044.7206 | 1211640.7119
47 | 2680073.2896 | 1211679.6461
48 | 2680088.0887 | 1212163.4469
49 | 2680464.4919 | 1212166.9211
50 | 2680066.5627 | 1211649.28
51 | 2680069.5291 | 1211612.6156
52 | 2680082.3437 | 1211683.7011
53 | 2680796.7086 | 1211637.8575
54 | 2680808.2342 | 1211639.1078
55 | 2679935.3887 | 1211532.9537
56 | 2679409.327 | 1212099.5503

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99267 | -0.14019 | 0.019134 | 0.0047955
1 | 0.99185 | -0.15602 | 0 | 0
2 | 0.99407 | -0.11334 | 0 | 0
3 | 0.98992 | -0.19315 | 0 | 0
4 | 0.99141 | -0.16444 | 0 | 0
5 | 0.99859 | -0.02671 | 0 | 0
6 | 0.99858 | -0.026851 | 0 | 0
7 | 0.99715 | -0.054041 | 0 | 0
8 | 1 | 0 | -0.0879 | -0.022009
9 | 0.98983 | -0.19502 | 0.0024844 | 0.00062264
10 | 0.99447 | -0.10487 | 0.00085391 | 0.00021401
11 | 0.99857 | -0.027205 | 0.0012591 | 0.00031556
12 | 0.99133 | -0.16602 | 0.0027581 | 0.00069125
13 | 0.99118 | -0.16901 | 0.0045079 | 0.0011298
14 | 0.99995 | -0.0009211 | 0.0028817 | 0.00072223
15 | 0.98934 | -0.20445 | 0 | 0
16 | 0.99275 | -0.13775 | 0 | 0
17 | 0.99113 | -0.16991 | 0.00080127 | 0.00020082
18 | 0.98602 | -0.26876 | 0 | 0
19 | 0.97921 | -0.40204 | 0.0027908 | 0.00069944
20 | 0.98682 | -0.25315 | 0.0098686 | 0.0024733
21 | 0.98758 | -0.23848 | 0 | 0
22 | 0.97908 | -0.40448 | 0 | 0
23 | 0.97669 | -0.45149 | 0 | 0
24 | 0.97743 | -0.43726 | 0 | 0
25 | 0.97808 | -0.42227 | 0.0076719 | 0.0019227
26 | 0.97869 | -0.41032 | 0.0010116 | 0.00025353
27 | 0.97773 | -0.42929 | 0 | 0
28 | 0.9789 | -0.4062 | 0 | 0
29 | 0.977 | -0.44376 | 0 | 0
30 | 0.97873 | -0.4095 | 0.00087423 | 0.0002191
31 | 0.97592 | -0.4652 | 0 | 0
32 | 0.97632 | -0.45716 | 0.0014516 | 0.00036379
33 | 0.97749 | -0.43393 | 0 | 0
34 | 0.97588 | -0.46591 | 0.00099241 | 0.00024872
35 | 0.97584 | -0.46669 | 0 | 0
36 | 0.97626 | -0.45844 | 0.0006188 | 0.00015509
37 | 0.97714 | -0.44084 | 0.0028647 | 0.00071797
38 | 0.97725 | -0.43871 | 0 | 0
39 | 0.97712 | -0.44128 | 0.00070822 | 0.0001775
40 | 0.97727 | -0.43815 | 0.0004583 | 0.00011486
41 | 0.97709 | -0.44179 | 0.0020128 | 0.00050447
42 | 0.97651 | -0.45312 | 0.0043464 | 0.0010893
43 | 0.97671 | -0.44927 | 0 | 0
44 | 0.97681 | -0.44728 | 0 | 0
45 | 0.97582 | -0.46712 | 0.0012894 | 0.00032316
46 | 0.97654 | -0.45448 | 0 | 0
47 | 0.9766 | -0.45336 | 0.0010039 | 0.00025161
48 | 0.97739 | -0.4381 | 0.0041896 | 0.00105
49 | 0.9772 | -0.44232 | 0 | 0
50 | 0.97642 | -0.45678 | 0.0053574 | 0.0013427
51 | 0.97652 | -0.45488 | 0 | 0
52 | 0.97658 | -0.45371 | 0.0019241 | 0.00048223
53 | 0.97698 | -0.44665 | 0 | 0
54 | 0.97698 | -0.44673 | 0.00036903 | 9.2487e-05
55 | 0.97642 | -0.45683 | 0.00055732 | 0.00013968
56 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.036918 | 0.0093314 | -0.03689 | -0.0093138 | 2.8006e-05 | 1.7609e-05 | 0.055368 | 0.055368 | 0.055368 | 0.99267 | -0.14019 | 0.99185 | -0.15602 | 15.2111
1 | -0.056052 | -0.014127 | 0.056125 | 0.014173 | 7.2109e-05 | 4.5797e-05 | 0.084051 | 0.084051 | 0.084051 | 0.99267 | -0.14019 | 0.99407 | -0.11334 | 23.0908
2 | 0.028818 | 0.0072916 | -0.028767 | -0.0072598 | 5.1255e-05 | 3.1862e-05 | 0.043259 | 0.043259 | 0.043259 | 0.99185 | -0.15602 | 0.98992 | -0.19315 | 11.8844
3 | 0.0080719 | 0.0020222 | -0.0080686 | -0.0020209 | 3.2377e-06 | 1.3126e-06 | 0.01211 | 0.01211 | 0.01211 | 0.99185 | -0.15602 | 0.99141 | -0.16444 | 3.3269
4 | -0.056125 | -0.014173 | 0.056359 | 0.014321 | 0.00023401 | 0.00014862 | 0.084051 | 0.08405 | 0.084051 | 0.99407 | -0.11334 | 0.99859 | -0.02671 | 23.0908
5 | 0.028767 | 0.0072598 | -0.028764 | -0.0072582 | 2.5685e-06 | 1.5968e-06 | 0.043259 | 0.043259 | 0.043259 | 0.98992 | -0.19315 | 0.98983 | -0.19502 | 11.8844
6 | 0.0027583 | 0.00069097 | -0.0027581 | -0.00069125 | 2.0736e-07 | -2.8329e-07 | 0.0041399 | 0.00414 | 0.00414 | 0.99141 | -0.16444 | 0.99133 | -0.16602 | 1.1374
7 | 0.0053103 | 0.0013299 | -0.0053092 | -0.0013298 | 1.155e-06 | 1.1411e-07 | 0.0079699 | 0.0079702 | 0.0079702 | 0.99141 | -0.16444 | 0.99118 | -0.16901 | 2.1896
8 | 0.0012591 | 0.00031529 | -0.0012591 | -0.00031536 | 8.4691e-09 | -7.8516e-08 | 0.0018761 | 0.0018762 | 0.0018762 | 0.99859 | -0.02671 | 0.99858 | -0.026851 | 0.51543
9 | 0.025643 | 0.0065817 | -0.025609 | -0.0065608 | 3.3965e-05 | 2.0929e-05 | 0.038266 | 0.038266 | 0.038266 | 0.99859 | -0.02671 | 0.99715 | -0.054041 | 10.5127
10 | -0.083261 | -0.021218 | 0.083368 | 0.021287 | 0.00010747 | 6.8538e-05 | 0.12419 | 0.12419 | 0.12419 | 0.99859 | -0.02671 | 1 | 0 | 34.1187
11 | 0.0012591 | 0.00031536 | -0.0012591 | -0.00031556 | 2.1215e-08 | -1.9666e-07 | 0.0018762 | 0.0018763 | 0.0018763 | 0.99858 | -0.026851 | 0.99857 | -0.027205 | 0.51545
12 | 0.025609 | 0.0065608 | -0.025546 | -0.006522 | 6.2908e-05 | 3.8771e-05 | 0.038266 | 0.038267 | 0.038267 | 0.99715 | -0.054041 | 0.99447 | -0.10487 | 10.5129
13 | 0.0028819 | 0.00072207 | -0.0028817 | -0.00072223 | 1.2644e-07 | -1.5962e-07 | 0.0042882 | 0.0042883 | 0.0042883 | 1 | 0 | 0.99995 | -0.0009211 | 1.1781
14 | 0.02628 | 0.0066355 | -0.026268 | -0.0066282 | 1.1878e-05 | 7.3413e-06 | 0.039524 | 0.039525 | 0.039525 | 0.98983 | -0.19502 | 0.98934 | -0.20445 | 10.8584
15 | 0.024692 | 0.006308 | -0.024653 | -0.0062839 | 3.9192e-05 | 2.4093e-05 | 0.036989 | 0.036989 | 0.036989 | 0.99447 | -0.10487 | 0.99275 | -0.13775 | 10.162
16 | 0.0008013 | 0.00020002 | -0.00080127 | -0.00020082 | 3.4331e-08 | -7.9357e-07 | 0.0012027 | 0.001203 | 0.001203 | 0.99118 | -0.16901 | 0.99113 | -0.16991 | 0.33049
17 | 0.026268 | 0.0066282 | -0.026225 | -0.0066018 | 4.2731e-05 | 2.6413e-05 | 0.039525 | 0.039525 | 0.039525 | 0.98934 | -0.20445 | 0.98758 | -0.23848 | 10.8585
18 | 0.024653 | 0.0062839 | -0.024338 | -0.0060901 | 0.00031513 | 0.00019385 | 0.036989 | 0.036992 | 0.036992 | 0.99275 | -0.13775 | 0.9789 | -0.4062 | 10.1627
19 | 0.016326 | 0.00411 | -0.016223 | -0.0040496 | 0.00010336 | 6.0399e-05 | 0.024645 | 0.024647 | 0.024647 | 0.98602 | -0.26876 | 0.97921 | -0.40204 | 6.771
20 | -0.016326 | -0.00411 | 0.016338 | 0.0041171 | 1.2189e-05 | 7.118e-06 | 0.024645 | 0.024644 | 0.024645 | 0.98602 | -0.26876 | 0.98682 | -0.25315 | 6.7705
21 | 0.013432 | 0.0033501 | -0.01343 | -0.0033493 | 1.5534e-06 | 8.6907e-07 | 0.020406 | 0.020406 | 0.020406 | 0.97921 | -0.40204 | 0.97908 | -0.40448 | 5.606
22 | -0.026207 | -0.0065904 | 0.026225 | 0.0066018 | 1.8375e-05 | 1.1359e-05 | 0.039525 | 0.039525 | 0.039525 | 0.98682 | -0.25315 | 0.98758 | -0.23848 | 10.8585
23 | 0.0088644 | 0.0022223 | -0.0088446 | -0.0022133 | 1.9819e-05 | 9.0314e-06 | 0.013472 | 0.013474 | 0.013474 | 0.97908 | -0.40448 | 0.97669 | -0.45149 | 3.7016
24 | 0.004566 | 0.001127 | -0.004559 | -0.0011273 | 7.0475e-06 | -3.9679e-07 | 0.0069333 | 0.006935 | 0.006935 | 0.97908 | -0.40448 | 0.97743 | -0.43726 | 1.9052
25 | 0.0059162 | 0.0014798 | -0.0059154 | -0.0014796 | 8.4374e-07 | 1.9338e-07 | 0.0090125 | 0.0090126 | 0.0090126 | 0.97669 | -0.45149 | 0.97654 | -0.45448 | 2.476
26 | 0.0029283 | 0.00073346 | -0.0029281 | -0.00073373 | 2.6199e-07 | -2.7158e-07 | 0.0044612 | 0.0044614 | 0.0044614 | 0.97669 | -0.45149 | 0.9766 | -0.45336 | 1.2257
27 | 0.004559 | 0.0011273 | -0.0045588 | -0.0011274 | 1.8088e-07 | -9.9336e-09 | 0.006935 | 0.0069351 | 0.0069351 | 0.97743 | -0.43726 | 0.97739 | -0.4381 | 1.9052
28 | -0.012032 | -0.0030017 | 0.012039 | 0.0030054 | 6.8301e-06 | 3.6883e-06 | 0.0183 | 0.0183 | 0.0183 | 0.97808 | -0.42227 | 0.97869 | -0.41032 | 5.0276
29 | 0.0043604 | 0.001079 | -0.004359 | -0.0010791 | 1.4455e-06 | -1.754e-07 | 0.0066288 | 0.0066292 | 0.0066292 | 0.97808 | -0.42227 | 0.97773 | -0.42929 | 1.8212
30 | -0.013051 | -0.0032589 | 0.013053 | 0.0032603 | 2.5535e-06 | 1.4168e-06 | 0.019838 | 0.019838 | 0.019838 | 0.97869 | -0.41032 | 0.9789 | -0.4062 | 5.4501
31 | 0.004359 | 0.0010791 | -0.004356 | -0.0010795 | 2.9772e-06 | -3.5832e-07 | 0.0066292 | 0.00663 | 0.00663 | 0.97773 | -0.42929 | 0.977 | -0.44376 | 1.8214
32 | 0.011285 | 0.0028298 | -0.011283 | -0.0028288 | 1.7753e-06 | 9.3399e-07 | 0.017154 | 0.017154 | 0.017154 | 0.9789 | -0.4062 | 0.97873 | -0.4095 | 4.7127
33 | 0.0022843 | 0.00056556 | -0.002282 | -0.00057047 | 2.3183e-06 | -4.91e-06 | 0.0034766 | 0.0034789 | 0.0034789 | 0.977 | -0.44376 | 0.97592 | -0.4652 | 0.95574
34 | 0.0020717 | 0.00051393 | -0.0020704 | -0.0005175 | 1.3158e-06 | -3.5714e-06 | 0.0031534 | 0.003155 | 0.003155 | 0.977 | -0.44376 | 0.97632 | -0.45716 | 0.86676
35 | 0.010409 | 0.0026097 | -0.010396 | -0.0026036 | 1.2108e-05 | 6.1307e-06 | 0.015825 | 0.015826 | 0.015826 | 0.97873 | -0.4095 | 0.97749 | -0.43393 | 4.3477
36 | 0.00099245 | 0.00024826 | -0.00099241 | -0.00024872 | 3.3553e-08 | -4.668e-07 | 0.001513 | 0.0015132 | 0.0015132 | 0.97592 | -0.4652 | 0.97588 | -0.46591 | 0.41572
37 | 0.0012895 | 0.00032222 | -0.0012894 | -0.00032295 | 9.2e-08 | -7.3417e-07 | 0.0019658 | 0.0019661 | 0.0019661 | 0.97592 | -0.4652 | 0.97584 | -0.46669 | 0.54014
38 | 0.00061884 | 0.00015371 | -0.0006188 | -0.00015509 | 3.743e-08 | -1.3799e-06 | 0.00094268 | 0.00094318 | 0.00094318 | 0.97632 | -0.45716 | 0.97626 | -0.45844 | 0.25911
39 | 0.0068223 | 0.0017091 | -0.006821 | -0.0017087 | 1.3707e-06 | 4.5251e-07 | 0.010385 | 0.010385 | 0.010385 | 0.97749 | -0.43393 | 0.97727 | -0.43815 | 2.8531
40 | 0.0035741 | 0.00089448 | -0.0035733 | -0.00089487 | 8.1177e-07 | -3.9698e-07 | 0.0054404 | 0.0054407 | 0.0054407 | 0.97749 | -0.43393 | 0.97725 | -0.43871 | 1.4947
41 | 0.0012894 | 0.00032295 | -0.0012894 | -0.00032316 | 2.5939e-08 | -2.0693e-07 | 0.0019661 | 0.0019662 | 0.0019662 | 0.97584 | -0.46669 | 0.97582 | -0.46712 | 0.54017
42 | -0.003573 | -0.00089505 | 0.0035733 | 0.00089487 | 3.629e-07 | -1.7729e-07 | 0.0054409 | 0.0054407 | 0.0054409 | 0.97714 | -0.44084 | 0.97725 | -0.43871 | 1.4947
43 | 0.00070823 | 0.00017708 | -0.00070822 | -0.0001775 | 1.4736e-08 | -4.138e-07 | 0.0010784 | 0.0010785 | 0.0010785 | 0.97714 | -0.44084 | 0.97712 | -0.44128 | 0.2963
44 | 0.0063627 | 0.0015938 | -0.0063616 | -0.0015935 | 1.1003e-06 | 3.1255e-07 | 0.0096876 | 0.0096877 | 0.0096877 | 0.97727 | -0.43815 | 0.97709 | -0.44179 | 2.6615
45 | 0.0043487 | 0.001089 | -0.0043476 | -0.0010892 | 1.1373e-06 | -1.3799e-07 | 0.0066224 | 0.0066227 | 0.0066227 | 0.97709 | -0.44179 | 0.97681 | -0.44728 | 1.8194
46 | -0.0043464 | -0.0010893 | 0.0043472 | 0.0010892 | 7.9821e-07 | -9.6363e-08 | 0.006623 | 0.0066228 | 0.006623 | 0.97651 | -0.45312 | 0.97671 | -0.44927 | 1.8195
47 | -0.0043472 | -0.0010892 | 0.0043476 | 0.0010892 | 4.1187e-07 | -4.9833e-08 | 0.0066228 | 0.0066227 | 0.0066228 | 0.97671 | -0.44927 | 0.97681 | -0.44728 | 1.8194
48 | 0.005358 | 0.0013428 | -0.0053574 | -0.0013427 | 5.8648e-07 | 8.1842e-08 | 0.0081643 | 0.0081644 | 0.0081644 | 0.97654 | -0.45448 | 0.97642 | -0.45678 | 2.243
49 | 0.00055738 | 0.00013686 | -0.00055737 | -0.00013733 | 1.0313e-08 | -4.7142e-07 | 0.00084831 | 0.00084848 | 0.00084848 | 0.97654 | -0.45448 | 0.97652 | -0.45488 | 0.2331
50 | 0.0019241 | 0.00048213 | -0.0019241 | -0.00048223 | 3.1976e-08 | -1.0367e-07 | 0.0029317 | 0.0029318 | 0.0029318 | 0.9766 | -0.45336 | 0.97658 | -0.45371 | 0.80543
51 | 0.00036917 | 7.7333e-05 | -0.0003691 | -8.4557e-05 | 6.7756e-08 | -7.2244e-06 | 0.00055701 | 0.00055931 | 0.00055931 | 0.97739 | -0.4381 | 0.9772 | -0.44232 | 0.15366
52 | 0.0003691 | 8.4557e-05 | -0.00036903 | -9.2335e-05 | 7.3633e-08 | -7.7775e-06 | 0.00055931 | 0.000562 | 0.000562 | 0.9772 | -0.44232 | 0.97698 | -0.44665 | 0.1544
53 | 0.00055737 | 0.00013733 | -0.00055732 | -0.00013968 | 5.1472e-08 | -2.3497e-06 | 0.00084848 | 0.00084933 | 0.00084933 | 0.97652 | -0.45488 | 0.97642 | -0.45683 | 0.23333
54 | 0.00036903 | 9.2335e-05 | -0.00036903 | -9.2487e-05 | 1.4493e-09 | -1.5229e-07 | 0.000562 | 0.00056206 | 0.00056206 | 0.97698 | -0.44665 | 0.97698 | -0.44673 | 0.15441

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.088863 | 0.022251

## res_load
| p_mw | q_mvar
0 | 0.019134 | 0.0047955
1 | 0.00096348 | 0.00024147
2 | 0.0024844 | 0.00062264
3 | 0.00085391 | 0.00021401
4 | 0.0012591 | 0.00031556
5 | 0.0027581 | 0.00069125
6 | 0.0045079 | 0.0011298
7 | 0.0028817 | 0.00072223
8 | 0.00080127 | 0.00020082
9 | 0.0027908 | 0.00069944
10 | 0.0098686 | 0.0024733
11 | 0.0076719 | 0.0019227
12 | 0.0010116 | 0.00025353
13 | 0.00087423 | 0.0002191
14 | 0.0014516 | 0.00036379
15 | 0.00099241 | 0.00024872
16 | 0.0006188 | 0.00015509
17 | 0.0028647 | 0.00071797
18 | 0.00070822 | 0.0001775
19 | 0.0004583 | 0.00011486
20 | 0.0020128 | 0.00050447
21 | 0.0043464 | 0.0010893
22 | 0.0012894 | 0.00032316
23 | 0.0010039 | 0.00025161
24 | 0.0041896 | 0.00105
25 | 0.0053574 | 0.0013427
26 | 0.0019241 | 0.00048223
27 | 0.00036903 | 9.2487e-05
28 | 0.00055732 | 0.00013968

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1