## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1362-22_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1362-22_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1362-22_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1362-22_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1362-22_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1362-22_0_4_node_24 | 0.4 | n |  | TRUE
6 | bus_LV_1362-22_0_4_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_1362-22_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1362-22_0_4_node_93 | 0.4 | n |  | TRUE
9 | bus_LV_1362-22_0_4_node_94 | 0.4 | n |  | TRUE
10 | bus_LV_1362-22_0_4_node_91 | 0.4 | n |  | TRUE
11 | bus_LV_1362-22_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1362-22_0_4_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_1362-22_0_4_node_89 | 0.4 | n |  | TRUE
14 | bus_LV_1362-22_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1362-22_0_4_node_58 | 0.4 | n |  | TRUE
16 | bus_LV_1362-22_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1362-22_0_4_node_59 | 0.4 | n |  | TRUE
18 | bus_LV_1362-22_0_4_node_137 | 0.4 | n |  | TRUE
19 | bus_LV_1362-22_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1362-22_0_4_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_1362-22_0_4_node_132 | 0.4 | n |  | TRUE
22 | bus_LV_1362-22_0_4_node_67 | 0.4 | n |  | TRUE
23 | bus_LV_1362-22_0_4_node_110 | 0.4 | n |  | TRUE
24 | bus_LV_1362-22_0_4_node_65 | 0.4 | n |  | TRUE
25 | bus_LV_1362-22_0_4_node_66 | 0.4 | n |  | TRUE
26 | bus_LV_1362-22_0_4_node_133 | 0.4 | n |  | TRUE
27 | bus_LV_1362-22_0_4_node_98 | 0.4 | n |  | TRUE
28 | bus_LV_1362-22_0_4_node_114 | 0.4 | n |  | TRUE
29 | bus_LV_1362-22_0_4_node_92 | 0.4 | n |  | TRUE
30 | bus_LV_1362-22_0_4_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_1362-22_0_4_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_1362-22_0_4_node_88 | 0.4 | n |  | TRUE
33 | bus_LV_1362-22_0_4_node_75 | 0.4 | n |  | TRUE
34 | bus_LV_1362-22_0_4_node_138 | 0.4 | n |  | TRUE
35 | bus_LV_1362-22_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1362-22_0_4_node_112 | 0.4 | n |  | TRUE
37 | bus_LV_1362-22_0_4_node_127 | 0.4 | n |  | TRUE
38 | bus_LV_1362-22_0_4_node_126 | 0.4 | n |  | TRUE
39 | bus_LV_1362-22_0_4_node_139 | 0.4 | n |  | TRUE
40 | bus_LV_1362-22_0_4_node_106 | 0.4 | n |  | TRUE
41 | bus_LV_1362-22_0_4_node_120 | 0.4 | n |  | TRUE
42 | bus_LV_1362-22_0_4_node_119 | 0.4 | n |  | TRUE
43 | bus_LV_1362-22_0_4_node_17 | 0.4 | n |  | TRUE
44 | bus_LV_1362-22_0_4_node_19 | 0.4 | n |  | TRUE
45 | bus_LV_1362-22_0_4_node_87 | 0.4 | n |  | TRUE
46 | bus_LV_1362-22_0_4_node_74 | 0.4 | n |  | TRUE
47 | bus_LV_1362-22_0_4_node_122 | 0.4 | n |  | TRUE
48 | bus_LV_1362-22_0_4_node_72 | 0.4 | n |  | TRUE
49 | bus_LV_1362-22_0_4_node_21 | 0.4 | n |  | TRUE
50 | bus_LV_1362-22_0_4_node_25 | 0.4 | n |  | TRUE
51 | bus_LV_1362-22_0_4_node_26 | 0.4 | n |  | TRUE
52 | bus_LV_1362-22_0_4_node_27 | 0.4 | n |  | TRUE
53 | bus_LV_1362-22_0_4_node_28 | 0.4 | n |  | TRUE
54 | bus_LV_1362-22_0_4_node_29 | 0.4 | n |  | TRUE
55 | bus_LV_1362-22_0_4_node_30 | 0.4 | n |  | TRUE
56 | bus_LV_1362-22_0_4_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_1362-22_0_4_node_47 | 0.4 | n |  | TRUE
58 | bus_LV_1362-22_0_4_node_40 | 0.4 | n |  | TRUE
59 | bus_LV_1362-22_0_4_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_1362-22_0_4_node_48 | 0.4 | n |  | TRUE
61 | bus_LV_1362-22_0_4_node_38 | 0.4 | n |  | TRUE
62 | bus_LV_1362-22_0_4_node_31 | 0.4 | n |  | TRUE
63 | bus_LV_1362-22_0_4_node_33 | 0.4 | n |  | TRUE
64 | bus_LV_1362-22_0_4_node_32 | 0.4 | n |  | TRUE
65 | bus_LV_1362-22_0_4_node_34 | 0.4 | n |  | TRUE
66 | bus_LV_1362-22_0_4_node_35 | 0.4 | n |  | TRUE
67 | bus_LV_1362-22_0_4_node_36 | 0.4 | n |  | TRUE
68 | bus_LV_1362-22_0_4_node_117 | 0.4 | n |  | TRUE
69 | bus_LV_1362-22_0_4_node_130 | 0.4 | n |  | TRUE
70 | bus_LV_1362-22_0_4_node_118 | 0.4 | n |  | TRUE
71 | bus_LV_1362-22_0_4_node_115 | 0.4 | n |  | TRUE
72 | bus_LV_1362-22_0_4_node_131 | 0.4 | n |  | TRUE
73 | bus_LV_1362-22_0_4_node_37 | 0.4 | n |  | TRUE
74 | bus_LV_1362-22_0_4_node_39 | 0.4 | n |  | TRUE
75 | bus_LV_1362-22_0_4_node_41 | 0.4 | n |  | TRUE
76 | bus_LV_1362-22_0_4_node_69 | 0.4 | n |  | TRUE
77 | bus_LV_1362-22_0_4_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_1362-22_0_4_node_42 | 0.4 | n |  | TRUE
79 | bus_LV_1362-22_0_4_node_43 | 0.4 | n |  | TRUE
80 | bus_LV_1362-22_0_4_node_44 | 0.4 | n |  | TRUE
81 | bus_LV_1362-22_0_4_node_45 | 0.4 | n |  | TRUE
82 | bus_LV_1362-22_0_4_node_46 | 0.4 | n |  | TRUE
83 | bus_LV_1362-22_0_4_node_79 | 0.4 | n |  | TRUE
84 | bus_LV_1362-22_0_4_node_80 | 0.4 | n |  | TRUE
85 | bus_LV_1362-22_0_4_node_51 | 0.4 | n |  | TRUE
86 | bus_LV_1362-22_0_4_node_52 | 0.4 | n |  | TRUE
87 | bus_LV_1362-22_0_4_node_53 | 0.4 | n |  | TRUE
88 | bus_LV_1362-22_0_4_node_54 | 0.4 | n |  | TRUE
89 | bus_LV_1362-22_0_4_node_56 | 0.4 | n |  | TRUE
90 | bus_LV_1362-22_0_4_node_57 | 0.4 | n |  | TRUE
91 | bus_LV_1362-22_0_4_node_76 | 0.4 | n |  | TRUE
92 | bus_LV_1362-22_0_4_node_140 | 0.4 | n |  | TRUE
93 | bus_LV_1362-22_0_4_node_107 | 0.4 | n |  | TRUE
94 | bus_LV_1362-22_0_4_node_108 | 0.4 | n |  | TRUE
95 | bus_LV_1362-22_0_4_node_77 | 0.4 | n |  | TRUE
96 | bus_LV_1362-22_0_4_node_141 | 0.4 | n |  | TRUE
97 | bus_LV_1362-22_0_4_node_73 | 0.4 | n |  | TRUE
98 | bus_LV_1362-22_0_4_node_60 | 0.4 | n |  | TRUE
99 | bus_LV_1362-22_0_4_node_61 | 0.4 | n |  | TRUE
100 | bus_LV_1362-22_0_4_node_62 | 0.4 | n |  | TRUE
101 | bus_LV_1362-22_0_4_node_63 | 0.4 | n |  | TRUE
102 | bus_LV_1362-22_0_4_node_64 | 0.4 | n |  | TRUE
103 | bus_LV_1362-22_0_4_node_90 | 0.4 | n |  | TRUE
104 | bus_LV_1362-22_0_4_node_121 | 0.4 | n |  | TRUE
105 | bus_LV_1362-22_0_4_node_111 | 0.4 | n |  | TRUE
106 | bus_LV_1362-22_0_4_node_70 | 0.4 | n |  | TRUE
107 | bus_LV_1362-22_0_4_node_71 | 0.4 | n |  | TRUE
108 | bus_LV_1362-22_0_4_node_144 | 0.4 | n |  | TRUE
109 | bus_LV_1362-22_0_4_node_146 | 0.4 | n |  | TRUE
110 | bus_LV_1362-22_0_4_node_143 | 0.4 | n |  | TRUE
111 | bus_LV_1362-22_0_4_node_136 | 0.4 | n |  | TRUE
112 | bus_LV_1362-22_0_4_node_78 | 0.4 | n |  | TRUE
113 | bus_LV_1362-22_0_4_node_124 | 0.4 | n |  | TRUE
114 | bus_LV_1362-22_0_4_node_96 | 0.4 | n |  | TRUE
115 | bus_LV_1362-22_0_4_node_81 | 0.4 | n |  | TRUE
116 | bus_LV_1362-22_0_4_node_113 | 0.4 | n |  | TRUE
117 | bus_LV_1362-22_0_4_node_82 | 0.4 | n |  | TRUE
118 | bus_LV_1362-22_0_4_node_83 | 0.4 | n |  | TRUE
119 | bus_LV_1362-22_0_4_node_84 | 0.4 | n |  | TRUE
120 | bus_LV_1362-22_0_4_node_85 | 0.4 | n |  | TRUE
121 | bus_LV_1362-22_0_4_node_86 | 0.4 | n |  | TRUE
122 | bus_LV_1362-22_0_4_node_95 | 0.4 | n |  | TRUE
123 | bus_LV_1362-22_0_4_node_116 | 0.4 | n |  | TRUE
124 | bus_LV_1362-22_0_4_node_123 | 0.4 | n |  | TRUE
125 | bus_LV_1362-22_0_4_node_97 | 0.4 | n |  | TRUE
126 | bus_LV_1362-22_0_4_node_125 | 0.4 | n |  | TRUE
127 | bus_LV_1362-22_0_4_node_99 | 0.4 | n |  | TRUE
128 | bus_LV_1362-22_0_4_node_100 | 0.4 | n |  | TRUE
129 | bus_LV_1362-22_0_4_node_128 | 0.4 | n |  | TRUE
130 | bus_LV_1362-22_0_4_node_129 | 0.4 | n |  | TRUE
131 | bus_LV_1362-22_0_4_node_101 | 0.4 | n |  | TRUE
132 | bus_LV_1362-22_0_4_node_102 | 0.4 | n |  | TRUE
133 | bus_LV_1362-22_0_4_node_103 | 0.4 | n |  | TRUE
134 | bus_LV_1362-22_0_4_node_104 | 0.4 | n |  | TRUE
135 | bus_LV_1362-22_0_4_node_105 | 0.4 | n |  | TRUE
136 | bus_LV_1362-22_0_4_node_134 | 0.4 | n |  | TRUE
137 | bus_LV_1362-22_0_4_node_148 | 0.4 | n |  | TRUE
138 | bus_LV_1362-22_0_4_node_135 | 0.4 | n |  | TRUE
139 | bus_LV_1362-22_0_4_node_109 | 0.4 | n |  | TRUE
140 | bus_LV_1362-22_0_4_node_149 | 0.4 | n |  | TRUE
141 | bus_LV_1362-22_0_4_node_147 | 0.4 | n |  | TRUE
142 | bus_LV_1362-22_0_4_node_150 | 0.4 | n |  | TRUE
143 | bus_LV_1362-22_0_4_node_151 | 0.4 | n |  | TRUE
144 | bus_LV_1362-22_0_4_node_142 | 0.4 | n |  | TRUE
145 | bus_LV_1362-22_0_4_node_145 | 0.4 | n |  | TRUE
146 | bus_MV_1_0_node_116 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1362-22_0_4_load_0 | 0 | 0.00034422 | 8.627e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1362-22_0_4_load_24 | 5 | 0.0030207 | 0.00075706 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1362-22_0_4_load_93 | 8 | 0.0014428 | 0.00036159 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1362-22_0_4_load_91 | 10 | 0.0020675 | 0.00051815 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1362-22_0_4_load_89 | 13 | 0.0038731 | 0.00097069 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1362-22_0_4_load_58 | 15 | 0.0024327 | 0.0006097 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1362-22_0_4_load_137 | 18 | 0.0063005 | 0.0015791 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1362-22_0_4_load_23 | 20 | 0.0038937 | 0.00097586 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1362-22_0_4_load_132 | 21 | 0.0033601 | 0.00084213 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1362-22_0_4_load_67 | 22 | 0.0027055 | 0.00067807 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1362-22_0_4_load_65 | 24 | 0.004895 | 0.0012268 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1362-22_0_4_load_66 | 25 | 0.0026234 | 0.00065748 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1362-22_0_4_load_133 | 26 | 0.0020145 | 0.00050488 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1362-22_0_4_load_98 | 27 | 0.0013559 | 0.00033982 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1362-22_0_4_load_92 | 29 | 0.0057952 | 0.0014524 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1362-22_0_4_load_20 | 30 | 0.0019993 | 0.00050108 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1362-22_0_4_load_16 | 31 | 0.0016093 | 0.00040332 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1362-22_0_4_load_88 | 32 | 0.003659 | 0.00091703 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1362-22_0_4_load_75 | 33 | 0.0050068 | 0.0012548 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1362-22_0_4_load_138 | 34 | 0.0020799 | 0.00052127 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1362-22_0_4_load_22 | 35 | 0.0006575 | 0.00016478 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1362-22_0_4_load_112 | 36 | 0.0013361 | 0.00033486 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1362-22_0_4_load_127 | 37 | 0.0073529 | 0.0018428 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1362-22_0_4_load_126 | 38 | 0.011371 | 0.00285 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1362-22_0_4_load_139 | 39 | 0.0017522 | 0.00043914 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1362-22_0_4_load_106 | 40 | 0.0017216 | 0.00043148 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1362-22_0_4_load_120 | 41 | 0.0021377 | 0.00053575 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1362-22_0_4_load_119 | 42 | 0.0046046 | 0.001154 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1362-22_0_4_load_17 | 43 | 0.0014607 | 0.0003661 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1362-22_0_4_load_19 | 44 | 0.0021816 | 0.00054675 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1362-22_0_4_load_87 | 45 | 0.0010523 | 0.00026373 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1362-22_0_4_load_74 | 46 | 0.0018839 | 0.00047214 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1362-22_0_4_load_122 | 47 | 0.002176 | 0.00054535 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1362-22_0_4_load_72 | 48 | 0.0042284 | 0.0010597 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1362-22_0_4_load_21 | 49 | 0.00040348 | 0.00010112 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1362-22_0_4_load_25 | 50 | 0.0017876 | 0.00044802 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1362-22_0_4_load_26 | 51 | 0.0023168 | 0.00058063 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1362-22_0_4_load_28 | 53 | 0.0038395 | 0.00096228 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1362-22_0_4_load_29 | 54 | 0.0024687 | 0.00061872 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1362-22_0_4_load_30 | 55 | 0.0017132 | 0.00042938 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1362-22_0_4_load_49 | 56 | 0.0037126 | 0.00093046 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1362-22_0_4_load_47 | 57 | 0.0038876 | 0.00097433 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1362-22_0_4_load_40 | 58 | 0.0019971 | 0.00050051 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1362-22_0_4_load_50 | 59 | 0.0047067 | 0.0011796 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1362-22_0_4_load_48 | 60 | 0.001727 | 0.00043282 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1362-22_0_4_load_38 | 61 | 0.0020005 | 0.00050138 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1362-22_0_4_load_31 | 62 | 0.0063046 | 0.0015801 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1362-22_0_4_load_32 | 64 | 0.0016215 | 0.00040639 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1362-22_0_4_load_34 | 65 | 0.0042251 | 0.0010589 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1362-22_0_4_load_35 | 66 | 0.0033772 | 0.00084641 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1362-22_0_4_load_36 | 67 | 0.0045718 | 0.0011458 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1362-22_0_4_load_130 | 69 | 0.0019784 | 0.00049585 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1362-22_0_4_load_118 | 70 | 0.0023065 | 0.00057806 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1362-22_0_4_load_115 | 71 | 0.0049413 | 0.0012384 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1362-22_0_4_load_131 | 72 | 0.0019809 | 0.00049645 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1362-22_0_4_load_37 | 73 | 0.0042485 | 0.0010648 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1362-22_0_4_load_39 | 74 | 0.0017192 | 0.00043086 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1362-22_0_4_load_41 | 75 | 0.001806 | 0.00045262 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1362-22_0_4_load_69 | 76 | 0.0016712 | 0.00041884 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1362-22_0_4_load_68 | 77 | 0.0038969 | 0.00097667 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1362-22_0_4_load_42 | 78 | 0.0043237 | 0.0010836 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1362-22_0_4_load_43 | 79 | 0.0014947 | 0.00037461 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1362-22_0_4_load_44 | 80 | 0.0021741 | 0.00054489 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1362-22_0_4_load_45 | 81 | 0.004696 | 0.0011769 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1362-22_0_4_load_46 | 82 | 0.0020576 | 0.00051567 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1362-22_0_4_load_79 | 83 | 0.0026369 | 0.00066086 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1362-22_0_4_load_80 | 84 | 0.0079688 | 0.0019972 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1362-22_0_4_load_51 | 85 | 0.0028104 | 0.00070436 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1362-22_0_4_load_52 | 86 | 0.0041929 | 0.0010509 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1362-22_0_4_load_53 | 87 | 0.010317 | 0.0025858 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1362-22_0_4_load_56 | 89 | 0.0073948 | 0.0018533 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1362-22_0_4_load_57 | 90 | 0.003131 | 0.00078471 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1362-22_0_4_load_140 | 92 | 0.003103 | 0.00077767 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1362-22_0_4_load_107 | 93 | 0.01051 | 0.002634 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1362-22_0_4_load_108 | 94 | 0.0099491 | 0.0024935 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1362-22_0_4_load_77 | 95 | 0.0046018 | 0.0011533 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1362-22_0_4_load_141 | 96 | 0.0038357 | 0.00096131 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1362-22_0_4_load_73 | 97 | 0.0055608 | 0.0013937 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1362-22_0_4_load_60 | 98 | 0.0021446 | 0.0005375 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1362-22_0_4_load_61 | 99 | 0.0016124 | 0.0004041 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1362-22_0_4_load_62 | 100 | 0.00089932 | 0.00022539 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1362-22_0_4_load_63 | 101 | 0.0024583 | 0.00061611 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1362-22_0_4_load_90 | 103 | 0.0034557 | 0.00086608 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1362-22_0_4_load_121 | 104 | 0.0018986 | 0.00047582 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1362-22_0_4_load_111 | 105 | 0.0013191 | 0.0003306 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1362-22_0_4_load_70 | 106 | 0.0022109 | 0.00055411 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1362-22_0_4_load_144 | 108 | 0.0022409 | 0.00056162 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1362-22_0_4_load_146 | 109 | 0.0046843 | 0.001174 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1362-22_0_4_load_143 | 110 | 0.0041848 | 0.0010488 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1362-22_0_4_load_78 | 112 | 0.001707 | 0.00042781 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1362-22_0_4_load_124 | 113 | 0.0018636 | 0.00046706 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1362-22_0_4_load_81 | 115 | 0.0071906 | 0.0018021 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1362-22_0_4_load_113 | 116 | 0.016709 | 0.0041877 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1362-22_0_4_load_82 | 117 | 0.0048749 | 0.0012218 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1362-22_0_4_load_83 | 118 | 0.017139 | 0.0042954 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1362-22_0_4_load_84 | 119 | 0.0087945 | 0.0022041 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1362-22_0_4_load_85 | 120 | 0.005436 | 0.0013624 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1362-22_0_4_load_86 | 121 | 0.010673 | 0.0026748 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1362-22_0_4_load_95 | 122 | 0.0044762 | 0.0011218 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1362-22_0_4_load_116 | 123 | 0.0023112 | 0.00057924 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1362-22_0_4_load_123 | 124 | 0.00303 | 0.00075939 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1362-22_0_4_load_97 | 125 | 0.0015422 | 0.00038652 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1362-22_0_4_load_125 | 126 | 0.0017412 | 0.00043638 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1362-22_0_4_load_99 | 127 | 0.0015637 | 0.0003919 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1362-22_0_4_load_100 | 128 | 0.0074857 | 0.0018761 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1362-22_0_4_load_101 | 131 | 0.0027218 | 0.00068214 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1362-22_0_4_load_102 | 132 | 0.0017071 | 0.00042783 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1362-22_0_4_load_104 | 134 | 0.0027072 | 0.0006785 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1362-22_0_4_load_105 | 135 | 0.0013782 | 0.00034541 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1362-22_0_4_load_134 | 136 | 0.0027353 | 0.00068553 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1362-22_0_4_load_148 | 137 | 0.0028132 | 0.00070505 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1362-22_0_4_load_135 | 138 | 0.0026142 | 0.00065517 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1362-22_0_4_load_109 | 139 | 0.016485 | 0.0041315 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1362-22_0_4_load_149 | 140 | 0.0030719 | 0.00076989 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_1362-22_0_4_load_150 | 142 | 0.0020338 | 0.00050972 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_1362-22_0_4_load_151 | 143 | 0.0098049 | 0.0024573 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_1362-22_0_4_load_142 | 144 | 0.0046766 | 0.0011721 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_1362-22_0_4_load_145 | 145 | 0.0040976 | 0.0010269 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 118 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1362-22_0_4_line_0 |  | 0 | 1 | 0.035921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1362-22_0_4_line_1 |  | 0 | 2 | 0.061125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1362-22_0_4_line_2 |  | 1 | 3 | 0.10418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1362-22_0_4_line_3 |  | 2 | 4 | 0.039611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1362-22_0_4_line_4 |  | 3 | 6 | 0.014446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1362-22_0_4_line_5 |  | 4 | 5 | 0.072012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1362-22_0_4_line_6 |  | 6 | 19 | 0.012946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1362-22_0_4_line_7 |  | 6 | 20 | 0.056229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1362-22_0_4_line_8 |  | 7 | 8 | 0.0097041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1362-22_0_4_line_9 |  | 7 | 9 | 0.017742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1362-22_0_4_line_10 |  | 7 | 10 | 0.034415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1362-22_0_4_line_11 |  | 8 | 26 | 0.14755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1362-22_0_4_line_12 |  | 9 | 27 | 0.0076898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1362-22_0_4_line_13 |  | 9 | 28 | 0.02126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1362-22_0_4_line_14 |  | 10 | 29 | 0.031548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1362-22_0_4_line_15 |  | 11 | 12 | 0.020555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1362-22_0_4_line_16 |  | 11 | 13 | 0.015892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1362-22_0_4_line_17 |  | 12 | 30 | 0.025976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1362-22_0_4_line_18 |  | 12 | 31 | 0.023456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1362-22_0_4_line_19 |  | 12 | 14 | 0.00495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1362-22_0_4_line_20 |  | 13 | 32 | 0.032042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1362-22_0_4_line_21 |  | 14 | 15 | 0.041928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1362-22_0_4_line_22 |  | 16 | 17 | 0.012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1362-22_0_4_line_23 |  | 16 | 18 | 0.024256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1362-22_0_4_line_24 |  | 17 | 33 | 0.0044346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1362-22_0_4_line_25 |  | 18 | 34 | 0.016786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1362-22_0_4_line_26 |  | 19 | 21 | 0.028506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1362-22_0_4_line_27 |  | 20 | 35 | 0.035272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1362-22_0_4_line_28 |  | 21 | 26 | 0.013335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1362-22_0_4_line_29 |  | 22 | 23 | 0.018786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1362-22_0_4_line_30 |  | 23 | 105 | 0.010758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1362-22_0_4_line_31 |  | 23 | 36 | 0.019928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1362-22_0_4_line_32 |  | 24 | 25 | 0.0055014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1362-22_0_4_line_33 |  | 25 | 101 | 0.020789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1362-22_0_4_line_34 |  | 27 | 125 | 0.0056767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1362-22_0_4_line_35 |  | 28 | 116 | 0.0049534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1362-22_0_4_line_36 |  | 28 | 115 | 0.0068127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1362-22_0_4_line_37 |  | 30 | 46 | 0.013234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1362-22_0_4_line_38 |  | 31 | 43 | 0.00094086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1362-22_0_4_line_39 |  | 32 | 103 | 0.0013888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1362-22_0_4_line_40 |  | 33 | 97 | 0.027313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1362-22_0_4_line_41 |  | 34 | 130 | 0.011174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1362-22_0_4_line_42 |  | 35 | 49 | 0.02954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1362-22_0_4_line_43 |  | 37 | 38 | 0.021034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1362-22_0_4_line_44 |  | 38 | 129 | 0.018984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1362-22_0_4_line_45 |  | 39 | 40 | 0.0051899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1362-22_0_4_line_46 |  | 40 | 133 | 1.8019e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1362-22_0_4_line_47 |  | 41 | 42 | 0.0057204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1362-22_0_4_line_48 |  | 42 | 85 | 0.011457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1362-22_0_4_line_49 |  | 43 | 44 | 0.011495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1362-22_0_4_line_50 |  | 44 | 45 | 0.0059301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1362-22_0_4_line_51 |  | 45 | 47 | 0.0021445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1362-22_0_4_line_52 |  | 46 | 48 | 0.011314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1362-22_0_4_line_53 |  | 47 | 124 | 0.011706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1362-22_0_4_line_54 |  | 48 | 97 | 0.0030074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1362-22_0_4_line_55 |  | 50 | 51 | 8.8848e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1362-22_0_4_line_56 |  | 50 | 52 | 0.012767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1362-22_0_4_line_57 |  | 51 | 53 | 0.0035867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1362-22_0_4_line_58 |  | 52 | 54 | 0.0097914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1362-22_0_4_line_59 |  | 52 | 55 | 0.0092225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1362-22_0_4_line_60 |  | 53 | 56 | 0.017442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1362-22_0_4_line_61 |  | 54 | 57 | 0.018409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1362-22_0_4_line_62 |  | 55 | 58 | 0.0067133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1362-22_0_4_line_63 |  | 56 | 59 | 0.0053068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1362-22_0_4_line_64 |  | 57 | 60 | 0.0037055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_1362-22_0_4_line_65 |  | 58 | 61 | 0.011827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1362-22_0_4_line_66 |  | 59 | 85 | 0.012216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1362-22_0_4_line_67 |  | 60 | 66 | 0.011103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_1362-22_0_4_line_68 |  | 61 | 73 | 0.0063625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1362-22_0_4_line_69 |  | 62 | 63 | 0.012631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1362-22_0_4_line_70 |  | 63 | 66 | 0.0063307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_1362-22_0_4_line_71 |  | 63 | 67 | 0.013436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_1362-22_0_4_line_72 |  | 64 | 65 | 0.0038536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1362-22_0_4_line_73 |  | 65 | 68 | 0.012155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1362-22_0_4_line_74 |  | 67 | 69 | 0.0043061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
75 | LV_1362-22_0_4_line_75 |  | 68 | 70 | 0.011269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
76 | LV_1362-22_0_4_line_76 |  | 68 | 71 | 0.0088093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_1362-22_0_4_line_77 |  | 69 | 72 | 0.011867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
78 | LV_1362-22_0_4_line_78 |  | 70 | 140 | 0.0067859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_1362-22_0_4_line_79 |  | 71 | 123 | 0.0053966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
80 | LV_1362-22_0_4_line_80 |  | 72 | 126 | 0.006678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
81 | LV_1362-22_0_4_line_81 |  | 73 | 74 | 0.00036145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1362-22_0_4_line_82 |  | 74 | 75 | 0.018543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1362-22_0_4_line_83 |  | 75 | 76 | 0.00030476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1362-22_0_4_line_84 |  | 76 | 77 | 0.007855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1362-22_0_4_line_85 |  | 77 | 106 | 0.012258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1362-22_0_4_line_86 |  | 78 | 79 | 0.00039323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1362-22_0_4_line_87 |  | 78 | 80 | 0.011548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1362-22_0_4_line_88 |  | 79 | 81 | 0.0030085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1362-22_0_4_line_89 |  | 80 | 82 | 0.0088091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1362-22_0_4_line_90 |  | 82 | 83 | 0.0050793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1362-22_0_4_line_91 |  | 83 | 84 | 0.0076785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1362-22_0_4_line_92 |  | 84 | 115 | 0.0071227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1362-22_0_4_line_93 |  | 86 | 87 | 0.026222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1362-22_0_4_line_94 |  | 86 | 88 | 0.012171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1362-22_0_4_line_95 |  | 88 | 89 | 0.0075421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1362-22_0_4_line_96 |  | 88 | 90 | 0.017848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1362-22_0_4_line_97 |  | 89 | 91 | 0.014546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1362-22_0_4_line_98 |  | 90 | 92 | 0.00083861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1362-22_0_4_line_99 |  | 91 | 95 | 0.018016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1362-22_0_4_line_100 |  | 92 | 96 | 0.015114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1362-22_0_4_line_101 |  | 93 | 94 | 0.0045941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1362-22_0_4_line_102 |  | 94 | 139 | 0.0225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1362-22_0_4_line_103 |  | 95 | 108 | 0.01421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1362-22_0_4_line_104 |  | 96 | 144 | 0.00045265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1362-22_0_4_line_105 |  | 98 | 99 | 0.018131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1362-22_0_4_line_106 |  | 98 | 100 | 0.011326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1362-22_0_4_line_107 |  | 99 | 101 | 0.0049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1362-22_0_4_line_108 |  | 100 | 102 | 0.0025235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1362-22_0_4_line_109 |  | 102 | 103 | 0.014989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1362-22_0_4_line_110 |  | 102 | 104 | 0.033788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1362-22_0_4_line_111 |  | 104 | 105 | 0.019684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1362-22_0_4_line_112 |  | 106 | 107 | 0.0096778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1362-22_0_4_line_113 |  | 107 | 108 | 0.015616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1362-22_0_4_line_114 |  | 107 | 109 | 0.010747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1362-22_0_4_line_115 |  | 108 | 110 | 0.017648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1362-22_0_4_line_116 |  | 109 | 111 | 0.015114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1362-22_0_4_line_117 |  | 110 | 145 | 0.011274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1362-22_0_4_line_118 |  | 111 | 141 | 0.026822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1362-22_0_4_line_119 |  | 111 | 138 | 0.0065367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1362-22_0_4_line_120 |  | 112 | 113 | 0.00028607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1362-22_0_4_line_121 |  | 113 | 114 | 0.014046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1362-22_0_4_line_122 |  | 114 | 126 | 0.0049515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
123 | LV_1362-22_0_4_line_123 |  | 114 | 122 | 0.014063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
124 | LV_1362-22_0_4_line_124 |  | 116 | 139 | 0.011037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1362-22_0_4_line_125 |  | 117 | 118 | 0.00091019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
126 | LV_1362-22_0_4_line_126 |  | 117 | 119 | 0.01269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
127 | LV_1362-22_0_4_line_127 |  | 118 | 120 | 0.021398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
128 | LV_1362-22_0_4_line_128 |  | 119 | 121 | 0.0043739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
129 | LV_1362-22_0_4_line_129 |  | 120 | 122 | 0.00054381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
130 | LV_1362-22_0_4_line_130 |  | 121 | 123 | 0.017449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
131 | LV_1362-22_0_4_line_131 |  | 125 | 127 | 0.0053376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1362-22_0_4_line_132 |  | 127 | 128 | 0.036987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1362-22_0_4_line_133 |  | 128 | 129 | 0.01131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1362-22_0_4_line_134 |  | 129 | 130 | 0.009649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1362-22_0_4_line_135 |  | 130 | 140 | 0.012962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
136 | LV_1362-22_0_4_line_136 |  | 131 | 132 | 0.0054272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1362-22_0_4_line_137 |  | 131 | 133 | 0.016793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1362-22_0_4_line_138 |  | 132 | 134 | 0.014636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1362-22_0_4_line_139 |  | 133 | 135 | 0.014954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1362-22_0_4_line_140 |  | 134 | 136 | 0.0013858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1362-22_0_4_line_141 |  | 135 | 137 | 0.010452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_1362-22_0_4_line_142 |  | 136 | 138 | 0.0054733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_1362-22_0_4_line_143 |  | 141 | 142 | 0.012069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_1362-22_0_4_line_144 |  | 141 | 143 | 0.009022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1362-22_0_4_trafo_83 | 0.63 MVA 20/0.4 kV | 146 | 118 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2683402.3447 | 1211948.4829 | 2683404.184 | 1211945.7402 | 2683421.83 | 1211926.63 | 2683426.7281 | 1211922.1954
1 | 2683475.8248 | 1211886.1254 | 2683444.3727 | 1211906.2208 | 2683426.7281 | 1211922.1954
2 | 2683378.3396 | 1212037.6168 | 2683371.6173 | 1212037.4338 | 2683372.1706 | 1212028.2911 | 2683373.3455 | 1212019.2683 | 2683386.7566 | 1211981.2865 | 2683394.4547 | 1211968.7526 | 2683404.9833 | 1211951.6108 | 2683402.3447 | 1211948.4829
3 | 2683475.8248 | 1211886.1254 | 2683478.0528 | 1211891.9827 | 2683494.3204 | 1211884.5054 | 2683503.9908 | 1211881.4721 | 2683507.4297 | 1211885.5118
4 | 2683378.3396 | 1212037.6168 | 2683391.4996 | 1212043.6602
5 | 2683507.4297 | 1211885.5118 | 2683481.3051 | 1211895.2414 | 2683457.4381 | 1211909.2722 | 2683444.2588 | 1211919.1145
6 | 2683391.4996 | 1212043.6602 | 2683396.2771 | 1212049.2418 | 2683399.9182 | 1212053.4955
7 | 2683391.4996 | 1212043.6602 | 2683422.4036 | 1212009.4477 | 2683431.3338 | 1212004.6746
8 | 2683549.5761 | 1212068.5883 | 2683545.4964 | 1212066.9079 | 2683541.1171 | 1212063.9372
9 | 2683544.2176 | 1212085.5021 | 2683547.8048 | 1212074.0671 | 2683549.5761 | 1212068.5883
10 | 2683549.5761 | 1212068.5883 | 2683565.261 | 1212075.0122 | 2683582.1621 | 1212079.4176
11 | 2683424.9454 | 1212020.0487 | 2683431.1401 | 1212014.4843 | 2683457.2894 | 1212001.3192 | 2683466.5004 | 1211999.0577 | 2683473.7055 | 1212000.5817 | 2683482.1172 | 1212004.9356 | 2683498.779 | 1212022.4581 | 2683533.3626 | 1212058.677 | 2683541.1171 | 1212063.9372
12 | 2683544.2176 | 1212085.5021 | 2683550.1952 | 1212090.3395
13 | 2683544.2176 | 1212085.5021 | 2683539.4191 | 1212097.1537 | 2683536.5917 | 1212105.3416
14 | 2683582.1621 | 1212079.4176 | 2683612.6898 | 1212087.3747
15 | 2683733.556 | 1212119.4344 | 2683750.1076 | 1212123.0914 | 2683753.6588 | 1212123.9863
16 | 2683753.6588 | 1212123.9863 | 2683752.2387 | 1212129.3365 | 2683750.1867 | 1212139.4879
17 | 2683733.556 | 1212119.4344 | 2683708.1917 | 1212113.8302
18 | 2683733.556 | 1212119.4344 | 2683728.4983 | 1212142.339
19 | 2683734.6269 | 1212114.6019 | 2683733.556 | 1212119.4344
20 | 2683744.9878 | 1212171.0804 | 2683746.7592 | 1212156.444 | 2683750.1867 | 1212139.4879
21 | 2683734.6269 | 1212114.6019 | 2683693.8956 | 1212104.6557
22 | 2683651.1013 | 1212097.908 | 2683639.5452 | 1212094.5549
23 | 2683639.5452 | 1212094.5549 | 2683637.6063 | 1212096.807 | 2683621.0903 | 1212110.2329
24 | 2683651.1013 | 1212097.908 | 2683655.3473 | 1212099.1872
25 | 2683607.7454 | 1212120.4128 | 2683619.4282 | 1212111.584 | 2683621.0903 | 1212110.2329
26 | 2683399.9182 | 1212053.4955 | 2683416.6243 | 1212030.3978
27 | 2683431.3338 | 1212004.6746 | 2683461.5261 | 1211988.5368 | 2683462.5626 | 1211988.576
28 | 2683416.6243 | 1212030.3978 | 2683422.5597 | 1212022.1916 | 2683424.9454 | 1212020.0487
29 | 2683806.1532 | 1212198.9059 | 2683803.8651 | 1212217.5524
30 | 2683806.1532 | 1212198.9059 | 2683795.5715 | 1212196.9676
31 | 2683806.1532 | 1212198.9059 | 2683808.5771 | 1212179.1255
32 | 2683764.6541 | 1212242.0993 | 2683761.9536 | 1212240.4679 | 2683760.3113 | 1212238.7921
33 | 2683760.3113 | 1212238.7921 | 2683751.6234 | 1212229.9271 | 2683747.5079 | 1212222.6868 | 2683747.4846 | 1212222.644
34 | 2683554.608 | 1212093.9106 | 2683550.1952 | 1212090.3395
35 | 2683536.5917 | 1212105.3416 | 2683535.023 | 1212110.0401
36 | 2683536.5917 | 1212105.3416 | 2683532.89 | 1212103.2551 | 2683531.2996 | 1212101.2446
37 | 2683695.2692 | 1212110.975 | 2683708.1917 | 1212113.8302
38 | 2683728.2954 | 1212143.2577 | 2683728.4983 | 1212142.339
39 | 2683744.9878 | 1212171.0804 | 2683744.8209 | 1212172.4592
40 | 2683681.499 | 1212107.066 | 2683655.3473 | 1212099.1872
41 | 2683598.8303 | 1212127.15 | 2683607.7454 | 1212120.4128
42 | 2683490.845 | 1211995.805 | 2683472.736 | 1211988.9606 | 2683462.5626 | 1211988.576
43 | 2683559.2583 | 1212157.1921 | 2683576.005 | 1212144.4654
44 | 2683591.1196 | 1212132.9791 | 2683576.005 | 1212144.4654
45 | 2683670.8694 | 1212330.9737 | 2683667.0493 | 1212327.4607
46 | 2683667.036 | 1212327.4485 | 2683667.0493 | 1212327.4607
47 | 2683716.1406 | 1212284.334 | 2683712.9181 | 1212279.6076
48 | 2683706.4639 | 1212270.1416 | 2683712.9181 | 1212279.6076
49 | 2683725.461 | 1212154.3971 | 2683728.1029 | 1212144.1296 | 2683728.2954 | 1212143.2577
50 | 2683725.461 | 1212154.3971 | 2683723.9832 | 1212160.1401
51 | 2683723.9832 | 1212160.1401 | 2683723.4488 | 1212162.217
52 | 2683695.2692 | 1212110.975 | 2683692.2866 | 1212110.316 | 2683684.3785 | 1212107.9335
53 | 2683720.5318 | 1212173.5537 | 2683723.4488 | 1212162.217
54 | 2683684.3785 | 1212107.9335 | 2683681.499 | 1212107.066
55 | 2683684.6964 | 1212238.2162 | 2683684.7465 | 1212238.2896
56 | 2683677.4169 | 1212227.7288 | 2683680.2413 | 1212231.6821 | 2683684.6964 | 1212238.2162
57 | 2683686.767 | 1212241.2531 | 2683684.7465 | 1212238.2896
58 | 2683677.4169 | 1212227.7288 | 2683671.7229 | 1212219.7633
59 | 2683677.4169 | 1212227.7288 | 2683669.97 | 1212233.1691
60 | 2683696.5928 | 1212255.6641 | 2683686.767 | 1212241.2531
61 | 2683662.4449 | 1212204.3401 | 2683666.5771 | 1212210.1763 | 2683666.5144 | 1212212.477 | 2683671.7229 | 1212219.7633
62 | 2683669.97 | 1212233.1691 | 2683664.5492 | 1212237.1293
63 | 2683696.5928 | 1212255.6641 | 2683699.5824 | 1212260.0487
64 | 2683660.3037 | 1212201.3159 | 2683662.4449 | 1212204.3401
65 | 2683654.9994 | 1212244.1059 | 2683664.5492 | 1212237.1293
66 | 2683706.4639 | 1212270.1416 | 2683699.5824 | 1212260.0487
67 | 2683660.3037 | 1212201.3159 | 2683653.888 | 1212192.2543
68 | 2683649.8618 | 1212247.8591 | 2683654.9994 | 1212244.1059
69 | 2683650.2299 | 1212187.0875 | 2683642.8307 | 1212176.8512
70 | 2683650.2299 | 1212187.0875 | 2683653.888 | 1212192.2543
71 | 2683650.2299 | 1212187.0875 | 2683639.5251 | 1212195.2074
72 | 2683628.9192 | 1212159.0203 | 2683626.5239 | 1212156.0015
73 | 2683618.3221 | 1212150.8943 | 2683620.9926 | 1212149.0305 | 2683626.5239 | 1212156.0015
74 | 2683639.5251 | 1212195.2074 | 2683636.0944 | 1212197.8097
75 | 2683618.3221 | 1212150.8943 | 2683611.6376 | 1212141.8213
76 | 2683618.3221 | 1212150.8943 | 2683611.0947 | 1212155.931
77 | 2683626.6393 | 1212204.9817 | 2683636.0944 | 1212197.8097
78 | 2683607.6126 | 1212136.358 | 2683611.6376 | 1212141.8213
79 | 2683611.0947 | 1212155.931 | 2683606.6672 | 1212159.0165
80 | 2683621.3187 | 1212209.0175 | 2683626.6393 | 1212204.9817
81 | 2683649.8618 | 1212247.8591 | 2683649.57 | 1212248.0723
82 | 2683649.57 | 1212248.0723 | 2683634.5968 | 1212259.011
83 | 2683634.5968 | 1212259.011 | 2683634.3507 | 1212259.1908
84 | 2683634.3507 | 1212259.1908 | 2683628.008 | 1212263.8244
85 | 2683618.1102 | 1212271.0552 | 2683628.008 | 1212263.8244
86 | 2683506.3367 | 1212069.687 | 2683506.0928 | 1212069.3786
87 | 2683513.5008 | 1212078.7437 | 2683506.3367 | 1212069.687
88 | 2683504.2263 | 1212067.019 | 2683506.0928 | 1212069.3786
89 | 2683513.5008 | 1212078.7437 | 2683518.9659 | 1212085.6526
90 | 2683522.117 | 1212089.6362 | 2683518.9659 | 1212085.6526
91 | 2683522.117 | 1212089.6362 | 2683526.8807 | 1212095.6584
92 | 2683526.8807 | 1212095.6584 | 2683531.2996 | 1212101.2446
93 | 2683553.1479 | 1212217.9281 | 2683550.1023 | 1212214.3022 | 2683543.0485 | 1212201.4616 | 2683540.1379 | 1212195.2758
94 | 2683561.2463 | 1212226.9888 | 2683559.1083 | 1212225.0242 | 2683553.1479 | 1212217.9281
95 | 2683561.2463 | 1212226.9888 | 2683566.8023 | 1212232.0893
96 | 2683561.2463 | 1212226.9888 | 2683548.3012 | 1212239.276
97 | 2683577.518 | 1212241.9265 | 2683566.8023 | 1212232.0893
98 | 2683547.6929 | 1212239.8534 | 2683548.3012 | 1212239.276
99 | 2683577.518 | 1212241.9265 | 2683590.1627 | 1212254.7591
100 | 2683536.7309 | 1212250.2583 | 2683547.6929 | 1212239.8534
101 | 2683531.7873 | 1212147.6167 | 2683531.3431 | 1212143.0441
102 | 2683531.3431 | 1212143.0441 | 2683530.8265 | 1212137.7266 | 2683531.0888 | 1212127.1344 | 2683532.118 | 1212120.6538
103 | 2683600.1359 | 1212264.8807 | 2683590.1627 | 1212254.7591
104 | 2683536.4026 | 1212250.57 | 2683536.7309 | 1212250.2583
105 | 2683741.0385 | 1212201.0331 | 2683741.0987 | 1212206.7197 | 2683742.4338 | 1212213.3761 | 2683745.1398 | 1212218.3415
106 | 2683742.589 | 1212189.8272 | 2683741.0269 | 1212199.9365 | 2683741.0385 | 1212201.0331
107 | 2683745.1398 | 1212218.3415 | 2683747.4846 | 1212222.644
108 | 2683742.9743 | 1212187.3333 | 2683742.589 | 1212189.8272
109 | 2683742.9743 | 1212187.3333 | 2683743.1832 | 1212185.9909 | 2683744.8209 | 1212172.4592
110 | 2683742.9743 | 1212187.3333 | 2683776.2096 | 1212193.4211
111 | 2683795.5715 | 1212196.9676 | 2683776.2096 | 1212193.4211
112 | 2683610.2956 | 1212276.7642 | 2683618.1102 | 1212271.0552
113 | 2683610.2956 | 1212276.7642 | 2683600.1359 | 1212264.8807
114 | 2683610.2956 | 1212276.7642 | 2683618.0184 | 1212284.2373
115 | 2683600.1359 | 1212264.8807 | 2683587.3541 | 1212277.0489
116 | 2683628.8798 | 1212294.7476 | 2683618.0184 | 1212284.2373
117 | 2683579.1886 | 1212284.8224 | 2683587.3541 | 1212277.0489
118 | 2683628.8798 | 1212294.7476 | 2683608.2519 | 1212311.9586
119 | 2683628.8798 | 1212294.7476 | 2683633.8431 | 1212299.0013
120 | 2683605.9113 | 1212220.6138 | 2683606.1401 | 1212220.4421
121 | 2683617.3737 | 1212212.0099 | 2683606.1401 | 1212220.4421
122 | 2683617.3737 | 1212212.0099 | 2683621.3187 | 1212209.0175
123 | 2683617.3737 | 1212212.0099 | 2683614.5087 | 1212208.245 | 2683609.0923 | 1212200.6459
124 | 2683535.023 | 1212110.0401 | 2683532.6973 | 1212117.0059 | 2683532.118 | 1212120.6538
125 | 2683595.9512 | 1212181.9513 | 2683596.4668 | 1212182.7014
126 | 2683595.9512 | 1212181.9513 | 2683588.7635 | 1212171.4935 | 2683588.7635 | 1212171.4935
127 | 2683608.7766 | 1212200.2031 | 2683600.9164 | 1212189.1754 | 2683596.4668 | 1212182.7014
128 | 2683588.7635 | 1212171.4935 | 2683592.352 | 1212168.9927
129 | 2683608.7766 | 1212200.2031 | 2683609.0923 | 1212200.6459
130 | 2683592.352 | 1212168.9927 | 2683606.6672 | 1212159.0165
131 | 2683554.608 | 1212093.9106 | 2683558.3804 | 1212096.9635 | 2683558.7238 | 1212097.3055
132 | 2683584.2996 | 1212123.9561 | 2683580.6976 | 1212119.1907 | 2683558.7238 | 1212097.3055
133 | 2683591.1196 | 1212132.9791 | 2683584.2996 | 1212123.9561
134 | 2683591.1196 | 1212132.9791 | 2683598.8303 | 1212127.15
135 | 2683598.8303 | 1212127.15 | 2683603.4243 | 1212132.7958 | 2683605.7577 | 1212133.8403 | 2683607.6126 | 1212136.358
136 | 2683654.2852 | 1212316.5207 | 2683650.1643 | 1212312.989
137 | 2683667.036 | 1212327.4485 | 2683654.2852 | 1212316.5207
138 | 2683639.0512 | 1212303.4647 | 2683650.1643 | 1212312.989
139 | 2683667.036 | 1212327.4485 | 2683657.0406 | 1212338.5709
140 | 2683637.999 | 1212302.563 | 2683639.0512 | 1212303.4647
141 | 2683650.0544 | 1212346.3449 | 2683657.0406 | 1212338.5709
142 | 2683637.999 | 1212302.563 | 2683633.8431 | 1212299.0013
143 | 2683608.2519 | 1212311.9586 | 2683617.3341 | 1212319.9356
144 | 2683608.2519 | 1212311.9586 | 2683600.8245 | 1212306.8067

## bus_geodata
| x | y | coords
0 | 2683426.7281 | 1211922.1954
1 | 2683402.3447 | 1211948.4829
2 | 2683475.8248 | 1211886.1254
3 | 2683378.3396 | 1212037.6168
4 | 2683507.4297 | 1211885.5118
5 | 2683444.2588 | 1211919.1145
6 | 2683391.4996 | 1212043.6602
7 | 2683549.5761 | 1212068.5883
8 | 2683541.1171 | 1212063.9372
9 | 2683544.2176 | 1212085.5021
10 | 2683582.1621 | 1212079.4176
11 | 2683753.6588 | 1212123.9863
12 | 2683733.556 | 1212119.4344
13 | 2683750.1867 | 1212139.4879
14 | 2683734.6269 | 1212114.6019
15 | 2683693.8956 | 1212104.6557
16 | 2683639.5452 | 1212094.5549
17 | 2683651.1013 | 1212097.908
18 | 2683621.0903 | 1212110.2329
19 | 2683399.9182 | 1212053.4955
20 | 2683431.3338 | 1212004.6746
21 | 2683416.6243 | 1212030.3978
22 | 2683803.8651 | 1212217.5524
23 | 2683806.1532 | 1212198.9059
24 | 2683764.6541 | 1212242.0993
25 | 2683760.3113 | 1212238.7921
26 | 2683424.9454 | 1212020.0487
27 | 2683550.1952 | 1212090.3395
28 | 2683536.5917 | 1212105.3416
29 | 2683612.6898 | 1212087.3747
30 | 2683708.1917 | 1212113.8302
31 | 2683728.4983 | 1212142.339
32 | 2683744.9878 | 1212171.0804
33 | 2683655.3473 | 1212099.1872
34 | 2683607.7454 | 1212120.4128
35 | 2683462.5626 | 1211988.576
36 | 2683808.5771 | 1212179.1255
37 | 2683559.2583 | 1212157.1921
38 | 2683576.005 | 1212144.4654
39 | 2683670.8694 | 1212330.9737
40 | 2683667.0493 | 1212327.4607
41 | 2683716.1406 | 1212284.334
42 | 2683712.9181 | 1212279.6076
43 | 2683728.2954 | 1212143.2577
44 | 2683725.461 | 1212154.3971
45 | 2683723.9832 | 1212160.1401
46 | 2683695.2692 | 1212110.975
47 | 2683723.4488 | 1212162.217
48 | 2683684.3785 | 1212107.9335
49 | 2683490.845 | 1211995.805
50 | 2683684.6964 | 1212238.2162
51 | 2683684.7465 | 1212238.2896
52 | 2683677.4169 | 1212227.7288
53 | 2683686.767 | 1212241.2531
54 | 2683671.7229 | 1212219.7633
55 | 2683669.97 | 1212233.1691
56 | 2683696.5928 | 1212255.6641
57 | 2683662.4449 | 1212204.3401
58 | 2683664.5492 | 1212237.1293
59 | 2683699.5824 | 1212260.0487
60 | 2683660.3037 | 1212201.3159
61 | 2683654.9994 | 1212244.1059
62 | 2683642.8307 | 1212176.8512
63 | 2683650.2299 | 1212187.0875
64 | 2683628.9192 | 1212159.0203
65 | 2683626.5239 | 1212156.0015
66 | 2683653.888 | 1212192.2543
67 | 2683639.5251 | 1212195.2074
68 | 2683618.3221 | 1212150.8943
69 | 2683636.0944 | 1212197.8097
70 | 2683611.6376 | 1212141.8213
71 | 2683611.0947 | 1212155.931
72 | 2683626.6393 | 1212204.9817
73 | 2683649.8618 | 1212247.8591
74 | 2683649.57 | 1212248.0723
75 | 2683634.5968 | 1212259.011
76 | 2683634.3507 | 1212259.1908
77 | 2683628.008 | 1212263.8244
78 | 2683506.3367 | 1212069.687
79 | 2683506.0928 | 1212069.3786
80 | 2683513.5008 | 1212078.7437
81 | 2683504.2263 | 1212067.019
82 | 2683518.9659 | 1212085.6526
83 | 2683522.117 | 1212089.6362
84 | 2683526.8807 | 1212095.6584
85 | 2683706.4639 | 1212270.1416
86 | 2683553.1479 | 1212217.9281
87 | 2683540.1379 | 1212195.2758
88 | 2683561.2463 | 1212226.9888
89 | 2683566.8023 | 1212232.0893
90 | 2683548.3012 | 1212239.276
91 | 2683577.518 | 1212241.9265
92 | 2683547.6929 | 1212239.8534
93 | 2683531.7873 | 1212147.6167
94 | 2683531.3431 | 1212143.0441
95 | 2683590.1627 | 1212254.7591
96 | 2683536.7309 | 1212250.2583
97 | 2683681.499 | 1212107.066
98 | 2683741.0385 | 1212201.0331
99 | 2683745.1398 | 1212218.3415
100 | 2683742.589 | 1212189.8272
101 | 2683747.4846 | 1212222.644
102 | 2683742.9743 | 1212187.3333
103 | 2683744.8209 | 1212172.4592
104 | 2683776.2096 | 1212193.4211
105 | 2683795.5715 | 1212196.9676
106 | 2683618.1102 | 1212271.0552
107 | 2683610.2956 | 1212276.7642
108 | 2683600.1359 | 1212264.8807
109 | 2683618.0184 | 1212284.2373
110 | 2683587.3541 | 1212277.0489
111 | 2683628.8798 | 1212294.7476
112 | 2683605.9113 | 1212220.6138
113 | 2683606.1401 | 1212220.4421
114 | 2683617.3737 | 1212212.0099
115 | 2683531.2996 | 1212101.2446
116 | 2683535.023 | 1212110.0401
117 | 2683595.9512 | 1212181.9513
118 | 2683596.4668 | 1212182.7014
119 | 2683588.7635 | 1212171.4935
120 | 2683608.7766 | 1212200.2031
121 | 2683592.352 | 1212168.9927
122 | 2683609.0923 | 1212200.6459
123 | 2683606.6672 | 1212159.0165
124 | 2683720.5318 | 1212173.5537
125 | 2683554.608 | 1212093.9106
126 | 2683621.3187 | 1212209.0175
127 | 2683558.7238 | 1212097.3055
128 | 2683584.2996 | 1212123.9561
129 | 2683591.1196 | 1212132.9791
130 | 2683598.8303 | 1212127.15
131 | 2683654.2852 | 1212316.5207
132 | 2683650.1643 | 1212312.989
133 | 2683667.036 | 1212327.4485
134 | 2683639.0512 | 1212303.4647
135 | 2683657.0406 | 1212338.5709
136 | 2683637.999 | 1212302.563
137 | 2683650.0544 | 1212346.3449
138 | 2683633.8431 | 1212299.0013
139 | 2683532.118 | 1212120.6538
140 | 2683607.6126 | 1212136.358
141 | 2683608.2519 | 1212311.9586
142 | 2683617.3341 | 1212319.9356
143 | 2683600.8245 | 1212306.8067
144 | 2683536.4026 | 1212250.57
145 | 2683579.1886 | 1212284.8224
146 | 2683617.3737 | 1212212.0099

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97984 | -0.38836 | 0.00034422 | 8.627e-05
1 | 0.97995 | -0.38617 | 0 | 0
2 | 0.97967 | -0.39172 | 0 | 0
3 | 0.98028 | -0.37979 | 0 | 0
4 | 0.97956 | -0.3939 | 0 | 0
5 | 0.97936 | -0.39785 | 0.0030207 | 0.00075706
6 | 0.98032 | -0.3789 | 0 | 0
7 | 0.98279 | -0.33057 | 0 | 0
8 | 0.98265 | -0.33322 | 0.0014428 | 0.00036159
9 | 0.98317 | -0.3232 | 0 | 0
10 | 0.98254 | -0.33545 | 0.0020675 | 0.00051815
11 | 0.98259 | -0.33468 | 0 | 0
12 | 0.98321 | -0.32248 | 0 | 0
13 | 0.98211 | -0.34412 | 0.0038731 | 0.00097069
14 | 0.9832 | -0.3227 | 0 | 0
15 | 0.98311 | -0.32454 | 0.0024327 | 0.0006097
16 | 0.98814 | -0.22684 | 0 | 0
17 | 0.98741 | -0.24089 | 0 | 0
18 | 0.9896 | -0.19852 | 0.0063005 | 0.0015791
19 | 0.98042 | -0.37695 | 0 | 0
20 | 0.98006 | -0.38396 | 0.0038937 | 0.00097586
21 | 0.98064 | -0.37264 | 0.0033601 | 0.00084213
22 | 0.9805 | -0.37558 | 0.0027055 | 0.00067807
23 | 0.98055 | -0.37466 | 0 | 0
24 | 0.98032 | -0.37902 | 0.004895 | 0.0012268
25 | 0.98035 | -0.37853 | 0.0026234 | 0.00065748
26 | 0.98078 | -0.36981 | 0.0020145 | 0.00050488
27 | 0.98394 | -0.30807 | 0.0013559 | 0.00033982
28 | 0.98147 | -0.3563 | 0 | 0
29 | 0.98237 | -0.33875 | 0.0057952 | 0.0014524
30 | 0.98434 | -0.30058 | 0.0019993 | 0.00050108
31 | 0.98296 | -0.32735 | 0.0016093 | 0.00040332
32 | 0.98125 | -0.36093 | 0.003659 | 0.00091703
33 | 0.98714 | -0.24608 | 0.0050068 | 0.0012548
34 | 0.99071 | -0.17708 | 0.0020799 | 0.00052127
35 | 0.98003 | -0.38464 | 0.0006575 | 0.00016478
36 | 0.98052 | -0.37515 | 0.0013361 | 0.00033486
37 | 0.98976 | -0.19547 | 0.0073529 | 0.0018428
38 | 0.9899 | -0.19272 | 0.011371 | 0.00285
39 | 0.98011 | -0.38278 | 0.0017522 | 0.00043914
40 | 0.98012 | -0.38262 | 0.0017216 | 0.00043148
41 | 0.9882 | -0.22555 | 0.0021377 | 0.00053575
42 | 0.98822 | -0.22533 | 0.0046046 | 0.001154
43 | 0.98296 | -0.32752 | 0.0014607 | 0.0003661
44 | 0.98287 | -0.32927 | 0.0021816 | 0.00054675
45 | 0.98283 | -0.32994 | 0.0010523 | 0.00026373
46 | 0.98493 | -0.28896 | 0.0018839 | 0.00047214
47 | 0.98282 | -0.33014 | 0.002176 | 0.00054535
48 | 0.98546 | -0.27865 | 0.0042284 | 0.0010597
49 | 0.98002 | -0.38486 | 0.00040348 | 0.00010112
50 | 0.98882 | -0.2135 | 0.0017876 | 0.00044802
51 | 0.98882 | -0.21354 | 0.0023168 | 0.00058063
52 | 0.98913 | -0.2076 | 0 | 0
53 | 0.98875 | -0.21493 | 0.0038395 | 0.00096228
54 | 0.99035 | -0.18397 | 0.0024687 | 0.00061872
55 | 0.98819 | -0.22565 | 0.0017132 | 0.00042938
56 | 0.98846 | -0.22052 | 0.0037126 | 0.00093046
57 | 0.9927 | -0.1389 | 0.0038876 | 0.00097433
58 | 0.98752 | -0.2386 | 0.0019971 | 0.00050051
59 | 0.98839 | -0.22187 | 0.0047067 | 0.0011796
60 | 0.99295 | -0.13424 | 0.001727 | 0.00043282
61 | 0.98636 | -0.26103 | 0.0020005 | 0.00050138
62 | 0.99404 | -0.11334 | 0.0063046 | 0.0015801
63 | 0.99411 | -0.11193 | 0 | 0
64 | 0.9945 | -0.10447 | 0.0016215 | 0.00040639
65 | 0.99451 | -0.10436 | 0.0042251 | 0.0010589
66 | 0.99368 | -0.12015 | 0.0033772 | 0.00084641
67 | 0.99506 | -0.093774 | 0.0045718 | 0.0011458
68 | 0.99457 | -0.10311 | 0 | 0
69 | 0.99538 | -0.087788 | 0.0019784 | 0.00049585
70 | 0.99343 | -0.12489 | 0.0023065 | 0.00057806
71 | 0.99549 | -0.085658 | 0.0049413 | 0.0012384
72 | 0.99625 | -0.071105 | 0.0019809 | 0.00049645
73 | 0.98575 | -0.2729 | 0.0042485 | 0.0010648
74 | 0.98572 | -0.27354 | 0.0017192 | 0.00043086
75 | 0.98403 | -0.30621 | 0.001806 | 0.00045262
76 | 0.98401 | -0.30674 | 0.0016712 | 0.00041884
77 | 0.98332 | -0.32012 | 0.0038969 | 0.00097667
78 | 0.98069 | -0.37158 | 0.0043237 | 0.0010836
79 | 0.98069 | -0.37163 | 0.0014947 | 0.00037461
80 | 0.9808 | -0.36938 | 0.0021741 | 0.00054489
81 | 0.98068 | -0.37188 | 0.004696 | 0.0011769
82 | 0.98091 | -0.36736 | 0.0020576 | 0.00051567
83 | 0.98098 | -0.366 | 0.0026369 | 0.00066086
84 | 0.9811 | -0.36358 | 0.0079688 | 0.0019972
85 | 0.98829 | -0.22396 | 0.0028104 | 0.00070436
86 | 0.97873 | -0.40983 | 0.0041929 | 0.0010509
87 | 0.97848 | -0.41475 | 0.010317 | 0.0025858
88 | 0.9789 | -0.40661 | 0 | 0
89 | 0.9791 | -0.4026 | 0.0073948 | 0.0018533
90 | 0.97865 | -0.4114 | 0.003131 | 0.00078471
91 | 0.97959 | -0.39291 | 0 | 0
92 | 0.97864 | -0.41158 | 0.003103 | 0.00077767
93 | 0.98038 | -0.37771 | 0.01051 | 0.002634
94 | 0.98042 | -0.37684 | 0.0099491 | 0.0024935
95 | 0.98021 | -0.38093 | 0.0046018 | 0.0011533
96 | 0.97852 | -0.41392 | 0.0038357 | 0.00096131
97 | 0.98562 | -0.27569 | 0.0055608 | 0.0013937
98 | 0.98073 | -0.371 | 0.0021446 | 0.0005375
99 | 0.98054 | -0.37481 | 0.0016124 | 0.0004041
100 | 0.98088 | -0.36818 | 0.00089932 | 0.00022539
101 | 0.98049 | -0.3757 | 0.0024583 | 0.00061611
102 | 0.98091 | -0.36752 | 0 | 0
103 | 0.98121 | -0.36157 | 0.0034557 | 0.00086608
104 | 0.98068 | -0.37196 | 0.0018986 | 0.00047582
105 | 0.98059 | -0.37387 | 0.0013191 | 0.0003306
106 | 0.98229 | -0.34018 | 0.0022109 | 0.00055411
107 | 0.9815 | -0.35565 | 0 | 0
108 | 0.98075 | -0.3703 | 0.0022409 | 0.00056162
109 | 0.98113 | -0.36279 | 0.0046843 | 0.001174
110 | 0.98061 | -0.37295 | 0.0041848 | 0.0010488
111 | 0.98069 | -0.37155 | 0 | 0
112 | 0.99708 | -0.055395 | 0.001707 | 0.00042781
113 | 0.99708 | -0.055387 | 0.0018636 | 0.00046706
114 | 0.99713 | -0.054508 | 0 | 0
115 | 0.98127 | -0.36031 | 0.0071906 | 0.0018021
116 | 0.98123 | -0.36111 | 0.016709 | 0.0041877
117 | 0.99989 | -0.0020357 | 0.0048749 | 0.0012218
118 | 1 | 0 | -0.44132 | -0.11248
119 | 0.99842 | -0.029923 | 0.0087945 | 0.0022041
120 | 0.99825 | -0.033096 | 0.005436 | 0.0013624
121 | 0.99793 | -0.039217 | 0.010673 | 0.0026748
122 | 0.99821 | -0.033913 | 0.0044762 | 0.0011218
123 | 0.99606 | -0.07475 | 0.0023112 | 0.00057924
124 | 0.98279 | -0.33078 | 0.00303 | 0.00075939
125 | 0.98452 | -0.29677 | 0.0015422 | 0.00038652
126 | 0.99675 | -0.061614 | 0.0017412 | 0.00043638
127 | 0.98508 | -0.28602 | 0.0015637 | 0.0003919
128 | 0.98896 | -0.21079 | 0.0074857 | 0.0018761
129 | 0.99023 | -0.1864 | 0 | 0
130 | 0.99148 | -0.16243 | 0 | 0
131 | 0.98024 | -0.38028 | 0.0027218 | 0.00068214
132 | 0.98029 | -0.37926 | 0.0017071 | 0.00042783
133 | 0.98012 | -0.38262 | 0 | 0
134 | 0.98046 | -0.37605 | 0.0027072 | 0.0006785
135 | 0.98006 | -0.38375 | 0.0013782 | 0.00034541
136 | 0.98048 | -0.37568 | 0.0027353 | 0.00068553
137 | 0.98004 | -0.38429 | 0.0028132 | 0.00070505
138 | 0.98056 | -0.37394 | 0.0026142 | 0.00065517
139 | 0.98085 | -0.36849 | 0.016485 | 0.0041315
140 | 0.99275 | -0.1379 | 0.0030719 | 0.00076989
141 | 0.98039 | -0.37731 | 0 | 0
142 | 0.98037 | -0.37775 | 0.0020338 | 0.00050972
143 | 0.98031 | -0.37891 | 0.0098049 | 0.0024573
144 | 0.97852 | -0.41396 | 0.0046766 | 0.0011721
145 | 0.98057 | -0.37378 | 0.0040976 | 0.0010269
146 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0033663 | -0.00084203 | 0.0033667 | 0.0008418 | 3.5195e-07 | -2.2725e-07 | 0.0051116 | 0.0051114 | 0.0051116 | 0.97984 | -0.38836 | 0.97995 | -0.38617 | 1.4043
1 | 0.0030221 | 0.00075576 | -0.0030216 | -0.00075622 | 4.8271e-07 | -4.6085e-07 | 0.0045888 | 0.0045891 | 0.0045891 | 0.97984 | -0.38836 | 0.97967 | -0.39172 | 1.2607
2 | -0.0033667 | -0.0008418 | 0.0033677 | 0.00084114 | 1.0206e-06 | -6.5977e-07 | 0.0051114 | 0.005111 | 0.0051114 | 0.97995 | -0.38617 | 0.98028 | -0.37979 | 1.4042
3 | 0.0030216 | 0.00075622 | -0.0030213 | -0.00075652 | 3.1284e-07 | -2.9848e-07 | 0.0045891 | 0.0045893 | 0.0045893 | 0.97967 | -0.39172 | 0.97956 | -0.3939 | 1.2608
4 | -0.0033677 | -0.00084114 | 0.0033678 | 0.00084105 | 1.4151e-07 | -9.1563e-08 | 0.005111 | 0.0051109 | 0.005111 | 0.98028 | -0.37979 | 0.98032 | -0.3789 | 1.4041
5 | 0.0030213 | 0.00075652 | -0.0030207 | -0.00075706 | 5.688e-07 | -5.423e-07 | 0.0045893 | 0.0045896 | 0.0045896 | 0.97956 | -0.3939 | 0.97936 | -0.39785 | 1.2609
6 | -0.0083238 | -0.0020821 | 0.0083245 | 0.0020824 | 7.748e-07 | 3.3263e-07 | 0.012633 | 0.012633 | 0.012633 | 0.98032 | -0.3789 | 0.98042 | -0.37695 | 3.4706
7 | 0.004956 | 0.001241 | -0.0049548 | -0.001241 | 1.1932e-06 | 5.4866e-08 | 0.0075222 | 0.0075225 | 0.0075225 | 0.98032 | -0.3789 | 0.98006 | -0.38396 | 2.0666
8 | 0.015171 | 0.0038071 | -0.015169 | -0.003806 | 1.9204e-06 | 1.1061e-06 | 0.022972 | 0.022972 | 0.022972 | 0.98279 | -0.33057 | 0.98265 | -0.33322 | 6.311
9 | -0.023036 | -0.0057786 | 0.023045 | 0.0057836 | 8.0948e-06 | 4.9558e-06 | 0.034881 | 0.034881 | 0.034881 | 0.98279 | -0.33057 | 0.98317 | -0.3232 | 9.5826
10 | 0.0078654 | 0.0019715 | -0.0078636 | -0.0019708 | 1.8303e-06 | 7.3543e-07 | 0.011909 | 0.011909 | 0.011909 | 0.98279 | -0.33057 | 0.98254 | -0.33545 | 3.2717
11 | 0.013726 | 0.0034444 | -0.013702 | -0.003431 | 2.391e-05 | 1.3437e-05 | 0.020787 | 0.020788 | 0.020788 | 0.98265 | -0.33322 | 0.98078 | -0.36981 | 5.7109
12 | -0.10943 | -0.027504 | 0.1095 | 0.027554 | 7.9121e-05 | 5.054e-05 | 0.16564 | 0.16564 | 0.16564 | 0.98317 | -0.3232 | 0.98394 | -0.30807 | 45.5062
13 | 0.086381 | 0.02172 | -0.086244 | -0.021633 | 0.00013632 | 8.6975e-05 | 0.13076 | 0.13076 | 0.13076 | 0.98317 | -0.3232 | 0.98147 | -0.3563 | 35.9237
14 | 0.0057961 | 0.0014526 | -0.0057952 | -0.0014524 | 9.1158e-07 | 1.8392e-07 | 0.008778 | 0.0087781 | 0.0087781 | 0.98254 | -0.33545 | 0.98237 | -0.33875 | 2.4116
15 | -0.032933 | -0.0082718 | 0.032953 | 0.0082838 | 1.9178e-05 | 1.2013e-05 | 0.04988 | 0.04988 | 0.04988 | 0.98259 | -0.33468 | 0.98321 | -0.32248 | 13.7034
16 | 0.032933 | 0.0082718 | -0.032919 | -0.0082625 | 1.4828e-05 | 9.2885e-06 | 0.04988 | 0.04988 | 0.04988 | 0.98259 | -0.33468 | 0.98211 | -0.34412 | 13.7034
17 | -0.046899 | -0.011779 | 0.046948 | 0.01181 | 4.9087e-05 | 3.1086e-05 | 0.070987 | 0.070987 | 0.070987 | 0.98321 | -0.32248 | 0.98434 | -0.30058 | 19.502
18 | 0.011514 | 0.0028864 | -0.011511 | -0.002885 | 2.6709e-06 | 1.4119e-06 | 0.017425 | 0.017425 | 0.017425 | 0.98321 | -0.32248 | 0.98296 | -0.32735 | 4.7872
19 | 0.002433 | 0.00060926 | -0.0024329 | -0.0006093 | 2.5165e-08 | -4.6673e-08 | 0.0036819 | 0.0036819 | 0.0036819 | 0.98321 | -0.32248 | 0.9832 | -0.3227 | 1.0115
20 | 0.029046 | 0.0072918 | -0.029022 | -0.0072773 | 2.3276e-05 | 1.4491e-05 | 0.044012 | 0.044012 | 0.044012 | 0.98211 | -0.34412 | 0.98125 | -0.36093 | 12.0913
21 | 0.0024329 | 0.0006093 | -0.0024327 | -0.0006097 | 2.1316e-07 | -3.9527e-07 | 0.0036819 | 0.0036821 | 0.0036821 | 0.9832 | -0.3227 | 0.98311 | -0.32454 | 1.0116
22 | 0.065834 | 0.016623 | -0.06579 | -0.016595 | 4.4267e-05 | 2.8178e-05 | 0.099183 | 0.099183 | 0.099183 | 0.98814 | -0.22684 | 0.98741 | -0.24089 | 27.248
23 | -0.065834 | -0.016623 | 0.065924 | 0.01668 | 8.948e-05 | 5.6956e-05 | 0.099183 | 0.099183 | 0.099183 | 0.98814 | -0.22684 | 0.9896 | -0.19852 | 27.248
24 | 0.06579 | 0.016595 | -0.065774 | -0.016585 | 1.6359e-05 | 1.0413e-05 | 0.099183 | 0.099183 | 0.099183 | 0.98741 | -0.24089 | 0.98714 | -0.24608 | 27.248
25 | -0.072224 | -0.018259 | 0.072299 | 0.018307 | 7.4315e-05 | 4.7346e-05 | 0.10866 | 0.10866 | 0.10866 | 0.9896 | -0.19852 | 0.99071 | -0.17708 | 29.8506
26 | -0.0083245 | -0.0020824 | 0.0083263 | 0.0020832 | 1.706e-06 | 7.3228e-07 | 0.012633 | 0.012633 | 0.012633 | 0.98042 | -0.37695 | 0.98064 | -0.37264 | 3.4706
27 | 0.001061 | 0.00026512 | -0.001061 | -0.00026554 | 3.4316e-08 | -4.225e-07 | 0.0016106 | 0.0016108 | 0.0016108 | 0.98006 | -0.38396 | 0.98003 | -0.38464 | 0.44253
28 | -0.011686 | -0.0029253 | 0.011688 | 0.0029261 | 1.5722e-06 | 8.3794e-07 | 0.017732 | 0.017731 | 0.017732 | 0.98064 | -0.37264 | 0.98078 | -0.36981 | 4.8713
29 | -0.0027055 | -0.00067807 | 0.0027057 | 0.00067791 | 1.1877e-07 | -1.6095e-07 | 0.0041059 | 0.0041059 | 0.0041059 | 0.9805 | -0.37558 | 0.98055 | -0.37466 | 1.128
30 | -0.0040418 | -0.0010125 | 0.004042 | 0.0010125 | 1.5176e-07 | -3.8575e-08 | 0.0061334 | 0.0061334 | 0.0061334 | 0.98055 | -0.37466 | 0.98059 | -0.37387 | 1.685
31 | 0.0013362 | 0.00033463 | -0.0013361 | -0.00033486 | 3.0724e-08 | -2.317e-07 | 0.0020276 | 0.0020277 | 0.0020277 | 0.98055 | -0.37466 | 0.98052 | -0.37515 | 0.55705
32 | -0.004895 | -0.0012268 | 0.0048951 | 0.0012268 | 1.1389e-07 | 3.525e-09 | 0.00743 | 0.00743 | 0.00743 | 0.98032 | -0.37902 | 0.98035 | -0.37853 | 2.0412
33 | -0.0075185 | -0.0018843 | 0.0075195 | 0.0018847 | 1.0153e-06 | 3.876e-07 | 0.011412 | 0.011412 | 0.011412 | 0.98035 | -0.37853 | 0.98049 | -0.3757 | 3.1351
34 | -0.11086 | -0.027894 | 0.11092 | 0.027932 | 5.9863e-05 | 3.824e-05 | 0.16769 | 0.16769 | 0.16769 | 0.98394 | -0.30807 | 0.98452 | -0.29677 | 46.0696
35 | 0.053687 | 0.013468 | -0.053674 | -0.01346 | 1.2308e-05 | 7.8143e-06 | 0.081399 | 0.081399 | 0.081399 | 0.98147 | -0.3563 | 0.98123 | -0.36111 | 22.3624
36 | 0.032558 | 0.0081652 | -0.032552 | -0.0081613 | 6.2253e-06 | 3.8981e-06 | 0.049363 | 0.049363 | 0.049363 | 0.98147 | -0.3563 | 0.98127 | -0.36031 | 13.5613
37 | -0.048948 | -0.012312 | 0.048975 | 0.012329 | 2.7183e-05 | 1.7229e-05 | 0.07401 | 0.07401 | 0.07401 | 0.98434 | -0.30058 | 0.98493 | -0.28896 | 20.3323
38 | 0.0099017 | 0.0024816 | -0.0099016 | -0.0024816 | 7.9272e-08 | 3.8807e-08 | 0.014989 | 0.014989 | 0.014989 | 0.98296 | -0.32735 | 0.98296 | -0.32752 | 4.1179
39 | 0.025363 | 0.0063603 | -0.025363 | -0.0063598 | 7.7052e-07 | 4.7559e-07 | 0.038464 | 0.038464 | 0.038464 | 0.98125 | -0.36093 | 0.98121 | -0.36157 | 10.5669
40 | 0.060767 | 0.01533 | -0.060681 | -0.015275 | 8.6005e-05 | 5.4695e-05 | 0.091636 | 0.091636 | 0.091636 | 0.98714 | -0.24608 | 0.98562 | -0.27569 | 25.1747
41 | -0.074378 | -0.018828 | 0.074431 | 0.018861 | 5.2358e-05 | 3.3365e-05 | 0.11178 | 0.11178 | 0.11178 | 0.99071 | -0.17708 | 0.99148 | -0.16243 | 30.7088
42 | 0.00040349 | 0.00010075 | -0.00040348 | -0.00010112 | 4.1567e-09 | -3.6955e-07 | 0.0006125 | 0.00061263 | 0.00061263 | 0.98003 | -0.38464 | 0.98002 | -0.38486 | 0.16831
43 | -0.0073529 | -0.0018428 | 0.0073539 | 0.0018432 | 9.6386e-07 | 3.4651e-07 | 0.011054 | 0.011054 | 0.011054 | 0.98976 | -0.19547 | 0.9899 | -0.19272 | 3.0369
44 | -0.018725 | -0.0046931 | 0.018731 | 0.0046965 | 5.6403e-06 | 3.3657e-06 | 0.028148 | 0.028148 | 0.028148 | 0.9899 | -0.19272 | 0.99023 | -0.1864 | 7.7329
45 | -0.0017522 | -0.00043914 | 0.0017522 | 0.00043908 | 1.3772e-08 | -5.6592e-08 | 0.0026602 | 0.0026602 | 0.0026602 | 0.98011 | -0.38278 | 0.98012 | -0.38262 | 0.73082
46 | -0.0034738 | -0.00087057 | 0.0034738 | 0.00087057 | 1.8645e-10 | -1.0434e-10 | 0.0052739 | 0.0052739 | 0.0052739 | 0.98012 | -0.38262 | 0.98012 | -0.38262 | 1.4489
47 | -0.0021377 | -0.00053575 | 0.0021377 | 0.00053569 | 2.2226e-08 | -5.9064e-08 | 0.0032188 | 0.0032188 | 0.0032188 | 0.9882 | -0.22555 | 0.98822 | -0.22533 | 0.8843
48 | -0.0067423 | -0.0016897 | 0.0067427 | 0.0016898 | 4.4281e-07 | 1.366e-07 | 0.010152 | 0.010152 | 0.010152 | 0.98822 | -0.22533 | 0.98829 | -0.22396 | 2.7891
49 | 0.0084409 | 0.0021155 | -0.0084402 | -0.0021152 | 7.0382e-07 | 3.0475e-07 | 0.012778 | 0.012778 | 0.012778 | 0.98296 | -0.32752 | 0.98287 | -0.32927 | 3.5105
50 | 0.0062586 | 0.0015684 | -0.0062584 | -0.0015684 | 1.9965e-07 | 5.2625e-08 | 0.0094753 | 0.0094753 | 0.0094753 | 0.98287 | -0.32927 | 0.98283 | -0.32994 | 2.6031
51 | 0.0052061 | 0.0013047 | -0.0052061 | -0.0013047 | 4.9962e-08 | 4.7995e-09 | 0.0078821 | 0.0078821 | 0.0078821 | 0.98283 | -0.32994 | 0.98282 | -0.33014 | 2.1654
52 | -0.050859 | -0.012801 | 0.050884 | 0.012817 | 2.506e-05 | 1.5895e-05 | 0.076856 | 0.076856 | 0.076856 | 0.98493 | -0.28896 | 0.98546 | -0.27865 | 21.1142
53 | 0.0030301 | 0.0007593 | -0.00303 | -0.00075939 | 9.2389e-08 | -8.921e-08 | 0.0045876 | 0.0045877 | 0.0045877 | 0.98282 | -0.33014 | 0.98279 | -0.33078 | 1.2603
54 | -0.055112 | -0.013877 | 0.05512 | 0.013882 | 7.8142e-06 | 4.9628e-06 | 0.08324 | 0.08324 | 0.08324 | 0.98546 | -0.27865 | 0.98562 | -0.27569 | 22.8683
55 | 0.024137 | 0.0060519 | -0.024137 | -0.0060519 | 4.396e-08 | 2.6995e-08 | 0.036323 | 0.036323 | 0.036323 | 0.98882 | -0.2135 | 0.98882 | -0.21354 | 9.9788
56 | -0.025925 | -0.0064999 | 0.025932 | 0.0065044 | 7.2868e-06 | 4.4997e-06 | 0.039013 | 0.039013 | 0.039013 | 0.98882 | -0.2135 | 0.98913 | -0.2076 | 10.7179
57 | 0.02182 | 0.0054713 | -0.021819 | -0.0054704 | 1.4503e-06 | 8.8216e-07 | 0.032837 | 0.032837 | 0.032837 | 0.98882 | -0.21354 | 0.98875 | -0.21493 | 9.021
58 | -0.1365 | -0.034546 | 0.13666 | 0.034645 | 0.00015502 | 9.9086e-05 | 0.20547 | 0.20547 | 0.20547 | 0.98913 | -0.2076 | 0.99035 | -0.18397 | 56.4486
59 | 0.11057 | 0.028041 | -0.11048 | -0.02798 | 9.583e-05 | 6.1213e-05 | 0.16646 | 0.16646 | 0.16646 | 0.98913 | -0.2076 | 0.98819 | -0.22565 | 45.7308
60 | 0.017979 | 0.0045081 | -0.017974 | -0.0045053 | 4.7888e-06 | 2.8412e-06 | 0.027058 | 0.027058 | 0.027058 | 0.98875 | -0.21493 | 0.98846 | -0.22052 | 7.4336
61 | -0.13913 | -0.035264 | 0.13943 | 0.035457 | 0.00030207 | 0.00019309 | 0.20918 | 0.20918 | 0.20918 | 0.99035 | -0.18397 | 0.9927 | -0.1389 | 57.4676
62 | 0.10876 | 0.027551 | -0.1087 | -0.027508 | 6.7612e-05 | 4.3185e-05 | 0.16388 | 0.16388 | 0.16388 | 0.98819 | -0.22565 | 0.98752 | -0.2386 | 45.0221
63 | 0.014262 | 0.0035748 | -0.014261 | -0.0035743 | 9.1731e-07 | 5.1906e-07 | 0.02147 | 0.02147 | 0.02147 | 0.98846 | -0.22052 | 0.98839 | -0.22187 | 5.8982
64 | -0.14332 | -0.036431 | 0.14335 | 0.036452 | 3.2119e-05 | 2.046e-05 | 0.21501 | 0.21501 | 0.21501 | 0.9927 | -0.1389 | 0.99295 | -0.13424 | 29.5343
65 | 0.1067 | 0.027007 | -0.10658 | -0.026934 | 0.00011478 | 7.3306e-05 | 0.16087 | 0.16087 | 0.16087 | 0.98752 | -0.2386 | 0.98636 | -0.26103 | 44.1954
66 | 0.0095541 | 0.0023947 | -0.0095531 | -0.0023942 | 9.4773e-07 | 4.5e-07 | 0.014384 | 0.014384 | 0.014384 | 0.98839 | -0.22187 | 0.98829 | -0.22396 | 3.9516
67 | -0.14508 | -0.036884 | 0.14518 | 0.036947 | 9.857e-05 | 6.2797e-05 | 0.2176 | 0.2176 | 0.2176 | 0.99295 | -0.13424 | 0.99368 | -0.12015 | 29.8898
68 | 0.10458 | 0.026433 | -0.10452 | -0.026395 | 5.9452e-05 | 3.7968e-05 | 0.15785 | 0.15785 | 0.15785 | 0.98636 | -0.26103 | 0.98575 | -0.2729 | 43.3663
69 | -0.0063046 | -0.0015801 | 0.006305 | 0.0015802 | 4.2186e-07 | 1.0625e-07 | 0.0094376 | 0.0094375 | 0.0094376 | 0.99404 | -0.11334 | 0.99411 | -0.11193 | 2.5927
70 | 0.14861 | 0.037831 | -0.14855 | -0.037794 | 5.8845e-05 | 3.7497e-05 | 0.22265 | 0.22265 | 0.22265 | 0.99411 | -0.11193 | 0.99368 | -0.12015 | 30.5844
71 | -0.15492 | -0.039411 | 0.15505 | 0.039498 | 0.0001357 | 8.6501e-05 | 0.23209 | 0.23209 | 0.23209 | 0.99411 | -0.11193 | 0.99506 | -0.093774 | 31.8808
72 | -0.0016215 | -0.00040639 | 0.0016215 | 0.00040635 | 8.5064e-09 | -4.4559e-08 | 0.0024262 | 0.0024262 | 0.0024262 | 0.9945 | -0.10447 | 0.99451 | -0.10436 | 0.66653
73 | -0.0058466 | -0.0014652 | 0.0058469 | 0.0014653 | 3.4882e-07 | 6.551e-08 | 0.0087478 | 0.0087478 | 0.0087478 | 0.99451 | -0.10436 | 0.99457 | -0.10311 | 2.4033
74 | -0.15962 | -0.040644 | 0.15967 | 0.040673 | 4.6091e-05 | 2.9386e-05 | 0.23893 | 0.23893 | 0.23893 | 0.99506 | -0.093774 | 0.99538 | -0.087788 | 32.8199
75 | 0.22145 | 0.056386 | -0.22122 | -0.056238 | 0.00023239 | 0.00014844 | 0.33164 | 0.33164 | 0.33164 | 0.99457 | -0.10311 | 0.99343 | -0.12489 | 45.5544
76 | -0.2273 | -0.057852 | 0.22749 | 0.057974 | 0.00019137 | 0.00012225 | 0.34038 | 0.34038 | 0.34038 | 0.99457 | -0.10311 | 0.99549 | -0.085658 | 46.7559
77 | -0.16165 | -0.041169 | 0.16178 | 0.041252 | 0.00013019 | 8.3013e-05 | 0.24189 | 0.24189 | 0.24189 | 0.99538 | -0.087788 | 0.99625 | -0.071105 | 33.2261
78 | 0.21891 | 0.05566 | -0.21878 | -0.055572 | 0.00013704 | 8.7528e-05 | 0.32818 | 0.32818 | 0.32818 | 0.99343 | -0.12489 | 0.99275 | -0.1379 | 45.0798
79 | -0.23243 | -0.059212 | 0.23255 | 0.05929 | 0.00012238 | 7.8182e-05 | 0.34777 | 0.34777 | 0.34777 | 0.99549 | -0.085658 | 0.99606 | -0.07475 | 47.7705
80 | -0.16376 | -0.041748 | 0.16384 | 0.041796 | 7.5064e-05 | 4.7867e-05 | 0.24484 | 0.24484 | 0.24484 | 0.99625 | -0.071105 | 0.99675 | -0.061614 | 33.6325
81 | 0.10028 | 0.02533 | -0.10027 | -0.025328 | 3.1085e-06 | 1.9849e-06 | 0.15144 | 0.15144 | 0.15144 | 0.98575 | -0.2729 | 0.98572 | -0.27354 | 41.6044
82 | 0.098554 | 0.024897 | -0.0984 | -0.024799 | 0.00015406 | 9.8361e-05 | 0.14884 | 0.14885 | 0.14885 | 0.98572 | -0.27354 | 0.98403 | -0.30621 | 40.8915
83 | 0.096594 | 0.024346 | -0.096591 | -0.024344 | 2.4399e-06 | 1.5577e-06 | 0.14611 | 0.14611 | 0.14611 | 0.98403 | -0.30621 | 0.98401 | -0.30674 | 40.1412
84 | 0.09492 | 0.023926 | -0.094859 | -0.023887 | 6.073e-05 | 3.8768e-05 | 0.14359 | 0.14359 | 0.14359 | 0.98401 | -0.30674 | 0.98332 | -0.32012 | 39.447
85 | 0.090962 | 0.02291 | -0.090875 | -0.022855 | 8.7146e-05 | 5.5618e-05 | 0.13769 | 0.13769 | 0.13769 | 0.98332 | -0.32012 | 0.98229 | -0.34018 | 37.8269
86 | 0.0061907 | 0.0015515 | -0.0061907 | -0.0015515 | 1.3011e-08 | 3.3652e-09 | 0.0093933 | 0.0093933 | 0.0093933 | 0.98069 | -0.37158 | 0.98069 | -0.37163 | 2.5806
87 | -0.010514 | -0.0026351 | 0.010516 | 0.0026357 | 1.1022e-06 | 5.5966e-07 | 0.015954 | 0.015954 | 0.015954 | 0.98069 | -0.37158 | 0.9808 | -0.36938 | 4.3829
88 | 0.004696 | 0.0011769 | -0.004696 | -0.0011769 | 5.728e-08 | -1.3008e-09 | 0.0071254 | 0.0071254 | 0.0071254 | 0.98069 | -0.37163 | 0.98068 | -0.37188 | 1.9575
89 | -0.01269 | -0.0031806 | 0.012691 | 0.0031813 | 1.2244e-06 | 6.7241e-07 | 0.019252 | 0.019252 | 0.019252 | 0.9808 | -0.36938 | 0.98091 | -0.36736 | 5.289
90 | -0.014748 | -0.0036969 | 0.014749 | 0.0036975 | 9.5343e-07 | 5.4608e-07 | 0.022373 | 0.022373 | 0.022373 | 0.98091 | -0.36736 | 0.98098 | -0.366 | 6.1465
91 | -0.017386 | -0.0043583 | 0.017388 | 0.0043595 | 2.0028e-06 | 1.1848e-06 | 0.026373 | 0.026373 | 0.026373 | 0.98098 | -0.366 | 0.9811 | -0.36358 | 7.2453
92 | -0.025357 | -0.0063567 | 0.025361 | 0.0063591 | 3.9507e-06 | 2.4385e-06 | 0.038459 | 0.038459 | 0.038459 | 0.9811 | -0.36358 | 0.98127 | -0.36031 | 10.5657
93 | 0.01032 | 0.002587 | -0.010317 | -0.0025858 | 2.4208e-06 | 1.2198e-06 | 0.01569 | 0.01569 | 0.01569 | 0.97873 | -0.40983 | 0.97848 | -0.41475 | 4.3105
94 | -0.014513 | -0.0036379 | 0.014515 | 0.0036391 | 2.222e-06 | 1.2691e-06 | 0.022065 | 0.022065 | 0.022065 | 0.97873 | -0.40983 | 0.9789 | -0.40661 | 6.0618
95 | -0.029266 | -0.0073373 | 0.029271 | 0.0073408 | 5.5976e-06 | 3.4876e-06 | 0.044488 | 0.044488 | 0.044488 | 0.9789 | -0.40661 | 0.9791 | -0.4026 | 12.2219
96 | 0.014751 | 0.0036982 | -0.014747 | -0.0036962 | 3.3652e-06 | 1.9294e-06 | 0.022423 | 0.022423 | 0.022423 | 0.9789 | -0.40661 | 0.97865 | -0.4114 | 6.1602
97 | -0.036666 | -0.0091941 | 0.036683 | 0.0092048 | 1.694e-05 | 1.0658e-05 | 0.055726 | 0.055726 | 0.055726 | 0.9791 | -0.4026 | 0.97959 | -0.39291 | 15.3094
98 | 0.011616 | 0.0029115 | -0.011616 | -0.0029115 | 9.8104e-08 | 5.2249e-08 | 0.017662 | 0.017662 | 0.017662 | 0.97865 | -0.4114 | 0.97864 | -0.41158 | 4.8523
99 | -0.036683 | -0.0092048 | 0.036704 | 0.009218 | 2.098e-05 | 1.32e-05 | 0.055726 | 0.055726 | 0.055726 | 0.97959 | -0.39291 | 0.98021 | -0.38093 | 15.3093
100 | 0.0085132 | 0.0021338 | -0.0085123 | -0.0021334 | 9.4966e-07 | 4.179e-07 | 0.012944 | 0.012944 | 0.012944 | 0.97864 | -0.41158 | 0.97852 | -0.41392 | 3.5561
101 | -0.01051 | -0.002634 | 0.01051 | 0.0026342 | 4.3837e-07 | 2.2263e-07 | 0.015952 | 0.015952 | 0.015952 | 0.98038 | -0.37771 | 0.98042 | -0.37684 | 4.3823
102 | -0.020459 | -0.0051277 | 0.020467 | 0.0051326 | 8.1354e-06 | 4.9228e-06 | 0.031052 | 0.031052 | 0.031052 | 0.98042 | -0.37684 | 0.98085 | -0.36849 | 8.5307
103 | -0.041306 | -0.010371 | 0.041327 | 0.010385 | 2.0956e-05 | 1.3233e-05 | 0.062712 | 0.062712 | 0.062712 | 0.98021 | -0.38093 | 0.98075 | -0.3703 | 17.2285
104 | 0.0046766 | 0.0011721 | -0.0046766 | -0.0011721 | 8.585e-09 | -1.9192e-10 | 0.0071116 | 0.0071116 | 0.0071116 | 0.97852 | -0.41392 | 0.97852 | -0.41396 | 1.9537
105 | 0.011593 | 0.0029062 | -0.011591 | -0.0029051 | 2.1035e-06 | 1.1175e-06 | 0.017589 | 0.017589 | 0.017589 | 0.98073 | -0.371 | 0.98054 | -0.37481 | 4.8322
106 | -0.013737 | -0.0034437 | 0.013739 | 0.0034447 | 1.8452e-06 | 1.038e-06 | 0.020843 | 0.020843 | 0.020843 | 0.98073 | -0.371 | 0.98088 | -0.36818 | 5.7262
107 | 0.0099782 | 0.002501 | -0.0099778 | -0.0025008 | 4.2133e-07 | 2.0785e-07 | 0.015143 | 0.015143 | 0.015143 | 0.98054 | -0.37481 | 0.98049 | -0.3757 | 4.16
108 | -0.014638 | -0.0036701 | 0.014639 | 0.0036704 | 4.6669e-07 | 2.6683e-07 | 0.022207 | 0.022207 | 0.022207 | 0.98088 | -0.36818 | 0.98091 | -0.36752 | 6.101
109 | -0.021901 | -0.0054899 | 0.021907 | 0.0054937 | 6.2042e-06 | 3.7814e-06 | 0.033223 | 0.033223 | 0.033223 | 0.98091 | -0.36752 | 0.98121 | -0.36157 | 9.1272
110 | 0.0072617 | 0.0018196 | -0.0072601 | -0.001819 | 1.5375e-06 | 5.5759e-07 | 0.011016 | 0.011016 | 0.011016 | 0.98091 | -0.36752 | 0.98068 | -0.37196 | 3.0263
111 | 0.0053616 | 0.0013432 | -0.0053611 | -0.0013431 | 4.8851e-07 | 6.4308e-08 | 0.008135 | 0.0081351 | 0.0081351 | 0.98068 | -0.37196 | 0.98059 | -0.37387 | 2.2349
112 | 0.088664 | 0.0223 | -0.088599 | -0.022259 | 6.5497e-05 | 4.1796e-05 | 0.13434 | 0.13434 | 0.13434 | 0.98229 | -0.34018 | 0.9815 | -0.35565 | 36.9068
113 | 0.051888 | 0.013045 | -0.051851 | -0.013022 | 3.6252e-05 | 2.3004e-05 | 0.07868 | 0.07868 | 0.07868 | 0.9815 | -0.35565 | 0.98075 | -0.3703 | 21.6153
114 | 0.036711 | 0.0092133 | -0.036699 | -0.0092055 | 1.2486e-05 | 7.855e-06 | 0.055661 | 0.055661 | 0.055661 | 0.9815 | -0.35565 | 0.98113 | -0.36279 | 15.2915
115 | 0.0082836 | 0.0020762 | -0.0082825 | -0.0020757 | 1.0453e-06 | 4.4636e-07 | 0.012568 | 0.012568 | 0.012568 | 0.98075 | -0.3703 | 0.98061 | -0.37295 | 3.4528
116 | 0.032014 | 0.0080315 | -0.032001 | -0.0080231 | 1.3363e-05 | 8.3617e-06 | 0.048557 | 0.048557 | 0.048557 | 0.98113 | -0.36279 | 0.98069 | -0.37155 | 13.3398
117 | 0.0040977 | 0.0010269 | -0.0040976 | -0.0010269 | 1.6346e-07 | -3.7606e-08 | 0.006218 | 0.0062181 | 0.0062181 | 0.98061 | -0.37295 | 0.98057 | -0.37378 | 1.7083
118 | 0.011843 | 0.002969 | -0.011839 | -0.0029673 | 3.2479e-06 | 1.7403e-06 | 0.01797 | 0.01797 | 0.01797 | 0.98069 | -0.37155 | 0.98039 | -0.37731 | 4.9367
119 | 0.020158 | 0.0050541 | -0.020156 | -0.0050527 | 2.2934e-06 | 1.3853e-06 | 0.030587 | 0.030587 | 0.030587 | 0.98069 | -0.37155 | 0.98056 | -0.37394 | 8.4031
120 | -0.001707 | -0.00042781 | 0.001707 | 0.00042781 | 6.9619e-10 | -3.2856e-09 | 0.0025475 | 0.0025475 | 0.0025475 | 0.99708 | -0.055395 | 0.99708 | -0.055387 | 0.69985
121 | -0.0035706 | -0.00089487 | 0.0035707 | 0.00089478 | 1.4956e-07 | -8.7492e-08 | 0.0053286 | 0.0053286 | 0.0053286 | 0.99708 | -0.055387 | 0.99713 | -0.054508 | 1.4639
122 | 0.16563 | 0.042269 | -0.16558 | -0.042233 | 5.6845e-05 | 3.6251e-05 | 0.24744 | 0.24744 | 0.24744 | 0.99713 | -0.054508 | 0.99675 | -0.061614 | 33.9895
123 | -0.1692 | -0.043164 | 0.16937 | 0.043271 | 0.00016848 | 0.00010746 | 0.25277 | 0.25277 | 0.25277 | 0.99713 | -0.054508 | 0.99821 | -0.033913 | 34.7215
124 | 0.036965 | 0.0092723 | -0.036952 | -0.0092641 | 1.3008e-05 | 8.1856e-06 | 0.05606 | 0.05606 | 0.05606 | 0.98123 | -0.36111 | 0.98085 | -0.36849 | 15.4011
125 | -0.26006 | -0.066519 | 0.26009 | 0.066535 | 2.5625e-05 | 1.6376e-05 | 0.3875 | 0.3875 | 0.3875 | 0.99989 | -0.0020357 | 1 | 0 | 53.2276
126 | 0.25519 | 0.065297 | -0.25485 | -0.065077 | 0.00034401 | 0.00021984 | 0.38024 | 0.38024 | 0.38024 | 0.99989 | -0.0020357 | 0.99842 | -0.029923 | 52.2311
127 | 0.17958 | 0.045943 | -0.17929 | -0.04576 | 0.00028719 | 0.00018324 | 0.26755 | 0.26755 | 0.26755 | 1 | 0 | 0.99825 | -0.033096 | 36.751
128 | 0.24605 | 0.062873 | -0.24594 | -0.062802 | 0.00011054 | 7.0632e-05 | 0.36714 | 0.36714 | 0.36714 | 0.99842 | -0.029923 | 0.99793 | -0.039217 | 50.4307
129 | 0.17386 | 0.044397 | -0.17385 | -0.044393 | 6.8634e-06 | 4.3783e-06 | 0.25944 | 0.25944 | 0.25944 | 0.99825 | -0.033096 | 0.99821 | -0.033913 | 35.638
130 | 0.23527 | 0.060128 | -0.23486 | -0.05987 | 0.00040357 | 0.00025783 | 0.35122 | 0.35122 | 0.35122 | 0.99793 | -0.039217 | 0.99606 | -0.07475 | 48.2448
131 | -0.11246 | -0.028319 | 0.11252 | 0.028356 | 5.7863e-05 | 3.6964e-05 | 0.17002 | 0.17002 | 0.17002 | 0.98452 | -0.29677 | 0.98508 | -0.28602 | 46.7099
132 | -0.11408 | -0.028747 | 0.1145 | 0.029011 | 0.00041217 | 0.00026332 | 0.17239 | 0.17239 | 0.17239 | 0.98508 | -0.28602 | 0.98896 | -0.21079 | 47.3588
133 | -0.12198 | -0.030887 | 0.12212 | 0.030978 | 0.00014305 | 9.1407e-05 | 0.18365 | 0.18365 | 0.18365 | 0.98896 | -0.21079 | 0.99023 | -0.1864 | 50.4531
134 | -0.14086 | -0.035675 | 0.14102 | 0.035779 | 0.00016231 | 0.00010376 | 0.2118 | 0.2118 | 0.2118 | 0.99023 | -0.1864 | 0.99148 | -0.16243 | 58.1859
135 | -0.21545 | -0.05464 | 0.2157 | 0.054802 | 0.00025447 | 0.00016253 | 0.32358 | 0.32358 | 0.32358 | 0.99148 | -0.16243 | 0.99275 | -0.1379 | 44.4474
136 | -0.010388 | -0.0026034 | 0.010389 | 0.0026036 | 5.0609e-07 | 2.5548e-07 | 0.015769 | 0.015769 | 0.015769 | 0.98024 | -0.38028 | 0.98029 | -0.37926 | 4.3322
137 | 0.0076664 | 0.0019212 | -0.0076655 | -0.0019209 | 8.5288e-07 | 3.3418e-07 | 0.011638 | 0.011638 | 0.011638 | 0.98024 | -0.38028 | 0.98012 | -0.38262 | 3.1972
138 | -0.012096 | -0.0030315 | 0.012098 | 0.0030325 | 1.8502e-06 | 9.9958e-07 | 0.01836 | 0.01836 | 0.01836 | 0.98029 | -0.37926 | 0.98046 | -0.37605 | 5.0441
139 | 0.0041917 | 0.0010503 | -0.0041915 | -0.0010504 | 2.271e-07 | -4.3108e-08 | 0.0063637 | 0.0063638 | 0.0063638 | 0.98012 | -0.38262 | 0.98006 | -0.38375 | 1.7483
140 | -0.014805 | -0.003711 | 0.014805 | 0.0037111 | 2.6236e-07 | 1.5043e-07 | 0.022469 | 0.022469 | 0.022469 | 0.98046 | -0.37605 | 0.98048 | -0.37568 | 6.1728
141 | 0.0028133 | 0.00070496 | -0.0028132 | -0.00070505 | 7.1507e-08 | -8.594e-08 | 0.0042713 | 0.0042713 | 0.0042713 | 0.98006 | -0.38375 | 0.98004 | -0.38429 | 1.1734
142 | -0.01754 | -0.0043966 | 0.017542 | 0.0043975 | 1.4545e-06 | 8.6183e-07 | 0.02662 | 0.02662 | 0.02662 | 0.98048 | -0.37568 | 0.98056 | -0.37394 | 7.3133
143 | 0.0020339 | 0.0005096 | -0.0020338 | -0.00050972 | 4.3127e-08 | -1.2458e-07 | 0.0030869 | 0.0030869 | 0.0030869 | 0.98039 | -0.37731 | 0.98037 | -0.37775 | 0.84806
144 | 0.0098056 | 0.0024577 | -0.0098049 | -0.0024573 | 7.4938e-07 | 3.6585e-07 | 0.014883 | 0.014883 | 0.014883 | 0.98039 | -0.37731 | 0.98031 | -0.37891 | 4.0887

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45846 | 0.11677

## res_load
| p_mw | q_mvar
0 | 0.00034422 | 8.627e-05
1 | 0.0030207 | 0.00075706
2 | 0.0014428 | 0.00036159
3 | 0.0020675 | 0.00051815
4 | 0.0038731 | 0.00097069
5 | 0.0024327 | 0.0006097
6 | 0.0063005 | 0.0015791
7 | 0.0038937 | 0.00097586
8 | 0.0033601 | 0.00084213
9 | 0.0027055 | 0.00067807
10 | 0.004895 | 0.0012268
11 | 0.0026234 | 0.00065748
12 | 0.0020145 | 0.00050488
13 | 0.0013559 | 0.00033982
14 | 0.0057952 | 0.0014524
15 | 0.0019993 | 0.00050108
16 | 0.0016093 | 0.00040332
17 | 0.003659 | 0.00091703
18 | 0.0050068 | 0.0012548
19 | 0.0020799 | 0.00052127
20 | 0.0006575 | 0.00016478
21 | 0.0013361 | 0.00033486
22 | 0.0073529 | 0.0018428
23 | 0.011371 | 0.00285
24 | 0.0017522 | 0.00043914
25 | 0.0017216 | 0.00043148
26 | 0.0021377 | 0.00053575
27 | 0.0046046 | 0.001154
28 | 0.0014607 | 0.0003661
29 | 0.0021816 | 0.00054675
30 | 0.0010523 | 0.00026373
31 | 0.0018839 | 0.00047214
32 | 0.002176 | 0.00054535
33 | 0.0042284 | 0.0010597
34 | 0.00040348 | 0.00010112
35 | 0.0017876 | 0.00044802
36 | 0.0023168 | 0.00058063
37 | 0.0038395 | 0.00096228
38 | 0.0024687 | 0.00061872
39 | 0.0017132 | 0.00042938
40 | 0.0037126 | 0.00093046
41 | 0.0038876 | 0.00097433
42 | 0.0019971 | 0.00050051
43 | 0.0047067 | 0.0011796
44 | 0.001727 | 0.00043282
45 | 0.0020005 | 0.00050138
46 | 0.0063046 | 0.0015801
47 | 0.0016215 | 0.00040639
48 | 0.0042251 | 0.0010589
49 | 0.0033772 | 0.00084641
50 | 0.0045718 | 0.0011458
51 | 0.0019784 | 0.00049585
52 | 0.0023065 | 0.00057806
53 | 0.0049413 | 0.0012384
54 | 0.0019809 | 0.00049645
55 | 0.0042485 | 0.0010648
56 | 0.0017192 | 0.00043086
57 | 0.001806 | 0.00045262
58 | 0.0016712 | 0.00041884
59 | 0.0038969 | 0.00097667
60 | 0.0043237 | 0.0010836
61 | 0.0014947 | 0.00037461
62 | 0.0021741 | 0.00054489
63 | 0.004696 | 0.0011769
64 | 0.0020576 | 0.00051567
65 | 0.0026369 | 0.00066086
66 | 0.0079688 | 0.0019972
67 | 0.0028104 | 0.00070436
68 | 0.0041929 | 0.0010509
69 | 0.010317 | 0.0025858
70 | 0.0073948 | 0.0018533
71 | 0.003131 | 0.00078471
72 | 0.003103 | 0.00077767
73 | 0.01051 | 0.002634
74 | 0.0099491 | 0.0024935
75 | 0.0046018 | 0.0011533
76 | 0.0038357 | 0.00096131
77 | 0.0055608 | 0.0013937
78 | 0.0021446 | 0.0005375
79 | 0.0016124 | 0.0004041
80 | 0.00089932 | 0.00022539
81 | 0.0024583 | 0.00061611
82 | 0.0034557 | 0.00086608
83 | 0.0018986 | 0.00047582
84 | 0.0013191 | 0.0003306
85 | 0.0022109 | 0.00055411
86 | 0.0022409 | 0.00056162
87 | 0.0046843 | 0.001174
88 | 0.0041848 | 0.0010488
89 | 0.001707 | 0.00042781
90 | 0.0018636 | 0.00046706
91 | 0.0071906 | 0.0018021
92 | 0.016709 | 0.0041877
93 | 0.0048749 | 0.0012218
94 | 0.017139 | 0.0042954
95 | 0.0087945 | 0.0022041
96 | 0.005436 | 0.0013624
97 | 0.010673 | 0.0026748
98 | 0.0044762 | 0.0011218
99 | 0.0023112 | 0.00057924
100 | 0.00303 | 0.00075939
101 | 0.0015422 | 0.00038652
102 | 0.0017412 | 0.00043638
103 | 0.0015637 | 0.0003919
104 | 0.0074857 | 0.0018761
105 | 0.0027218 | 0.00068214
106 | 0.0017071 | 0.00042783
107 | 0.0027072 | 0.0006785
108 | 0.0013782 | 0.00034541
109 | 0.0027353 | 0.00068553
110 | 0.0028132 | 0.00070505
111 | 0.0026142 | 0.00065517
112 | 0.016485 | 0.0041315
113 | 0.0030719 | 0.00076989
114 | 0.0020338 | 0.00050972
115 | 0.0098049 | 0.0024573
116 | 0.0046766 | 0.0011721
117 | 0.0040976 | 0.0010269

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1