## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1362-23_0_1_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1362-23_0_1_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1362-23_0_1_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1362-23_0_1_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1362-23_0_1_node_216 | 0.4 | n |  | TRUE
5 | bus_LV_1362-23_0_1_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1362-23_0_1_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1362-23_0_1_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1362-23_0_1_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1362-23_0_1_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1362-23_0_1_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1362-23_0_1_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1362-23_0_1_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1362-23_0_1_node_224 | 0.4 | n |  | TRUE
14 | bus_LV_1362-23_0_1_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_1362-23_0_1_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1362-23_0_1_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_1362-23_0_1_node_217 | 0.4 | n |  | TRUE
18 | bus_LV_1362-23_0_1_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_1362-23_0_1_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1362-23_0_1_node_215 | 0.4 | n |  | TRUE
21 | bus_LV_1362-23_0_1_node_234 | 0.4 | n |  | TRUE
22 | bus_LV_1362-23_0_1_node_225 | 0.4 | n |  | TRUE
23 | bus_LV_1362-23_0_1_node_226 | 0.4 | n |  | TRUE
24 | bus_LV_1362-23_0_1_node_227 | 0.4 | n |  | TRUE
25 | bus_LV_1362-23_0_1_node_228 | 0.4 | n |  | TRUE
26 | bus_LV_1362-23_0_1_node_235 | 0.4 | n |  | TRUE
27 | bus_MV_0_node_7 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1362-23_0_1_load_0 | 0 | 0.0042871 | 0.0010745 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1362-23_0_1_load_1 | 1 | 0.0012913 | 0.00032362 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1362-23_0_1_load_2 | 2 | 0.0018917 | 0.0004741 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1362-23_0_1_load_216 | 4 | 0.00077338 | 0.00019383 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1362-23_0_1_load_4 | 5 | 0.0017321 | 0.00043409 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1362-23_0_1_load_5 | 6 | 0.0003749 | 9.3958e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1362-23_0_1_load_6 | 9 | 0.0019571 | 0.00049049 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1362-23_0_1_load_7 | 10 | 0.0030121 | 0.0007549 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1362-23_0_1_load_9 | 11 | 0.0038819 | 0.00097289 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1362-23_0_1_load_10 | 12 | 0.00097888 | 0.00024533 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1362-23_0_1_load_224 | 13 | 0.00059563 | 0.00014928 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1362-23_0_1_load_12 | 14 | 0.001933 | 0.00048445 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1362-23_0_1_load_217 | 17 | 0.00077722 | 0.00019479 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1362-23_0_1_load_15 | 18 | 0.0011556 | 0.00028962 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1362-23_0_1_load_225 | 22 | 0.0013711 | 0.00034363 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1362-23_0_1_load_226 | 23 | 0.0014876 | 0.00037282 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1362-23_0_1_load_228 | 25 | 0.00202 | 0.00050625 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1362-23_0_1_load_235 | 26 | 0.00059787 | 0.00014984 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1362-23_0_1_line_0 |  | 0 | 1 | 0.064544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1362-23_0_1_line_1 |  | 0 | 2 | 0.035625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1362-23_0_1_line_2 |  | 1 | 3 | 0.12106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1362-23_0_1_line_3 |  | 2 | 4 | 0.38927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1362-23_0_1_line_4 |  | 3 | 5 | 0.23233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1362-23_0_1_line_5 |  | 3 | 6 | 0.046256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1362-23_0_1_line_6 |  | 4 | 21 | 0.46846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1362-23_0_1_line_7 |  | 4 | 20 | 0.2572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1362-23_0_1_line_8 |  | 5 | 7 | 0.0062537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1362-23_0_1_line_9 |  | 6 | 8 | 0.28639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1362-23_0_1_line_10 |  | 7 | 11 | 0.020118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1362-23_0_1_line_11 |  | 7 | 9 | 0.028201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1362-23_0_1_line_12 |  | 8 | 13 | 0.057453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1362-23_0_1_line_13 |  | 9 | 10 | 0.063214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1362-23_0_1_line_14 |  | 11 | 12 | 0.021641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1362-23_0_1_line_15 |  | 13 | 22 | 0.2647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1362-23_0_1_line_16 |  | 14 | 15 | 0.037068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1362-23_0_1_line_17 |  | 14 | 16 | 0.027846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1362-23_0_1_line_18 |  | 15 | 17 | 0.17512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1362-23_0_1_line_19 |  | 16 | 18 | 0.009151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1362-23_0_1_line_20 |  | 18 | 19 | 0.03728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1362-23_0_1_line_21 |  | 19 | 20 | 0.14342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1362-23_0_1_line_22 |  | 21 | 26 | 0.020748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1362-23_0_1_line_23 |  | 22 | 23 | 0.049936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1362-23_0_1_line_24 |  | 23 | 24 | 0.050039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1362-23_0_1_line_25 |  | 24 | 25 | 0.15354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1362-23_0_1_trafo_7 | 0.63 MVA 20/0.4 kV | 27 | 10 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2684785.733 | 1213381.8803 | 2684773.8043 | 1213391.5194 | 2684731.9485 | 1213407.2683 | 2684728.1175 | 1213409.6032
1 | 2684785.733 | 1213381.8803 | 2684813.4424 | 1213359.4898
2 | 2684649.9783 | 1213487.3795 | 2684668.9051 | 1213486.6476 | 2684676.3121 | 1213483.9732 | 2684687.4628 | 1213474.4586 | 2684692.9297 | 1213463.9738 | 2684702.6416 | 1213432.7578 | 2684706.6116 | 1213426.0319 | 2684715.0124 | 1213417.5901 | 2684728.1175 | 1213409.6032
3 | 2684813.4424 | 1213359.4898 | 2684949.7831 | 1212994.8727
4 | 2684649.9783 | 1213487.3795 | 2684623.0514 | 1213456.5881 | 2684604.5017 | 1213430.7524 | 2684595.7065 | 1213424.1789 | 2684568.8432 | 1213411.345 | 2684516.929 | 1213370.3599 | 2684477.7114 | 1213335.1148
5 | 2684649.9783 | 1213487.3795 | 2684642.2247 | 1213487.7141 | 2684617.4953 | 1213485.1393 | 2684604.0516 | 1213482.881
6 | 2684949.7831 | 1212994.8727 | 2685310.3364 | 1212695.7879
7 | 2684710.6355 | 1212938.1453 | 2684721.3741 | 1212937.9199 | 2684749.725 | 1212942.4367 | 2684768.0017 | 1212950.1459 | 2684862.7469 | 1213003.306 | 2684874.9955 | 1213007.483 | 2684891.7763 | 1213008.1667 | 2684936.9885 | 1212997.0252 | 2684949.7831 | 1212994.8727
8 | 2684473.06 | 1213330.9346 | 2684477.7114 | 1213335.1148
9 | 2684542.0941 | 1213567.7356 | 2684532.3563 | 1213558.5359 | 2684515.6014 | 1213540.0641 | 2684501.7294 | 1213521.8555 | 2684495.2774 | 1213510.7568 | 2684486.6962 | 1213483.7285 | 2684483.5581 | 1213480.0149 | 2684468.188 | 1213471.0135 | 2684463.1731 | 1213465.7168 | 2684462.8087 | 1213459.2629 | 2684470.5636 | 1213453.48 | 2684478.7777 | 1213452.8182 | 2684505.7891 | 1213455.2024 | 2684562.5485 | 1213475.9094 | 2684604.0516 | 1213482.881
10 | 2684473.06 | 1213330.9346 | 2684463.5256 | 1213322.3606 | 2684457.6745 | 1213318.0028
11 | 2684473.06 | 1213330.9346 | 2684477.9998 | 1213331.8941 | 2684486.8476 | 1213332.631 | 2684500.7651 | 1213335.8748
12 | 2684542.0941 | 1213567.7356 | 2684588.7812 | 1213601.2202
13 | 2684557.7446 | 1213341.1525 | 2684549.999 | 1213341.4429 | 2684542.5139 | 1213344.7945 | 2684531.1437 | 1213348.8916 | 2684525.3071 | 1213350.6434 | 2684520.1338 | 1213349.5471 | 2684514.4621 | 1213346.6315 | 2684507.2131 | 1213340.8361 | 2684500.7651 | 1213335.8748
14 | 2684439.4838 | 1213306.3237 | 2684452.2188 | 1213313.9394 | 2684457.6745 | 1213318.0028
15 | 2684588.7812 | 1213601.2202 | 2684589.5395 | 1213601.7641 | 2684608.84 | 1213617.4927 | 2684658.0917 | 1213663.8889 | 2684672.5575 | 1213672.322 | 2684682.129 | 1213672.3468 | 2684695.759 | 1213664.7576 | 2684734.5585 | 1213623.3925 | 2684744.4069 | 1213619.9746 | 2684772.5916 | 1213625.2675 | 2684783.3008 | 1213625.4199 | 2684805.1196 | 1213618.948 | 2684805.1196 | 1213618.948
16 | 2684493.5787 | 1212982.1067 | 2684506.9827 | 1212984.1201 | 2684521.2233 | 1212985.5339 | 2684527.9143 | 1212988.3862 | 2684529.7318 | 1212989.0339
17 | 2684551.2079 | 1213006.0946 | 2684543.2673 | 1212998.1435 | 2684538.1393 | 1212993.301 | 2684535.3224 | 1212991.0262 | 2684529.7318 | 1212989.0339
18 | 2684331.4921 | 1212915.807 | 2684493.5787 | 1212982.1067
19 | 2684551.2079 | 1213006.0946 | 2684560.324 | 1213006.8942
20 | 2684596.9292 | 1213002.396 | 2684584.6811 | 1213005.6689 | 2684572.0752 | 1213007.925 | 2684560.324 | 1213006.8942
21 | 2684710.6355 | 1212938.1453 | 2684705.4144 | 1212938.249 | 2684695.5902 | 1212939.8883 | 2684680.7716 | 1212945.4594 | 2684661.8483 | 1212956.5314 | 2684640.5956 | 1212971.1283 | 2684628.876 | 1212983.1921 | 2684616.7485 | 1213002.5884 | 2684607.9152 | 1213009.3564 | 2684601.9967 | 1213008.8277 | 2684596.9292 | 1213002.396
22 | 2685329.4619 | 1212687.7228 | 2685323.5189 | 1212690.473 | 2685316.5415 | 1212693.8309 | 2685310.3364 | 1212695.7879
23 | 2684805.1196 | 1213618.948 | 2684814.9998 | 1213618.6439 | 2684822.5728 | 1213620.3082 | 2684836.0069 | 1213626.5034 | 2684850.6055 | 1213636.1598
24 | 2684896.9066 | 1213648.6179 | 2684877.2282 | 1213649.8831 | 2684867.6156 | 1213647.4114 | 2684850.6055 | 1213636.1598
25 | 2684896.9066 | 1213648.6179 | 2684907.8105 | 1213658.5686 | 2684901.1011 | 1213671.4705 | 2684877.1833 | 1213691.4433 | 2684822.2427 | 1213715.0328 | 2684795.2444 | 1213721.9645 | 2684793.3869 | 1213727.0415

## bus_geodata
| x | y | coords
0 | 2684785.733 | 1213381.8803
1 | 2684728.1175 | 1213409.6032
2 | 2684813.4424 | 1213359.4898
3 | 2684649.9783 | 1213487.3795
4 | 2684949.7831 | 1212994.8727
5 | 2684477.7114 | 1213335.1148
6 | 2684604.0516 | 1213482.881
7 | 2684473.0601 | 1213330.9346
8 | 2684542.0941 | 1213567.7356
9 | 2684500.7651 | 1213335.8748
10 | 2684557.7446 | 1213341.1525
11 | 2684457.6745 | 1213318.0028
12 | 2684439.4838 | 1213306.3237
13 | 2684588.7812 | 1213601.2202
14 | 2684529.7318 | 1212989.0339
15 | 2684493.5787 | 1212982.1067
16 | 2684551.2079 | 1213006.0946
17 | 2684331.4921 | 1212915.807
18 | 2684560.324 | 1213006.8942
19 | 2684596.9292 | 1213002.396
20 | 2684710.6355 | 1212938.1453
21 | 2685310.3364 | 1212695.7879
22 | 2684805.1196 | 1213618.948
23 | 2684850.6055 | 1213636.1598
24 | 2684896.9066 | 1213648.6179
25 | 2684793.3869 | 1213727.0415
26 | 2685329.4619 | 1212687.7228
27 | 2684557.7446 | 1213341.1525

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99165 | -0.16131 | 0.0042871 | 0.0010745
1 | 0.99232 | -0.1482 | 0.0012913 | 0.00032362
2 | 0.99141 | -0.16584 | 0.0018917 | 0.0004741
3 | 0.99373 | -0.12088 | 0 | 0
4 | 0.98955 | -0.20237 | 0.00077338 | 0.00019383
5 | 0.99767 | -0.044712 | 0.0017321 | 0.00043409
6 | 0.99348 | -0.12568 | 0.0003749 | 9.3958e-05
7 | 0.99779 | -0.04248 | 0 | 0
8 | 0.99205 | -0.15353 | 0 | 0
9 | 0.99844 | -0.030023 | 0.0019571 | 0.00049049
10 | 1 | 0 | -0.028937 | -0.0068701
11 | 0.9977 | -0.044192 | 0.0038819 | 0.00097289
12 | 0.99768 | -0.044563 | 0.00097888 | 0.00024533
13 | 0.99176 | -0.15912 | 0.00059563 | 0.00014928
14 | 0.9879 | -0.23447 | 0.001933 | 0.00048445
15 | 0.98788 | -0.23499 | 0 | 0
16 | 0.98797 | -0.23312 | 0 | 0
17 | 0.98775 | -0.23743 | 0.00077722 | 0.00019479
18 | 0.98799 | -0.23267 | 0.0011556 | 0.00028962
19 | 0.98813 | -0.23009 | 0 | 0
20 | 0.98863 | -0.22017 | 0 | 0
21 | 0.98929 | -0.20743 | 0 | 0
22 | 0.99058 | -0.18209 | 0.0013711 | 0.00034363
23 | 0.99042 | -0.18521 | 0.0014876 | 0.00037282
24 | 0.99032 | -0.18701 | 0 | 0
25 | 0.99004 | -0.19253 | 0.00202 | 0.00050625
26 | 0.98928 | -0.20765 | 0.00059787 | 0.00014984
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.011432 | -0.0028512 | 0.01144 | 0.0028549 | 7.1188e-06 | 3.7228e-06 | 0.01715 | 0.01715 | 0.01715 | 0.99165 | -0.16131 | 0.99232 | -0.1482 | 4.7116
1 | 0.0071454 | 0.0017767 | -0.0071438 | -0.0017762 | 1.5344e-06 | 5.2253e-07 | 0.010717 | 0.010717 | 0.010717 | 0.99165 | -0.16131 | 0.99141 | -0.16584 | 2.9443
2 | -0.012731 | -0.0031785 | 0.012747 | 0.0031875 | 1.6536e-05 | 9.0173e-06 | 0.019086 | 0.019086 | 0.019086 | 0.99232 | -0.1482 | 0.99373 | -0.12088 | 5.2434
3 | 0.0052521 | 0.0013021 | -0.0052431 | -0.0013013 | 9.0617e-06 | 7.8924e-07 | 0.0078779 | 0.0078797 | 0.0078797 | 0.99141 | -0.16584 | 0.98955 | -0.20237 | 2.1647
4 | -0.018613 | -0.0046524 | 0.018681 | 0.0046927 | 6.7656e-05 | 4.0278e-05 | 0.027867 | 0.027866 | 0.027867 | 0.99373 | -0.12088 | 0.99767 | -0.044712 | 7.6558
5 | 0.0058658 | 0.0014648 | -0.0058644 | -0.0014646 | 1.3377e-06 | 2.5701e-07 | 0.0087816 | 0.0087818 | 0.0087818 | 0.99373 | -0.12088 | 0.99348 | -0.12568 | 2.4126
6 | 0.00059802 | 0.00014365 | -0.00059788 | -0.00014958 | 1.417e-07 | -5.9257e-06 | 0.00089709 | 0.00089918 | 0.00089918 | 0.98955 | -0.20237 | 0.98929 | -0.20743 | 0.24703
7 | 0.0038717 | 0.00096382 | -0.0038684 | -0.00096503 | 3.2673e-06 | -1.21e-06 | 0.0058197 | 0.0058208 | 0.0058208 | 0.98955 | -0.20237 | 0.98863 | -0.22017 | 1.5991
8 | -0.020413 | -0.0051267 | 0.020415 | 0.0051281 | 2.1743e-06 | 1.3099e-06 | 0.030449 | 0.030449 | 0.030449 | 0.99767 | -0.044712 | 0.99779 | -0.04248 | 8.3652
9 | 0.0054895 | 0.0013706 | -0.0054823 | -0.0013697 | 7.2582e-06 | 9.4221e-07 | 0.0082203 | 0.0082216 | 0.0082216 | 0.99348 | -0.12568 | 0.99205 | -0.15353 | 2.2587
10 | 0.0048612 | 0.0012179 | -0.0048608 | -0.0012179 | 3.9649e-07 | -8.9959e-09 | 0.0072494 | 0.0072495 | 0.0072495 | 0.99779 | -0.04248 | 0.9977 | -0.044192 | 1.9916
11 | -0.025276 | -0.006346 | 0.025291 | 0.0063552 | 1.503e-05 | 9.2504e-06 | 0.037699 | 0.037699 | 0.037699 | 0.99779 | -0.04248 | 0.99844 | -0.030023 | 10.3568
12 | 0.0054823 | 0.0013697 | -0.0054808 | -0.0013695 | 1.4564e-06 | 1.9049e-07 | 0.0082216 | 0.0082218 | 0.0082218 | 0.99205 | -0.15353 | 0.99176 | -0.15912 | 2.2587
13 | -0.027248 | -0.0068457 | 0.027287 | 0.0068699 | 3.9104e-05 | 2.4199e-05 | 0.040615 | 0.040615 | 0.040615 | 0.99844 | -0.030023 | 1 | 0 | 11.1581
14 | 0.00097889 | 0.00024506 | -0.00097888 | -0.00024533 | 1.7297e-08 | -2.7153e-07 | 0.0014599 | 0.00146 | 0.00146 | 0.9977 | -0.044192 | 0.99768 | -0.044563 | 0.40109
15 | 0.0048852 | 0.0012202 | -0.0048798 | -0.0012202 | 5.3314e-06 | 5.4599e-10 | 0.0073282 | 0.0073294 | 0.0073294 | 0.99176 | -0.15912 | 0.99058 | -0.18209 | 2.0136
16 | 0.00077733 | 0.00019214 | -0.00077731 | -0.0001926 | 1.9028e-08 | -4.6242e-07 | 0.0011699 | 0.0011701 | 0.0011701 | 0.9879 | -0.23447 | 0.98788 | -0.23499 | 0.32145
17 | -0.0027103 | -0.00067659 | 0.0027105 | 0.00067634 | 1.7394e-07 | -2.4524e-07 | 0.0040814 | 0.0040813 | 0.0040814 | 0.9879 | -0.23447 | 0.98797 | -0.23312 | 1.1213
18 | 0.00077731 | 0.0001926 | -0.00077722 | -0.00019479 | 8.9968e-08 | -2.1842e-06 | 0.0011701 | 0.0011709 | 0.0011709 | 0.98788 | -0.23499 | 0.98775 | -0.23743 | 0.32167
19 | -0.0027105 | -0.00067634 | 0.0027105 | 0.00067626 | 5.716e-08 | -8.0605e-08 | 0.0040813 | 0.0040812 | 0.0040813 | 0.98797 | -0.23312 | 0.98799 | -0.23267 | 1.1212
20 | -0.0038661 | -0.00096587 | 0.0038666 | 0.0009657 | 4.738e-07 | -1.7425e-07 | 0.0058217 | 0.0058215 | 0.0058217 | 0.98799 | -0.23267 | 0.98813 | -0.23009 | 1.5994
21 | -0.0038666 | -0.0009657 | 0.0038684 | 0.00096503 | 1.8224e-06 | -6.717e-07 | 0.0058215 | 0.0058208 | 0.0058215 | 0.98813 | -0.23009 | 0.98863 | -0.22017 | 1.5993
22 | 0.00059788 | 0.00014958 | -0.00059787 | -0.00014984 | 6.2915e-09 | -2.6237e-07 | 0.00089918 | 0.00089928 | 0.00089928 | 0.98929 | -0.20743 | 0.98928 | -0.20765 | 0.24705
23 | 0.0035087 | 0.00087658 | -0.0035082 | -0.00087689 | 5.2004e-07 | -3.099e-07 | 0.0052697 | 0.00527 | 0.00527 | 0.99058 | -0.18209 | 0.99042 | -0.18521 | 1.4478
24 | 0.0020207 | 0.00050408 | -0.0020205 | -0.00050461 | 1.7286e-07 | -5.3326e-07 | 0.003035 | 0.0030353 | 0.0030353 | 0.99042 | -0.18521 | 0.99032 | -0.18701 | 0.83387
25 | 0.0020205 | 0.00050461 | -0.00202 | -0.00050625 | 5.3056e-07 | -1.6354e-06 | 0.0030353 | 0.003036 | 0.003036 | 0.99032 | -0.18701 | 0.99004 | -0.19253 | 0.83406

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.031949 | 0.007625

## res_load
| p_mw | q_mvar
0 | 0.0042871 | 0.0010745
1 | 0.0012913 | 0.00032362
2 | 0.0018917 | 0.0004741
3 | 0.00077338 | 0.00019383
4 | 0.0017321 | 0.00043409
5 | 0.0003749 | 9.3958e-05
6 | 0.0019571 | 0.00049049
7 | 0.0030121 | 0.0007549
8 | 0.0038819 | 0.00097289
9 | 0.00097888 | 0.00024533
10 | 0.00059563 | 0.00014928
11 | 0.001933 | 0.00048445
12 | 0.00077722 | 0.00019479
13 | 0.0011556 | 0.00028962
14 | 0.0013711 | 0.00034363
15 | 0.0014876 | 0.00037282
16 | 0.00202 | 0.00050625
17 | 0.00059787 | 0.00014984

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1