## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1362-8_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1362-8_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1362-8_0_5_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_1362-8_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1362-8_0_5_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1362-8_0_5_node_39 | 0.4 | n |  | TRUE
6 | bus_LV_1362-8_0_5_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1362-8_0_5_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_1362-8_0_5_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1362-8_0_5_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1362-8_0_5_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1362-8_0_5_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_1362-8_0_5_node_33 | 0.4 | n |  | TRUE
13 | bus_LV_1362-8_0_5_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1362-8_0_5_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_1362-8_0_5_node_35 | 0.4 | n |  | TRUE
16 | bus_LV_1362-8_0_5_node_36 | 0.4 | n |  | TRUE
17 | bus_LV_1362-8_0_5_node_34 | 0.4 | n |  | TRUE
18 | bus_LV_1362-8_0_5_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1362-8_0_5_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1362-8_0_5_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1362-8_0_5_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1362-8_0_5_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1362-8_0_5_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1362-8_0_5_node_37 | 0.4 | n |  | TRUE
25 | bus_LV_1362-8_0_5_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_1362-8_0_5_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_1362-8_0_5_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1362-8_0_5_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1362-8_0_5_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1362-8_0_5_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_1362-8_0_5_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_1362-8_0_5_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_1362-8_0_5_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_1362-8_0_5_node_27 | 0.4 | n |  | TRUE
35 | bus_MV_1_0_node_141 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1362-8_0_5_load_0 | 0 | 0.004273 | 0.0010709 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1362-8_0_5_load_3 | 3 | 0.0076613 | 0.0019201 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1362-8_0_5_load_39 | 5 | 0.00065263 | 0.00016357 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1362-8_0_5_load_32 | 7 | 0.016523 | 0.004141 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1362-8_0_5_load_9 | 9 | 0.005868 | 0.0014707 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1362-8_0_5_load_33 | 12 | 0.0096552 | 0.0024198 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1362-8_0_5_load_8 | 13 | 0.04002 | 0.01003 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1362-8_0_5_load_35 | 15 | 0.0065331 | 0.0016373 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1362-8_0_5_load_36 | 16 | 0.096901 | 0.024286 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1362-8_0_5_load_34 | 17 | 0.0097432 | 0.0024419 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1362-8_0_5_load_19 | 18 | 0.0034185 | 0.00085676 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1362-8_0_5_load_13 | 19 | 0.004443 | 0.0011135 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1362-8_0_5_load_11 | 20 | 0.0040331 | 0.0010108 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1362-8_0_5_load_12 | 21 | 0.0013012 | 0.00032611 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1362-8_0_5_load_37 | 24 | 0.097261 | 0.024376 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1362-8_0_5_load_29 | 25 | 0.097749 | 0.024498 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1362-8_0_5_load_20 | 26 | 0.0066526 | 0.0016673 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1362-8_0_5_load_21 | 27 | 0.0027044 | 0.0006778 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1362-8_0_5_load_31 | 32 | 0.096329 | 0.024142 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1362-8_0_5_load_30 | 33 | 0.0022659 | 0.0005679 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1362-8_0_5_load_27 | 34 | 0.062073 | 0.015557 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1362-8_0_5_line_0 |  | 0 | 1 | 0.040539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1362-8_0_5_line_1 |  | 1 | 2 | 0.011011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1362-8_0_5_line_2 |  | 2 | 6 | 0.029875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1362-8_0_5_line_3 |  | 3 | 4 | 0.061395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1362-8_0_5_line_4 |  | 3 | 5 | 0.02931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1362-8_0_5_line_5 |  | 4 | 8 | 0.047316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1362-8_0_5_line_6 |  | 6 | 7 | 0.027292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1362-8_0_5_line_7 |  | 7 | 11 | 0.017296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1362-8_0_5_line_8 |  | 8 | 12 | 0.035385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1362-8_0_5_line_9 |  | 9 | 10 | 0.016949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1362-8_0_5_line_10 |  | 10 | 20 | 0.0044853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1362-8_0_5_line_11 |  | 10 | 21 | 0.0088773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1362-8_0_5_line_12 |  | 11 | 21 | 0.022174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1362-8_0_5_line_13 |  | 12 | 17 | 0.041389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1362-8_0_5_line_14 |  | 13 | 14 | 0.051721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1362-8_0_5_line_15 |  | 14 | 18 | 0.012168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1362-8_0_5_line_16 |  | 14 | 19 | 0.029373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1362-8_0_5_line_17 |  | 15 | 16 | 0.058742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1362-8_0_5_line_18 |  | 16 | 23 | 0.02032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_1362-8_0_5_line_19 |  | 17 | 32 | 0.020873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1362-8_0_5_line_20 |  | 18 | 20 | 0.017427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1362-8_0_5_line_21 |  | 19 | 22 | 0.035278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1362-8_0_5_line_22 |  | 22 | 23 | 0.046084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1362-8_0_5_line_23 |  | 23 | 24 | 0.040054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_1362-8_0_5_line_24 |  | 24 | 25 | 0.016157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1362-8_0_5_line_25 |  | 25 | 31 | 0.018324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_1362-8_0_5_line_26 |  | 26 | 27 | 0.017116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1362-8_0_5_line_27 |  | 26 | 28 | 0.035765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1362-8_0_5_line_28 |  | 27 | 29 | 0.030974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1362-8_0_5_line_29 |  | 28 | 30 | 0.053396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1362-8_0_5_line_30 |  | 28 | 31 | 0.034133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_1362-8_0_5_line_31 |  | 29 | 32 | 0.05302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1362-8_0_5_line_32 |  | 30 | 33 | 0.0086298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1362-8_0_5_line_33 |  | 31 | 34 | 0.034744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1362-8_0_5_trafo_36 | 0.63 MVA 20/0.4 kV | 35 | 16 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2682496.6366 | 1213017.2207 | 2682519.643 | 1213050.5993
1 | 2682496.6366 | 1213017.2207 | 2682503.9756 | 1213008.9946
2 | 2682483.0749 | 1212987.5916 | 2682503.9756 | 1213008.9946
3 | 2682631.7185 | 1213024.9511 | 2682621.7992 | 1213042.2806 | 2682604.0516 | 1213066.9509 | 2682596.4995 | 1213074.9986
4 | 2682596.4995 | 1213074.9986 | 2682604.6592 | 1213103.1497
5 | 2682650.8867 | 1212981.6773 | 2682631.7185 | 1213024.9511
6 | 2682503.2657 | 1212969.1699 | 2682483.0749 | 1212987.5916
7 | 2682516.234 | 1212957.6862 | 2682503.2657 | 1212969.1699
8 | 2682650.8867 | 1212981.6773 | 2682665.1195 | 1212949.2806
9 | 2682537.4608 | 1212971.4556 | 2682526.1786 | 1212984.1036
10 | 2682537.4608 | 1212971.4556 | 2682540.4496 | 1212968.1112
11 | 2682537.4608 | 1212971.4556 | 2682531.5485 | 1212964.8335
12 | 2682516.234 | 1212957.6862 | 2682521.2184 | 1212953.2634 | 2682531.5485 | 1212964.8335
13 | 2682665.1195 | 1212949.2806 | 2682665.714 | 1212947.9274 | 2682681.9429 | 1212911.4647
14 | 2682561.7536 | 1212947.6095 | 2682594.3837 | 1212987.7389
15 | 2682561.7536 | 1212947.6095 | 2682552.6533 | 1212955.6873
16 | 2682561.7536 | 1212947.6095 | 2682551.4496 | 1212926.3419 | 2682548.3178 | 1212921.5309
17 | 2682610.3816 | 1212931.8104 | 2682578.1083 | 1212882.7282
18 | 2682566.9446 | 1212865.7501 | 2682578.1083 | 1212882.7282
19 | 2682690.4306 | 1212892.395 | 2682681.9429 | 1212911.4647
20 | 2682552.6533 | 1212955.6873 | 2682550.1232 | 1212957.9331 | 2682542.4074 | 1212965.9204 | 2682540.4496 | 1212968.1112
21 | 2682529.072 | 1212891.9653 | 2682548.3178 | 1212921.5309
22 | 2682566.9446 | 1212865.7501 | 2682549.1666 | 1212876.133 | 2682529.072 | 1212891.9653
23 | 2682566.9446 | 1212865.7501 | 2682586.8216 | 1212852.4721 | 2682599.012 | 1212841.8795
24 | 2682599.012 | 1212841.8795 | 2682611.0537 | 1212831.4161 | 2682611.1462 | 1212831.2338
25 | 2682613.3784 | 1212813.8813 | 2682614.6437 | 1212819.0689 | 2682614.5686 | 1212824.4936 | 2682611.1462 | 1212831.2338
26 | 2682682.1554 | 1212835.6323 | 2682677.4779 | 1212834.3272 | 2682669.0064 | 1212825.4648
27 | 2682644.2938 | 1212799.6114 | 2682669.0064 | 1212825.4648
28 | 2682711.9897 | 1212843.9564 | 2682682.1554 | 1212835.6323
29 | 2682599.0542 | 1212808.0347 | 2682606.3143 | 1212805.5336 | 2682624.1707 | 1212797.1866 | 2682626.4656 | 1212802.0882 | 2682640.8639 | 1212796.017 | 2682644.2938 | 1212799.6114
30 | 2682613.3784 | 1212813.8813 | 2682628.8936 | 1212807.2586 | 2682640.0445 | 1212802.5099 | 2682644.2938 | 1212799.6114
31 | 2682711.9897 | 1212843.9564 | 2682690.4306 | 1212892.395
32 | 2682599.0542 | 1212808.0347 | 2682595.7382 | 1212800.0674
33 | 2682613.3784 | 1212813.8813 | 2682601.1499 | 1212819.0932 | 2682580.8778 | 1212826.1077

## bus_geodata
| x | y | coords
0 | 2682519.643 | 1213050.5993
1 | 2682496.6366 | 1213017.2207
2 | 2682503.9756 | 1213008.9946
3 | 2682596.4995 | 1213074.9986
4 | 2682631.7185 | 1213024.9511
5 | 2682604.6592 | 1213103.1497
6 | 2682483.0749 | 1212987.5916
7 | 2682503.2657 | 1212969.1699
8 | 2682650.8867 | 1212981.6773
9 | 2682526.1786 | 1212984.1036
10 | 2682537.4608 | 1212971.4556
11 | 2682516.234 | 1212957.6862
12 | 2682665.1195 | 1212949.2806
13 | 2682594.3837 | 1212987.7389
14 | 2682561.7536 | 1212947.6095
15 | 2682610.3816 | 1212931.8104
16 | 2682578.1083 | 1212882.7282
17 | 2682681.9429 | 1212911.4647
18 | 2682552.6533 | 1212955.6873
19 | 2682548.3178 | 1212921.5309
20 | 2682540.4496 | 1212968.1112
21 | 2682531.5485 | 1212964.8335
22 | 2682529.072 | 1212891.9653
23 | 2682566.9446 | 1212865.7501
24 | 2682599.012 | 1212841.8795
25 | 2682611.1462 | 1212831.2339
26 | 2682669.0064 | 1212825.4648
27 | 2682682.1554 | 1212835.6323
28 | 2682644.2938 | 1212799.6114
29 | 2682711.9897 | 1212843.9564
30 | 2682599.0542 | 1212808.0347
31 | 2682613.3784 | 1212813.8813
32 | 2682690.4306 | 1212892.395
33 | 2682595.7382 | 1212800.0674
34 | 2682580.8778 | 1212826.1077
35 | 2682566.9446 | 1212865.7501

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98741 | -0.24206 | 0.004273 | 0.0010709
1 | 0.98757 | -0.23897 | 0 | 0
2 | 0.98761 | -0.23813 | 0 | 0
3 | 0.97155 | -0.54947 | 0.0076613 | 0.0019201
4 | 0.97203 | -0.54005 | 0 | 0
5 | 0.97153 | -0.54982 | 0.00065263 | 0.00016357
6 | 0.98773 | -0.23584 | 0 | 0
7 | 0.98784 | -0.23376 | 0.016523 | 0.004141
8 | 0.97239 | -0.53279 | 0 | 0
9 | 0.98868 | -0.21738 | 0.005868 | 0.0014707
10 | 0.98877 | -0.21561 | 0 | 0
11 | 0.98817 | -0.22734 | 0 | 0
12 | 0.97267 | -0.52737 | 0.0096552 | 0.0024198
13 | 0.98789 | -0.23266 | 0.04002 | 0.01003
14 | 0.98979 | -0.19576 | 0 | 0
15 | 0.99965 | -0.0066922 | 0.0065331 | 0.0016373
16 | 1 | 0 | -0.48661 | -0.12379
17 | 0.97336 | -0.51367 | 0.0097432 | 0.0024419
18 | 0.9894 | -0.20344 | 0.0034185 | 0.00085676
19 | 0.99183 | -0.15642 | 0.004443 | 0.0011135
20 | 0.98888 | -0.21337 | 0.0040331 | 0.0010108
21 | 0.98859 | -0.21911 | 0.0013012 | 0.00032611
22 | 0.99441 | -0.10662 | 0 | 0
23 | 0.99779 | -0.041943 | 0 | 0
24 | 0.99417 | -0.11105 | 0.097261 | 0.024376
25 | 0.99307 | -0.13212 | 0.097749 | 0.024498
26 | 0.98563 | -0.27445 | 0.0066526 | 0.0016673
27 | 0.98361 | -0.31345 | 0.0027044 | 0.0006778
28 | 0.99008 | -0.18923 | 0 | 0
29 | 0.98003 | -0.38293 | 0 | 0
30 | 0.98996 | -0.19138 | 0 | 0
31 | 0.99223 | -0.14814 | 0 | 0
32 | 0.9739 | -0.50303 | 0.096329 | 0.024142
33 | 0.98995 | -0.19173 | 0.0022659 | 0.0005679
34 | 0.99026 | -0.1864 | 0.062073 | 0.015557
35 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.004273 | -0.0010709 | 0.0042737 | 0.0010708 | 6.3036e-07 | -1.1519e-07 | 0.0064394 | 0.0064392 | 0.0064394 | 0.98741 | -0.24206 | 0.98757 | -0.23897 | 1.7691
1 | -0.0042737 | -0.0010708 | 0.0042738 | 0.0010708 | 1.7121e-07 | -3.132e-08 | 0.0064392 | 0.0064392 | 0.0064392 | 0.98757 | -0.23897 | 0.98761 | -0.23813 | 1.769
2 | -0.0042738 | -0.0010708 | 0.0042743 | 0.0010707 | 4.6451e-07 | -8.5048e-08 | 0.0064392 | 0.0064391 | 0.0064392 | 0.98761 | -0.23813 | 0.98773 | -0.23584 | 1.769
3 | -0.008314 | -0.0020833 | 0.0083177 | 0.0020849 | 3.7329e-06 | 1.6284e-06 | 0.012733 | 0.012733 | 0.012733 | 0.97155 | -0.54947 | 0.97203 | -0.54005 | 3.4982
4 | 0.00065264 | 0.00016321 | -0.00065263 | -0.00016357 | 1.0981e-08 | -3.5592e-07 | 0.00099945 | 0.00099958 | 0.00099958 | 0.97155 | -0.54947 | 0.97153 | -0.54982 | 0.27461
5 | -0.0083177 | -0.0020849 | 0.0083206 | 0.0020862 | 2.8768e-06 | 1.2544e-06 | 0.012733 | 0.012733 | 0.012733 | 0.97203 | -0.54005 | 0.97239 | -0.53279 | 3.4981
6 | -0.0042743 | -0.0010707 | 0.0042747 | 0.0010706 | 4.2433e-07 | -7.7785e-08 | 0.0064391 | 0.0064389 | 0.0064391 | 0.98773 | -0.23584 | 0.98784 | -0.23376 | 1.769
7 | -0.020797 | -0.0052116 | 0.020804 | 0.0052155 | 6.3656e-06 | 3.8525e-06 | 0.031328 | 0.031328 | 0.031328 | 0.98784 | -0.23376 | 0.98817 | -0.22734 | 8.6065
8 | -0.0083206 | -0.0020862 | 0.0083227 | 0.0020871 | 2.1513e-06 | 9.3778e-07 | 0.012733 | 0.012733 | 0.012733 | 0.97239 | -0.53279 | 0.97267 | -0.52737 | 3.4981
9 | -0.005868 | -0.0014707 | 0.0058685 | 0.0014708 | 4.9574e-07 | 9.9903e-08 | 0.0088317 | 0.0088316 | 0.0088317 | 0.98868 | -0.21738 | 0.98877 | -0.21561 | 2.4263
10 | -0.027985 | -0.0070195 | 0.027988 | 0.0070214 | 2.9837e-06 | 1.852e-06 | 0.042118 | 0.042118 | 0.042118 | 0.98877 | -0.21561 | 0.98888 | -0.21337 | 11.5708
11 | 0.022117 | 0.0055488 | -0.022113 | -0.0055465 | 3.6884e-06 | 2.2467e-06 | 0.033286 | 0.033286 | 0.033286 | 0.98877 | -0.21561 | 0.98859 | -0.21911 | 9.1446
12 | -0.020804 | -0.0052155 | 0.020812 | 0.0052204 | 8.1609e-06 | 4.9388e-06 | 0.031328 | 0.031328 | 0.031328 | 0.98817 | -0.22734 | 0.98859 | -0.21911 | 8.6065
13 | -0.017978 | -0.004507 | 0.01799 | 0.004514 | 1.1741e-05 | 7e-06 | 0.027504 | 0.027503 | 0.027504 | 0.97267 | -0.52737 | 0.97336 | -0.51367 | 7.5559
14 | -0.04002 | -0.01003 | 0.04009 | 0.010074 | 7.0476e-05 | 4.4441e-05 | 0.06028 | 0.06028 | 0.06028 | 0.98789 | -0.23266 | 0.98979 | -0.19576 | 16.5604
15 | 0.035468 | 0.0089066 | -0.035455 | -0.0088984 | 1.2977e-05 | 8.1488e-06 | 0.053328 | 0.053328 | 0.053328 | 0.98979 | -0.19576 | 0.9894 | -0.20344 | 14.6505
16 | -0.075558 | -0.018981 | 0.0757 | 0.019071 | 0.00014216 | 9.0606e-05 | 0.11361 | 0.11361 | 0.11361 | 0.98979 | -0.19576 | 0.99183 | -0.15642 | 31.2108
17 | -0.0065331 | -0.0016373 | 0.0065352 | 0.0016379 | 2.0832e-06 | 5.6284e-07 | 0.0097247 | 0.0097245 | 0.0097247 | 0.99965 | -0.0066922 | 1 | 0 | 2.6716
18 | 0.47843 | 0.12215 | -0.47746 | -0.12153 | 0.00096762 | 0.00061821 | 0.7127 | 0.7127 | 0.7127 | 1 | 0 | 0.99779 | -0.041943 | 48.9494
19 | -0.027733 | -0.0069558 | 0.027747 | 0.0069646 | 1.4071e-05 | 8.7457e-06 | 0.042398 | 0.042398 | 0.042398 | 0.97336 | -0.51367 | 0.9739 | -0.50303 | 11.6479
20 | 0.032037 | 0.0080417 | -0.032021 | -0.0080322 | 1.5174e-05 | 9.4875e-06 | 0.048186 | 0.048187 | 0.048187 | 0.9894 | -0.20344 | 0.98888 | -0.21337 | 13.2381
21 | -0.080143 | -0.020185 | 0.080335 | 0.020307 | 0.00019137 | 0.00012202 | 0.12027 | 0.12027 | 0.12027 | 0.99183 | -0.15642 | 0.99441 | -0.10662 | 33.042
22 | -0.080335 | -0.020307 | 0.080585 | 0.020466 | 0.00024999 | 0.00015939 | 0.12027 | 0.12027 | 0.12027 | 0.99441 | -0.10662 | 0.99779 | -0.041943 | 33.042
23 | 0.39688 | 0.10106 | -0.39556 | -0.10022 | 0.0013179 | 0.00084138 | 0.59243 | 0.59243 | 0.59243 | 0.99779 | -0.041943 | 0.99417 | -0.11105 | 40.689
24 | 0.2983 | 0.075846 | -0.29799 | -0.075653 | 0.00030246 | 0.00019274 | 0.44686 | 0.44686 | 0.44686 | 0.99417 | -0.11105 | 0.99307 | -0.13212 | 30.6908
25 | 0.20025 | 0.051155 | -0.20009 | -0.051056 | 0.00015501 | 9.8262e-05 | 0.30039 | 0.30039 | 0.30039 | 0.99307 | -0.13212 | 0.99223 | -0.14814 | 20.6313
26 | 0.12815 | 0.032662 | -0.12791 | -0.032508 | 0.00024075 | 0.00015386 | 0.19367 | 0.19367 | 0.19367 | 0.98563 | -0.27445 | 0.98361 | -0.31345 | 53.206
27 | -0.13481 | -0.034329 | 0.13536 | 0.034685 | 0.00055658 | 0.00035575 | 0.20371 | 0.20371 | 0.20371 | 0.98563 | -0.27445 | 0.99008 | -0.18923 | 55.9652
28 | 0.12521 | 0.03183 | -0.12479 | -0.031564 | 0.00041745 | 0.00026678 | 0.18958 | 0.18958 | 0.18958 | 0.98361 | -0.31345 | 0.98003 | -0.38293 | 52.0821
29 | 0.0022662 | 0.00056727 | -0.002266 | -0.00056781 | 2.3227e-07 | -5.3796e-07 | 0.0034057 | 0.0034059 | 0.0034059 | 0.99008 | -0.18923 | 0.98996 | -0.19138 | 0.9357
30 | -0.13763 | -0.035252 | 0.1379 | 0.035427 | 0.00027455 | 0.00017483 | 0.20712 | 0.20712 | 0.20712 | 0.99008 | -0.18923 | 0.99223 | -0.14814 | 28.4504
31 | 0.12479 | 0.031564 | -0.12408 | -0.031107 | 0.00071458 | 0.00045667 | 0.18958 | 0.18958 | 0.18958 | 0.98003 | -0.38293 | 0.9739 | -0.50303 | 52.0822
32 | 0.002266 | 0.00056781 | -0.0022659 | -0.0005679 | 3.7542e-08 | -8.6927e-08 | 0.0034059 | 0.003406 | 0.003406 | 0.98996 | -0.19138 | 0.98995 | -0.19173 | 0.93571
33 | 0.062187 | 0.015629 | -0.062073 | -0.015557 | 0.00011336 | 7.2099e-05 | 0.093275 | 0.093275 | 0.093275 | 0.99223 | -0.14814 | 0.99026 | -0.1864 | 25.6249

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58351 | 0.14807

## res_load
| p_mw | q_mvar
0 | 0.004273 | 0.0010709
1 | 0.0076613 | 0.0019201
2 | 0.00065263 | 0.00016357
3 | 0.016523 | 0.004141
4 | 0.005868 | 0.0014707
5 | 0.0096552 | 0.0024198
6 | 0.04002 | 0.01003
7 | 0.0065331 | 0.0016373
8 | 0.096901 | 0.024286
9 | 0.0097432 | 0.0024419
10 | 0.0034185 | 0.00085676
11 | 0.004443 | 0.0011135
12 | 0.0040331 | 0.0010108
13 | 0.0013012 | 0.00032611
14 | 0.097261 | 0.024376
15 | 0.097749 | 0.024498
16 | 0.0066526 | 0.0016673
17 | 0.0027044 | 0.0006778
18 | 0.096329 | 0.024142
19 | 0.0022659 | 0.0005679
20 | 0.062073 | 0.015557

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1