## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1372-18_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1372-18_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1372-18_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1372-18_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1372-18_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1372-18_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1372-18_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1372-18_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1372-18_0_5_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_1372-18_0_5_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_1372-18_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1372-18_0_5_node_32 | 0.4 | n |  | TRUE
12 | bus_LV_1372-18_0_5_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_1372-18_0_5_node_27 | 0.4 | n |  | TRUE
14 | bus_LV_1372-18_0_5_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_1372-18_0_5_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1372-18_0_5_node_43 | 0.4 | n |  | TRUE
17 | bus_LV_1372-18_0_5_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_1372-18_0_5_node_38 | 0.4 | n |  | TRUE
19 | bus_LV_1372-18_0_5_node_31 | 0.4 | n |  | TRUE
20 | bus_LV_1372-18_0_5_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_1372-18_0_5_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_1372-18_0_5_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_1372-18_0_5_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1372-18_0_5_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1372-18_0_5_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1372-18_0_5_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1372-18_0_5_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1372-18_0_5_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1372-18_0_5_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_1372-18_0_5_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_1372-18_0_5_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_1372-18_0_5_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_1372-18_0_5_node_40 | 0.4 | n |  | TRUE
34 | bus_LV_1372-18_0_5_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_1372-18_0_5_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_1372-18_0_5_node_37 | 0.4 | n |  | TRUE
37 | bus_LV_1372-18_0_5_node_39 | 0.4 | n |  | TRUE
38 | bus_LV_1372-18_0_5_node_41 | 0.4 | n |  | TRUE
39 | bus_LV_1372-18_0_5_node_42 | 0.4 | n |  | TRUE
40 | bus_LV_1372-18_0_5_node_44 | 0.4 | n |  | TRUE
41 | bus_MV_133_1_node_183 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1372-18_0_5_load_0 | 0 | 0.073451 | 0.018409 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1372-18_0_5_load_6 | 6 | 0.016208 | 0.0040621 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1372-18_0_5_load_7 | 7 | 0.024319 | 0.0060949 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1372-18_0_5_load_24 | 8 | 0.0024662 | 0.00061808 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1372-18_0_5_load_15 | 9 | 0.066157 | 0.01658 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1372-18_0_5_load_8 | 10 | 0.077982 | 0.019544 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1372-18_0_5_load_30 | 12 | 0.01219 | 0.0030551 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1372-18_0_5_load_27 | 13 | 0.0092121 | 0.0023088 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1372-18_0_5_load_43 | 16 | 0.030404 | 0.0076199 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1372-18_0_5_load_35 | 17 | 0.01872 | 0.0046918 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1372-18_0_5_load_31 | 19 | 0.026758 | 0.0067061 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1372-18_0_5_load_28 | 20 | 0.0010841 | 0.0002717 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1372-18_0_5_load_9 | 21 | 0.0082168 | 0.0020593 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1372-18_0_5_load_12 | 23 | 0.00364 | 0.00091227 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1372-18_0_5_load_16 | 24 | 0.008915 | 0.0022343 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1372-18_0_5_load_21 | 27 | 0.036937 | 0.0092572 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1372-18_0_5_load_19 | 29 | 0.019472 | 0.0048801 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1372-18_0_5_load_25 | 30 | 0.025854 | 0.0064797 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1372-18_0_5_load_29 | 31 | 0.0087565 | 0.0021946 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1372-18_0_5_load_33 | 32 | 0.0085078 | 0.0021323 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1372-18_0_5_load_40 | 33 | 0.015036 | 0.0037684 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1372-18_0_5_load_36 | 34 | 0.01215 | 0.003045 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1372-18_0_5_load_34 | 35 | 0.0085872 | 0.0021522 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1372-18_0_5_load_37 | 36 | 0.030407 | 0.0076208 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1372-18_0_5_load_39 | 37 | 0.0060933 | 0.0015271 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1372-18_0_5_load_41 | 38 | 0.01268 | 0.003178 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1372-18_0_5_load_42 | 39 | 0.010569 | 0.0026487 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1372-18_0_5_load_44 | 40 | 0.0011397 | 0.00028563 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1372-18_0_5_line_0 |  | 0 | 1 | 0.05195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_1372-18_0_5_line_1 |  | 0 | 2 | 0.049306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_1372-18_0_5_line_2 |  | 1 | 3 | 0.02551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_1372-18_0_5_line_3 |  | 1 | 4 | 0.02196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1372-18_0_5_line_4 |  | 2 | 5 | 0.05037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1372-18_0_5_line_5 |  | 2 | 6 | 0.019041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1372-18_0_5_line_6 |  | 2 | 7 | 0.071067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_1372-18_0_5_line_7 |  | 3 | 8 | 0.022602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_1372-18_0_5_line_8 |  | 3 | 9 | 0.043254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1372-18_0_5_line_9 |  | 4 | 10 | 0.024186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1372-18_0_5_line_10 |  | 5 | 11 | 0.024558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1372-18_0_5_line_11 |  | 5 | 12 | 0.017603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1372-18_0_5_line_12 |  | 6 | 13 | 0.00275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1372-18_0_5_line_13 |  | 8 | 14 | 0.022801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_1372-18_0_5_line_14 |  | 9 | 15 | 0.053782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1372-18_0_5_line_15 |  | 11 | 16 | 0.02752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1372-18_0_5_line_16 |  | 11 | 17 | 0.025851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1372-18_0_5_line_17 |  | 11 | 18 | 0.039598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1372-18_0_5_line_18 |  | 12 | 19 | 0.030665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1372-18_0_5_line_19 |  | 13 | 20 | 0.007486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1372-18_0_5_line_20 |  | 14 | 29 | 0.036309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_1372-18_0_5_line_21 |  | 15 | 23 | 0.01265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1372-18_0_5_line_22 |  | 15 | 22 | 0.051278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1372-18_0_5_line_23 |  | 17 | 32 | 0.021191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1372-18_0_5_line_24 |  | 18 | 33 | 0.0094684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1372-18_0_5_line_25 |  | 18 | 34 | 0.012949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1372-18_0_5_line_26 |  | 20 | 31 | 0.051902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1372-18_0_5_line_27 |  | 21 | 22 | 0.01984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1372-18_0_5_line_28 |  | 24 | 25 | 0.036299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1372-18_0_5_line_29 |  | 25 | 26 | 0.053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1372-18_0_5_line_30 |  | 26 | 27 | 0.074442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1372-18_0_5_line_31 |  | 26 | 28 | 0.041046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1372-18_0_5_line_32 |  | 26 | 29 | 0.033329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1372-18_0_5_line_33 |  | 28 | 30 | 0.021688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1372-18_0_5_line_34 |  | 32 | 35 | 0.021562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1372-18_0_5_line_35 |  | 33 | 38 | 0.036742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1372-18_0_5_line_36 |  | 34 | 36 | 0.013179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1372-18_0_5_line_37 |  | 36 | 37 | 0.040693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1372-18_0_5_line_38 |  | 38 | 39 | 0.034657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1372-18_0_5_line_39 |  | 39 | 40 | 0.13129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1372-18_0_5_trafo_7 | 0.63 MVA 20/0.4 kV | 41 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2691122.4848 | 1208863.8439 | 2691127.3513 | 1208868.2879 | 2691156.4263 | 1208903.1041
1 | 2691188.5543 | 1208940.5041 | 2691162.9213 | 1208910.8817 | 2691156.4263 | 1208903.1041
2 | 2691122.4848 | 1208863.8439 | 2691115.9962 | 1208872.017 | 2691106.6158 | 1208883.8484
3 | 2691122.4848 | 1208863.8439 | 2691130.0433 | 1208854.3197 | 2691136.3098 | 1208846.7547
4 | 2691188.5543 | 1208940.5041 | 2691193.8414 | 1208951.2476 | 2691195.9507 | 1208961.4756 | 2691192.1592 | 1208989.1694
5 | 2691188.5543 | 1208940.5041 | 2691204.6013 | 1208930.2536
6 | 2691188.5543 | 1208940.5041 | 2691128.9086 | 1208979.1416
7 | 2691106.6158 | 1208883.8484 | 2691097.0715 | 1208894.9656 | 2691091.3284 | 1208900.4622
8 | 2691106.6158 | 1208883.8484 | 2691075.6308 | 1208863.1061 | 2691073.2 | 1208861.4679 | 2691070.9751 | 1208859.4028
9 | 2691136.3098 | 1208846.7547 | 2691122.9576 | 1208838.8678 | 2691115.3692 | 1208834.6576
10 | 2691192.1592 | 1208989.1694 | 2691194.1746 | 1209001.0637 | 2691199.4909 | 1209012.3747
11 | 2691192.1592 | 1208989.1694 | 2691174.5872 | 1208990.2091
12 | 2691204.6013 | 1208930.2536 | 2691204.6013 | 1208930.2536 | 2691207.2185 | 1208931.0978
13 | 2691073.8709 | 1208915.125 | 2691081.2848 | 1208909.0897 | 2691091.0454 | 1208900.7331 | 2691091.3284 | 1208900.4622
14 | 2691024.2742 | 1208845.0328 | 2691028.4025 | 1208846.5412 | 2691044.807 | 1208841.2546 | 2691059.5108 | 1208848.7617 | 2691070.9751 | 1208859.4028
15 | 2691199.4909 | 1209012.3747 | 2691182.0027 | 1209033.6237
16 | 2691199.4909 | 1209012.3747 | 2691215.9799 | 1208992.4659
17 | 2691199.4909 | 1209012.3747 | 2691214.4396 | 1209028.1915 | 2691227.9839 | 1209039.8841
18 | 2691174.5872 | 1208990.2091 | 2691169.9082 | 1208990.4859 | 2691153.5036 | 1209010.6294
19 | 2691214.343 | 1208933.396 | 2691207.2185 | 1208931.0978
20 | 2691073.8709 | 1208915.125 | 2691066.5536 | 1208920.3168 | 2691043.7951 | 1208933.4451 | 2691042.812 | 1208933.8509
21 | 2691024.2742 | 1208845.0328 | 2691019.7038 | 1208856.8281
22 | 2691042.5004 | 1208797.1122 | 2691032.4854 | 1208821.6313 | 2691024.2742 | 1208845.0328
23 | 2691229.4966 | 1208976.1458 | 2691215.9799 | 1208992.4659
24 | 2691227.9839 | 1209039.8841 | 2691233.6085 | 1209032.2673
25 | 2691227.9839 | 1209039.8841 | 2691223.3347 | 1209045.1054 | 2691217.7479 | 1209047.1759
26 | 2691257.1003 | 1208927.2334 | 2691244.4042 | 1208943.0927 | 2691214.343 | 1208933.396
27 | 2691042.5004 | 1208797.1122 | 2691060.3282 | 1208805.8179
28 | 2690970.4021 | 1208942.0206 | 2690979.5482 | 1208928.084 | 2690990.0242 | 1208913.1893 | 2690990.8326 | 1208912.0226
29 | 2690970.4021 | 1208942.0206 | 2690975.2826 | 1208945.0525 | 2690975.3316 | 1208947.3215 | 2690975.7436 | 1208949.2179 | 2690977.1006 | 1208950.9731 | 2690979.3823 | 1208951.9196 | 2690982.0712 | 1208952.5833 | 2690985.1715 | 1208952.1969 | 2690988.2135 | 1208951.1426 | 2690997.8028 | 1208946.5302 | 2690999.998 | 1208951.6448 | 2691012.0045 | 1208946.5689
30 | 2691012.0045 | 1208946.5689 | 2691020.6536 | 1208963.7123 | 2691024.2309 | 1208994.3428 | 2691048.5579 | 1208996.2456
31 | 2690980.1849 | 1208965.0962 | 2691001.7513 | 1208955.8299 | 2690999.998 | 1208951.6448 | 2691012.0045 | 1208946.5689
32 | 2691012.0045 | 1208946.5689 | 2691042.812 | 1208933.8509
33 | 2690980.1849 | 1208965.0962 | 2690983.0257 | 1208986.5976
34 | 2691229.4966 | 1208976.1458 | 2691243.25 | 1208959.5399
35 | 2691233.6085 | 1209032.2673 | 2691238.6356 | 1209025.4595 | 2691251.2423 | 1209003.0262 | 2691252.9184 | 1209001.1094
36 | 2691217.7479 | 1209047.1759 | 2691213.3947 | 1209048.7893 | 2691208.7854 | 1209050.9091 | 2691206.6345 | 1209053.6227
37 | 2691181.3575 | 1209085.5131 | 2691206.6345 | 1209053.6227
38 | 2691252.9184 | 1209001.1094 | 2691258.3228 | 1208994.929 | 2691275.8553 | 1208975.1289
39 | 2691275.8553 | 1208975.1289 | 2691383.819 | 1209049.8414

## bus_geodata
| x | y | coords
0 | 2691156.4263 | 1208903.1041
1 | 2691122.4848 | 1208863.8439
2 | 2691188.5543 | 1208940.5041
3 | 2691106.6158 | 1208883.8484
4 | 2691136.3098 | 1208846.7547
5 | 2691192.1592 | 1208989.1695
6 | 2691204.6013 | 1208930.2536
7 | 2691128.9086 | 1208979.1416
8 | 2691091.3284 | 1208900.4622
9 | 2691070.9751 | 1208859.4028
10 | 2691115.3692 | 1208834.6576
11 | 2691199.4909 | 1209012.3747
12 | 2691174.5872 | 1208990.2091
13 | 2691207.2185 | 1208931.0978
14 | 2691073.8709 | 1208915.125
15 | 2691024.2742 | 1208845.0328
16 | 2691182.0027 | 1209033.6237
17 | 2691215.9799 | 1208992.4659
18 | 2691227.9839 | 1209039.8841
19 | 2691153.5036 | 1209010.6294
20 | 2691214.343 | 1208933.396
21 | 2691060.3282 | 1208805.8179
22 | 2691042.5004 | 1208797.1122
23 | 2691019.7038 | 1208856.8281
24 | 2690990.8326 | 1208912.0226
25 | 2690970.4021 | 1208942.0206
26 | 2691012.0045 | 1208946.5689
27 | 2691048.5579 | 1208996.2456
28 | 2690980.1849 | 1208965.0962
29 | 2691042.812 | 1208933.8509
30 | 2690983.0257 | 1208986.5976
31 | 2691257.1003 | 1208927.2334
32 | 2691229.4966 | 1208976.1458
33 | 2691233.6085 | 1209032.2673
34 | 2691217.7479 | 1209047.1759
35 | 2691243.25 | 1208959.5399
36 | 2691206.6345 | 1209053.6227
37 | 2691181.3575 | 1209085.5131
38 | 2691252.9184 | 1209001.1094
39 | 2691275.8553 | 1208975.1289
40 | 2691383.819 | 1209049.8414
41 | 2691110.0447 | 1208991.3613

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98726 | -0.24335 | 0.073451 | 0.018409
1 | 0.98426 | -0.30151 | 0 | 0
2 | 0.99094 | -0.17239 | 0 | 0
3 | 0.98324 | -0.32123 | 0 | 0
4 | 0.98267 | -0.33237 | 0 | 0
5 | 0.98645 | -0.25918 | 0 | 0
6 | 0.99033 | -0.18432 | 0.016208 | 0.0040621
7 | 1 | 0 | -0.56237 | -0.14406
8 | 0.98275 | -0.33078 | 0.0024662 | 0.00061808
9 | 0.98012 | -0.38227 | 0.066157 | 0.01658
10 | 0.98093 | -0.36648 | 0.077982 | 0.019544
11 | 0.9847 | -0.29317 | 0 | 0
12 | 0.98582 | -0.27146 | 0.01219 | 0.0030551
13 | 0.99028 | -0.18525 | 0.0092121 | 0.0023088
14 | 0.98227 | -0.34016 | 0 | 0
15 | 0.97953 | -0.39385 | 0 | 0
16 | 0.98393 | -0.30823 | 0.030404 | 0.0076199
17 | 0.98385 | -0.30983 | 0.01872 | 0.0046918
18 | 0.98147 | -0.35608 | 0 | 0
19 | 0.98506 | -0.28619 | 0.026758 | 0.0067061
20 | 0.99021 | -0.18656 | 0.0010841 | 0.0002717
21 | 0.97899 | -0.40447 | 0.0082168 | 0.0020593
22 | 0.97914 | -0.4015 | 0 | 0
23 | 0.97949 | -0.39468 | 0.00364 | 0.00091227
24 | 0.97777 | -0.42803 | 0.008915 | 0.0022343
25 | 0.97807 | -0.42213 | 0 | 0
26 | 0.97851 | -0.41353 | 0 | 0
27 | 0.97596 | -0.46371 | 0.036937 | 0.0092572
28 | 0.97753 | -0.43286 | 0 | 0
29 | 0.98073 | -0.37012 | 0.019472 | 0.0048801
30 | 0.97701 | -0.4431 | 0.025854 | 0.0064797
31 | 0.9898 | -0.19464 | 0.0087565 | 0.0021946
32 | 0.98351 | -0.31636 | 0.0085078 | 0.0021323
33 | 0.98113 | -0.36283 | 0.015036 | 0.0037684
34 | 0.98089 | -0.36748 | 0.01215 | 0.003045
35 | 0.98334 | -0.31969 | 0.0085872 | 0.0021522
36 | 0.98045 | -0.3762 | 0.030407 | 0.0076208
37 | 0.98022 | -0.3807 | 0.0060933 | 0.0015271
38 | 0.9803 | -0.37908 | 0.01268 | 0.003178
39 | 0.97992 | -0.38644 | 0.010569 | 0.0026487
40 | 0.97979 | -0.38916 | 0.0011397 | 0.00028563
41 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.25148 | 0.06373 | -0.25078 | -0.063284 | 0.00070064 | 0.00044576 | 0.37929 | 0.37929 | 0.37929 | 0.98726 | -0.24335 | 0.98426 | -0.30151 | 26.05
1 | -0.32493 | -0.082139 | 0.32604 | 0.082846 | 0.0011098 | 0.00070775 | 0.48999 | 0.48999 | 0.48999 | 0.98726 | -0.24335 | 0.99094 | -0.17239 | 33.6534
2 | 0.17255 | 0.043586 | -0.17239 | -0.043483 | 0.00016291 | 0.00010297 | 0.26099 | 0.26099 | 0.26099 | 0.98426 | -0.30151 | 0.98324 | -0.32123 | 17.9254
3 | 0.078224 | 0.019699 | -0.078109 | -0.019625 | 0.00011524 | 7.3473e-05 | 0.11829 | 0.11829 | 0.11829 | 0.98426 | -0.30151 | 0.98267 | -0.33237 | 32.4985
4 | 0.19475 | 0.049385 | -0.19394 | -0.048869 | 0.00080879 | 0.00051634 | 0.29264 | 0.29264 | 0.29264 | 0.99094 | -0.17239 | 0.98645 | -0.25918 | 40.1977
5 | 0.035285 | 0.008852 | -0.035265 | -0.0088394 | 2.0049e-05 | 1.2586e-05 | 0.052988 | 0.052988 | 0.052988 | 0.99094 | -0.17239 | 0.99033 | -0.18432 | 14.5572
6 | -0.55607 | -0.14108 | 0.56072 | 0.14406 | 0.0046521 | 0.0029737 | 0.83562 | 0.83562 | 0.83562 | 0.99094 | -0.17239 | 1 | 0 | 57.3914
7 | 0.09414 | 0.02378 | -0.094097 | -0.023754 | 4.3049e-05 | 2.6405e-05 | 0.14254 | 0.14254 | 0.14254 | 0.98324 | -0.32123 | 0.98275 | -0.33078 | 9.7896
8 | 0.078252 | 0.019702 | -0.078025 | -0.019557 | 0.00022761 | 0.00014512 | 0.11846 | 0.11846 | 0.11846 | 0.98324 | -0.32123 | 0.98012 | -0.38227 | 32.5434
9 | 0.078109 | 0.019625 | -0.077982 | -0.019544 | 0.00012692 | 8.0921e-05 | 0.11829 | 0.11829 | 0.11829 | 0.98267 | -0.33237 | 0.98093 | -0.36648 | 32.4985
10 | 0.15495 | 0.039082 | -0.1547 | -0.038921 | 0.00025174 | 0.00016049 | 0.23382 | 0.23382 | 0.23382 | 0.98645 | -0.25918 | 0.9847 | -0.29317 | 32.1181
11 | 0.03899 | 0.0097873 | -0.038967 | -0.0097729 | 2.2838e-05 | 1.4392e-05 | 0.05882 | 0.05882 | 0.05882 | 0.98645 | -0.25918 | 0.98582 | -0.27146 | 16.1593
12 | 0.019057 | 0.0047773 | -0.019057 | -0.0047768 | 8.4559e-07 | 5.0579e-07 | 0.028635 | 0.028635 | 0.028635 | 0.99033 | -0.18432 | 0.99028 | -0.18525 | 7.8668
13 | 0.09163 | 0.023136 | -0.091589 | -0.023111 | 4.1183e-05 | 2.5202e-05 | 0.1388 | 0.1388 | 0.1388 | 0.98275 | -0.33078 | 0.98227 | -0.34016 | 9.5331
14 | 0.011868 | 0.0029768 | -0.011861 | -0.0029733 | 6.5479e-06 | 3.5133e-06 | 0.018018 | 0.018019 | 0.018019 | 0.98012 | -0.38227 | 0.97953 | -0.39385 | 4.9502
15 | 0.030425 | 0.0076335 | -0.030404 | -0.0076199 | 2.1818e-05 | 1.3614e-05 | 0.04598 | 0.04598 | 0.04598 | 0.9847 | -0.29317 | 0.98393 | -0.30823 | 12.6319
16 | 0.035851 | 0.0089978 | -0.035822 | -0.0089799 | 2.8456e-05 | 1.7883e-05 | 0.05418 | 0.05418 | 0.05418 | 0.9847 | -0.29317 | 0.98385 | -0.30983 | 14.8846
17 | 0.088419 | 0.02229 | -0.088154 | -0.022121 | 0.00026528 | 0.00016928 | 0.13366 | 0.13366 | 0.13366 | 0.9847 | -0.29317 | 0.98147 | -0.35608 | 36.7198
18 | 0.026777 | 0.0067178 | -0.026758 | -0.0067061 | 1.8787e-05 | 1.1633e-05 | 0.04042 | 0.04042 | 0.04042 | 0.98582 | -0.27146 | 0.98506 | -0.28619 | 11.1043
19 | 0.0098446 | 0.0024681 | -0.0098439 | -0.0024678 | 6.1432e-07 | 2.9686e-07 | 0.014793 | 0.014793 | 0.014793 | 0.99028 | -0.18525 | 0.99021 | -0.18656 | 4.064
20 | 0.091589 | 0.023111 | -0.091458 | -0.023027 | 0.00013116 | 8.3027e-05 | 0.1388 | 0.1388 | 0.1388 | 0.98227 | -0.34016 | 0.98073 | -0.37012 | 19.0663
21 | 0.0036402 | 0.00091221 | -0.00364 | -0.00091227 | 1.4506e-07 | -6.6388e-08 | 0.0055298 | 0.0055298 | 0.0055298 | 0.97953 | -0.39385 | 0.97949 | -0.39468 | 1.5192
22 | 0.008221 | 0.0020611 | -0.008218 | -0.0020598 | 2.9993e-06 | 1.2743e-06 | 0.012489 | 0.012489 | 0.012489 | 0.97953 | -0.39385 | 0.97914 | -0.4015 | 3.4311
23 | 0.017102 | 0.0042882 | -0.017096 | -0.004285 | 5.3167e-06 | 3.1337e-06 | 0.025866 | 0.025866 | 0.025866 | 0.98385 | -0.30983 | 0.98351 | -0.31636 | 7.1061
24 | 0.039461 | 0.0099011 | -0.039448 | -0.0098931 | 1.271e-05 | 8.015e-06 | 0.059831 | 0.059831 | 0.059831 | 0.98147 | -0.35608 | 0.98113 | -0.36283 | 16.437
25 | 0.048693 | 0.01222 | -0.048667 | -0.012203 | 2.6469e-05 | 1.6777e-05 | 0.07383 | 0.07383 | 0.07383 | 0.98147 | -0.35608 | 0.98089 | -0.36748 | 20.2829
26 | 0.0087598 | 0.0021961 | -0.0087565 | -0.0021946 | 3.3728e-06 | 1.4912e-06 | 0.013164 | 0.013164 | 0.013164 | 0.99021 | -0.18656 | 0.9898 | -0.19464 | 3.6165
27 | -0.0082168 | -0.0020593 | 0.008218 | 0.0020598 | 1.1605e-06 | 4.932e-07 | 0.012489 | 0.012489 | 0.012489 | 0.97899 | -0.40447 | 0.97914 | -0.4015 | 3.4311
28 | -0.008915 | -0.0022343 | 0.0089175 | 0.0022355 | 2.5055e-06 | 1.1481e-06 | 0.013567 | 0.013567 | 0.013567 | 0.97777 | -0.42803 | 0.97807 | -0.42213 | 3.7273
29 | -0.0089175 | -0.0022355 | 0.0089212 | 0.0022371 | 3.6582e-06 | 1.6758e-06 | 0.013567 | 0.013567 | 0.013567 | 0.97807 | -0.42213 | 0.97851 | -0.41353 | 3.7272
30 | 0.037025 | 0.0093129 | -0.036937 | -0.0092572 | 8.8534e-05 | 5.5729e-05 | 0.056316 | 0.056316 | 0.056316 | 0.97851 | -0.41353 | 0.97596 | -0.46371 | 15.4715
31 | 0.025891 | 0.0065023 | -0.025867 | -0.0064875 | 2.3866e-05 | 1.4759e-05 | 0.039377 | 0.039377 | 0.039377 | 0.97851 | -0.41353 | 0.97753 | -0.43286 | 10.8178
32 | -0.071837 | -0.018052 | 0.071986 | 0.018147 | 0.0001492 | 9.507e-05 | 0.10926 | 0.10926 | 0.10926 | 0.97851 | -0.41353 | 0.98073 | -0.37012 | 30.0163
33 | 0.025867 | 0.0064875 | -0.025854 | -0.0064797 | 1.2611e-05 | 7.7991e-06 | 0.039377 | 0.039377 | 0.039377 | 0.97753 | -0.43286 | 0.97701 | -0.4431 | 10.8179
34 | 0.0085886 | 0.0021528 | -0.0085872 | -0.0021522 | 1.3653e-06 | 6.0021e-07 | 0.012994 | 0.012994 | 0.012994 | 0.98351 | -0.31636 | 0.98334 | -0.31969 | 3.5699
35 | 0.024412 | 0.0061247 | -0.024393 | -0.006113 | 1.8889e-05 | 1.1626e-05 | 0.037026 | 0.037026 | 0.037026 | 0.98113 | -0.36283 | 0.9803 | -0.37908 | 10.1721
36 | 0.036517 | 0.0091578 | -0.036502 | -0.0091482 | 1.5167e-05 | 9.5406e-06 | 0.055399 | 0.055399 | 0.055399 | 0.98089 | -0.36748 | 0.98045 | -0.3762 | 15.2194
37 | 0.0060946 | 0.0015275 | -0.0060933 | -0.0015271 | 1.3056e-06 | 3.2254e-07 | 0.0092498 | 0.00925 | 0.00925 | 0.98045 | -0.3762 | 0.98022 | -0.3807 | 2.5412
38 | 0.011713 | 0.002935 | -0.011708 | -0.0029328 | 4.1078e-06 | 2.1923e-06 | 0.017779 | 0.017779 | 0.017779 | 0.9803 | -0.37908 | 0.97992 | -0.38644 | 4.8842
39 | 0.0011398 | 0.00028407 | -0.0011397 | -0.00028563 | 1.4745e-07 | -1.5594e-06 | 0.0017303 | 0.0017309 | 0.0017309 | 0.97992 | -0.38644 | 0.97979 | -0.38916 | 0.47551

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58669 | 0.15015

## res_load
| p_mw | q_mvar
0 | 0.073451 | 0.018409
1 | 0.016208 | 0.0040621
2 | 0.024319 | 0.0060949
3 | 0.0024662 | 0.00061808
4 | 0.066157 | 0.01658
5 | 0.077982 | 0.019544
6 | 0.01219 | 0.0030551
7 | 0.0092121 | 0.0023088
8 | 0.030404 | 0.0076199
9 | 0.01872 | 0.0046918
10 | 0.026758 | 0.0067061
11 | 0.0010841 | 0.0002717
12 | 0.0082168 | 0.0020593
13 | 0.00364 | 0.00091227
14 | 0.008915 | 0.0022343
15 | 0.036937 | 0.0092572
16 | 0.019472 | 0.0048801
17 | 0.025854 | 0.0064797
18 | 0.0087565 | 0.0021946
19 | 0.0085078 | 0.0021323
20 | 0.015036 | 0.0037684
21 | 0.01215 | 0.003045
22 | 0.0085872 | 0.0021522
23 | 0.030407 | 0.0076208
24 | 0.0060933 | 0.0015271
25 | 0.01268 | 0.003178
26 | 0.010569 | 0.0026487
27 | 0.0011397 | 0.00028563

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1